50681 | 0 | ASCO VALVE INCORPORATED |  |  |  |  | 2014-12-15 | 2014-12-16 09:01 | 2015-08-19 | INTERIM REPORT - POTENTIAL PART 21 NOTIFICATION The following report was received via fax: ASCO reviewed a Part 21 notification, received from Steris Isomedix Services, to see if the reported non conformance would impact qualification levels. Based on this review, ASCO determined that even if the radiation levels, applied to components, were lower than reported on the original certifications, the additional radiation dose added to meet the 10% margin suggested by IEEE 323 would envelope this variation. Therefore, the qualification levels listed in ASCO qualification reports would not be impacted. Based on this review, ASCO determined that it was not necessary to implement 10 CFR part 21 notifications since the reported qualification levels remain unchanged. If you have any questions, you can contact Michael Adase at Michael.adase@emerson.com or 803-641-9345. Note: The NRC has received reports from four (4) other Steris Isomedix customers concerning this issue; EN #50253, #50285, #50359, and #50434. * * * UPDATE AT 1507 EDT ON 8/19/2015 * * * The following, in part, was received from Asco Valve, Inc. via fax: "On December 15, 2014, ASCO Valve Inc. (ASCO) issued an interim report to the USNRC. The interim report was issued because ASCO was awaiting additional information from Steris and was not able to complete their evaluation of Ref B within the 60 day time limit. A December 19, 2014 update from Steris contained no additional substantive information. Although further information from Steris was not received, ASCO has since received the 'Industry Guidance Position Paper Responding to the 2014 Steris 10 CFPR Part 21', from the NUGEQ [Nuclear Utility Group on Equipment Qualification]. "ASCO has completed the review and calculated the minimum radiation exposure applied during qualification of ASCO nuclear qualified products at Steris. Based on this review, ASCO has determined that the minimum dose is less than what was originally reported in the ASCO qualification reports. ASCO is in the process of updating our reports and revising our certifications. "Since ASCO is not able to determine what, if any impact these reduced radiation dose levels will have on the qualification testing of safety related equipment, we are forwarding this information to allow for a review of applicable qualification documentation and reports." Notified R1DO (DeFrancisco), R2DO (Heisserer), R3DO (Riemer), R4DO (Hay), and Part 21 Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-12-16
50680 | 0 | MIDWEST TESTING |  |  |  |  | 2014-12-16 07:42 | 2014-12-16 09:21 | 2015-01-05 | LOST HUMBOLDT 5001EZ DENSITY GAUGE A trailer containing a Humboldt 5001EZ Density gauge was found missing/stolen by a technician staying at the Holiday Inn Express in Oklahoma City, OK. The gauge was chained and locked to the trailer. The licensee reported that there have been no press or media inquiries and no rewards are currently being considered for the return of the density gauge. The licensee was performing work in OK under reciprocity. The gauge is a Humboldt 5001EZ model, Serial Number: 3309 containing 10 mCi of Cs-137 and 40 mCi of Am-241/Be. The local police department and the State of Oklahoma were notified. * * * UPDATE FROM JOE HONICH TO CHARLES TEAL AT 0920 EST ON 1/5/15 * * * The Oklahoma Police Department located the gauge. It was dumped on the side of the road in a cardboard box. The gauge was fully intact and did not appear to be tampered with. The gauge is currently in the possession of an Oklahoma licensee until arrangements can be made for a transfer back to Midwest Testing. Notified R3DO (Cameron), R4DO (Pick) and NMSS Events via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-12-24
50679 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-12-13 | 2014-12-15 14:41 | 2014-12-15 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following report was received from the Commonwealth of Virginia via email: "On Saturday, December 13th [2014], a CPN MCIDR moisture/density gauge was run over at a temporary jobsite in Leesburg, Virginia (Battlefield Parkway and Sycolin Road). The licensee's authorized user was performing a test and walked about 20 feet away from the gauge. The general contractor's bulldozer operator did not see the gauge because the bulldozer blade was raised, which obstructed his view when driving the bulldozer up the slope. "The gauge was completely destroyed with the source in the transmission position. The authorized user contacted the construction testing services manager who then contacted the radiation safety officer. Both individuals arrived on scene and were able to retract the source into the shielded position using a pair of pliers. A radiation survey was performed at 1 meter indicating a reading of 0.4 mrem/hr. The gauge was then placed into the transportation case and returned to storage where a wipe test was performed. The wipe test has been sent to a licensed service provider for analysis and if no contamination is present, the gauge will be returned [pending final resolution]. "The licensee submitted an incident report, which is under review by the [Virginia] Radioactive Materials Program. The incident and suggested corrective actions will also be re-examined during the next inspection." Event Report ID No.: VA-14-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-12-23
50678 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-12-15 07:30 | 2014-12-15 13:58 | 2014-12-15 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On December 15, 2014, at 0730 hours [CST] the Control Room Emergency Ventilation (CREV) system was declared inoperable due to a partially stuck open main control room door. The door was unable to be closed to establish the boundary of the control room envelope. As a result, Technical Specification 3.7.4, Condition C, was entered. A repair plan and schedule is being developed. "The CREV system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions as well as protection of the operators from a high dose environment assumed during a design basis accident. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV system could impact the plant's ability to mitigate the consequences of an accident as stated in Chapter 6 of the UFSAR. This event is also reportable under 10 CFR 50.72(b)(3)(xiii) since this condition also impacts the control room as an Emergency Response Facility. "At 0910 [CST] exited Tech Spec 3.7.4, Condition C, for CREV System Inoperable due to inoperable Control Room Envelope (CRE). The Control Room door is now closed. Completed post maintenance smoke test, satisfactory. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-12-15
50677 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-12-13 01:52 | 2014-12-13 10:00 | 2014-12-13 | MALFUNCTION OF SMOKE DETECTION SYSTEM IN CONTAINMENT DUE TO HIGH HUMIDITY "At 0152 CST on December 13, 2014, both strings of the Unit 2 containment smoke detection system were declared non-functional due to a non-radioactive steam leak inside containment. The steam leak was causing spurious alarms to the smoke detection system. This condition prevents identification and assessment of a fire in containment. Required compensatory measures have been established. Since a fire in the containment building is an entry condition for the site's emergency plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been informed." The steam leak was caused by a faulty main steam flow detector. The licensee has shut down the reactor to effect repairs. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-13
50676 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-12-12 09:57 | 2014-12-12 22:27 | 2014-12-12 | HIGH ENERGY LINE BREAK ISOLATION DOOR INOPERABLE The boundary door between the A and B safety related switchgear rooms was found not to be latching. This door is credited in the high energy line break (HELB) analysis. Both trains of safety related switchgear were affected for approximately 36 minutes. The technical specification action statement was entered, the door was repaired, and the action statement was exited. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-12-12
50675 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-12-12 15:00 | 2014-12-12 21:15 | 2014-12-12 | UNANALYZED CONDITION WITH REACTOR CORE ISOLATION COOLING "Engineering identified fuse and breaker coordination issues with Reactor Core Isolation Cooling (RCIC) valves operated at the Remote Shutdown Panel (RSDP). The coordination issues are such that, given a fire in the main control room, it is possible that RCIC valve power supply breakers could trip prior to tripping control power fuses. Operation of RCIC from the RSDP could be impaired in this scenario without compensatory actions to reset breakers. RCIC is the single credited source of makeup to the reactor pressure vessel during this scenario. The current licensing basis (Fire Protection Report) does not identify the compensatory actions required to reset breakers prior to RCIC operation at the RSDP. This condition is applicable to Unit 1 and Unit 2. "This report is being made pursuant to 10CFR50.72(b)(3)(ii)(B), 'Event or Condition that results in an unanalyzed condition that significantly degrades plant safety'." Actions are being taken to amend the appropriate operating procedures to take the required steps to ensure proper operation of RCIC in the postulated scenario. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-12-12
50674 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-12-12 13:24 | 2014-12-12 18:20 | 2014-12-12 | BOTH SECONDARY CONTAINMENT AIRLOCK DOORS OPENED SIMULTANEOUSLY "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), 'Event or Condition that could have prevented fulfillment of a Safety Function needed to Control the Release of Radioactive Material' and 10CFR50.72(b)(3)(v)(D), 'Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident.' Unit 1 and Unit 2 were in Mode 1 and no movement of irradiated fuel, core alterations, or OPDRVs [Operations with the Potential to Drain the Reactor Vessel] were in progress in the secondary containment. "An employee entered a secondary containment interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately 10 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor building differential pressure, as observed in the Main Control Room, has remained less than -0.25 inches of water column at all times. Initial investigation determined that the interlock for the doors was malfunctioning. Administrative controls [barricades and signs] have been put in place to ensure the doors remain closed pending repairs to the interlock." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-12-12
50673 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2014-12-10 | 2014-12-12 14:40 | 2014-12-12 | MARYLAND AGREEMENT STATE REPORT - MISADMINISTRATION OF I-125 SEEDS DURING PROSTATE THERAPY The following information was obtained from the State of Maryland via email: "Post implant CT determined that all seeds missed the prostate and were deposited in an unintended area of soft tissue at the base of the patient's penis. A medical determination has been made to not remove the seeds due to the difficulty of removal. The patient will be followed over the next two weeks to determine whether damage to the urethra has occurred. The licensee states that the patient has been informed. "Preliminary root cause evaluation is that the Medical Center's ultrasound unit used to guide insertion is 12 years old and has a poor (grainy) display. No defect with the Mick applicator has been determined. "The Maryland Radiation Program will conduct an on-site investigation of this incident." The patient was administered 53 seeds at a nominal 0.36 mCi I-125 per seed manufactured by Best Industries. Intended dose to the prostate was 108 Gy. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2014-12-22
50672 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-12-12 02:48 | 2014-12-12 11:34 | 2014-12-12 | AUXILIARY BUILDING NORMAL VENTILATION RADIATION MONITOR FAILED "At 0248 CST on December 12, 2014, 2R-30, Auxiliary Building Normal Vent Radiation Monitor, failed. This monitor was the redundant monitor for 2R-37, Auxiliary Building Normal Vent Radiation Monitor, which was previously taken out of service for planned maintenance. With 2R-30 and 2R-37 out of service, there are no monitors that will allow for timely classification of two Emergency Action Levels (EALS) - NUE (Notification of Unusual Event) and Alert Classifications. This results in a loss of emergency assessment capability while 2R-30 and 2R-37 are out of service. This is a reportable condition in accordance with 10CFR50.72(b)(3)(xiii). "The Auxiliary Building ventilation effluent monitor readings were normal and there were no elevated readings in Auxiliary Building area monitors prior to the unavailability of these monitors. "The health and safety of the public was not affected by this issue. "The activity to repair and return one of the monitors to service is continuous until restored. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-12
50671 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-12-11 09:30 | 2014-12-11 17:11 | 2014-12-11 | FITNESS FOR DUTY REPORT A non-licensed contract employee working in a supervisory role had a confirmed positive finding for illegal drugs resulting from a follow-up fitness-for-duty test. The employee's access to the plant has been revoked. The licensee notified the NRC Senior Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2014-12-11
50670 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2014-12-11 09:45 | 2014-12-11 14:52 | 2014-12-11 | BOTH SECONDARY CONTAINMENT AIRLOCK DOORS OPENED SIMULTANEOUSLY "Station personnel simultaneously opened the inner and outer air lock doors from Unit 2 Reactor Enclosure to the Refuel Floor. Reactor Enclosure Secondary Containment Integrity was declared inoperable per Unit 2 TS 3.6.5.1.1, due to failure to meet surveillance requirement U2 TS 4.6.5.1.1.b.2, due to the report of both containment airlock doors on 352' momentarily open at the same time. Reactor Enclosure D/P [differential pressure] remained steady at 0.35 inches vacuum water gauge. "Reactor Enclosure Secondary Containment Integrity was declared operable following verification that at least one air lock door to each access of secondary containment was closed per U2 TS 4.6.5.1.1.b.2. Total time was approximately 5 seconds." The secondary containment doors do not have a mechanical interlock and this event has been classified as a human performance error. The licensee notified the NRC Resident Inspector | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-12-11
50669 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-12-10 | 2014-12-11 13:25 | 2014-12-11 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the State of California via email: "On December 10, 2014, the Assistant Radiation Safety Officer of Koury Geotechnical Services contacted the Radiologic Health Branch Brea office regarding a moisture density gauge that was run over by a construction vehicle at a construction site at 6500 Atlantic Avenue in Long Beach. The gauge was a CPN Model MC1-DRP gauge, S/N MD30901675 (10 mCi Cs-137, 50 mCi Am:Be-241). The gauge was in use as the Cs-137 source was extended approximately 8 inches in the soil at the time of the incident. The source rod has been damaged. The electrical body was also damaged but there was no evidence that the protective shield or the Am:Be-241source was damaged. The Long Beach Fire Department was notified and responded to the incident. Fire Department personnel did a visual inspection and radiation survey of the area and noted that the area was secured at least 50 feet from the gauge and noted that the dose rates at this boundary were at background. Long Beach Hazmat then arrived to take control of the area from the Fire Department. After assessing the situation they contacted Los Angeles County Radiation Management to assist in placing the sources in a safe condition. Thomas Gray and Associates (California materials license number 2105) was also contacted to assist in remediating the damaged gauge. The Health Physicist from Los Angeles County, with assistance from the Thomas Gray technician, was able to place the Cs-137 source into the shielded position and verified that the shutter block was in the proper position. A visual inspection of the body was performed and indicated that there was no damage to the shielding. Wipes were taken on the body of the gauge then tested using a survey meter with a geiger-mueller pancake probe. The wipes were at background indicating that the sources were not leaking. An MCA [multi-channel analyzer] was used to verify that both the Cs-137 and AmBe-241 sources were present. The gauge body was placed in the transport case along with the rest of the gauge parts then turned over to the Koury technician to take to Maurer Technical Services (California radioactive license 6163) to be shipped to the manufacturer so that it can be repaired or the sources recycled. "The investigation is on-going and any citations will be determined at a later date." CA Report No.: 5010-121014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-12-19
50668 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-12-11 08:00 | 2014-12-11 07:45 | 2014-12-11 | PLANNED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER Turkey Point will be conducting routine preventative maintenance on the Technical Support Center [TSC] HVAC. The expected start of the preventative maintenance is 12/11/14, 0800 EST. Planned completion is 12/11/14, 1800 EST. This maintenance renders the TSC non-functional. The planned TSC alternative will be the Control Room. This event is reported in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been informed. * * * UPDATE FROM JIM RUSSELL TO HOWIE CROUCH AT 1625 EST ON 12/11/14 * * * The TSC was declared operable at 1445 EST. The licensee has notified the NRC Resident Inspector. Notified R2DO (Desai). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-11
50667 | 0 | HEMLOCK SEMICONDUCTOR |  |  |  |  | 2014-12-09 22:00 | 2014-12-10 19:43 | 2014-12-15 | FIXED GAUGE SHUTTER STUCK IN CLOSED POSITION "At approximately 2200 EST, on December 09, 2014, an area operator attempted to open the shutter on source holder 10071961 (Hemlock identifier). The shutter operation failed with the shutter stuck in the closed position. The operator then contacted an area Equipment Care Operator who verified the shutter would not operate. The area operator informed a day tech of the failed shutter operation on December 10, 2014. Operating the shutter was part of a routine annual calibration PM [preventive maintenance]. The process was previously shut down, therefore, this incident caused no loss of production. The source holder is located at S-457 on HP tank 35600." Fixed gauge: Vega America Source Holder Model SHF 2-B with Cs-137 800 millicurie source. * * * UPDATE FROM CHRISTOPHER VAN HAMPLER TO DANIEL MILLS AT 0904 EST ON 12/15/2014 * * * The licensee performed a radiation survey of the fixed gauge which indicated higher than expected radiation readings (40 mR/hr at <30 cm). Based on these readings, the licensee has determined that the shutter is stuck in a partially open position. The licensee has contacted the manufacturer to repair the device. Notified R3DO (Skokowski) and NMSS Events Notification (via email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-12-18
50666 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-12-10 13:44 | 2014-12-10 17:13 | 2014-12-10 | INADVERTENT LOSS OF VITAL INDICATION DURING MAINTENANCE "On December 10, 2014, at 1344 [EST], channel 1 of Refueling Water Storage Tank (RWST) level indication failed low during maintenance activities on channel 2. At that time, operators entered abnormal procedure 1-AP-3, 'Loss of Vital Indication, on Unit 1.' Additionally, Technical Specification (TS) 3.0.3 was entered due to 2 channels inoperable that affect Recirculation Spray (RS) pump auto-start capability. Had a Containment Depressurization Actuation (CDA) occurred during the time that both channels were inoperable, accident mitigation would have been adversely impacted. At 1356, both level indications returned to normal. At 1417, channel 2 was declared Operable and TS 3.0.3 was cleared. At 1439, channel 1 was declared Operable. "Therefore, this 8-hour report is being made per 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function due to the RS pump auto-start concern." Technicians inadvertently went to the incorrect channel (Channel 1) during planned maintenance activity of Channel 2, causing the loss of both channels simultaneously for a short period of time. The licensee has notified the NRC Resident Inspector and will be notifying the Louisa County Administrator. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-12-10
50665 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-12-08 | 2014-12-10 15:11 | 2014-12-10 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was provided by the State of California via email: "On December 9, 2014, the RSO [Radiation Safety Officer] of Geocon, Inc., contacted San Diego County Radiologic Health regarding a gauge that was run over and damaged at a temporary jobsite on December 8, 2014. ICE RAM-South [Inspection Compliance Enforcement Radioactive Material] was notified of the incident and an inspector contacted the RSO. The gauge, a Troxler model 3440, S/N 27309 (8 mCi Cs-137, 40 mCi Am:Be-241), was left unattended by the operator while talking with another worker when a loader ran over the gauge and struck the gauge handle. The damage to the gauge was to the electrical housing and the scalar rod (snapped into two pieces near the gauge body but remained attached at the handle). The Cs-137 source was locked in the shielded position just prior to the incident. The Cs-137 source remained in the shielded position and the source rod and the protective housing containing the Am:Be-241 source were intact after the incident. After the incident, the area was secured and the RSO was contacted. The RSO arrived at the scene and performed a radiation survey (make/model and type not reported). The RSO found that the dose rates were normal for a gauge out of the transport case (dose rate and background not reported). After inspecting the gauge, it was determined that the gauge could be placed in the transport case in its normal position. The RSO then surveyed the transport case and found that the dose rates were normal for a gauge in the transport case (not reported). "The RSO was instructed to prepare a report of the incident to be submitted to our office within 30 days. The investigation is on-going and any citations will be determined at a later date. " CA Report No: 120914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-12-18
50664 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-12-05 | 2014-12-10 13:54 | 2014-12-10 | AGREEMENT STATE REPORT - DAMAGED SHIPMENT WITH REMOVABLE SURFACE CONTAMINATION The following information was provided by the Commonwealth of Pennsylvania: "Event date and time: Unknown at this time. "Event type: Removable contamination greater than the limits specified in 49 CFR 173.443. "Notifications: The Department [PA DEP Bureau of Radiation Protection] was notified via email of this event [on December 5, 2014]. The event is immediately reportable as per 10 CFR 20.1906(d)(1). "Event Description: A shipment exhibited damage consisting of a tear in the metal wall near the floor-wall junction of its container. Radiological surveillance around the tear exhibited removable surface contamination in the amount of 12,000 dpm/100 cm2 beta-gamma. "Cause of the Event: Unknown at this time. "ACTIONS: All areas were decontaminated and moved to a radioactive waste disposal container. The Department plans a reactive inspection. More information will be given when known, including the isotopes of concern." PA Event Report ID No: PA140023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-12-18
50663 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-12-09 18:30 | 2014-12-10 00:31 | 2015-01-30 | HIGH ENERGY LINE BREAK DOOR FOUND CLOSED "At 1830 [CST] on December 9, 2014 Door 410B, a HELB (High Energy Line Break) door between the east and west sides of the ground floor of the reactor building, was found closed. This door is one half of a pair of double doors that are normally open to provide a HELB energy and flooding release path to mitigate postulated HELB events. The closed HELB door has the potential to impact safe shutdown by exposing both divisions of safe shutdown components to unanalyzed environmental conditions. With the potential loss of both divisions of safe shutdown equipment, no safe shutdown path would exist. This condition is being reported as an unanalyzed condition as defined by [10 CFR] 50.72(b)(3)(ii)(B). The HELB door was immediately opened and returned to normal configuration. Door 410A remained open during the time that Door 410B was closed and provided an available, but not yet analyzed, release path that could have mitigated the consequences of this event. The health and safety of the general public was not impacted as a result of this condition. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM JON LAUDENBACH TO CHARLES TEAL ON 1/30/15 AT 1513 EST * * * "Further analysis has determined that the condition did not significantly degrade plant safety. "Door 410B in the Reactor Building was found closed. This door is one half of a pair of double door (Doors 410A and 410B) that normally open to provide a High Energy Line Break (HELB) energy and flooding release path to mitigate postulated HELB events. The condition of one half of the double door closed was not previously analyzed. "A subsequent completed engineering evaluation analyzed this condition, Door 410B being closed and Door 410A being open, for the following environmental conditions: peak compartment temperatures, block wall differential pressure, radiation dose, and flooding. The environmental conditions found the Reactor Building in response to Door 410B being closed with 410A being open does not affect the operability of safety related equipment housed within the Reactor Building or the ability to safely shut-down the plant and maintain the plant shutdown condition following a HELB event. "The NRC Resident Inspector has been notified." Notified R3DO (Dickson). | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-12-10
50662 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-12-09 18:25 | 2014-12-09 20:02 | 2014-12-30 | NON-FUNCTIONAL FIRE BARRIER DISCOVERED AFFECTING BOTH SAFE SHUTDOWN PATHS "During an inspection of a fire penetration between Fire Area 1404, Switchgear Room 1G and Fire Area 1408, Switchgear Room 1F in the diesel generator building, the penetration was determined to be non-functional as a 3 hour fire barrier. In the event of a postulated fire in the affected areas, both safe shutdown paths on Unit 1 could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10 CFR 50.72(b)(3)(ii)(B). "Compensatory measures were established in accordance with the plant's Fire Hazard Analysis (FHA). The presence of the compensatory measures in addition to automatic fire detection in the fire areas ensure that the safe shutdown paths are preserved until the degraded condition can be repaired. "[Condition report No.] CR904013" The licensee notified the NRC Resident Inspector * * * RETRACTION PROVIDED BY KENNY HUNTER TO JEFF ROTTON AT 0915 EST ON 12/30/2014 * * * "Further investigation revealed that after removing the outermost two inches of loose silicone foam material, and taking additional measurements there remained adequate silicone foam material to provide 10 inches of silicone foam sealing the penetration. Plant design shows that the wall in question is 18 inches thick and also that 9 inches of silicone foam is required in the penetration in order maintain a 3 hour fire rating for the wall/penetration. Since there is adequate foam in the penetration to maintain the 3 hour fire rating the penetration is fully functional. "Based on this information, this penetration in its 'as found' state does NOT represent a condition that seriously degrades a principal safety barrier. As such this condition has been determined to no longer meet reporting requirement 10CFR50.72(b)(3) and is therefore NOT reportable. Based on this information the previous notification for Event 50662 is being retracted." The licensee notified the NRC Resident Inspector. Notified R2DO (Bartley) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-12-09
50661 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2014-12-07 12:00 | 2014-12-09 16:00 | 2015-01-14 | DISCOVERED VULNERABILITY IN SECURITY SYSTEM Discovered a vulnerability in a safeguard system that could allow unauthorized or undetected access to a controlled access area for which compensatory measures have not been employed. Contact the Headquarters Operations Officer for additional details. * * * UPDATE 1242 EST ON 01/14/15 FROM TOM NEWTON TO S. SANDIN VIA EMAIL * * * The licensee provided the Ops Center a copy of their written report. The original has been sent by U.S. Mail. Notified NPR SS (Reed) and DPR/PR (Hsueh) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | MA | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2014-12-09
50660 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-12-02 | 2014-12-09 15:38 | 2014-12-09 | AGREEMENT STATE REPORT - LEAKING NI-63 SEALED SOURCES The following information was provided by the Commonwealth of Massachusetts via email: "Morpho Detection is in the process of moving its facility, and as part of this process wipe-tests were conducted on older Ni-63 sealed sources (approx. 8 - 10 millicuries per source), that were in storage prior to transfer to a contractor for disposal. The leak tests showed that four groups of sealed sources had results that were above the threshold limit of 5 nanocuries. Thus one or more of the sealed sources within each group showed signs of leakage or contamination. Licensee reports that additional wipe tests were not conducted to determine the specific sources that were leaking. "The Ni-63 sealed sources were identified by the licensee as Model Number NER-004 and GE Homeland Protection detector heads containing those sources. "Overall, the leak tests revealed that Ni-63 contamination ranged from 0.030 to 0.98 microcuries for the four groups of sealed sources that were analyzed. "Wipes were taken by the licensee by swabbing the exterior of a group of sealed sources of similar type (R&D dual-source detector heads were differentiated from R&D single source detector heads, etc.), thus the multiple sources within a group were swabbed with a single swab which was ultimately analyzed by a licensed contractor (Radiation Safety Control Services, Stratham NH). "Subsequent to finding contamination, the sources were placed in containers, sealed, and wipe-tests (using swabs) were carried out on the exterior of the storage containers along with the interior and exterior of the cabinet in which they were being stored The wipe tests of the containers and cabinet showed no levels that indicated Ni-63 contamination. "The licensee disposed of the sealed sources by contracting the services of Viola Environmental Services (12/09/14). "The Agency [Commonwealth of Massachusetts] considers this event open. "Equipment problems: R&D Dual-source detector heads (9 dual sources), 1 swab, resulted in a finding of 0.98 microcuries EntryScan detector heads (6 sources), 1 swab, resulted in a finding of 0.069 microcuries R&D Single-source detector heads (9 single sources), 1 swab, resulted in a finding of 0.155 microcuries Ni-63 bare sources (9 sources), 1 swab, resulted in a finding of 0.0301 microcuries" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-12-17
50659 | 0 | DTE ENERGY |  |  |  |  | 2014-11-14 14:00 | 2014-12-08 14:07 | 2014-12-08 | LOST DEVICE WITH CADMIUM-109 SOURCE The licensee reports the loss of General License Niton XRF (X-Ray Fluorescence) Device, serial # 8622, containing a (Cadmium) Cd-109 source, Serial # NR-7169. The original device source strength was 40 milliCurie however, the current source strength is assayed at .26 milliCurie. The licensee believes the device was accidently disposed of as waste for recycling from the Detroit, MI facility. Efforts to locate and recover the device have been unsuccessful. More information will be provided as it becomes available. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-12-16
50658 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-10-07 09:35 | 2014-12-08 12:23 | 2014-12-08 | INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. "On October 7, 2014, at 2135 [CDT], while in a refueling outage with the reactor non-critical (Mode 5), work activities were in progress that included replacement of an excess flow check valve and execution of a Technical Specification Surveillance Procedure on the Automatic Depressurization System. Subsequent to valving in a level transmitter (LT), water levels in both the variable and reference legs of the LT were disturbed resulting in a Unit 1 full scram and Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolation signals due to receipt of an invalid low reactor water level signal. The PCIS Groups 2, 3, 6, and 8 isolations caused the initiation of Trains A, B, and C of the Standby Gas Treatment System and Control Room Emergency Ventilation Subsystem 'A'. The Reactor and Refuel Zone ventilation fans tripped and the secondary containment dampers isolated. "Operations personnel responded to the PCIS initiation, ensured all equipment operated as designed, and placed affected systems back in service. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 943038. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-12-08
50657 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2014-12-04 16:00 | 2014-12-05 17:15 | 2014-12-05 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following report was received from the State of Utah via email: "A portable gauge was run over by a compactor at a construction site [located at the University of Utah Business Loop Parking Garage]. The gauge was damaged and required disassembly to withdraw the source. The source was withdrawn to the shielded position. Leak test wipes were taken and sent to a laboratory for analysis. The [Licensee] RSO [Radiation Safety Officer] placed the gauge inside the transport case. The RSO verified transport index readings were normal. The RSO transported the gauge to the licensee's facility and stored it until the leak test results were verified to be below 0.005 microcuries. Additional information and photographs will be forthcoming." Utah Event Report ID: UT140005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2014-12-15
50656 | 0 | FEDERAL BUREAU OF PRISONS |  |  |  |  | 2014-11-17 | 2014-12-05 11:21 | 2014-12-05 | MISSING TRITIUM EXIT SIGNS The Federal Bureau of Prisons in Duluth, Minnesota reported the loss of generally licensed devices (self-illuminating tritium exit signs) as required by 10 CFR 31.5(a)(10) and 10 CFR 20.2201(a)(1). Four (4) tritium exit signs are assumed to be missing. A thorough search was conducted but failed to locate the missing signs. The serial numbers are known for 3 of the 4 missing signs; 309482 - 11.47 Ci, 309489 - 11.47 Ci, C601373 - 20 Ci. The licensee has notified R3 (Piskura). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-12-15
50655 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-10-27 | 2014-12-04 15:08 | 2014-12-04 | AGREEMENT STATE REPORT - STUCK AND ABANDONED SOURCE The following report was received from the State of Louisiana via fax: "The source became stuck/lost down a strategic oil reserve cavern belonging to US DOE. Cavern named WH 9A, in West Hackberry field, Cameron/Cameron Parish, LA. "STC [the licensee] was logging/taking measurements in/down a strategic oil reserve cavern for the Department of Energy when the 125 mCi source became lost down cavern, STC abandoned in place the Cs-137 source and applied all practical applicable P/A procedures pertaining to a cavern. The source was declared irretrievable November 11, 2014, and requested approval of the information on the plaque. The source is believed to be on the bottom of the cavern at depth of 3,575 ft. Schlumberger, after several 'fishing' attempts, decided to 'cap'/abandon the location and move on. "LDEQ [Louisiana Department of Environmental Quality] was notified of the lodged source on October 27, 2014 [approximately] 1720 CDT. At that time, Schlumberger requested direction to abandon the irretrievable source. The request was granted by [LDEQ]. "On October 27, 2014, STC contacted LDEQ with a preliminary notification reporting that a well-logging source was lost down-hole in a DOE Strategic Oil Reserve Cavern in Cameron Parish, LA. The source, a Gulf Nuclear, 125 mCi Cs-137 source, S/N CSV-129. This incident was reported and will be abandoned and maintained by the requirements of LAC 33: XV. 2051 and 2099, Appendix B. "LDEQ considers this event closed." Louisiana Event Report ID No.: LA - 140012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-12-12
50654 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2014-12-04 11:50 | 2014-12-04 14:42 | 2014-12-04 | OFFSITE NOTIFICATION DUE TO EMERGENCY SIREN INADVERTENTLY SOUNDING "At 1150 [EST], the Shift Manager was notified that TMI [Three Mile Island] emergency plan siren 128 was inadvertently sounding. This siren is no longer alarming. Repairs to the siren have been completed. "This notification is being made under 10 CFR 50.72(b)(2)(xi), 'News release or notification of other government agency'. "The licensee has notified the NRC Resident Inspector." The licensee notified applicable state and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-12-04
50653 | -1 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-11-28 06:00 | 2014-12-03 18:46 | 2014-12-19 | COMPENSATORY ACTIONS NOT TAKEN WITHIN ALLOWED TIME Compensatory actions required for a security degradation were not taken within the allowed time. The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 12/19/14 AT 1456 EST FROM MARK MOEBES TO DONG PARK * * * Based on a review of the site Physical Security Plan, the licensee has retracted this report after determining it does not meet the 1-hour reporting criteria. The NRC Resident Inspector has been notified. Notified R2DO (O'Donohue) and Part 73 group via email. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-12-03
50652 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-12-03 09:50 | 2014-12-03 16:02 | 2014-12-03 | CONTROL ROOM AREA RADIATION MONITOR FAILED LOW "At 0950 CST on December 3, 2014, R-1 Control Room Area Radiation Monitor failed low and was taken out of service. This monitor has no redundant monitor that will allow timely classification of two Emergency Action Levels (EALs) - NUE (Notification of Unusual Event) and Alert classifications - when out of service. This results in a Loss of Emergency Assessment Capability while R-1 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Control Room readings were normal as evidenced on R-1 prior to its failure. Compensatory measures have been established with a Portable Area Monitor installed in the Control Room adjacent to R-1. Corrective maintenance is in progress and will continue until the monitor is returned to service. "The health and safety of the public was not affected by this issue. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-03
50651 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2014-11-10 | 2014-12-03 09:52 | 2014-12-03 | AGREEMENT STATE - POTENTIAL RADIOGRAPHER OVER-EXPOSURE The following information was provided by the State of Oklahoma via email: "Advanced Inspection Technologies (OK-27588-02) has reported [to the State of Oklahoma] that the dosimeter issued to one of their radiographers reported a dose of 16.294 R for the period of October 10 to November 10. The report from Landauer states that the results are 'inconclusive' and the dosimeter was reprocessed. The second read was also inconclusive. Energy level was characterized as high but type not specified. The licensee believes the dosimeter was damaged or otherwise compromised. Investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2014-12-11
50650 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-12-03 00:22 | 2014-12-03 05:05 | 2014-12-03 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "An unexpected main turbine trip causing a reactor trip occurred on 12/03/2014 [at 0022 CST] with the plant operating in Mode 1 at 100 percent power. As part of the plant design, an expected, valid actuation of the Auxiliary Feedwater System occurred in response to the reactor trip. As part of the Auxiliary Feedwater actuation, the 'B' Motor Driven Auxiliary Feedwater Pump to 'D' Steam Generator throttle valve did not throttle as expected and was manually isolated. All other systems functioned normally in response to the plant conditions. The plant is currently stable in Mode 3 at 0 percent power. Safety related buses are receiving normal off-site power and the grid is currently stable. "The NRC Resident Inspector was notified." All control rods fully inserted on the reactor trip. Steam generator levels are being maintained by the AFW system and decay heat is being removed by the main condenser. No primary or secondary safety relief valves lifted during the transient. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-12-03
50649 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-12-02 20:50 | 2014-12-03 01:10 | 2014-12-03 | MANUAL REACTOR TRIP DUE TO FAILURE OF CONDENSATE PUMP "Initiated a manual Unit 1 reactor trip due to imminent failure of 1P-25B Condensate Pump. Unit 1 had commenced a rapid down power due to the degradation of the pump. The event is reportable under 10CFR50.72(b)(2)(iv)(B) for a manual actuation of the reactor protection system when the reactor is critical and 10CFR50.72(b)(3)(iv)(A) for an actuation of specified system (6) PWR auxiliary feedwater system. Auxiliary feedwater system actuation was due to low steam generator water levels in both 'A' and 'B' Steam Generators, an expected system response during a reactor trip. Decay heat removal is by forced circulation and is being controlled by auxiliary feedwater system and condenser steam dumps. "After the trip, both main steam generator feedwater pumps were secured due to feed pump suction pressure remaining low post trip. "All other plant systems functioned as required. All control rods fully inserted in the core due to the manual trip. There was no ECCS actuation. Off-site power has been maintained throughout the event." No primary or secondary safety relief valves lifted during the reactor trip. Unit 1 is in a normal shutdown electrical lineup. There was no effect on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 62 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-12-03
50648 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2014-12-02 09:00 | 2014-12-02 17:15 | 2014-12-02 | AGREEMENT STATE - MEDICAL EVENT INVOLVING OVERDOSAGE DURING HDR BRACHYTHERAPY TREATMENT The following information was received via email: "The licensee reported a medical event at 0958 PST involving a patient treated for vaginal cancer. The treatment involved an Ir-192 high dose rate afterloader (HDR) source at 5.369 Curies activity (December 2nd) delivered to the vaginal vault via a 3 cm single-channel cylinder for a prescribed dose fraction of 400 cGy (rad). Instead, a 5 cm single-channel cylinder was used that delivered a 700 cGy dose (rad), or 75 percent (300 cGy) above the prescribed dose. The licensee stated that an afternoon patient's treatment plan was being reviewed on the console while the morning patient was being prepped for treatment and the patient subsequently treated with the other patient's plan. The licensee failed to verify the patient's identification before starting the treatment. The cause is therefore determined to be human error. The licensee stated that the patient was scheduled for three fractionated doses at 400 cGy (rad) each for a total dose of 1200 cGy (rad). This was the 2nd fraction so the total dose delivered to the patient is currently 1100 cGy (rad). The licensee performed a biological effective dose (BED) calculation and that the final effective dose is within 4 percent and 10 percent of the intended dose in terms of short/long term effects and the final fraction dose will most likely not be administered. The licensee notified the patient's physician who will notify the patient of the error. The licensee will submit a formal report to Oregon RPS including corrective actions to prevent recurrence." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2014-12-10
50647 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-11-07 | 2014-12-02 17:15 | 2014-12-02 | AGREEMENT STATE - MEDICAL EVENT INVOLVING UNDERDOSAGE TO PATIENT OF Y-90 SIR-SPHERES The following is a synopsis of information received via E-mail: The Cedars Sinai Medical Center (CSMC) Radiation Physics Manager (RPM) contacted Los Angeles County Radiation Management (LA County) via telephone to report a potential medical event that had occurred at CSMC. The RPM stated that the event resulted from a dosage administration to the patient of yttrium-90 SIR-Spheres less than that prescribed. LA County requested that a written report be submitted. Per the written report, the treatment plan required administration of 31 milliCuries (mCi) of Y-90 through a catheter via the hepatic artery. During setup, the interventional radiologist (IR) noted a potential air bubble in one of the lines connected to the catheter. The IR disconnected the line and flushed it with solution to clear the air bubble. The IR then activated the SIR-Sphere device without realizing that the line was still disconnected from the catheter. The radioactive material spilled into the sterile 4 inch by 4 inch gauze and drapes on the sterile field. The patient received 13 mCi, which was 42 percent of the prescribed dosage of 31 mCi. The RPM stated that the referring physician and patient were notified and that the patient did not report any side effects as a result of the incorrect dosage administration. Based on CSMC's written report, it was determined that this event required 24-hr notification to the NRC Operations Center. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-12-10
50646 | 0 | HYDROLAKE INC |  |  |  |  | 2014-11-28 06:33 | 2014-12-01 16:44 | 2014-12-17 | FIRE DAMAGED LABORATORY CONTAINING NRC GENERAL LICENSED MATERIAL An NRC general licensee reported that a fire damaged their facility. Inside this facility was an ASOMA Model 200 (Serial # 4649) device containing 13 mCi of Cm-244. The device is assumed to be damaged or destroyed. The licensee has limited access to the area and is contacting a qualified contractor to assist with disposal of the device. The ASOMA Model 200 is an Energy Dispersive-X-Ray Fluorescent (ED-XRF) benchtop analyzer. * * * UPDATE FROM ANTHONY FURLICH TO DANIEL MILLS AT 0839 EST ON 12/15/2014 * * * Licensee hired a licensed contractor to recover the damaged source. The source was successfully recovered and was verified to be intact with no leakage. The source has been shipped to a licensed disposal facility. Notified R3DO (Skokowski) and NMSS Events Notification (via Email) * * * UPDATE FROM ANTHONY FURLICH TO JOHN SHOEMAKER AT 1118 EST ON 12/17/14 * * * This report was received via email: The licensee completed the final report on the recovery and disposition of the Asoma Model 200 X-ray spectrometer which was damaged in the fire at the licensee's lab on November 29, 2014. All the surveys showed no elevated activity. Notified R3DO (McCraw) and NMSS Events Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(a) |  |  |  | 0 | 2014-12-09
50645 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-11-30 13:54 | 2014-11-30 17:26 | 2014-11-30 | AUTOMATIC AUXILIARY FEEDWATER ACTUATION DUE TO PLANNED REACTOR TRIP "This is an non-emergency event notification to the NRCOC [NRC Operations Center] in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to preplanned manual actuation of Reactor Protection System and auto-initiation of AFW due to beginning of cycle operating conditions, IAW 4-GOP-103 (General Operating Procedure). "On 11/30/14 at 1354 EST, Unit 4 reactor power was reduced to approximately 23% and manually tripped as a pre-planned evolution to facilitate repairs to an unidentified steam leak on Unit 4 High Pressure Turbine. All systems and components operated as designed. Unit 4 is currently stable in Mode 3, AFW has been secured." The licensee has notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-11-30
50644 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-11-26 11:29 | 2014-11-28 10:57 | 2014-11-28 | AGREEMENT STATE REPORT - Y-90 THERASPHERE UNDERDOSE TO LIVER The following email was received from the State of Ohio: "On Wednesday, November 26, 2014 at 1129 [EST], the Interventional Radiologist Authorized User [AU] physician began to administer the prescribed activity of 1.38 GBq Y-90 micro-spheres (Theraspherer) for an estimated dose of 125 Gy to segment 7 of the right liver lobe. After a couple of 20 cc syringes of saline had been pushed through the administration kit, the Nuclear Medicine technologist made an ion chamber measurement of the dose vial and tubing set and observed a very high reading of 2.5 Roentgens/hour using a Keithley 451B/RYR, serial number 2935, ion chamber with the beta window open. This was a very high measurement, so the AU physician continued to push an additional 6 syringes of saline for a total of 8 syringes through the administration set with very little reduction in the ion chamber reading. At that point the AU physician decided to call an end to the therapy. "The administration set was moved out of the room and using the manufacturer's template, the Nalgene jar containing the dose vial and tubing set in the plastic beta shield was measured as 0.55 mR/hr versus a pre-therapy measurement of 2.3 mR/hr. This meant that approximately 24 percent of the dose remained in the dose vial and/or tubing set and micro-catheter. "The RSO then asked the Nuclear Medicine technologist to take the Nalgene jar to the hot lab to measure the dose vial, tubing set and micro-catheter individually in the dose calibrator. Each of the items were carefully wrapped and measured in the dose calibrator using a calibration factor of 048 for the dose vial and 086 for the tubing sets. The Capintec CRC 15-R, serial number 156151, dose calibrator measurements were 0.009 GBq in the dose vial, 0.31 GBq in the 'D' line tubing set and 0.038 in the micro-catheter for a total of 0.357 GBq of the 1.44 GBq decayed to the time of administration which equals about 24.8 percent of the total dose. "The prescribed dose was 1.38 GBq which would deliver about 125 Gy to the segment 7 of the right liver lobe; subtracting the 0.357 GBq the calculated dose to the liver segment was 98.15 Gy or about 78 percent of the prescribed dose. "The Radiation Safety Officer contacted BTG International (Canada) to file an incident report and provided all of the specific details of the incident (Incident Report Number: OTT-PC-14-0073). The BTG representative asked to check with the AU physician to see if he administered the saline at approximately 20 cc/min, and not less than 10 cc/min so that the micro-spheres would not settle out of suspension during the administration. The tubing set and dose vial will be stored for decay-in-storage and returned to the manufacturer for further analysis. "After interviewing the Authorized User physician following the case, he said that there was no medical reason related to the patient that lead to the under dose, and that he intended to administer the entire 125 Gy to the liver segment throughout the therapy. He also mentioned that the delivered 98.15 Gy to a small segment of the liver (segment 7) was therapeutic and provided optimal treatment dose to the tumor. He explained that the delivered dose that differed by more than 20 percent from the prescribed dose had no consequences to the patient and there is no requirement to repeat the treatment. He also mentioned that he pushed the saline with at least a rate of 10 cc/min or higher not exceeding 20 cc/min. "According to the Ohio Administrative Code, 3701:1-58-101, Report and Notification of a Medical Event, the total dose exceeded 0.5 Sv (50 rem) to an organ and differed from the prescribed dose by more than 20 percent, and therefore, met the reporting criteria. A telephonic report was made by the Radiation Safety Officer to the Ohio Department of Health at 1615 [EST] on 11/26/2014 regarding this incident. The Authorized User physician that administered the therapy was the referring physician and notified the patient the day of the procedure. The Nuclear Medicine imaging following the therapy indicated that the microspheres were administered to the correct liver region." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-12-08
50643 | 0 | VETERANS HEALTH ADMINISTRATION |  |  |  |  | 2014-11-26 08:00 | 2014-11-26 14:54 | 2014-11-26 | RECEIPT OF A PACKAGE WITH REMOVABLE SURFACE CONTAMINATION "Per 10 CFR 20.1906(d), [licensee is] reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. The package was received today (November 26, 2014) at around 0800 PST by VA Central California Health Care System. This facility holds permit number 04-01935-03 under the VHA [Veterans Health Administration] master materials license. The package was checked-in and surveyed around 0830 PST. Wipe tests performed on the external surface of the package indicated a removable contamination level of 7155 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. The package contained seven unit dosages of radiopharmaceuticals ranging between 10 and 40 millicuries each of Technetium-99m and was shipped from Cardinal Health in Fresno, California. The specific radionuclide that resulted in the contamination was not identified but does not appear to be Technetium-99m. The wipe counting statistics were based on Ba-133. The inner packaging materials were not contaminated. The facility immediately notified the vendor/shipper, who serves as the final delivery carrier, about the contaminated package at about 0835 PST. VHA National Health Physics Program was notified around 0845 PST with initial information. As corrective actions, the packaging materials were bagged and set aside in a restricted area at the facility for further evaluation." The licensee notified the NRC Region III Project Manager (Null). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2014-12-04
50642 | 0 | U. S. GEOLOGICAL SURVEY |  |  |  | 1000 KW TRIGA MARK I | 2014-11-25 14:21 | 2014-11-25 17:13 | 2014-11-25 | REACTOR CONSOLE KEY LEFT IN CONTROL CONSOLE UNATTENDED "On Tuesday, November 25, 2014, a violation of Technical Specification A.1, 'Shutdown,' occurred at the USGS TRIGA research reactor. Contrary to the specification, the key to the console key switch was left in the control console, in the OFF position, while the control room was unoccupied. This condition existed intermittently for approximately nine minutes during the time period from 1421 MST to 1436 MST, when the Reactor Supervisor discovered the key. The reactor was shutdown during this time period, and the staff members were performing routine maintenance. The facility shutdown checklist had been completed, and the key had been locked in a lock box, but the key was subsequently removed from the lock box by a Senior Reactor Operator and put in the console switch for maintenance checks. The reactor was continuously occupied by reactor staff during this event, and there were no non-staff personnel present. This event is being reported to the NRC's facility inspector, NRC Operations Center, the USGS Reactor Administrator, and the USGS Reactor Operations Committee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | CO | NPR | [5 empty] | 0 | 2014-11-25
50641 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2014-11-25 12:11 | 2014-11-25 17:07 | 2014-11-25 | DEFICIENCY IN METHODOLOGY USED FOR EMERGENCY CORE COOLING SYSTEM PERFORMANCE REQUIREMENTS "On Tuesday November 25, 2014, at 1211 CST, Arkansas Nuclear One, Unit 1 (ANO-1) reviewed AREVA 10 CFR 50.46 Notification Letter FAB14-00632. This letter indicates that a deficiency was discovered in the uranium thermal conductivity models used in the ANO-1 Loss of Coolant Accident (LOCA) analysis of record. When the deficiency is corrected, the LOCA Peak Cladding Temperature (PCT) limits may be in excess of 2200 degrees Fahrenheit (F). 10 CFR 50.46 paragraph (b) defines the acceptance criteria for the LOCA analysis process. The ANO-1 licensing basis PCT is evaluated for compliance with the criterion 10 CFR 50.46(b)(1) and must not exceed a PCT of 2200 degrees F. "During AREVA's review of the issue, AREVA had provided compensatory measures in the form of reductions in LOCA linear heat rates as a contingency in case the errors were found to be substantiated, which were then translated into reduced axial imbalance limits so that ANO-1 would operate within 10 CFR 50.46 limits. As a precautionary measure pending the completed analysis, ANO-1 implemented the compensatory measures on October 20, 2014, and as a result, the errors reported have no impact on current plant operation or public health and safety. This event is being conservatively reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). "Based on 50.46(a)(3)(ii) criteria, ANO-1 will submit a written report within 30 days. "ANO-1 has notified the NRC Senior Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-25
50640 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2014-11-25 12:12 | 2014-11-25 16:35 | 2014-11-25 | DEFICIENCY IN METHODOLOGY USED FOR EMERGENCY CORE COOLING SYSTEM PERFORMANCE REQUIREMENTS "On Tuesday, November 25, 2014, at 1212 EST, Duke Energy Carolinas, LLC (Duke Energy) reviewed AREVA 10CFR50.46 Notification Letter FAB 14-00631. This letter indicates that a deficiency was discovered in the uranium thermal conductivity models used in the Oconee Nuclear Station Loss of Coolant Accident (LOCA) analysis of record. When the deficiency is corrected, the LOCA Peak Cladding Temperature (PCT) limits may be in excess of 2200 degrees F. 10CFR50.46 paragraph (b) defines the acceptance criteria for the LOCA analysis process. The Oconee licensing basis PCT is evaluated for compliance with the criterion 10CFR50.46(b)(1) and must not exceed a PCT of 2200 degrees F. "On October 20, 2014, AREVA recommended actions in the form of reductions in LOCA linear heat rates, which were then translated into reduced axial imbalance limits for the excore and backup incore detector systems. This was done to ensure that Duke Energy operated within 10CFR50.46 limits in the event of a loss of the full incore detector system. The full incore detector system is the primary method for evaluating imbalance and the imbalance limits are unaffected by the reduction in LOCA linear heat rates. The full incore detector system is operable and meets Technical Specification 3.2.2. In addition, the Reactor Protection System (RPS) trip limits for imbalance are not derived from the LOCA analysis and are not affected. "When AREVA notified Duke Energy of the deficiency, Duke Energy confirmed that existing administrative limits bound the AREVA recommended actions and as a result, the errors reported have no impact on plant operation or public health and safety. "This event affects all three (3) units and is being reported in accordance with 10CFR50.72(b)(3)(ii)(B). "Based on 10CFR50.46(a)(3)(ii) criteria, Duke Energy will submit a written report within 30 days. "Duke Energy has notified the NRC Senior Resident Inspector." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-25
50639 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-11-25 12:00 | 2014-11-25 16:32 | 2014-11-25 | NON-CONSERVATISMS IN METHODOLOGY USED FOR EMERGENCY CORE COOLING SYSTEM PERFORMANCE REQUIREMENTS "On Tuesday, November 25, 2014, at 1200 EST, the FirstEnergy Nuclear Operating Company (FENOC) reviewed AREVA 10CFR50.46 Notification Letter FAB14-00625 for the Davis-Besse Nuclear Power Station (DBNPS). This letter indicates that certain non-conservatisms were discovered in the methodology application and inputs used by AREVA for nuclear fuel core configurations with Mark-B-HTP fuel when operated under certain conditions. When corrected, this increases the Peak Cladding Temperature (PCT) in excess of the value prescribed in 10CFR50.46(b)(1) under Loss of Coolant Accident (LOCA) conditions. The DBNPS reactor core contains Mark-B-HTP fuel. 10CFR50.46 paragraph (b) defines the acceptance criteria for the LOCA analysis process. The DBNPS licensing basis PCT is evaluated for compliance with and must not exceed the criterion prescribed in 10CFR50.46(b)(1). "AREVA had provided compensatory measures in terms of plant axial imbalance limits and Fq linear heat rate limits associated with reductions in LOCA linear heat rates so that the DBNPS operates within 50.46 limits. FENOC implemented the compensatory measures at the DBNPS on October 23, 2014, per AREVA recommendations, and as a result the errors reported have no impact on current plant operation or public health and safety. Preliminary analysis of past operating conditions indicate that the DBNPS did not exceed the 50.46(b)(1) criteria for PCT. This 8-hour notification is being reported in accordance with 10CFR50.72(b)(3)(ii)(B). "Based on 50.46(a)(3)(ii) criteria, FENOC will submit a report within 30 days for the DBNPS. "FENOC has notified the DBNPS NRC Senior Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-25
50638 | -1 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-11-24 | 2014-11-25 15:31 | 2014-11-26 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following was received via email: "A patient arrived for a rest/stress imaging procedure on 11/24/14. The rest dose was written to be 8 mCi Tc-99m, and the stress dose was written to be 24 mCi Tc-99m. The patient received the rest dose as written and the scan was performed. The patient was then to receive the 24 mCi stress dose, but instead received a 5 mCi stress dose (same drug, but only 21% of the intended activity) that was intended as the rest dose for another patient. Once the error was discovered, the patient was informed of the error and sent home with the intention of rescheduling the procedure at a later date. The licensee will submit the 15 day report to VRMP [Virginia Radioactive Materials Program] at which time the corrective actions will be reviewed and verified during their next inspection. " Virginia Incident #: VA-14-23 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 11/25/14 AT 1637 EST FROM MIKE WELLING TO DONG PARK * * * This report is being retracted, because it does not meet 10CFR35.3045 criteria. Notified R1DO (Noggle) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-12-03
50637 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-24 | 2014-11-25 15:07 | 2014-11-25 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK SOURCE The following was received via email: "On November 25, 2014, the Agency [State of Texas] was notified by the licensee that on November 24, 2014, an INC IR100 radiography camera, Serial # 4374 with an Iridium-192 source, Model 32, Serial #W951, Activity - 1887 GBq (51 Ci) failed to operate properly at a field site. While the source was being cranked out, the drive cable went too far when the stopper in the pistol grip failed, resulting in the inability to reengage the drive cable and retrieve the source back into the camera. The licensee's RSO responded to the scene to inspect and retrieve the source. No individual received any significant additional exposure due to this event. The RSO received the highest dose of 23 mrem. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-12-03
50636 | 0 | AREVA, INC. |  |  |  |  | 2014-10-19 | 2014-11-25 10:10 | 2014-11-25 | PART 21 - DEFECT IN LOCA ANALYSIS FOR B&W PLANTS The following information was summarized from the report obtained from the vendor via facsimile: "The defect is related to the thermal conductivity model in the codes TACO3 and GDTACO which are used in the AREVA LOCA model for B&W plants. The thermal conductivity model does not adequately represent the change in conductivity with burnup for the fuel. The correction of the thermal conductivity model results in the peak cladding temperature limit in 10 CFR 50.46 (2200 degrees F) being exceeded. "The defect exists for the following plants: Oconee Nuclear Station Unit 1, Oconee Nuclear Station Unit 2, Oconee Nuclear Station Unit 3, Arkansas Nuclear One Unit 1, Three Mile Island Unit 1, and Davis-Besse Unit 1" If there are any technical questions or concerns, please contact: Gayle Elliott AREVA, lnc., 3315 Old Forest Road Lynchburg, VA 24501 Ph. # 434-841-0306. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-11-25
50635 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2014-10-06 | 2014-11-24 07:58 | 2014-11-24 | PART 21 - TYPE 67 AFR REGULATORS WITH IMPROPERLY DEDICATED DIAPHRAGM VALVE SEATS The following information was summarized from the report obtained from the vendor via facsimile: "The purpose of this Fisher Information Notice is to alert CPNPP [Comanche Peak Nuclear Power Plant], that as of October 6, 2014, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the performance of the Equipment, including their safety-related function. "Fisher is informing CPNPP of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21. "Fisher has determined that parts kits for the Equipment were provided with improperly dedicated parts that had not been properly processed per active valve requirements. Specifically, Fisher provided diaphragm assemblies for the Type 67 AFR regulator with improperly dedicated diaphragm valve seats." If there are any technical questions or concerns, please contact: Guy Scaggs Quality Manager Emerson Process Management Instrument & Valve Services Company 757 Old Clemson Road Columbia, SC 29229 Fax: (803) 736-3105 Phone: (803) 736-3105 guy.scaggs@emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-11-24
50634 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-21 | 2014-11-22 10:07 | 2014-11-22 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA FAILED TO OPERATE PROPERLY The following was received via email from the State of Texas: "On November 21, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee that an INC IR100 radiography camera, serial #4386, with an iridium-192 source, model 32, serial #W957, activity - 1554 GBq (42 Ci) failed to operate properly at a field site. The technician had an indication that the source was fully inside the camera when the flag indicator changed, however they were unable to disconnect the drive cable from the pig tail. The pig tail was not fully inside the camera. The licensee's RSO [Radiation Safety Officer] responded to the scene to inspect and retrieve the source. [The RSO] moved the source to another camera. The [RSO determined the] locking mechanism had worn out on the camera. No individual received any significant additional exposure due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Report: # I 9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-12-01
50633 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-11-20 | 2014-11-21 17:25 | 2014-11-21 | AGREEMENT STATE REPORT - OVEREXPOSURE TO AN EMBRYO / FETUS "The Department [Colorado Department of Public Health and Environment] was notified via e-mail that a patient discovered she was pregnant after undergoing a PET examination. Dose is estimated to be on the order of 1 - 1.5 rem. "A written report is expected within 15 days. No other information is available at this time." Colorado Event Report ID No.: CO14-014-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-12-01
50632 | 0 | U.S. NAVY |  |  |  |  | 2014-11-13 | 2014-11-21 09:42 | 2014-11-21 | LOST SR-90 SOURCE During an underway replenishment in the Fifth Fleet area of operations, a storage box containing a CH53 helicopter blade with an in-blade inspection system (IBIS) was dropped over the side and is irretrievable due to the depth of the water. The IBIS contained a 500 microCuries Sr-90 source. The licensee has notified their NRC Project Manager (Seeley). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-12-01
50631 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-11-20 14:52 | 2014-11-20 17:29 | 2014-11-20 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISORY LICENSED EMPLOYEE A supervisory licensed employee had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2014-11-20
50630 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-11-20 10:22 | 2014-11-20 16:29 | 2014-11-20 | CONTAINMENT DECLARED INOPERABLE DUE TO CONTAINMENT FAN COIL LEAK "At 1022 CST on November 20, 2014, a cooling water leak of approximately 20 to 30 drops per minute was identified on the 14 Containment Fan Coil Unit NW side lower face gasket. Unit 1 Containment was declared inoperable, which required entry into Technical Specifications (TS) LCO 3.6.1 Condition A, containment inoperable, applicable in MODES 1, 2, 3, and 4. Immediate actions were taken to isolate the Fan Coil Unit within 1 hour from the initial identification of the leak. 14 Containment Fan Coil Unit was isolated and Containment was declared operable and TS 3.6.1 Condition A was exited at 1109 CST. A Work Request (WR) was initiated and 14 Containment Fan Coil Unit has been restored to an operable condition. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "The plant remains in a safe condition and there was no effect to the health and safety of the public. "The licensee has notified the NRC Resident Inspector." The licensee verified the other Unit 1 Containment Fan Coil Units did not have the same problem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-11-20
50629 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-11-19 16:18 | 2014-11-19 21:44 | 2014-11-19 | FIRE PENETRATION NOT MEETING REQUIREMENTS "During a fire inspection activity involving inspection of fire penetrations that serve as Appendix R barriers, degradation of a fire penetration was identified that was sufficient to prevent this penetration from meeting Appendix R requirements as a 3 hour fire barrier. In the event of a postulated fire in the affected areas both safe shutdown paths on Unit 1 and 2 could be compromised. Given this information the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were put in place in accordance with the plant's Fire Hazard Analysis (FHA) for the degraded penetration in the affected fire areas. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded conditions can be corrected." The degraded fire penetration is located between the turbine deck and the main control room. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-19
50628 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-11-19 15:37 | 2014-11-19 16:42 | 2014-11-19 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "On 11/19/2014, Wolf Creek determined that the alternative shutdown procedure for responding to a fire in the control room does not address all potential operating modes of the credited emergency diesel generator. During the 2014 Triennial Fire Protection Inspection, it was postulated that a loss of offsite power following a fire in the control room would cause the Train B emergency diesel generator (EDG) to start and load to the bus. The fire is also postulated to cause damage to the Train B essential service water (ESW) pump control circuit and prevent the pump from automatically starting and cooling the EDG. Additionally, the fire is postulated to cause spurious operation of another large load that is not normally sequenced onto the bus following a loss of offsite power. This postulated scenario loads the EDG to approximately 53% of its rated load without cooling. This scenario was not considered when developing the control room fire response strategy. Preliminary calculations show that operators have 3.6 minutes to establish cooling prior to the EDG tripping on high jacket water temperature. Performance timing determined that operators would establish cooling in approximately 10 minutes. "Based on this information, it was determined that this condition is unanalyzed and is potentially reportable per 10 CFR 50.72(b)(3)(ii)(B). An hourly fire watch compensatory measure is in place in the control room, consistent with procedural requirements for a Post Fire Safe Shutdown circuit analysis deficiency." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-19
50627 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-11-19 09:43 | 2014-11-19 09:57 | 2015-02-27 | EAL REQUIRED GASEOUS WASTE EFFLUENT RADIATION MONITORS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "The Beaver Valley Power Station (BVPS) Unit 1 Special Particulate, Iodine and Noble Gas (SPING 4) monitors were removed from service for a planned equipment upgrade/replacement. During the replacement process certain Emergency Action Level (EAL) required monitors will not be functional, therefore, alternate methods of monitoring have been placed in effect. The replacement activities are expected to take approximately 60 days. A follow-up notification will be made after the required monitors are returned to service and declared functional. "This is an 8 hour notification per 10 CFR 50.72(b)(3)(xiii). No BVPS Unit 2 systems will be adversely affected by the Unit 1 replacement activity. "The NRC Resident Inspector has been notified." * * * UPDATE FROM PATRICK HARTIG TO CHARLES TEAL AT 1728 EST ON 2/27/15 * * * "The planned equipment upgrade was completed and the Beaver Valley Power Station (BVPS) Unit 1 Particulate, Iodine and Noble Gas (PING) monitors were returned to service and declared functional at 1714 EST on 2/27/2015. "The NRC Resident Inspector has been notified." Notified R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-11-19
50626 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2014-07-10 | 2014-11-19 09:41 | 2014-11-19 | SECURITY REPORT - REQUIREMENTS OF PART 73 NOT MET The licensee discovered that the requirements of 10CFR73.38(d)(6) were not met in preparing a fuel shipment. Notified NRR (Reed, Tran, Boyle). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | MA | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2014-11-19
50625 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-11-18 19:00 | 2014-11-19 03:39 | 2014-11-19 | UNANALYZED CONDITION DUE TO ALL FOUR SAFETY INJECTION ACCUMULATORS INOPERABLE "Following shift turnover from days to nights on 11/18/2014, it was discovered that all (4) of the Safety Injection (SI) Accumulator Outlet Isolation Valve breakers were unlocked and closed. At the time of discovery, 3 of the safety injection accumulator valves were open and 1 was closed for testing. At that time the plant was in MODE 3 at normal operating pressure and temperature. The plant had been performing RCS pressure isolation valve testing prior to shift turnover. The condition was discovered during testing of valves associated with the 'C' safety injection accumulator. "After discovery of the condition, Operations directed that the 'A', 'B', and 'D' SI Accumulator Outlet Isolation Valve breakers be opened and locked. This action was completed by approximately 1930 [CST] on 11/18/2014. "The NRC Resident Inspector was notified." The plant entered T.S. 3.0.3 for approximately 30 minutes while restoring the 'A', 'B' and 'D' accumulators to operable (breakers opened and locked with their associated outlet valves open). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-11-19
50624 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-11-17 06:08 | 2014-11-18 19:25 | 2014-11-18 | EMERGENCY SIREN MALFUNCTION "On November 17, 2014, Miami Dade County notified the site of an alarming single Emergency Plan siren. Following this notification from the County, a courtesy ENS Notification was made to the NRC Operations Center and the State of Florida State Warning Point. The siren has been repaired and returned to service. At no time was there an emergency requiring the siren activation. FPL [Florida Power and Light] did not issue a news release. "This notification is made in accordance with 10 CFR 50.72(b)(2)(xi) for notification to 'other government agencies.' "The NRC Senior Resident has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-11-18
50623 | 0 | TECHNOLOGY FOR ENERGY CORP. |  |  |  |  | 2014-11-18 | 2014-11-18 15:09 | 2015-01-06 | PART 21 - LACK OF PROPER POWER SUPPLY INDICATION The following information was summarized from the report obtained from the vendor via facsimile: Technology for Energy Corporation [TEC] has determined that the Model 1414 Valve Flow Monitoring Systems power supply may not provide proper output voltage contrary to power supply status indicators on the rack. This may result in the power supply not providing necessary power to its associated input sensor. A subsequent loss of the sensor output would result in the inability of the system to indicate any valve flow. Depending on the specific configuration, signals from more than one sensor could be lost on a single failure. This Model 1414 system design dates back to 1979. TEC has not been made aware of any instances of the described failure mode in the 35 year history of the product design, suggesting that the robustness of power supply design and the users periodic maintenance of the system has provided for acceptable continued operation. The potentially affected plants include Clinton Unit 1; Comanche Peak Units 1 & 2; Nine Mile Point Unit 2; Palo Verde Units 1, 2, & 3; River Bend Unit 1; Susquehanna Units 1 & 2; Watts Bar Units 1 & 2. * * * UPDATED FROM DONNA MULLALY TO DONALD NORWOOD AT 1329 EST ON 11/24/2014 * * * After submitting the original Part 21 notification, TEC discovered that Columbia Generating Station had been omitted from the list of affected plants. "The following correction should be applied: The potentially affected plants include Clinton Unit 1; Columbia Generating Station, Comanche Peak Units 1 & 2; Nine Mile Point Unit 2; Palo Verde Units 1, 2, & 3; River Bend Unit 1; Susquehanna Units 1 & 2; and Watts Bar Units 1 & 2." Notified R4DO (Campbell). Notified via E-mail R1DO (Noggle), R2DO (Ehrhardt), R3DO (Duncan) and Part 21 Group. * * * UPDATE FROM DONNA MULLALY TO JOHN SHOEMAKER AT 0820 EST ON 01/06/2015 * * * The following information was received via fax on 12/19/2014: TEC considers this event closed. Notified R1DO (Jackson), R2DO (Hopper), R3DO (Kunowski), R4DO (Pick), and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-11-18
50622 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-11-18 09:00 | 2014-11-18 13:29 | 2014-11-18 | SECONDARY CONTAINMENT INTERLOCK DOORS OPEN SIMULTANEOUSLY "On November 18, 2014, at 0900 [CST], the Shift Manager was notified that two Secondary Containment interlock doors were open simultaneously. The doors were immediately closed and Secondary Containment pressure remained negative throughout the event. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open. As a result entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to Secondary Containment being inoperable. "This event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." The State of Illinois has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-11-18
50621 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-17 | 2014-11-18 11:25 | 2014-11-18 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "On November 17, 2014, the Agency [Texas Department of State Health] was notified by the licensee that a Troxler Model 3430, Gauge Serial No. 26893 containing a cesium-137 source, serial No. 750-92, activity - 0.30 GBq (8 mCi), and an americium-241 source, serial No. 47-23385, activity - 1.48 GBq (40 mCi), was damaged at a field site. The technician had placed the device at a sample location and extended the cesium source into the inspection hole. The technician then noticed a road grader driving directly at him so he ran out of the way and when he turned around the grader had run over the moisture density gauge. The licensee's RSO [Radiation Safety Officer] responded to the scene to inspect and recover the gauge. The device case was severely damaged, but the licensee was able to return the cesium source to the shielded position and secure it in position. The RSO verified the americium source was still in the device. The RSO took the damaged device to their facility for disposal. No individual received any significant additional exposure due to this event." Texas Event #I-9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-11-26
50620 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-11-04 | 2014-11-18 09:32 | 2014-11-18 | AGREEMENT STATE REPORT - I-125 SEED RETRIEVED FROM PATIENT AND THEN LOST The following information was obtained from the State of New York via facsimile: "A radioactive source or I-125 seed used for localization in breast surgery was misplaced by the Pathology Department at Roswell Park Cancer Institute (DOH# 2923). This event occurred on Thursday, October 9, 2014 and the source was officially determined to be lost on November 4, 2014. "Two breast localization seeds (I-125) were not extracted from a specimen on October 9, 2014 by a Clinical Pathology Fellow. The Pathology department did, however, receive written documentation that the seeds were removed from the patient and they were sent with the specimen to the Pathology Department. The seeds were not returned to Nuclear Medicine per Institute Policy. "An extensive search and survey was conducted of Pathology, Nuclear Medicine and Environmental Services areas. One of the two seeds was discovered in trash removed from the Pathology department. Further search and surveys of these areas were repeated but to no avail. Trash and regulated medical waste were surveyed and inspected. Over the course of the next few weeks, Radiation Safety surveyed and explored all radioactive waste in an effort to locate the lost source. Aforementioned search and surveys were again conducted without discovery of the missing seed. It was believed that the missing source would eventually be located in Institute trash or more likely Institute radioactive waste. "All Institute trash and waste is surveyed for radioactive material. The radioactive waste may be stored in various short and long-term storage locations. Unfortunately, the seed was never found and officially declared lost on November 4, 2014. "Corrective Action and Recommendations: 1. The incident was reviewed and discussed with pertinent Pathology staff. A training oversight was discovered and Pathology Department Fellows are now trained to anticipate radioactive seeds in breast surgical specimens and to remove them prior to surgical specimen evaluation. (Required Corrective Action) 2. Radiation Safety and Environmental Services have emphasized the importance of monitoring all trash and regulated medical waste during the annual in-service conducted on August 6, 2014 and again on October 29, 2014. (Required Corrective Action) 3. Any further information regarding this matter will be communicated to the Bureau of Environmental Radiation Protection, NYS DOH [New York State Department of health]. (Required Corrective Action)" New York State Event Report Number: NY-14-05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-11-26
50619 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-11-14 16:00 | 2014-11-17 13:16 | 2014-11-18 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE LOST DURING SHIPPING The following was received from the State of Nebraska via fax: "On November 4, 2014 Simon Contractors, a Nebraska licensee, shipped a Troxler model 3450, s/n 355 containing 8 mCi of Cs-137 (s/n 750-5840) and 40 mCi of Am-241:Be (s/n 47-3188) to Qal-Tek Associates by YRC Freight. Qal-Tek is located in Idaho Falls, ID. YRC Freight picked up the gauge from Simon Contractors in North Platte, NE on November 4, 2014. YRC transported the gauge to their terminal in Kansas City, MO. The gauge was expected to arrive at Qal-Tek on November 11. Since the gauge was not delivered, Qal-Tek contacted YRC on November 13. On November 14, YRC contacted Qal-Tek and YRC considered the gauge as lost. At 1630 [CST] on the 14th, Qal-Tek contacted Simon Contractors and notified them of the status of the gauge. Qal-Tek also contacted the NRC of the event. On Monday, November 17 at 0815 [CST], Simon called the Nebraska Health and Human Services, Office of Radiological Health to report the missing gauge." This is the same incident as NRC Event # 50615 (reported by Qal-Tek). * * * UPDATE FROM JIM DEFRAIN TO CHARLES TEAL AT 0920 EST ON 11/18/14 * * * The gauge has been located by YRC Freight. Notified R4DO (Hagar) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2014-11-25
50618 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-11-15 03:53 | 2014-11-15 08:14 | 2014-11-15 | VALID ACTUATION OF THE REACTOR PROTECTION SYSTEM FOR ABNORMAL ROD POSITION INDICATION "This notification is being made as required by 10CFR 50.72(b)(3)(iv)(A) due to control room operators opening the Farley Nuclear Plant Unit 2 reactor trip breakers via the main control board hand switch during reactor startup procedures. This is a valid actuation of the reactor protection system. The reactor was not critical at the time the reactor trip breakers were opened. "While withdrawing control rods for reactor startup and low power physics testing with control bank C at approximately 50 steps, Digital Rod Position indication for one of the control rods (M12) changed to 90 steps. The control room operators stopped withdrawing rods and entered FNP-2-AOP-19 (Malfunction of the Rod Control System). The reactor trip breakers were opened at 0353 CST. All rods inserted as expected. All other systems functioned normally. The plant is stable at normal operating pressure and temperature. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-11-15
50617 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-11-05 07:29 | 2014-11-14 23:17 | 2014-11-17 | AGREEMENT STATE REPORT - NON-CONSERVATIVE RADIOLOGICAL SCAN FOR BUILDINGS RELEASED FOR USE The following report was received via e-mail: "The Department of the Navy has provided the California Department of Public Health with a cover letter and report dealing with nonconservative scan speeds being used for the release of buildings on the Hunters Point Naval Facility. Some of the buildings involved are under NRC jurisdiction and some under State of California jurisdiction. The buildings involved that are NRC jurisdiction are Parcel B (103, 113, 113A, 130, 140, 146), Parcel C (203, 214, 241, 271, 272), Parcel E (half of Bldg 439, half of Bldg 810), and Parcel G (351, 351A, 365, 366, 401, 411). We are informing NRC of this issue so you can independently review this report and take whatever action they deem necessary. The buildings that are under State jurisdiction are all in Parcel E (406, 414, 521, half of Bldg 439, and half of Bldg 810). RHB will schedule additional surveys as required to verify the safety of release of these buildings. RHB does not perceive any particular threat to the public or workers from these buildings but an evaluation should be done just to be sure." California Event #: 111414 * * * RETRACTION FROM JOHN FASSELL TO DANIEL MILLS AT 1308 EST ON 11/17/14 * * * This event is being retracted, because it has been determined that it is not a 24-hr reportable event. Notified R1DO (Jackson), R4DO (Hagar), NMSS Events Notification (Email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-11-24
50616 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-11-14 10:45 | 2014-11-14 18:12 | 2014-11-14 | AGREEMENT STATE REPORT - TRUCK CARRYING RADIOGRAPHY CAMERA INVOLVED IN TRAFFIC ACCIDENT The following was received from the State of Louisiana via email: "IRISNDT-LA was transporting a SPEC Model 300 exposure device, S/N 004, loaded with Co-60 greater than Cat. 2 concerns, S/N C 60-49. The exposure device and source were being returned to IRISNDT, 905 GA Ave., Deer Park, TX. Texas License TX L0 6435. They were driving in the flow of traffic when the utility trailer, loaded with the exposure device was rear-ended by a pick-up truck at 1030 [CST]. The LSP [Louisiana State Police] and LDEQ [Louisiana department of Environmental Quality] responded as well as the LA RSO and the CRSO who was in town on other business. A field assessment was conducted at the site and then the device was transported to the New Orleans, LA office. Additional evaluations and wipe test were performed and sent for evaluation. It appears that no shielding or radiation containment was compromised. The exposure device is being transported to Source Production & Equipment, the manufacturer, for a more extensive evaluation. All personnel involved with the radioactive source during this incident were T&Red by IRISNDT under their IC security procedures. LA and TX Licenses and other documents were with the device. All radioactive sources are secured at the New Orleans office. No radioactive material was released or determined to be leaking at the time of this preliminary report. The radiography equipment will be transported to a location where an extensive evaluation of the equipment will be conducted. The outward appearance does not indicate there is severe or excessive damage to the exposure device resulting in a radioactive material release. The two carded radiographers involved in the traffic accident were taken for a medical evaluation and released with no serious injuries. Updates will be provided when 'new' information is available." Louisiana incident # LA1400011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-11-24
50615 | 0 | QAL-TEK ASSOCIATES, LLC |  |  |  |  | 2014-11-14 12:50 | 2014-11-14 15:56 | 2014-11-17 | MOISTURE DENSITY GAUGE LOST IN TRANSIT Qal-Tek Associates, LLC reported that a Troxler Model 3450 Moisture/Density Gauge (Serial # 355) was lost in transit by the shipper. The device was being shipped from the owner, Simon Contracting in North Platte, NE, to Qal-Tek for repair. The device contains 8mCi Cs-137 and 40 mCi Am/Be. This is the same incident as NRC Event # 50619. * * * UPDATE ON 11/17/14 AT 1703 EST FROM GLENN SAWTELLE TO DONG PARK * * * The following was received from the licensee via email: "The event 50615 initiated last Friday, November 14th has been resolved. The shipping company YRC Freight notified Qal-Tek Associates and Simon Consultants today, November 17th, that the Troxler nuclear density gauge reported 'lost' in this event was located in a YRC Hazardous Materials storage trailer. Apparently, the shipping information had separated from the device case. The NDG [Nuclear Density Gauge] was not damaged in any way and has all other Radioactive Materials labels intact. The NDG will be shipped to the Qal-Tek office in Idaho Falls, ID, for previously anticipated service. The Nebraska state Radiation Protection authorities have been informed." Notified R1DO (Jackson), ILTAB and NMSS Events Notification via email. Notified Canada via facsimile. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-11-24
50614 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-11-13 15:12 | 2014-11-14 13:18 | 2014-11-14 | MEDICAL TREATMENT OF CONTAMINATED INDIVIDUAL "An employee with a chemical burn on his left wrist reported to the onsite dispensary located within the restricted area. First aid was administered. A whole body radiological survey of the employee and plant clothing was performed; the maximum amount of contamination present was on the lower legs of the employee's plant issued coveralls, 2,300 dpm/100cm2. The employee was able to return to work following treatment. The employee remained inside the Restricted Area over the entire course of the event." The licensee notified NRC Region-2 (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-11-14
50613 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-13 | 2014-11-14 12:01 | 2014-11-14 | AGREEMENT STATE REPORT - LOST CHECK SOURCE The following was received from the State of Texas via email: "On November 14, 2014, the agency [Texas Department of State Health Services] was notified by the licensee, Weatherford International, that a 10 microCurie Americium-241 source [Serial # A1-531] was lost from its R&D facility in Houston, TX. The source was identified as missing during an inventory on 11/10/2014. After searching the company's R&D facility, the loss was reported to the [Texas] Department of State Health Services. The licensee's RSO suggested the source may have been swept out with trash. The source was last verified to be in its storage location December of last year [2013]. The company keeps a log of source usage and searched each use location in the building. The source is only used in the same building where it is stored." Texas incident # I-9252 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-11-24
50612 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-11-13 09:00 | 2014-11-14 10:52 | 2014-11-14 | AGREEMENT STATE REPORT - FIRE IMPACTING LICENSABLE MATERIAL The following report was received from the State of Tennessee via email: "[Tennessee Department of Environment Conservation] TDEC was notified on 11/13/14, by a representative of [Toxco, Inc. d/b/a Toxco Materials Management Center] TMMC that a fire had occurred [at approximately 0900 EST] in an area in Building B where evaporation of liquid radioactive wastes was being conducted. Four employees attempted to extinguish the fire but were unsuccessful. The City of Oak Ridge fire department responded to the site and extinguished the fire. Four TMMC employees were sent to the local hospital for smoke inhalation related symptoms and are being evaluated for potential intake of radioactive materials. Air sampling of the building and area were performed during the event. The samples are being evaluated for results and consideration of potential impacts. [Tennessee] State inspectors are onsite investigating. The quantity of mixed fission product involved is unknown at this time. [Tennessee Department of Health] DRH inspectors are onsite and detailed information will be forthcoming." State Event Report ID NO: TN-14-211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-11-24
50611 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-11-13 | 2014-11-13 15:47 | 2014-11-13 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of California via email: "On November 13, 2014, at approximately 0648 [PST], the RSO of Heider Engineering Services, Inc., RML #6463-36, contacted Cal OES [California Office of Emergency Services] concerning the moisture/density gauge, Troxler, Model 3430, serial number 63801 (Cs-137, 0.3 GBq, Am-241, 1.50 GBq) that had been stolen from a transport vehicle in front of a private residence at 140 North Shasta Way, Upland, CA 91786, between the evening of November 12, 2014 and approximately 0600 [PST] November 13, 2014 when the Authorized User left his home to go to the worksite. The Authorized User has contacted Local Law Enforcement officials in Upland, CA to request an investigation of the private residence where the Troxler radioactive gauge was taken and to take the report of the authorized user that was in possession of the gauge prior to the theft. A copy of the theft report will be sent to RHB Brea [California Radiological Health Branch -Brea] as part of this report. The RSO will utilize local papers to attempt to retrieve the stolen gauge as well as notifying local servicing vendors of radioactive gauges to be alert of the serial number of the stolen gauge in case it turns up for any of their services. "The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. This is being reported to the NRC Operations Center as a 24-hour report under 10CFR30.50(b)(2) since the radioactive gauge has been stolen and it cannot be determined what condition the sources are currently in." CA 5010 NUMBER 111314 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-11-21
50610 | 0 | FLOWSERVE |  |  |  |  | 2014-11-13 | 2014-11-13 14:45 | 2014-11-13 | PART 21 - MILLER AIR CYLINDER SEALS DEDICATION ISSUE The following was received from the licensee via fax: "This is to notify the US Nuclear Regulatory Commission that, in accordance with the provisions of 10 CFR Part 21, we have identified a potential issue and are submitting our evaluation of the event. "Description: Flowserve supplied a quantity of two Size 6 Class 900 Anchor Darling Double Disc gate valves with tag numbers CV-3027 and CV-3056 to Palisades Nuclear Plant in 2007. The valves are actuated by Miller air cylinders and have a safety function to maintain the system pressure boundary by remaining fully open during injection and to subsequently move to the fully closed position upon receipt of a recirculation actuation signal. This Miller air cylinder is not spring-assisted and thus uses air to perform the safety-related function. As such, the air cylinder, any tubing, and seals associated with the air system would also be considered safety related. When the valve was tested prior to shipment, the actuator was dedicated as an assembly and performed adequately. However, the seals containing the air system in the Miller Air Cylinder and Flow Control valve were not individually dedicated as a basic component - that is, the seal material was not verified. There is no indication that the material is defective, but in addition to the functional testing at the Flowserve facility, the material of the seals should have been checked and verified. The Flow Control Valve was ordered with Nitrile (Buna-N) seals while the Air Cylinder was ordered with Viton seals. While the seal materials were not verified, the only possible seal material for these items would have been Viton, Buna-N, or EPR. "Scope: Flowserve has performed a review of all other air cylinders provided from the Raleigh facility over the last 12 years and found no other instances of this issue. Therefore, the scope of this notification is limited to only the two tag numbers 01-3027 and CV-3056 at Palisades Nuclear Plant. "Proposed Action: Flowserve will provide safety-related replacement seal kits for all seals containing the air system for the CV-3027 and CV-3056 valves. This will be sent on a zero dollar purchase order to Palisades Nuclear plant and will be completed as soon as Flowserve receives the purchase order." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-11-13
50609 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-12 12:45 | 2014-11-13 11:58 | 2014-11-13 | AGREEMENT STATE REPORT- LOST AND THEN FOUND RADIOGRAPHY CAMERA The following information was received from the State of Texas via email: "On November 13, 2014, the licensee notified the Agency [Texas Department of State Health Services, Radiation Branch] that on November 12, 2014, at approximately [1500 CST] it was notified by local law enforcement that one of its industrial radiography cameras had been found on the side of a road approximately 3 miles from the licensee's facility. The licensee determined that the SPEC 150 camera containing a 38 Curie Iridium-192 source had fallen from one of its trucks at approximately [1245 CST] while in route to a temporary job site. The camera had not been secured inside the truck before it left the licensee's facility but had been left on the tailgate. The licensee retrieved the camera and there was no apparent damage to the device. There are no known exposures resulting from this event. Further information will be provided as it is obtained in accordance with SA- 300." Notified DHS SWO, DOE, FEMA, HHS, NICC, USDA and EPA. Notified FDA, NuclearSSA and DNDO-JAC via email. Texas Incident: I-9251 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-11-21
50608 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-11-09 | 2014-11-13 10:54 | 2014-11-13 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE GUIDE TUBE CRUSHED PREVENTING SOURCE FROM RETRACTING The following report was received from the State of Colorado via email: "Event description: On 11/9/14, the licensee was working at Denver International Airport when an object fell onto the guide tube damaging it in such a way that the source could not be retracted. The radiography crew contacted the RSO [Radiation Safety Officer] who arrived at the scene, cut the guide tube open, removed the drive cable and retracted the source. At all times during the incident, the public dose line was maintained therefore the RSO believes that there were no exposures to the public above dose limits. Additionally doses to radiation workers were minimal. "The RSO notified the [Colorado Department of Health] Department on 11/9/14, however they used the wrong phone number and left a message for someone in a different division than the Radiation Program. The licensee contacted the [Colorado State] Radiation Program at approximately 8 am on 11/10/14 to describe the incident. "The licensee is preparing a detailed report to submit to the [Colorado Department of Health] Department." Colorado Event Report ID No.: CO14-I14-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-11-21
50607 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2014-11-12 15:48 | 2014-11-12 18:31 | 2014-11-12 | MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR WATER LEVEL "On November 12, 2014 at 1548 [EST], Unit 2 was manually tripped due to a lowering 2B steam generator level caused by the spurious (slow) closure of 2B Main Feedwater Isolation Valve, HCV-09-2B. "All CEAs [control element assemblies] fully inserted into the core. All safety systems responded as expected with the 2B Auxiliary Feedwater Actuation System Channel 2 (AFAS 2) actuating on low 2B steam generator level. Decay heat removal is from main feedwater to the 2A steam generator and manual control of auxiliary feedwater to the 2B steam generator, with steam bypass to the main condenser. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the AFAS 2 actuation." During the transient, no relief or safety valves lifted. The grid is stable and the plant is in its normal shutdown electrical lineup at normal operating pressure and temperature. The cause of the feedwater isolation valve malfunction is under investigation. There was no effect on Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-11-12
50606 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2014-11-12 08:57 | 2014-11-12 14:42 | 2014-11-12 | NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed supervisor tested positive for alcohol on a follow-up fitness-for-duty test. His access to the facility was terminated. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-11-12
50605 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2014-10-14 | 2014-11-12 13:02 | 2014-11-12 | MISPLACED RADIOACTIVE SHIPMENT A shipment consisting of eight boxes of radioactive material was shipped from Albuquerque, New Mexico to Port Harcourt, Nigeria on 9/29/2014. The shipment was confirmed to have arrived at Lagos Airport in Nigeria on 10/14/2014, but it didn't clear customs and it was not transported to its final destination in Port Harcourt, Nigeria. The radioactive material consisted of: "2 boxes 18"x18"x15" Iridium-192, 320 mCi Total (160mCi each box) "3 boxes 18"x18"x15" Scandium-46, 120 mCi Total (40mCi each box) "3 boxes 18"x18"x15" Antimony-124, 120 mCi Total (40mCi each box)" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2014-11-20
50604 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-11-12 02:02 | 2014-11-12 10:44 | 2014-11-12 | NO FUNCTIONAL SMOKE DETECTION CAPABILITY IN CONTAINMENT "At 0202 [CST] on November 12, 2014, it was determined that Unit 2 had no functional smoke detection capability in the containment. During post modification testing on the smoke detection system, it was discovered that both trains of detection were not functional. Required compensatory measures have been established. Since a fire in the containment is an entry condition for the site's Emergency Plan, this is considered an unplanned loss of emergency assessment capability and is being reported per 10 CFR 50.72(b)(3)(xiii). "[Farley] Condition Report: 892818. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-11-12
50603 | -1 | PARKVIEW HEALTH |  |  |  |  | 2014-11-11 | 2014-11-11 16:25 | 2014-11-21 | GYNECOLOGICAL BRACHYTHERAPY TREATMENT TO LARGER AREA THAN PRESCRIBED AREA A patient was prescribed four 550 cGy gynecologic brachytherapy treatments totaling 2200 cGy. The third treatment prescribed a treatment area of 5 cm instead of the actual treated area of 7 cm. The patient was released after the outpatient treatment. The hospital in attempting to notify the physician of the incident. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM YUENIAN ZHANG TO HOWIE CROUCH AT 0929 EST ON 11/21/14 * * * Based on the results of an onsite inspection from NRC Region 3 Inspectors (Craffey and Lambert), it was determined that this event did not meet the regulatory report threshold and is being retracted by the licensee. Notified R3DO (Peterson) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2014-11-19
50602 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2014-11-06 19:00 | 2014-11-07 14:02 | 2015-06-08 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE/DENSITY GAUGE The following report was received from the State of Washington via email: "Associated Earth Sciences reported to the State of Washington, Department of Health, Office of Radiation Protection that a Troxler portable gauge, model 3411, serial number 11272, containing 0.1 Ci Cs-137 and .005 Ci Am/Be, was stolen from the back of a pickup while parked overnight at a gauge user's resident apartment complex in Bothell, Washington. The gauge was last seen at 1900 PST the previous night and discovered missing at 0730 PST on November 7. "The gauge was located in a locked black plastic tool box secured in the bed of the pickup. The tool box containing the portable gauge was stolen from the bed of the truck. Two cables and locks were reported used to secure each side of the tool box to the bed of the truck. It was unclear how the tool box was removed from the truck bed. The licensee reported no cut lock or cable was left behind. It was also unclear if the tool box lid was locked with the same locks and cables used to secure the tool box to the truck. The licensee was asked to provide a photo of their system used to secure the gauge and tool box to the truck. The gauge transport box inside the tool box was reported locked with a single lock. The handle of the gauge was also reported locked. "The gauge user was asked why the gauge was not returned to the licensed storage location at the end of the day per the condition in the license. The user reported the job site was close to his house and he wanted to avoid the hour and a half drive to the licensed facility to check out a gauge. The theft was reported to the Bothell Police Department and police report #14-25445 was made. "A follow-up with the licensee will be conducted to investigate possible citations for not returning the gauge for overnight storage in the licensed storage location and proper security for transporting the gauge in a vehicle." State of Washington Incident Number: WA-14-045. * * * UPDATE AT 1358 EDT ON 6/8/2015 FROM STEPHEN MATTHEWS TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "As of June 8, 2015, the gauge has not been located. Associated Earth Sciences sent [Washington Office of Radiation Protection] a letter dated June 5, 2015 documenting their corrective actions, which consisted of re-training their portable gauge operators, specifically for transportation security. Since the theft occurred over six months ago we feel there is no way to avoid closing this incident as of today, June 8, 2015." Notified the R4DO (Werner), NMSS Events Resource (Email), Canada (Fax), and ILTAB (Email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-11-17
50601 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-11-07 08:47 | 2014-11-07 11:13 | 2014-11-07 | AUTOMATIC REACTOR SCRAM DUE TO LOSS OF FEEDWATER "The Perry Nuclear Power Plant experienced an automatic reactor scram due to a loss of feedwater, which resulted in receiving valid reactor vessel water Level 3 and Level 2 initiation signals. The High Pressure Core Spray system and the Reactor Core Isolation Cooling system started and injected. Reactor water level and pressure have been stabilized in the required bands. The motor feed pump automatically started and is being used to control reactor vessel water level. The High Pressure Core Spray and Reactor Core Isolation Cooling systems have been returned to the standby mode. As a result of receiving a reactor vessel water Level 2 signal a Balance of Plant containment isolation signal was received. All systems isolated as required and the plant is restoring isolated systems in accordance with plant procedures. "During the scram, all rods fully inserted into the core. Decay heat is being removed via turbine bypass valves to the main condenser. The electrical grid is stable and is supplying plant loads. An emergency diesel generator [Division 3 High Pressure Core Spray] started, as designed, as a result of the reactor vessel water Level 2 signal. No safety relief valves lifted as a result of the transient. "The plant is stable with cooldown and depressurization to Mode 4 in progress. The cause of the loss of feedwater is under investigation. "The NRC Resident Inspector has been notified. The State of Ohio and local officials will be notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2014-11-07
50600 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2014-11-06 11:16 | 2014-11-06 18:22 | 2014-11-07 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO DROPPED CONTROL ELEMENT ASSEMBLY "On November 6, 2014 at 1116 Mountain Standard Time (MST), Control Element Assembly (CEA) 15 dropped fully into the core while all other CEAs remained fully withdrawn. Limiting Condition for Operation (LCO) 3.1.5 Condition A was entered for one CEA misaligned from its group which requires restoration of the CEA within 2 hours. An initial power reduction was performed upon receipt of the deviation in accordance with technical specifications. The CEA could not be aligned within 2 hours and LCO 3.1.5 Condition C was entered at 1316 MST which requires entry into Mode 3 within 6 hours. Power reduction continues as necessary to comply with technical specifications. "No major equipment was inoperable prior to the event that contributed to the event. No emergency classification was required per the Emergency Plan. No automatic essential safety feature actuations occurred and none were required. The Emergency Diesel Generators did not start and were not required. Safety related buses remain energized. The offsite power grid is stable. Other LCOs were entered as required by technical specifications." The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY RYAN LANE TO JEFF ROTTON AT 0012 EST ON 11/07/2014 * * * "Efforts to repair the CEA control system and realign CEA 15 with the other CEAs in its regulating group were unsuccessful. Shutdown of Unit 2 was completed at 1636 [MST] in accordance with normal operating procedures to comply with the shutdown requirements of LCO 3.1.5 Condition C. Unit 2 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. All equipment responded as expected with the exception of steam generator # 2 economizer feedwater regulating valve which remained 3 percent open. The economizer feedwater isolation valves to both steam generators were manually closed to isolate the economizer feedwater flow paths. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. "The NRC Resident Inspector has been informed of the Unit 2 shutdown." Notified R4DO (Miller) | 0 | 20 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-11-06
50599 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2014-11-05 | 2014-11-06 15:23 | 2014-11-06 | AGREEMENT STATE REPORT - LOST AND RECOVERED RADIOGRAPHY CAMERA The following was received from the State of Oklahoma via email: "Hi-Tech Testing Service, an Oklahoma industrial radiography licensee based in Mustang, Oklahoma, reports that they temporarily lost custody of an industrial radiography camera containing an iridium source. At about 1:40 PM today, the Hi-Tech RSO reported by phone to DEQ [Department of Environmental Quality] that while doing radiography overnight at a compressor station near Perkins, Oklahoma, radiographers unintentionally left the radiography camera (with source inside) at the site. The error was discovered this morning when an inspector from Hi-Tech's client found the camera at the site. The client contacted Hi-Tech, who recovered the camera and have it in their possession. They report no evidence that the camera was tampered with or that there was an overexposure involved. DEQ will do an investigation of the incident. "The above is very preliminary, based on phone reports from the licensee. It is basically all the information known to DEQ at this time. It will be updated as more information becomes available." THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2014-11-14
50598 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-11-05 16:25 | 2014-11-06 13:41 | 2014-11-06 | FITNESS FOR DUTY - LICENSED OPERATOR IN VIOLATION OF THE FITNESS FOR DUTY POLICY A licensed operator has been found in violation of the Northern States Power Minnesota Fitness for Duty Policy. The individual's access to the plant has been suspended and the operator has been removed from duty. The NRC Resident Inspector has been informed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2014-11-06
50597 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2014-11-05 19:38 | 2014-11-06 04:30 | 2014-12-22 | SIX UNIT 2 CONTROL ROD DRIVE HYDRAULIC CONTROL UNITS INOPERABLE "Six (6) U2 CRD [Control Rod Drive] HCU [Hydraulic Control Unit] accumulators were identified with riser brackets that were installed incorrectly. This issue impacts U2 CRD HCU accumulators only. The incorrect riser bracket installation could challenge the ability of the CRD hydraulic control unit to perform its design function during a seismic event. "Identified U2 control rods associated with HCU accumulators that had riser brackets installed incorrectly were declared inoperable. This condition has been corrected since initial identification, restoring all control rods to operable status. Reference IR 2407342. "This notification is made pursuant to 10CFR 50.72(b)(3)(v) regarding the reportability of multiple failures that could have prevented fulfillment of a safety function. "The NRC Resident Inspector will be notified." * * * RETRACTION FROM MATT SEELEY TO HOWIE CROUCH AT 1144 EST ON 12/22/14 * * * "The purpose of this notification is to retract the ENS notification made on November 6, 2014 (ENS 50597). An Engineering Evaluation has determined that the function of the affected U2 CRD HCU Accumulators was not affected as discussed in Chapters 6 and 15 of the Updated Final Safety Analysis Report. Therefore, the threshold for reporting the issue as an event or condition that could have prevented the fulfillment of a safety function was not met (NUREG 1022, Revision 3, Event Report Guidelines Section 3.2.7). "The NRC Resident Inspector has been notified." Notified R3DO (Dickson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2014-11-06
50596 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-11-05 13:10 | 2014-11-05 20:37 | 2014-11-05 | UNANALYZED CONDITION REGARDING APPENDIX R PROCEDURES "On November 5, 2014, during a review of recommended procedure changes, TVA determined procedures for Appendix R fires did not include all the required operator manual actions to address inadvertent opening of the pressurizer spray valves. Failure to secure the reactor coolant pumps or auxiliary spray would invalidate Appendix R assumptions for not overfilling the pressurizer during an Appendix R event. Failure to take all the required actions would place WBN [Watts Bar Nuclear] Unit 1 in an unanalyzed condition. "The three affected procedures have been revised on 11/5/2014, to correct the condition. "The NRC Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-11-05
50595 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-11-05 11:15 | 2014-11-05 17:17 | 2014-11-05 | SECONDARY CONTAINMENT ZONES 2 AND 3 UNINTENTIONALLY CROSSTIED "On November 5, 2014 at 1115 [EST], Secondary Containment Zone 3 (Unit 1 & 2 Reactor Building) was unintentionally crosstied to Secondary Containment Zone 2 (Unit 2 Reactor Building) for several seconds during passage of personnel through a personnel airlock. Secondary Containment Zone 2 & Zone 3 ventilation remained in service and stable. "LCO 3.6.4.1 was entered and exited based on the prohibited crosstie of Secondary Containment Zones. Tech Spec Secondary Containment Operability requires that at least one door remain closed for airlocks where two doors are provided when an access opening between Secondary Containment Zones is being used for exit and entry. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-11-05
50594 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-10-26 19:35 | 2014-11-05 14:04 | 2014-11-05 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - ALERT DECLARATION NOT MADE DURING EVENT INVOLVING URANIUM HEXAFLUORIDE LEAK "On 10/26/14, Honeywell declared a 'Plant Emergency' at 1935 [CDT] in accordance with the Honeywell Emergency Response Plan due to a [Uranium Hexafluoride] UF6 leak on a primary cold trap. The incident was mitigated and the 'All clear' was declared at 0216 on 10/27/14. There were no injuries related to the incident. After review of additional observations and other evidence not directly involved with the response, Honeywell has determined that the event should have been upgraded at 1942 [CDT] on 10/26/14, to an 'Alert' classification per our classification criteria. This notification constitutes the NRC notification related to the incident. Honeywell is currently investigating the cause of the incident." The licensee has notified NRC Region II and will notify state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | IL | FUE | [5 empty] | 0 | 2014-11-05
50593 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2014-11-04 11:00 | 2014-11-04 18:00 | 2014-11-04 | UNIT 2 HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE "On November 4, 2014, at 1100 [CST], LS 2-2365 (HPCI Turbine Inlet Drain Pot Level Switch) was determined to be inoperable during planned testing. HPCI was inoperable (for the planned testing) at the time of discovery. The function of LS 2-2365 is to detect a failure of the HPCI steam trap (i.e., outlet of the HPCI inlet drain pot) by providing a control room alarm and opening an alternate drain path. "HPCl is a single train safety system and this notification is being made in accordance with 10CFR50.72 (b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-11-04
50592 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-11-03 | 2014-11-04 10:41 | 2014-11-04 | AGREEMENT STATE REPORT - DAMAGED GUIDE TUBE ON INDUSTRIAL RADIOGRAPHY EQUIPMENT The following was received from the State of Texas via email: "On November 3, 2014, the Agency was notified by the licensee's Radiation Safety Officer (RSO) that one of his crews was unable to retract a 34.9 curie cobalt-60 source into a QSA Global 680A exposure device. The crew was performing radiography at a field site [in Houston, TX] using a magnetic stand to support the guide tube and collimator. The stand fell on the guide tube crimping the guide tube in two places about one inch apart. The radiographer attempted to retract the source, but it would not go past the crimped section of the guide tube. The radiographer returned the source to the collimator. "One of the radiographers contacted the site RSO(SRSO). A recovery team was sent to the location to retrieve the source. The team slid a steel plate below the collimator. The guide tube was pulled to free the collimator from its holder causing it to drop onto the steel plate. The collimator was approached from the shielded side and using a pair of tongs, the collimator was rolled to face the outlet port towards the steel plate. Six bags of lead shot were placed on the collimator. The dose rate at the crimped section of the guide tube was then measured at 200 millirem per hour. Additional bags of lead shot were placed on the collimator. The licensee's first attempt to remove the crimps in the guide tube using channel locks was unsuccessful. The licensee then removed the outer coating on the guide tube in the areas the tube was crimped and then used channel locks to remove the crimps. This was successful and the source was returned to the fully shielded position. "The highest exposure to any individual involved in the event was seven millirem. The licensee reported no exposures were received to members of the general public due to this event. The guide tube was taken out of service. The exposure device and crankout device were inspected and returned to service. The source was leak tested, but the results have not been received. " Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-11-12
50591 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-11-03 08:00 | 2014-11-03 16:56 | 2014-11-03 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee with an injured hand and knee reported to the on-site dispensary this morning after slipping and falling in a gravel area. First aid was administered. A whole body radiological survey of the employee and plant clothing was performed; the maximum amount of contamination present was on the upper back of the employee's plant issued coveralls, 1,700 dpm/100cm2. Upon the completion of first aid activities, the employee routinely exit monitored from the facility and reported to an off-site medical facility for further evaluation." No additional contamination found on the employee. The licensee has notified NRC Region II (Hartland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-11-03
50590 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-11-03 12:40 | 2014-11-03 13:58 | 2014-11-03 | AGREEMENT STATE REPORT - RADIOPHARMACEUTICAL PACKAGE WITH EXTERNAL CONTAMINATION The following information was obtained from the State of Ohio via email: "At 12:40 pm [EST] on Nov. 3, 2014, the RSO [Radiation Safety Officer] from the University of Cincinnati Medical Center called the ODH-BRP [Ohio Department of Health - Bureau of Radiation Protection] to report receipt of a contaminated package that exceeded the contamination levels for reporting that occurred that morning. The 300 centimeters squared wipe of the outside of the package yielded 1433 dpm per centimeters squared. The wipe on the inside of the package yielded a contamination rate of 29,244 dpm per centimeters squared. The TI [transportation index] listed on the package was 0.9, and the licensee measured 2.0 at the time of the package receipt. The package was a shipment of two doses of 15 mCi of F-18 FDG with a reference time of 1100 [EST]. The receiving licensee has placed the package in storage for radioactive decay. "The shipping nuclear pharmacy licensee, PETNET, was notified by the University of Cincinnati Medical Center of the package contamination. The licensee's courier arrived back at the pharmacy for vehicle and personnel contamination [survey] at approximately 1310 [EST]. The driver and the vehicle were surveyed and did not have any measurable contamination. "Receiving licensee University of Cincinnati Medical Center Ohio license number 02110 31 0001 Cincinnati, OH "Shipping licensee PETNET Solutions Ohio license number 02500 31 0001 Cincinnati, OH" Ohio event report number 2014-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-11-11
50589 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2014-11-02 12:45 | 2014-11-03 11:12 | 2014-11-03 | OFFSITE NOTIFICATION DUE TO WORKER INJURY "On Sunday, November 2, 2014 at 1245 PST, a process operator driving a motorized transport cart sans any load was making a turn and lost his balance and put his foot on the floor. The cart caught his ankle under the standing platform for the driver. The process operator broke his ankle as a result. "The process operator was surveyed by Health and Safety Technicians, found to be free of any radioactive contamination. The process operator was then transported to the local hospital by ambulance. "This industrial accident is reportable to the Washington State labor and Industries and the OSHA toll free hotline was also called." "The NRC is being informed of this event under the requirements of 10CFR70 Appendix A criterion (C). 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a new release is planned or notification of other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification.'" The NRC Regional Office was notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2014-11-03
50588 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-11-02 07:20 | 2014-11-02 12:26 | 2014-12-31 | OPERATIONS SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "On November 2, 2014 EST, the bus providing power to the Health Physics emergency HVAC system for climate control tripped unexpectedly and has been out of service for greater than 30 minutes. The Health Physics emergency HVAC system for climate control is required for functionality of the Operations Support Center (OSC), which is a required emergency response facility (ERF). Actions to determine the cause of loss of 1R24-S030 Load Center and to return ERF to functional status are in progress with high priority. In the interim, the backup OSC remains fully functional and capable of providing the required support as defined in the Hatch Emergency Plan and emergency implementing procedures. "This notification is being made in accordance with the plant's Technical Requirements Manual Specifications to make the notification within 8 hours in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the unplanned loss of an emergency response facility. An update will be provided once the OSC has been restored to normal operation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOHN MITCHELL TO HOWIE CROUCH AT 2126 EST ON 11/2/14 * * * Power was restored to the 1R24-S030 Load Center at 1955 EST. At 2038 EST, power to the Health Physics emergency HVAC system was restored. The OSC was returned to service at 2120 EST. The licensee has notified the NRC Resident Inspector. Notified R2DO (Blamey). * * * RETRACTION FROM KENNY HUNTER TO DANIEL MILLS AT 1641 EST on 12/31/14 * * * "In accordance with NUREG 1022, Revision 3, Supplement 1, the NRC endorsed NEI 13-01, 'Reportable Action Levels for Loss of Emergency Preparedness Capabilities,' such that 'if a licensee has a 'backup ERF' that is capable of performing the functions of the primary facility, the licensee's emergency assessment capability is not significantly impaired if the primary facility is not available.' Based on this information this condition is not reportable. "Although NUREG 1022, Rev. 3, Supplement 1 did not require an event notification report to be made, an initial notification was generated based on requirements within licensee control documents. These documents have been updated to reflect the guidance provided in the supplement to NUREG 1022. This report is therefore being retracted in accordance with NUREG 1022, Rev. 3, Supplement 1 since a backup ERF remained fully functional and capable of providing the required support during the event. "The licensee notified the NRC Resident Inspector." Notified R2DO (Hopper). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-11-02
50587 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-11-01 02:48 | 2014-11-01 05:03 | 2014-11-01 | DUAL UNIT MANUAL REACTOR TRIPS DUE TO LOWERING CONDENSER VACUUM AND DEGRADED FOREBAY "On November 1, 2014, at 0249 [EDT], DC Cook Unit 1 reactor was manually tripped and at 0248 [EDT] DC Cook Unit 2 was manually tripped due lowering condenser vacuum caused by degraded forebay conditions (observed thick grass and sand). U-1 and U-2 entered Abnormal Operating Procedure for Degraded Forebay on November 1, 2014 at 0153 [EDT]. Conditions degraded in U-1 and U-2 until all but 2 screens in each unit were tripped on overload and main condenser vacuum was lowering. U-1 and U-2 met criteria in the Degraded Forebay procedure to remove the units from service and remove all circulating water pumps from service. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The electrical grid is stable. Unit 1 and Unit 2 are being supplied by offsite power. All control rods fully inserted in both units. Decay heat is being removed by steam generator PORVs. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip with the exception of U-1 turbine driven auxiliary feed pump. DC Cook Unit 1 and Unit 2 remain stable in Mode 3 while conducting the post trip review. No radioactive release is in progress as a result of this event. "Additional information received determined the Unit 1 turbine driven auxiliary feedwater pump tripped for unknown reasons. Feedwater flow to all steam generators was maintained by the U-1 east and west motor driven auxiliary feedwater pumps. "U-2 reactor power was lowered from 100 percent to 50 percent over the hour prior to the trip in accordance with the Degraded Forebay Procedure. "The DC Cook NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY RICHARD HARRIS TO JEFF ROTTON AT 0945 EDT ON 11/01/2014 * * * At 0921 EDT, DC Cook issued a press release regarding the event described earlier. The licensee notified the NRC Resident Inspector. Notified R3DO (Lipa) | 0 | 0 | 0 | 100 | 50 | 0 | -1 | -1 | 0 | M/R | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-11-01
50586 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-31 17:40 | 2014-11-01 02:07 | 2014-11-01 | AUTOMATIC EMERGENCY DIESEL GENERATOR START DUE TO LOSS OF OFFSITE 230KV STARTUP POWER SUPPLY "At 1740 PDT, Diablo Canyon Power Plant experienced a loss of the offsite 230 kV startup power source. This was due to a 230 kV switchyard bus differential relay actuation during a rainstorm, resulting in valid anticipatory starts of each unit's three emergency diesel generators. All diesels successfully started but were not loaded. All systems operated as designed with no problems observed. "The 230 kV startup power source is the offsite power system designed to be immediately available following an accident. However, the safety related onsite emergency diesel system would have provided power to mitigate the consequences of an accident while the 230 kV [supply] was unavailable. "Unit 1 remains on line at 100 percent power. Unit 2 is currently in Mode 5 in the process of completing a planned refueling outage. Unit 2 power was supplied from the 500kV offsite power source at the time of this event and was therefore unaffected. "The offsite 230 kV startup power source has been restored to service." The NRC Resident Inspector has been notified. The normal offsite power supply remained available and unaffected. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-11-01
50585 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-10-31 12:15 | 2014-10-31 15:54 | 2014-10-31 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the State of New York via fax: "New York State Department of Health was notified on October 31, 2014 by the Radiation Safety Officer of Materials Testing Laboratories, Inc. of the theft of a moisture/density device from a locked vehicle on Friday October 31, 2014. The device is identified as a Troxler Model 4640, serial no. 722 containing 8 millicuries of Cesium 137. The device was apparently being stored within the locked vehicle. The transport case was tethered to the frame of the vehicle with the cable locked to the hasp of the carrying case. The operator of the device discovered that the back lift gate to the 2009 Chrysler Aspen SUV was opened and the lock was removed from the carrying case. The device was stolen from the transport case. Nothing else in the vehicle was stolen. "Local law enforcement have responded and are investigating." New York Event ID No.: NY-14-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-11-10
50584 | 0 | BEAUMONT HEALTH SYSTEM |  |  |  |  | 2014-10-30 10:00 | 2014-10-30 18:17 | 2014-10-30 | PATIENT RECEIVED DOSE GREATER THAN PRESCRIBED DOSE "This is a notification of a medical event that occurred on October 30, 2014 at 1000 EDT in which the Y-90 SIR-Sphere dose delivered to the patient's posterior portion of the right lobe of the liver was more than the prescribed dose by 20 percent or more (10 CFR 35.3045). This patient had a dual administration, with the correct dose administered in accordance with the written directive to the anterior portion of the right lobe of the liver (0.43 GBq and 53.4 Gy). The medical event occurred before this, when the patient who was prescribed a dose of 0.39 GBq (64.5 Gy) was administered a dose that was 20.5% more than the prescribed dose. The posterior portion of the right lobe of the liver was administered 0.47 GBq (77.5 Gy), which was the intended dose for the anterior portion of the right lobe of the liver. The total dose to the right lobe of the liver (both posterior and anterior portions) was 0.90 GBq (142 Gy) compared to the planned dose of 0.91 GBq (143.6 Gy). Our color coding procedure failed to prevent this error. The radiopharmacy staff had applied the green colored dot to the QMP [Quality Management Program] and Dose Planning Forms appropriate for the posterior portion of the right lobe. The medical physicist applied the green colored dot to the checklist intended for the anterior portion of the right lobe rather than to the checklist intended for the posterior portion of the right lobe. The error was not caught during the time out prior to the dose administration. Upon completion of the first of the dual administrations, the medical physicist identified and reported the error to the authorized user and RSO. A time out was called and the decision was made to prepare a new Y-90 SIR-Sphere dosage for the anterior portion of the right lobe in accordance with the written directive. The correct dose was then administered in accordance with the written directive to the anterior portion of the right lobe of the liver (0.43 GBq and 53.4 Gy). "To prevent this from occurring, the color coding procedure was revised by the Radiopharmacy and modeled after their blood labeling process. The check list was revised to instruct the medical physicist that 'If dual administration case, verify correct color dots on QMP form, dose plan, and checklist.' Before a dual administration case is started, the dose planning page with the correct corresponding color dot will be pulled from the paperwork and placed in the control room. This allows the AU [authorized user], physicist, and remaining team (techs, nurses) to see the plan clearly. Once the physician (AU) gains access to the first treatment site, they will give the verbal notice to the physicist, so they can assemble the corresponding dose. With the finished assembly in place table side, the AU and physicist will verify the dose intended for the location. As it pertains to this case, the physician would say, 'We are in the posterior right lobe, the dosage is 0.52 GBq and is labeled with the orange dot, correct?' The QMP was revised to include these revised procedures. No adverse effect is expected for the patient. Both the patient and the referring physician were notified on October 30, 2014." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2014-11-07
50583 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2014-10-29 13:30 | 2014-10-30 17:15 | 2014-10-30 | STUCK SOURCE IN A VARIAN HIGH DOSE RATE AFTERLOADER Staff at the New Milford Cancer Center in New Milford, CT were performing their daily quality assurance checks on their Varian Medical Systems high dose rate (HDR) afterloader when the 7.2 Ci (estimated) Ir-192 source became stuck in the safe position. New Milford contacted the vendor who dispatched a support team to investigate. The Varian RSO surveyed the area and found the dose rate at 5 cm was 1.5 mR/hr which was within normal parameters with the source in the shielded position. While attempting to free the source, it became stuck outside of the shielded position. Dose rates increased to 20 mR/hr at the entrance to the maze, 280 mR/hr at the turn (approximately 15 feet from the HDR) and 5.4 R/hr at 0.5 meters. The service manager was able to use the emergency hand crank to return the source to its shielded position. During the retrieval, the RSO received 9 mR while the service manager received 27 mR. Based on past issues and current symptoms, Varian technicians replaced the drive mechanism and will be installing a new source wire. Once all repairs are made, the HDR will be placed into service with the Varian team on hand during the first post-maintenance use. Varian, an NRC licensee, is making this report since New Milford Cancer Center (license number 0617892-01) did not exceed any reporting thresholds due to this event. The vendor has notified R1 (Modes). See similar events in Event Notifications 46695 and 46758. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-11-07
50582 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-10-30 11:00 | 2014-10-30 14:35 | 2014-10-30 | OFFSITE NOTIFICATION AND PRESS RELEASE REGARDING BOONE DAM STABILITY ISSUES "On October 30, 2014, at 1100 EDT, TVA conducted a briefing for government officials and other stakeholders regarding the decision to accelerate the Boone Reservoir annual drawdown after discovery of a sink hole near the base of the embankment and a small amount of water and sediment found seeping from the river below the dam. TVA is continuously monitoring the dam and conducting an investigation to determine the source of the water seepage. "The dam is located upstream of all three TVA nuclear sites. There are currently no nuclear plant operability or safety issues, and TVA is assessing the impacts on the plant licensing bases. "A press release was issued at approximately 1300 EDT. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification other government agencies and a news release. "The NRC Senior Resident Inspector was notified." | 17 | 100 | 100 | 17 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-30
50581 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-30 12:20 | 2014-10-30 12:48 | 2014-10-30 | OFFSITE NOTIFICATION REGARDING BOONE DAM STABILITY ISSUES "On October 30, 2014, at 1100 EDT, TVA conducted a briefing for government officials and other stakeholders regarding the decision to accelerate the Boone Reservoir annual drawdown after discovery of a sink hole near the base of the embankment and a small amount of water and sediment found seeping from the river below the dam. TVA is continuously monitoring the dam and conducting an investigation to determine the source of the water seepage. "The dam is located upstream of all three TVA nuclear sites. There are currently no nuclear plant operability or safety issues, and TVA is assessing the impacts on the plant licensing bases" The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-30
50580 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-30 11:00 | 2014-10-30 14:07 | 2014-10-30 | OFFSITE NOTIFICATION AND PRESS RELEASE REGARDING BOONE DAM STABILITY ISSUES "On October 30, 2014, at 1100 EDT, TVA conducted a briefing for government officials and other stakeholders regarding the decision to accelerate the Boone Reservoir annual drawdown after discovery of a sink hole near the base of the embankment and a small amount of water and sediment found seeping from the river below the dam. TVA is continuously monitoring the dam and conducting an investigation to determine the source of the water seepage. "The dam is located upstream of all three TVA nuclear sites. There are currently no nuclear plant operability or safety issues, and TVA is assessing the impacts on the plant licensing bases. "A press release was issued at approximately 1300 EDT. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of other government agencies and a news release. "The NRC Senior Resident Inspector was notified." The licensee is evaluating this event for potential impact on the design basis flooding level. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-30
50579 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-10-28 17:08 | 2014-10-30 13:05 | 2014-10-30 | REACTOR BUILDING VACUUM BELOW TECHNICAL SPECIFICATION LIMIT "On the evening of October 28, 2014 at 1708 EDT, with James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100 percent power, the Reactor Building differential pressure decreased below the JAF Technical Specification (TS) Surveillance Requirement (SR) value of at least 0.25 inches water vacuum for a period of thirty-four (34) seconds. This occurred during restoration of the Reactor Building Ventilation System (RBVS) following planned maintenance. The Reactor Building differential pressure was 0.50 inches water vacuum with the 'A' RBVS fans in-service in conjunction with the Standby Gas Treatment System (SGTS). The Reactor Building differential pressure decreased to 0.19 inches water vacuum when the SGTS was secured. The Reactor Building Vent was subsequently isolated, and the alternate 'B' RBVS fans were placed in-service; the differential pressure increased to within the required 0.25 inches water vacuum value. "The JAF TS bases associated with Secondary Containment state that, 'for Secondary Containment to be considered OPERABLE, it must have adequate leak tightness to ensure that the required vacuum can be established and maintained.' Troubleshooting activities indicated that the transient was due to a non-safety related, non-TS damper downstream of one of the 'A' RBVS fans that did not fully stroke open. The subject damper is not part of Secondary Containment, and has no safety related function. This condition did not impact the leak tightness of Secondary Containment or the ability of the associated equipment to establish and maintain the required differential pressure. Secondary Containment would have fulfilled its safety function. "However, because the JAF TS SR value of 0.25 inches water vacuum was not met, Secondary Containment was considered Technical Specification INOPERABLE for a period of thirty-four (34) seconds. The Secondary Containment is considered a single-train system; therefore, this condition is reportable pursuant to 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-10-30
50578 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2014-10-28 16:15 | 2014-10-29 19:12 | 2014-10-29 | AGREEMENT STATE REPORT - FIRE IN RADIOCHEMISTRY LAB CAUSES CONTAMINATION OF FUME HOOD "On October 28, 2014 at 1615 PDT, a fire started in a fume hood in radiochemistry lab MSM 173 hood 2 [located at the University of Nevada, Las Vegas]. The researcher was working with uranium, which is pyrophoric. The fire damaged a container of used pipettes containing Tc-99 (maximum of 150 microCi), which resulted in contamination of the fume hood. The damage to the container and loss of integrity of the licensed material resulted in this report. "The lab was immediately closed and surveys performed. There were no personnel or airborne contamination detected. The two HEPA filters for the fume hood exhaust prevented a release to the environment. The [licensee] issued a Stop Work order for all radiochemistry labs and initiated an investigation and will follow-up with additional reports to the Nevada Radiation Control Program." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2014-11-06
50577 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-10-29 03:00 | 2014-10-29 17:32 | 2014-10-29 | UNANALYZED CONDITION DUE TO MATERIAL IN A THERMOCOUPLE HOUSING "While performing troubleshooting on a thermocouple, uranium-bearing material was found inside the sealed housing containing the wiring block for the thermocouple. A very small amount (less than one ounce) of wet paste-like material was removed from the housing for analysis. The leak appears to be low concentration material that has penetrated the enclosed thermocouple well. The material was contained within the housing; however, the electrical conduit exiting the housing connects to an electrical panel that is an unfavorable geometry. "Potential health and safety consequences: "No actual safety consequences occurred due to this event. The potential consequences would result if a sufficient volume of HEU solution were to leak through the thermocouple well and drain through the electrical conduit into an unfavorable geometry electrical panel, which could under worst case conditions lead to a criticality accident. The leaked material was contained within the instrument housing and no personnel exposures resulted. "Sequence of occurrences leading to the event: "The integrity of a thermocouple well failed allowing a very small quantity of low concentration material to enter the housing containing the thermocouple connections. The leak was identified during troubleshooting operational issues with the system. At this point, the failure mechanism of the thermocouple well is unknown. "Additional actions taken in response to the event: Similar systems are being inspected to determine if additional failures are present. Also, corrective actions to include modification of the unfavorable geometry electrical panels that have not been previously modified are underway to eliminate this failure pathway. "What is the safety significance of the event? Low safety significance due to limited quantity as well as geometry of container. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2014-11-03
50576 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-10-28 15:30 | 2014-10-29 15:45 | 2014-10-29 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURES FOR NON-OCCUPATIONAL WORKERS The following information was provided by the State of Ohio via email: "At 1530 EDT on 10/28/14, an INEOS Supervisor noticed that the indicator for the High-High Level gauge for the tank in the DIN1 reactor showed that the gauge was in the open position. The gauge shutter was closed immediately upon this discovery. The level gauge contains a 1 Ci Cs-137 source (assay date 1993). "The open shutter could have caused exposures to non-occupational workers who were working in the area performing cleaning and maintenance. The tank had been emptied for cleaning and contractors have been entering the tank for maintenance. Workers would have passed through the beam while using the access ladder to gain entry to the tank to perform their work. At the time of the original notification by the licensee, it was unknown how many individuals might have been exposed and for how long. The licensee was advised to take prompt action to determine the exposure to the individuals and it was recommended that he contact a CHP Health Physics Consultant as soon as possible. "ODH [Ohio Department of Health] responded on 10/29/14. Investigation determined that work actually began on 10/26/14 and that five (5) individuals were involved, all non-occupational workers. Any exposure would have been primarily from passing through beam on access ladder enroute to work in tank, which was taking place approximately 25 feet below the beam inside the tank. There was one (1) individual who was performing a maintenance task in or near the beam for approximately 15 minutes at a distance of approximately 12 inches from the gauge. "Licensee has contacted a local gauge manufacturer which has experienced staff available to assist with dose reconstruction. "Information on gauge and source model/type/serial number not available at time of this entry. More information to follow as available. "Initial investigation would indicate that exposures may exceed allowances for non-occupational workers, but not at a level that would result in serious health issues." Ohio Item Number: OH140012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-11-06
50575 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-09-11 | 2014-10-29 14:35 | 2014-10-29 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE CANNOT BE RETRACTED The following information was provided by the State of Louisiana via fax: "On September 12, 2014, LA DEQ [Louisiana Department of Environmental Quality] received a notification from the [licensee] Radiation Safety Officer [RSO]. [The RSO] stated a crew was making exposures at a fab shop [in Walker, LA] at approximately 1730 CDT. The exposure device was on an I-beam when the device slid off of the beam onto the front guide tube outlet connection. The radiographer realized the source could not be retracted back into the shielded position. "The lead radiographer contacted the RSO and received instructions on how to secure/shield the area from potential/unnecessary exposures. An assistant RSO, was dispatched to the site to perform the retrieval and he arrived approximately 1830 CDT. [The assistant RSO] was able to retract/shield the source when he removed the crimped drive cable. The source retrieval was completed approximately 1920 CDT. The crew members exposures were both less than 30 mrem and the assistant RSO's exposure was less than 100 mrem. "The exposure device and associated equipment (crank out control and source guide tube) were shipped to QSA Global for a materials evaluation. The equipment was evaluated and passed the quality assurance requirements for Type B radiography equipment. The male connector on the source guide tube was replaced and was returned to the customer. The equipment involved in the incident and returned to the customer after the repair and evaluation: QSA 880 Delta, s/n D9829. QSA source model A424-9, Ir-192 source, s/n 16863C with an activity of 69 Ci. QSA control model SAN88225R and a Swivel End Stop QSA GST TAN48906. "[The licensee] is Departmental [LA DEQ] approved and licensed to perform source retrievals." License No.: LA-15838-Lol, AI#s. 12540; 165525. Louisiana Event Report ID No.: LA-140010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-11-06
50574 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-10-29 09:05 | 2014-10-29 14:08 | 2014-10-29 | POSITIVE FITNESS FOR DUTY TEST RESULTS A contractor employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The contractor employee's unescorted access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2014-10-29
50573 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-29 07:11 | 2014-10-29 13:54 | 2014-12-22 | LOSS OF CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM OPERABILITY "At 0711 EDT, Salem Unit 2 entered TSAS [Technical Specification Action Statement] 3.0.3 due to the Salem Unit 1 - 1B Vital instrument bus inverter failing which resulted in a loss of the Unit 1 - 1B Vital instrument bus. The loss of power to the 1B Vital instrument bus resulted in Salem Unit 2 initiating the accident pressurized mode of control room ventilation. All dampers and fans repositioned correctly with the exception of the Unit 1 Control Room Emergency Air Conditioning System (CREACS) intake dampers, 1CAA48, 50, and 51. The 1CAA48 was pinned closed to support Unit 1 - 1A125VDC scheduled maintenance. The 1CAA50 and 51 failed to move to the open position (required for Unit 2 accident pressurized mode) due to the loss of power to the 1B Vital Instrument Bus. With the 1CAA48, 50 and 51 dampers closed, this isolated the Unit 1 CREACS intake in the closed position. For an accident in Unit 2, the CREACS intake for Unit 1 is required to open. "Salem Unit 2 exited TSAS 3.0.3 at 0822 EDT when the 1CAA50 and 51 were pinned in the open position to implement accident pressurized mode for Salem Unit 2 in accordance with S1/S2.OP-SO.CAV-0001, Control Area Ventilation Operation. "Salem Unit One is Defueled. "This event is being reported under the requirements of 10 CFR 50.72(b)(3)(v)(D) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to perform mitigation of the consequences of an accident.' "The licensee has notified the NRC Resident Inspector. No one was injured as a result of the failure of 1B Vital instrument inverter." The licensee notified Lower Alloways Township. * * * RETRACTION FROM BILL MUFFLEY TO HOWIE CROUCH AT 1529 EST ON 12/22/14 * * * "A subsequent review of the condition reported on 10/29/2014 in EN 50573 determined that the Control Room Emergency Air Conditioning System (CREACS) was operable and capable of performing its safety function. Therefore, there was no reportable condition. "Circuit analysis identified that the Unit 2 Control Room Intake Isolation (CRIX) Train B circuit remained fully functional and able to respond to a Unit 2 Safety Injection (SI) signal or actuation from radiation monitor 2R1B Channel 1 (radiation levels in the Unit 2 normal Control Area Ventilation intake). The loss of the 1B vital instrument bus did not affect the normal actuation circuitry. The appropriate Unit 1 dampers would have received an open signal and the appropriate Unit 2 dampers would have received a closed signal, thereby isolating the Unit 2 CREACS intake and opening the Unit 1 CREACS intake. Thus, the CREACS would have been capable of mitigating the consequences of an accident. "The NRC Resident Inspector has been notified." Notified R1DO (Ferdas). | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-10-29
50572 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-10-28 | 2014-10-29 12:37 | 2014-10-29 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE CAN NOT BE RETRACTED The following information was received from the Commonwealth of Pennsylvania via email: "The Department's [PA Department of Radiation Protection] Southwest Office informed the Central Office of this event on October 28, 2014. This event is reportable to the Department within 24-hours per 10 CFR 30.50(b)(2), and within 30 days as per 10 CFR 34.101(a)2. "While radiographing a pipe in the field, a crew had an incident where the camera fell and crimped the guide tube, and the source could not be retracted. The area was immediately secured after the event, and recovery operation initiated. The recovery was completed within two hours. Using long handled pliers under lead sheets, the licensee was able to un-crimp the guide tube and retract the source back into the camera. The readings with the lead sheets in place were in the range of 10 to 15 milli-roentgen per hour (mR/h). Electronic dosimetry readings of those involved with the recovery were provided to the Department [Radiation Protection], with no whole body results above 40 mR. "Camera Information: Model: AEA / QSA 880 Delta Serial#: D12920 "Source Information: Model: AEA / QSA A424-9 Serial #: 11088G Isotope: lr-192 Activity: 99 Ci "CAUSE OF THE EVENT: The camera was not tied down to the pipe, it slid off the supporting structure, fell, and crimped the guide tube. "ACTIONS: The licensee was able to un-crimp the guide tube and retract the source back into the camera. The Department plans a reactive inspection." PA Event Report ID No.: PA140022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-11-06
50571 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2014-10-29 11:20 | 2014-10-29 12:50 | 2014-10-29 | MAXIMUM ALLOWABLE PRIMARY CONTAINMENT LEAKAGE RATE EXCEEDED "This notification is to report a condition involving higher than allowable through-seat leakage of two redundant feedwater system check valves (28A and 96A). Unit 2 is currently shut down and primary containment is not required to be operable. Therefore, there is currently no safety impact due to this discovered condition. "This leakage was identified as a result of planned local leak rate testing of the feedwater primary containment isolation valves for the 'A' feedwater line being performed during the current P2R20 refueling outage. At approximately 1100 EDT, Engineering determined that the primary containment penetration pathway leakage through the redundant check valves resulted in a condition where the maximum allowable primary containment leakage rate (La) was exceeded. In accordance with NUREG-1022, Rev. 3, Event Report Guidelines 10 CFR 50.72 and 50.73, Section 3.2.4, this occurrence is an example of a reportable condition. Therefore, this notification is being made pursuant to 10CFR 50.72(b)(3)(ii)(A). "This condition has been entered in the plant corrective action program (IR 2402909). "The NRC Resident Inspector has been informed of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-10-29
50570 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-10-17 05:45 | 2014-10-27 17:29 | 2014-10-27 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE/DENSITY GAUGE The following information was provided by the State of California via email: "Twining, Inc. notified RHB [California Radiation Health Branch] that at approximately 0545 [PDT on 10/17/2014], a Troxler 4640 moisture/density gauge, containing 10 mCi of Cs-137 and 50 mCi of Am-241, was stolen from an employee's vehicle while he was in his hotel room [located in Oakdale, CA]." Oakdale Police Department Report Number: 14-3399 California Event Report Number: 10172014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-11-04
50569 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-10-23 10:46 | 2014-10-25 23:41 | 2014-10-25 | TURBINE BUILDING EXHAUST SAMPLE RACK DECLARED NON-FUNCTIONAL "A planned outage for the Turbine Building Exhaust Air Radiation Indicating Switch (TEA-RIS-13) and the Turbine Building Process Radiation Monitoring Sample Rack (TEA-SR-26) for health inspection was initiated at 1046 PDT on 10/23/14. Due to maintenance retests taking longer than expected and in anticipation of possibly exceeding 72 hours for the planned outage, this event is being reported as a major loss of assessment capability under regulation 10 CFR 50.72(b)(3)(xiii). Compensatory measures have been implemented to obtain radiation readings from the associated effluent release pathway during the outage. Field team assessment function was unaffected and remains available. "The Resident Inspector will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-10-25
50568 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-10-25 11:30 | 2014-10-25 13:42 | 2014-10-25 | VENTILATION PROCESS RADIATION MONITORS OUT OF SERVICE FOR PLANNED MAINTENANCE The normal and high range ventilation process radiation monitors (3HVR*RE 10 A/B) were removed from service for preplanned maintenance for greater than 72 hours. The radiation monitors will be returned to service following maintenance and completion of operational testing. The licensee has notified the NRC Resident Inspector, the State of Connecticut and Waterford township.. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Defueled; FMode3: Defueled | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-10-25
50567 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-10-24 19:03 | 2014-10-24 20:59 | 2014-10-24 | NORMAL RANGE RADIATION MONITOR OUT OF SERVICE FOR UNPLANNED MAINTENANCE The normal range Supplemental Leakage Collection and Release System (SLCRS) was removed from service due to a sample pump failure. Compensatory sampling and monitoring is being established per the Radiological Effluent Monitoring and Offsite Dose Calculation Manual. Following the sample pump repairs and restoration, the Radiation Monitor will be returned to service. The licensee notified the NRC Resident Inspector, the State of Connecticut and Waterford township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Defueled; FMode3: Defueled | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-10-24
50566 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-10-24 01:30 | 2014-10-24 19:50 | 2014-10-24 | DISCOVERED SAFEGUARDS SYSTEM VULNERABILITY Discovered vulnerability in a safeguard system that could allow unauthorized access to the Independent Spent Fuel Storage Installation area for which compensatory measures have not been employed. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-10-24
50565 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-08-27 11:09 | 2014-10-24 14:49 | 2014-10-24 | INVALID ACTUATION OF GENERAL CONTAINMENT ISOLATION SIGNALS "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. "On August 27, 2014, at 1109 hours Central Daylight Savings Time (CDT), while in a forced unit outage with the reactor noncritical (Mode 3) and with all control rods fully inserted, instrument mechanics were attempting to backfill reactor water level transmitter (LT) 3-53 sensing lines following performance of LT replacement. During this effort, water levels in both the variable and reference legs of the LT were disturbed resulting in a Browns Ferry Nuclear Plant (BFN) Unit 1 full scram and Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolation signals due to receipt of an invalid low reactor water level signal. The PCIS Groups 2, 3, 6, and 8 isolations caused the initiation of Trains B and C of the Standby Gas Treatment (SBGT) System and Control Room Emergency Ventilation (CREV) Subsystem 'A'. The Reactor and Refuel Zone ventilation fans tripped and the secondary containment dampers isolated. Train A of the SBGT System was tagged out of service during the event. "Operations personnel responded to the PCIS initiation, ensured all equipment operated as designed, and placed affected systems back in service. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 928777. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-10-24
50564 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-10-03 | 2014-10-24 12:28 | 2014-10-24 | AGREEMENT STATE REPORT - LOST PORTABLE FLUORESCENCE ANALYZER "During a routine request for an annual inventory audit by the Agency [Illinois Emergency Management Agency], the generally licensed registrant was unable to locate their hand held thin metal alloy analyzer. The unit was a 'triple head' unit containing 3 sources. It was replaced by a newer x-ray producing unit a few years ago but was retained as a back up. Current and past employees were questioned during the investigation and the registrant will continue its search although they believe it unlikely to be fruitful. When it went unused, it was believed to be discarded with other equipment and junked. At this time, the radioactive iron and cadmium sources are decayed to less than milliCurie quantities and have a negligible radiation profile associated with them and they pose no threat to public health and safety were they some how removed from the device. The americium source however remains and if disposed as described, the device would show no elevated radiation levels from its surface. Based on similar equipment information in the sealed source device registry, if the internal shutter mechanism were somehow to be rotated open with the Am-241 source in the analyze position, the only measurable radiation would be found at the front of the device and would be less than 2 millirem/h at a foot. Pending additional developments, the Agency is considering this matter closed." Device Name: FLUORESCENCE ANALYZER. Model Number: XL 309-831S. Manufacturer: NITON. Serial Number: U3052 6125LY. Containing the following sources; Sealed Source: .014 Ci, AM-241. Manufacturer: AMERSHAM. Model Number: AMC.P4. Serial Number: 1076CW Sealed Source: .0007 Ci, CD-109. Manufacturer: AMERSHAM Model Number: IEC.A1. Serial Number: 8819LG. Sealed Source: .000007 Ci, CD-109. Manufacturer: AMERSHAM. Model Number: CUCP.1. Serial Number: 6125LY. Cause: Human Error. Illinois Item Number: IL14020. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-11-03
50563 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2014-10-23 09:38 | 2014-10-23 18:06 | 2014-10-23 | FITNESS FOR DUTY - NON LICENSED SUPERVISOR FAILED FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive result for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. The NRC Resident Inspector has been informed. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Defueled | Power Operation | Power Operation | Defueled | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2014-10-23
50562 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-09-12 13:42 | 2014-10-23 16:42 | 2014-10-23 | INVALID SPECIFIED SYSTEM ACTUATION "The following information is provided as a 60 day telephone notification to the NRC in accordance with 10 CFR 50.73(a)(1) reported under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of the Unit 1, Train 'A' Emergency Diesel Generator on September 12, 2014, at 1342 CDT. Per NUREG-1022, R.3, page 33, the following information should be provided for an invalid actuation reported under 10 CFR 50.73(a)(1): (a) the specific train(s) and system(s) that were actuated, (b) whether each train actuation was complete or partial, (c) whether or not the system started and functioned successfully. "(a) The specific train(s) and system(s) that actuated were: Unit 1, Train 'A' Emergency Diesel Generator. "(b) Whether each train actuation was complete or partial: The actuation of the Unit 1, Train 'A' Emergency Diesel Generator was a complete actuation. "(c) Whether or not the system started and functioned successfully: The Unit 1, Train 'A' Emergency Diesel Generator started and functioned successfully. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-10-23
50561 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2014-10-23 09:59 | 2014-10-23 16:11 | 2014-10-23 | FITNESS FOR DUTY - EMPLOYEE SUPERVISOR FAILED FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive result for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been suspended. The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2014-10-23
50560 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-10-23 01:07 | 2014-10-23 09:48 | 2014-12-17 | SECONDARY CONTAINMENT INOPERABLE DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "At 0107 CDT on October 23rd, 2014, both doors in one of the Secondary Containment airlocks were momentarily open concurrently. This occurred during vessel drain down following refueling activities, an Operation with the Potential to Drain the Reactor Vessel (OPDRV), which required Secondary Containment to be operable. The doors being open at the same time resulted in the momentary inoperability of Secondary Containment. One of the doors was immediately closed, and Secondary Containment was restored to an operable status. "The station [Duane Arnold] has now completed the OPDRV associated with vessel drain down, and Secondary Containment is no longer required to be operable. "The Resident Inspector has been notified." * * * RETRACTION FROM BOB MURRELL TO JOHN SHOEMAKER AT 1232 EST ON 12/17/14 * * * "The purpose of this notification is to retract a previous report made on 10/23/2014, at 0948 [EDT] (EN 50560). Notification of the event to the NRC was initially made as a result of an event where both doors in one of the Secondary Containment airlocks were momentarily open concurrently. This occurred during vessel drain down following refueling activities, an Operation with the Potential to Drain the Reactor Vessel (OPDRV), which required Secondary Containment to be operable. The doors being open at the same time resulted in the momentary inoperability of Secondary Containment. One of the doors was immediately closed, and Secondary Containment was restored to an operable status. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the doors in question were not mechanically degraded such that they were incapable of being closed. A momentary condition of having both secondary containment airlock doors open for a matter of seconds is not an event or condition that could have prevented the fulfillment of a safety. Furthermore, the conduct of OPDRVs during a momentary opening of both secondary containment doors that is immediately rectified does not constitute a condition prohibited by TS. Therefore, this event is not considered a Safety System Functional Failure or a Condition Prohibited by TS and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. The NRC Senior Resident Inspector has been notified. Notified the R3DO (McCraw). . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-10-23
50559 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-10-22 14:39 | 2014-10-22 18:35 | 2014-10-22 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-10-22
50558 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-10-22 08:42 | 2014-10-22 14:05 | 2014-10-22 | FITNESS FOR DUTY - EMPLOYEE SUPERVISOR FAILED FFD TEST A non-licensed employee supervisor had a confirmed positive result for alcohol during a random fitness-for-duty test. The employee's access to the plant has been revoked. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-10-22
50557 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-10-21 | 2014-10-22 10:07 | 2014-10-22 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK OPEN The following was received via email: "On October 21, 2014, the Office of Virginia Radiological Health Program (RHP) received a report from the licensee that one of the radioactive source holders, Ronan Model SA1-E37, Serial# M-1818, containing 750 millicuries (414.6 millicuries, decay corrected) of Cs-137, was not 'functioning per the design.' The problem was discovered on October 21, 2014 while the licensee was conducting periodic shutter checks. The shutter is kept in the open position during operations and does not pose an additional radiation exposure [risk] to personnel. The licensee performs radiation survey around the source and is in compliance. The licensee has contacted the Ronan Engineering to repair the gauge. The agency will continue to monitor the situation until the shutter is repaired." VA Report # VA-2014-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-10-30
50556 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2014-10-20 17:35 | 2014-10-21 13:23 | 2014-10-21 | ITEM RELIED ON FOR SAFETY NOT FUNCTIONING "At 1735 [PDT] on 10/20/2014 as part of an annual PM [Preventive Maintenance] AREVA staff noticed that a check valve on a steam supply line (designated as an IROFS [item relied on for safety]) was leaking. This IROFS is one of two IROFS in one accident sequence. The failed check valve had been in this state for more than 8 hours. "The initial reportability evaluation made at 1745 [PDT] on 10/20/2014 wrongly concluded that the condition was not reportable. When the reportability evaluation was peer reviewed at 0930 [PDT] on 10/21/2014, the reviewer correctly noticed that an IROFS credited in the initial evaluation was not applicable to one accident sequence. "Safety Significance of Events: Minor. The limiting accident sequence (070-18.1 in the AREVA Richland ISA summary) maintains a controlled event index number of -4 (remains highly unlikely). "Potential Criticality Pathways Involved: A primary to secondary leak in a heat exchanger has to exist, steam pressure has to drop below 60 psig, a low pressure interlock (on IROFS) has to fail. "Corrective Actions to Restore Safety Systems: System was down [and] will remain down until appropriate actions are complete." Licensee will contact Region II Fuel Cycle Division. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 1 | 2014-10-29
50555 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-10-17 | 2014-10-21 12:12 | 2014-10-21 | AGREEMENT STATE REPORT - PROCESS GAUGE STUCK SHUTTER The following information was received via email: "The licensee called to report a radioactive material gauge with stuck shutter in the open position on a continuous process Vega Model SHLG1, SN 63133 gauge with a 300 milliCurie Cs-137 source. There are no adverse exposure or other problems. Routine operations will continue. The gauge manufacturer will be contacted." TN Report ID Number: TN-14-197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-10-29
50554 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2014-10-17 | 2014-10-21 11:32 | 2014-10-21 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following information was received via email: "This is the initial notification that, on Friday, October 17th in Nuclear Medicine at OHSU [Oregon Health and Science University], a patient who was supposed to receive 25 mCi Tc-99m Sestamibi for a parathyroid scan was injected with 25.9 mCi of Tc-99m MDP, a bone scanning agent. "The patient was notified, as was the referring physician. The patient was accompanied to meet with the referring physician. At this time, the exam will not be rescheduled. Investigation with the injecting technologist still in progress, and a letter will be sent to the patient. "Radiation protection services will follow up with additional information." Oregon Incident Number: 14-0040 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2014-10-29
50553 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2014-10-20 13:53 | 2014-10-20 16:32 | 2014-10-20 | BOTH SECONDARY CONTAINMENT AIRLOCK DOORS OPEN SIMULTANEOUSLY "At 1353 EDT on 10/20/2014, both Reactor Building Airlock doors at NMP1 were opened simultaneously for a few seconds. This results in a momentary loss of Secondary Containment operability (TS 3.4.3). The doors were closed and operability was restored. "Secondary Containment being inoperable is an 8 hour notification per 10CFR50.73(b)(3)(v)(C), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-10-20
50552 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-10-20 | 2014-10-20 16:03 | 2014-10-20 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE RETRACTION FAILURE The following information was received via facsimile: "On October 20, 2014, the Agency [Texas Department of State Health Services] received notice that there had been a radiography source retraction failure at a temporary field site. A pipe had fallen from a stand onto the guide tube, causing a crimp. The source was retrieved by squeezing the crimp with pliers several times, allowing retraction. The individual performing the retrieval received 198 mR according to a pocket dosimeter. The camera was an INC IR-100 (sn 6832) with an Ir-192 source at 44 Ci (sn W644 ). Additional information will be supplied as it is received in accordance with SA-300." This event occurred at a field site in Encinal, Texas. Texas Incident #: I-9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-28
50551 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-10-20 02:18 | 2014-10-20 03:55 | 2014-10-20 | AUTOMATIC REACTOR SCRAM ON LOSS OF FEEDWATER "The Perry Power Plant experienced a reactor scram during a shift of non-essential vital power supply to the alternate source. Feedwater was lost resulting in receiving a valid level 3 and level 2 signal. High Pressure Core Spray and Reactor Core Isolation Cooling started and injected. Reactor level and pressure have been stabilized to required bands. The motor feed pump has been started and is controlling level. High Pressure Core Spray and Reactor Core Isolation Cooling have been returned to standby." During the scram, all rods fully inserted into the core. Decay heat is being removed via the steam dumps to the condenser. The electrical grid is stable and supplying plant loads. An emergency diesel generator started, as designed, as a result of the level 2 signal but did not load. No safety valves lifted as a result of the transient. The cause of the loss of feedwater is under investigation. The licensee will be notifying the State of Ohio and Perry Township and has notified the NRC Resident Inspector. * * * UPDATE FROM DOUG SHORTER TO HOWIE CROUCH AT 0933 EDT ON 10/20/14 * * * "The plant is currently in Mode 3, stable with cooldown and depressurization to Mode 4 in progress. Level control is being provided by the motor feedwater pump. Troubleshooting of the cause of the scram and loss of feed water is on-going. "The initial notification identified 10CFR50.72(b)(3)(iv)(A), 'Specified System Actuation', as a reporting criteria. The specific system that actuated was not provided. As a result of receiving a reactor vessel water level 2 signal a containment/BOP isolation signal was received. All systems isolated as required and the plant is restoring isolated systems in accordance with procedure." The licensee will be notifying the State of Ohio and Perry Township and has notified the NRC Resident Inspector. Notified R3DO (Pelke). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2014-10-20
50550 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-10-19 20:51 | 2014-10-20 01:36 | 2014-11-24 | MANUAL REACTOR TRIP RESULTING IN AUX FEEDWATER ACTUATION "This is an 8-hour notification being made to report that a valid ESF [emergency safety features] auxiliary feed water system actuation occurred. Salem Unit 1 was in mode 1 at 19% reactor power and executed a planned manual reactor trip to begin a scheduled refueling outage (1R23). The 11, 12, and 13 AFW [auxiliary feedwater] pumps were not in service prior to the reactor trip and as a result, narrow range levels in 12, 13, and 14 steam generators reached 14% before recovering. This resulted in a valid ESF actuation for low steam generator water level. Steam generator water levels were restored to normal post trip values as part of the procedurally directed response to a reactor trip. "All safety related equipment was operational before the reactor trip and AFW actuation and responded as required. There were no equipment failures that contributed to this event. There were no personnel injuries as a result of' this event. "The NRC Resident Inspector has been informed." A transformer alarm caused the operators to trip the reactor prior to reaching the step in the procedure to start the AFW pumps. * * * UPDATE FROM JOHN OSBORNE TO DONALD NORWOOD AT 1555 EST ON 11/24/2014 * * * "On October 20, 2014 at 0136 EDT, Salem Unit 1 reported an 8 hour notification of a valid ESF Auxiliary Feed Water System actuation following a manual reactor trip at the start of the S1R23 refueling outage. After additional review it was determined that the manual reactor trip met the criteria for a four hour report in accordance with 10CFR50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical...'." The licensee notified the NRC Resident Inspector. Notified R1DO (Noggle). | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-10-20
50549 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-10-01 16:56 | 2014-10-18 15:20 | 2014-10-18 | TWO INVALID SPECIFIED SYSTEM ACTUATIONS OF SAFETY INJECTION "This 60-day telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report [two separate] invalid actuations of the Unit 4 Safety Injection (SI) System in accordance with 10 CFR 50.73(a)(2)(iv)(A). "On October 1, 2014 at approximately 1656 [EDT], Sl was actuated on low pressurizer pressure when the Sl signal block was inadvertently removed during pressure transmitter calibrations. The actuation was invalid because it was not in response to an actual plant condition requiring the need for Sl. Containment and containment ventilation isolation were initiated, and the following equipment automatically started: 4B residual heat removal pump; 3A, 3B and 4B high head safety injection (HHSI) pumps; 3A, 3B and 4B diesel generators (DG). This was a partial Sl actuation because of equipment removed from service or already in service due to unit outage conditions. Actuated equipment started and functioned successfully. Emergency core cooling system (ECCS) injection did not occur. The DGs started but did not load. "On October 7, 2014 at approximately 1607 [EDT while unit was in a defueled status], Sl was actuated on low pressurizer pressure during restoration of power to the Train A instrumentation rack. The Sl actuation occurred when a fuse was inserted reenergizing the logic circuit because an incorrect test switch was manipulated during a prior procedure step. Properly positioning the correct test switch would have blocked the low pressurizer pressure signal. The actuation was invalid because it was not in response to an actual plant condition requiring the need for Sl. Containment isolation, containment ventilation isolation, control room isolation, feedwater isolation, and turbine trip were initiated, and the following equipment automatically started: 3A, 3B and 4A HHSI pumps; 3A, 3B, 4A and 4B DGs: 4A intake cooling water pump with isolation of turbine plant cooling water heat exchangers. This was a partial Sl actuation because of equipment removed from service or already in service due to unit outage conditions. Actuated equipment started and functioned successfully. ECCS injection did not occur. The DGs started but did not load. "The NRC Senior Resident Inspector has been notified." .. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-10-18
50548 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-10-15 10:30 | 2014-10-17 12:16 | 2014-10-17 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO MOVEMENT OF TREATMENT CYLINDER "At approximately 1030 [MST] on October 15, 2014, the Agency [Arizona Radiation Regulatory Agency] was informed that the licensee had a medical event involving a High Dose Rate afterloader containing a 4.641 curie Iridium-192 source. A patient was receiving the third of three fractions involving a vaginal cylinder. When the Physicist entered the room after the treatment had concluded, he noticed that the cylinder had fallen out of the vaginal canal and was lying on the treatment table. The patient was unaware of the cylinders' position, but remembers feeling an 'oozing sensation' at the beginning of the treatment. The treatment time was for 431.3 seconds and the total prescribed dose for the fraction was 600 centigray and the total dose for all three fractions was 1800 centigray. The patient was also receiving external beam therapy at a rate of 200 centigray for 26 fractions, for a total dose of 5200 centigray. The patient received the last fraction on October 16th. "The Agency is investigating the event. "The Governor's office is being notified of this event." Arizona First Notice Event No.: 14-025 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-10-27
50547 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2014-10-16 13:45 | 2014-10-17 11:54 | 2014-10-17 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The following information was provided by the State of Utah via email: "Event Description: The licensee failed to properly secure a moisture density gauge in a locked transportation case before leaving a temporary jobsite in a pickup truck. The device fell out of the truck onto the road. The licensee has not been able to locate the device. The local law enforcement agency has been notified." The event location was 900 East and 5200 South, Murray, Utah. The device is a Troxler Model 3440, Serial number - 69079. This device contains 8 mCi of Cs-137 and 40 mCi of Am-241. UT Event Report ID No.: UT140004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2014-10-27
50546 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-10-17 03:03 | 2014-10-17 07:46 | 2014-10-17 | AUTOMATIC REACTOR SCRAM ON HIGH AVERAGE POWER RANGE MONITOR FLUX "At 0303 [CDT], River Bend Nuclear Station sustained a reactor scram due to high Average Power Range Monitor [APRM] flux, suspected due to a malfunction of the Electrohydraulic Control System. Reactor recirculation pump 'B' tripped, reactor recirculation pump 'A' responded appropriately. All other systems responded appropriately except for loss of feed water due to low suction pressure trip from isolating the condensate demineralizers. Reactor water level did not get out of level band. Condensate demineralizers and feedwater were restored to service. Level 3 [isolation] was initiated due to scram. [One] system, Suppression Pool Cooling isolated accordingly due to level 3 signal. Currently the plant is in mode 3, hot shutdown. Plant will remain in mode 3 until investigation of scram is complete." During the scram, all rods inserted into the core. No relief valves lifted as a result of the transient. All safety equipment is available although reactor core isolation cooling is functional but inoperable due to an earlier issue discovered during a surveillance test. The reactor is at normal pressure and temperature for Mode 3. The cause of the high APRM flux and the identified anomalies are under investigation. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DANIEL PIPKIN TO DANIEL MILLS AT 1043 EDT ON 10/17/2014 * * * The licensee is updating the notification to include an 8 hour notification for a specified system actuation due to the Level 3 isolation signal. Licensee is proceeding to cold shutdown to troubleshoot the EHC system. The licensee will notify the NRC Resident Inspector. Notified R4DO (Haire). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-10-17
50545 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2014-10-16 | 2014-10-16 16:34 | 2014-10-17 | PART 21 - INSUFFICIENT SPOT WELD ON WIRE WOUND RESISTOR The following information was excerpted from a facsimile from AMETEK Solidstate Controls: Ohmite 5 watt, 470 ohm wire wound resistor with component Date Code 1201 is mounted on a printed circuit board installed in power supplies manufactured by Ametek Solidstate Controls. "Component Description: Ohmite 5 watt, 470 ohm wire wound resistor with Date Code 1201 "Problem You Could See: Internal open - (100 hour burn-in performed) "Probable Cause: Insufficient spot weld on the wire wound resistor "Effect on System Performance: Resistor opens "Action Required: Notify NRC and affected utilities. Prepare replacements. "Ametek Solidstate Controls Corrective Action Taken: Notified affected utilities of the potential defect and advised that the power supplies be returned to our factory. Further corrective action will be to install new boards with unaffected resistors, retest, perform 100 hour burn in and return." Person notifying the NRC: Mr. Robert George, Director of Quality, 875 Dearborn Drive, Columbus, OH 43085, Telephone: (614) 846-7500 * * * UPDATE ON 10/17/14 AT 0755 EDT FROM ROBERT GEORGE TO DONG PARK * * * The affected plants are Waterford, Indian Point and Salem. Notified R1DO (Cook), R2DO (Ayres), R3DO (Daley), R4DO (Allen) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-10-16
50544 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-09-25 | 2014-10-16 13:47 | 2014-10-16 | AGREEMENT STATE REPORT - LOST GENERAL LICENSED MATERIAL: AM-241 STATIC ELIMINATOR BARS The following was provided by the Commonwealth of Virginia via email: "On September 25, 2014, the Virginia Radioactive Materials Program (RMP) received a phone call from NRC Region 1 that one static eliminator bar, NRD A2003 serial number SA772 containing Am-241, Activity 19.6 mCi as of 4/16/1973 was found in Hedgesville, West Virginia and picked by the NRC inspectors. Record from NRD LLC indicated that this static eliminator bar was sold to O'Sullivan Films, which is located in Winchester, Virginia. In addition, the record from NRD LLC indicated that two other static eliminator bars, NRD A2003, Serial numbers 1229 and 1230, each containing 21 mCi of Am-241 as of 4/18/1975, were also sold to this company. Virginia RMP contacted O'Sullivan Films to investigate this case. O'Sullivan Films investigated the case and reported to RMP by the letter dated October 15, 2014 stating that O'Sullivan Films has not possessed these static eliminator bars and found no documentation that supports O'Sullivan Films having possessed, disposed of or returned these devices. "Currently, no information is available regarding the whereabouts of these static eliminator bars." VA Event Report ID No.: VA-14-18 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-10-24
50543 | 0 | MUNSON MEDICAL CENTER |  |  |  |  | 2014-10-16 09:45 | 2014-10-16 13:46 | 2014-10-16 | PALLADIUM-103 BRACHYTHERAPY SEED BROKEN "A Palladium-103 (Pd-103) brachytherapy seed (Theragenics Model 200 nominal activity 1.5 mCi) broke when the Mick shielded magazine was removed from the applicator. An activity of [approximately] 0.5 mCi for the lost portion of the seed was calculated by measuring the remaining portion of the seed. It was not recovered and presumed to have washed down a sink drain. The seed was broken and lost October 15, 2014 around 0945 [EDT]. The incident was discovered around 1645. Surveys of the area for the lost portion returned no radiation above background. Contamination from the seed is remote because the Pd-103 is coated on (adhered to) a graphite pellet. No personnel radiation exposure data available. It is unlikely the person involved received measurable dose. "The process for removing the cartridge at the end of a procedure will be reviewed to reduce the chance of this happening again." The licensee contacted NRC Region 3 DNMS personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-10-24
50542 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2014-10-16 10:42 | 2014-10-16 13:14 | 2014-10-16 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "Nine Mile Point Unit 1 (NMP1) had a momentary loss of Secondary Containment due to both Reactor Building airlock doors being opened at the same time. "At 1042 EDT on 10/16/2014, both Reactor Building airlock doors at NMP1 were opened simultaneously for less than 5 seconds. This results in a momentary loss of Secondary Containment operability (TS 3.4.3). The doors were closed and operability was restored. "Secondary Containment being inoperable is an 8 hour notification per 10 CFR 50.72(b)(3)(v)(C), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Senior Resident Inspector was notified." The licensee will be notifying the State of New York Public Service Commission. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-10-16
50541 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-10-15 | 2014-10-16 12:12 | 2014-10-16 | AGREEMENT STATE REPORT - STOLEN X-RAY FLUORESCENCE DEVICE The following was received from the State of Texas via email: "On October 15, 2014, the Agency [State of Texas] received a call from the licensee reporting that a Thermo Niton device model number XLP-818 containing 30 millicuries of americium-241 had been stolen. The device and a portable x-ray device were discovered missing from a locked cabinet on October 13, 2014. After initiating an investigation and searching for the devices, the licensee is confident that both devices were locked up in a cabinet on Friday, October 10, 2014 and went missing the following Monday morning. The licensee stated they did not believe any individual would receive any exposure due to this event. The licensee investigation is in progress. Additional information will be provided as it is received in accordance with SA 300." Texas Incident #: I-9244 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-24
50540 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-10-15 17:00 | 2014-10-15 22:23 | 2014-10-15 | APPENDIX R UNANALYZED CONDITION AFFECTING THE TURBINE DRIVEN AUX FEEDWATER PUMP "WBN U1 [Watts Bar Nuclear Unit-1] Appendix R (APP R) procedures do not include all the required operator manual actions to ensure manual control of the Unit 1 Turbine Driven Auxiliary Feed (TDAFW) Pump during a fire in room 713-A1A or 737-A1A. The current APP R procedure includes actions to transfer the Unit 1 TDAFW Pump to local control, but does not account for the potential loss of 125 VDC or 120 VAC to the Unit 1 TDAFW pump controls. "Without procedural guidance to transfer the 120 VAC and 125 VDC supplies, the operation of the Unit 1 TDAFW pump may not be completed within the required time. Failure to take all the required actions to control the Unit 1 TDAFW Pump places WBN Unit 1 in an unanalyzed condition. "WBN has instituted a fire impairment for the affected rooms and established an hourly roving fire watch. "The NRC Resident Inspector has been notified of this condition." The affected components are the trip throttle valve and the local control panel. Procedures should be in place by 10/16/2014 to rectify this situation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-10-15
50539 | 0 | WATERFORD STEAM ELECTRIC STATION |  |  |  |  | 2014-08-12 15:08 | 2014-10-15 18:10 | 2014-10-15 | PART 21 - DEFECTIVE ALLEN BRADLEY RELAY "This is a non-emergency notification from Waterford 3 required under 10 CFR PART 21 concerning the deviation of a dedicated basic component from manufacturing specifications, which could have possibly caused a substantial safety hazard. "On 04/23/2014, Control Room Emergency Filtration Unit A automatically started unexpectedly. It was determined that the equipment inadvertent actuation occurred due to an Allen Bradley Type 700RTC relay failure. The failure mode resulted in the associated equipment actuating as it would to perform its safety function, not adversely impacting steady state plant operations. The failed relay was replaced on 4/25/2014. "Independent failure analysis performed by Southwest Research Institute (SwRI) on an Allen Bradley model 700RTC000020U1 relay that failed in service at Waterford 3 Nuclear Station (WF3) identified that the relay's L22 coil was electrically open. Detailed destructive analysis of the L22 coil revealed corrosion of the winding in multiple locations. Corrosion products removed from various locations near the failure site on the L22 coil contained significant concentrations of chlorine. The independent failure analysis concluded the in-plant failure observed at Waterford 3 was caused by corrosion near the start end of the relay's L22 coil winding. The source of the corrosive material that damaged the winding was not apparent; however, based on review of storage practices at Waterford 3, it is likely that it was introduced during manufacture of the coil. On 8/12/2014, Waterford 3 engineering determined this relay condition was a PART 21 deviation. The qualifying vendor (Qual Tech NP) has been contacted and they have provided the completed failure analysis to the manufacturer (Allen Bradley). "Entergy concluded that for the application of this relay where a malfunction occurred, it did not result in a substantial safety hazard. However, on 10/10/2014, at approximately 1233 CDT, Entergy completed an evaluation concluding that had this relay type been installed, with the same deviation, in other safety related normally energized applications, it could possibly have resulted in a substantial safety hazard, and thus is a PART 21 defect. "The Waterford 3 Site VP was informed 10/14/2014." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-10-15
50538 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-10-14 10:00 | 2014-10-15 15:05 | 2014-10-15 | AGREEMENT STATE REPORT - INDIVIDUAL CONTAMINATED AFTER A FALL The following was received via e-mail: "An individual at Erwin Resin Solutions (ERS) fell 20 feet into a contaminated storage vault. The individual suffered serious head injuries and was transported by ambulance to the Johnson City Medical Center in Johnson City, TN. Ambulance and hospital staff were notified of the possibility of radioactive contamination on the individual. ERS sent health physics technicians to the hospital to survey and assess for contamination. At approximately 1300 EDT, notification was made to the Tennessee Division of Radiological Health that the injured individual was deceased. The radiation safety officer at Johnson City Medical Center indicated that the individual's maximum dose rate was 0.3 Mr per hour. Emergency room staff were surveyed and found to have no contamination. "Some emergency workers did require decontamination prior to being released." Tennessee Report: TN-14-194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-10-23
50537 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-10-14 | 2014-10-15 13:47 | 2014-10-15 | AGREEMENT STATE REPORT - SOURCE FAILS TO RETRACT INTO CAMERA The following report was received via e-mail: "On October 15, 2014, the Agency [Texas Department of Health] was notified by the licensee's radiation safety officer (RSO) that on October 14, 2014, a radiography crew could not retract a 38.5 curie iridium-192 source to the fully retracted and locked position in a QSA 880D exposure device (camera). The lead radiographer who had just completed the third shot of the day at a temporary field site could not fully retract the source into the camera, feeling increased binding in the crank assembly. The radiographer cranked the source back out into the collimator and contacted the RSO who was onsite. The RSO and radiographers increased the control area. After three attempts to retrieve the source, the RSO retrieved the source by disconnecting the handles of the crank mechanism. She was able to manually pull the cable until the source was retrieved into the camera. The RSO received the highest dose of 196 mrem on her 0 - 5R range pocket dosimeter. The crank assembly and drive cable will be sent to the manufacturer for inspection. The RSO stated the camera and guide tube appeared to be operating normally. Additional information will be provided in accordance with SA-300. "QSA 880D camera serial #D1127 Source Model A-424-9, serial #16137C" Texas Incident Number: I-9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-23
50536 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2014-10-14 10:03 | 2014-10-14 17:31 | 2014-10-14 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "The Technical Support Center Air Conditioning Unit is not operating properly and has been declared non-functional. The Air Conditioning Unit functions to cool the Technical Support Center during normal and accident conditions. Current environmental conditions are acceptable. The Corrective Action process has been initiated. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 3, since this condition affects an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-10-14
50535 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2014-10-13 07:45 | 2014-10-14 15:43 | 2014-10-14 | AGREEMENT STATE REPORT - MOISTURE GAUGE STOLEN AND LATER RECOVERED The following report was received via e-mail: "Yesterday, we [North Carolina Department of Health and Human Services] had a stolen gauge incident here in NC. The gauge was recovered the same day. The gauge in question is a Troxler portable nuclear gauge, model 4640B. This gauge has a sealed source with 9 milliCuries of Cesium 137. We have uploaded a record of this incident to NMED. Our local incident number for this event is NC140039. "What follows is a brief narrative supplied by one of our inspectors: "At 0745 [EDT] this morning [a North Carolina inspector] received a phone call from the assistant to the RSO at Barnhill Contracting: "At approximately 2300 [EDT] October 13, 2014 on exit 22 off I-95 in Lumberton, NC, one of their trucks with a PNG [portable nuclear gauge] was stolen. The employee had stepped away from the truck to speak with the project foreman when an individual jumped into the truck and drove off. The Lumberton police and the RSO were contacted. The RSO contacted the Division of Emergency Management at 919-825-2500. The RSO travelled to the site. The truck, with the gauge still locked and secured, was located by the Lumberton Police within about an hour and a half. The individual ran from the scene when the police located the truck. It appears the only thing stolen was the light from the top of the truck. The gauge was still securely locked in the metal box on the back of the truck. There were no injuries reported. The RSO again notified the Division of Emergency Management that the gauge had been found. [The assistant RSO] will forward a copy of the police report (#14-42002) to [the State] when she receives it." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2014-10-22
50534 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-09-08 | 2014-10-14 15:16 | 2014-10-14 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK OPEN The following report was received via fax: "On 9/8/12 while conducting a 6 month physical inventory, the licensee, Carmeuse Lime & Stone, discovered the shutter was unable to close on a Berthold Systems, Inc. fixed gauging device model LB 300 L, serial# 190-02-08, containing 16 mCi Cs-137. The licensee contacted Berthold Systems, Inc. on 9/10/2012 to repair the shutter. The gauging device was repaired by the manufacturer on 1/31/2013. The delay in repair was due to an unavailability of repair parts. The repair parts had to be shipped from Germany. A leak test was conducted following repairs and indicated less than 185 Bq (0.005 micro-curies). The root cause of the failure of the on/off mechanism was due to corrosion and dust due to the gauging device's environment. This licensee produces industrial grade lime and the gauging device is operated in a dusty environment. This event was not reported to the KY RHB as required by regulation and was discovered during a routine health and safety inspection conducted on 6/3/2014." Kentucky Event: KY140004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2014-10-22
50533 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-10-14 03:41 | 2014-10-14 07:37 | 2014-10-15 | MANUAL REACTOR TRIP DUE TO LOSS OF A START-UP TRANSFORMER "This notification is being made as required by 10 CFR 50.72(b)(2)(iv)(B) due to a Farley Nuclear Plant Unit 2 manual reactor trip. The trip was initiated when the in service train of CCW cooling to the Reactor Coolant Pumps was lost due to a loss of the 2B Start Up Transformer (SUT). The control room team manually tripped the reactor then tripped all three reactor coolant pumps as required by station procedure. There was a line of severe thunderstorms with lightning passing through the plant site at the time of loss of the 2B Start Up Transformer. The 2B emergency diesel generator was out of service for maintenance therefore there was a loss of the 'B' train emergency power 4160V electrical bus ('B' train LOSP [Loss of Offsite Power]). 'A' train emergency power remained energized from offsite sources. The plant is stable at normal operating pressure and temperature. At 0433 [CDT], 2B Reactor Coolant Pump was re-started when support conditions were re-established. Heat sink is adequate using the 2A Motor Driven Auxiliary Feedwater Pump. "Unit 2 'B' train power was restored by starting the 2C emergency diesel generator at 0523 [CDT]. This restored power to the Digital Rod Position Indication system, and control rod K-8 in control bank 'C' indicated full out, and all other control rods fully inserted. An emergency boration is in progress to compensate for the stuck rod. "Additionally, the reactor trip resulted in a valid actuation of the Aux Feedwater system which is an eight hour non-emergency report per 10 CFR 50.72(b)(3)(iv)(A)." During the transient, one primary PORV momentarily opened, then reseated. Decay heat is being directed to the atmospheric relief valves with no indicated primary to secondary leakage. There was no impact on Unit 1. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2125 EDT ON 10/15/2014 FROM BLAKE MITCHELL TO MARK ABRAMOVITZ * * * "Digital rod position indication troubleshooting was conducted on 10/14/2014 and confirmed all control rods, including control rod K-8, fully inserted following the reactor trip." The licensee notified the NRC Resident Inspector. Notified the R2DO (Ayres), NRR EO (Davis) and IRD (Gott). | 0 | 0 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-10-14
50532 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-10-13 19:35 | 2014-10-14 01:30 | 2014-12-08 | HIGH PRESSURE CORE INJECTION DEGRADED ACCIDENT MITIGATION CAPABILITY "During the plant response to the trip of the B Recirculating water pump, reactor water level rose to the HPCI [High Pressure Core Injection] high water level trip setpoint as indicated on the associated instrumentation. With this high water level trip actuated, the HPCI high drywell pressure initiation signal would not have allowed the HPCI system to perform its intended safety function if required. If the HPCI system received the low water level initiation signal, the system would have been able to perform Its intended safety function. This high water level signal was actuated from 1935 [EDT] until reset at 1940 [EDT]. This is reportable under 50.72(b)(3)(v)." The licensee notified NRC Resident Inspector. * * * RETRACTION PROVIDED BY DAVID CALLAN TO JEFFREY HERRERA AT 1404 EDT ON 12/08/14 * * * "Further review has determined that the condition was not a result of procedural errors/inadequacies, equipment failures, or design / analysis inadequacies. Plant systems responded as per design when the HPCI system high water level trip actuated when reactor vessel water level rose to the HPCI high water level trip setpoint. HPCI initiation has two logics: one for low-low vessel water level and the other for a high drywell pressure. A vessel low-low water level is an indication that reactor coolant is being lost with a need for HPCI injection for core cooling. High drywell pressure could indicate a line break in the Reactor Coolant Pressure Boundary inside the drywell. The HPCI level instrumentation is designed to shut down the HPCI system upon high water level to prevent HPCI turbine damage due to gross moisture carryover and will re-initiate HPCI if vessel water level drops to the initiation water level setpoint. A HPCI high drywell pressure initiation signal, above setpoint, would have made up the logic for HPCI initiation and as per design, HPCI would have injected at the vessel low low level setpoint without operator action to reset the trip. In this instance, the trip was reset as prescribed by station procedures. HPCI was capable of performing its safety function after the high water level trip reset either by operator action or instrumentation (low low level initiation)." The licensee will be notifying the NRC Resident Inspector. Notified R1DO (Rogge). | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-10-14
50531 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-10-13 14:25 | 2014-10-13 20:48 | 2014-10-13 | UNANALYZED CONDITION DUE TO A MISSING FIRE BARRIER "As part of a fire modeling analysis evaluating a missing fire barrier reported in ENS notification 50475 (a gap where the ventilation duct passes through the wall from the Bus 150/160 room to the Auxiliary Feedwater (AFW) pump room), an additional missing fire barrier was identified. The barrier is related to separation of redundant pressurizer heater banks credited for safe shutdown. For Fire Area 32 (AFW pump room), Group E Pressurizer Heaters are credited for safe shutdown because Group A and Group B Pressurizer Heater cables could be affected by a fire in this area. It was determined that a cable associated with the Group C, D, and E Pressurizer Heaters is routed in Fire Area 32. Therefore, a fire in Fire Area 32 could affect all five Pressurizer Heater Groups. An evaluation has previously demonstrated that Mode 3 Hot Standby could be maintained with no charging pumps or pressurizer heaters available, but it has not been determined if Mode 5 could be achieved. Therefore, this missing fire barrier meets the reporting criteria for 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "The protection of the health and safety of the public was not affected by this issue. Unit 1 is in mode 6 and no fire has occurred. Compensatory measures (fire watches) are in place for Fire Area 32. "The licensee has notified the NRC Senior Resident Inspector." Unit 2 has a different cable routing and is not affected. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-10-13
50530 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-10-13 13:27 | 2014-10-13 15:39 | 2014-10-13 | OFFSITE NOTIFICATION - DROPPED CONTROL ROD DURING REFUELING OPERATIONS "At 1530 CDT on 10/13/14, Cooper Nuclear Station will make a press release to the local media. This press release is with regards to the control rod blade which was dropped over the core during refueling operations when the control rod blade fell from the lifting tool and came to rest on the reactor vessel top guide in a section that contained no fuel. This press release was authorized at 1327 CDT." The control rod was dropped on 10/11/2014. There was no damage to the reactor fuel. The control rod is being replaced and is in the spent fuel pool. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-13
50529 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-10-13 07:58 | 2014-10-13 11:13 | 2014-10-13 | AUTOMATIC REACTOR TRIP DUE TO A SPURIOUS OVERPOWER / DELTA TEMPERATURE SIGNAL "Unit 2 reactor automatically tripped at 0758 [EDT] hours on 10/13/2014, due to a spurious overpower/delta temperature signal on all three channels. The cause of the spurious signal is unknown at this time. Currently, reactor coolant system temperature is being maintained stable at 546 [F] degrees. All three auxiliary feedwater pumps automatically initiated as designed on low-low steam generator level following the trip. All systems responded as expected with the exception [both] of the intermediate range neutron indication[s], which was determined to be under-compensated. The source range indication did not automatically energize and was energized manually. All other systems operated as required. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of reactor protection system activation and 10 CFR 50. 72(b )(3)(iv)(A) for 8-hour notification of automatic actuation of auxiliary feedwater. The NRC resident has been notified of this event and is on site. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events." There was no testing in progress when the reactor trip occurred. The reactor trip was considered uncomplicated. All control rods fully inserted. Decay heat is being released via main feedwater and the condenser steam dumps. Normal offsite power is available. There was no effect on Surry Unit 1 which continues to operate at 100% power. The licensee is investigating the cause of the overpower/delta temperature actuation. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-10-13
50528 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-12 20:18 | 2014-10-12 22:17 | 2014-10-16 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. * * * RETRACTION PROVIDED BY MIKE NIEMEYER TO JEFF ROTTON AT 1449 EDT ON 10/16/2014* * * Investigation revealed the compensatory measures were established within requirements to make this event a loggable event under 10 CFR 73, Appendix G (II)(a). The licensee notified the NRC Resident Inspector. Notified R4DO (Haire) and Part 73.71 Group via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-10-12
50527 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-12 06:00 | 2014-10-12 13:07 | 2014-12-02 | SERVICE WATER PUMPS INOPERABLE "At 0226 [EDT on 10/12/14], the 25 Service Water Pump Traveling Screen differential pressure transmitter high side valve, 2LD2729-HIV was discovered closed while performing the monthly bubbler blow down activity. The associated 25 Service Water Pump was operable at this time. The differential pressure transmitter high side valve, 2LD2729-HIV, in the closed/discovered position would have prevented the operation of the 25 Service Water Traveling Screen due to high differential pressure. The 25 Service Water Traveling Screen needs to be operable to support 25 Service Water Pump operability. 25 Service Water Pump Traveling Water Screen was restored to operable after differential pressure transmitter high side valve, 2LD2729-HIV was reopened. The station subsequently verified all Unit 1 and 2 high side and low side differential pressure transmitter valves positions were correct. "At 0600 [EDT on 10/12/14], it was identified that the last manipulation of differential pressure transmitter high side valve, 2LD2729-HIV was on 9/7/14. Based on the last known manipulation it is assumed that differential pressure transmitter high side valve, 2LD2729-HIV remained closed from that time until the condition was discovered. Review of other activities performed from 9/7/2014 to present determined that surveillance testing of 21 Service Water Pump resulted in 21, 22, and 23 Service Water Pumps being inoperable on 9/18/2014 for several hours. During that surveillance, combined with the mis-positioned instrument valve on 25 Service Water Pump, five of the six Service Water Pumps would have been inoperable which may have prevented the fulfillment of a safety function. "This event is being reported under the requirements of 10CFR50.72(b)(3)(v)(B) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to remove residual heat.' "The licensee has notified the NRC Resident Inspector. No one was injured as a result of the failure of 25 Service Water Traveling Screen inoperability." * * * RETRACTION FROM ROBERT CORDREY TO DONALD NORWOOD AT 1543 EST ON 12/2/2014 * * * "The purpose of this call is to retract event number 50527. On October 12, 2014, at 1307 EDT, notification was made to the NRC Operations Center by Salem Unit 2 reporting a condition under the requirements of 10CFR50.72(b)(3)(v) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function of structures or systems that are needed to: ...(D) Mitigate the consequences of an accident.' "Subsequent to this report, Salem Unit 2 determined that the condition in which the 25 Service Water (SW) pump may have been considered inoperable, in conjunction with the other SW loop being out of service, was not occurring at the time of discovery and was thus not reportable under the reporting requirement of 10CFR50.72(b)(3)(v). "Further analysis of the event determined that the valve mis-positioning of the 25 SW pump traveling screen differential pressure transmitter which defeated the auto-start function of the traveling screen, did not impair the safety function of the traveling screen to minimize carryover of debris to the suction of the 25 SW pump. Thus, during the time in question, the 25 SW pump remained operable which maintained one loop of SW operable during the period of time the other service water loop was removed from service for pump testing. One loop of SW with two pumps operable from different safety related buses is capable of performing the safety function of the SW system during a design basis accident. "This event is not considered a safety system functional failure and is not reportable to the NRC under the requirements of 10CFR50.72(b)(3)(v) or 10CFR50.73(a)(2)(v). "The NRC Resident Inspector has been notified." Notified R1DO (Dentel) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2014-10-12
50526 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-12 09:44 | 2014-10-12 12:41 | 2014-10-12 | MANUAL REACTOR TRIP DURING REACTOR STARTUP "VEGP [Vogtle Electric Generating Plant] Unit 2 was performing startup and had taken reactor critical at 0929 EDT. When attempting to stabilize power to collect critical data, control rods were inserted with Control Bank D the expected group to insert. Control Bank A inserted instead of Control Bank D. Power had reached 6 E-2 percent as indicated by IR [intermediate range] indication when control room crew performed a manual reactor trip. AFW [auxiliary feed water] was in service to support plant conditions prior to the trip and did not receive any actuation signal. All equipment operated as expected. Unit 2 is currently stable in Mode 3 at normal operating temperature and pressure." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-10-12
50525 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-10-12 04:26 | 2014-10-12 10:29 | 2014-10-12 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE FOR MEDICAL TREATMENT "At 0426 CST [on 10/12/14], a potentially contaminated individual [contract employee] was transported off-site for medical attention at Nemaha County Hospital. The individual had been working in a contaminated area in the main condenser. When the Incident Commander (IC) and Emergency Medical Technicians (EMT) arrived on station the individual was no longer in the contaminated area but was still in the Radiological Controlled Area (RCA). Radiological Protection personnel were dispatched with the individual in the ambulance and surveyed him in route. At 0445 CST, prior to arrival at the hospital, it was confirmed that the individual was not contaminated." The individual was suffering from a heat related medical condition. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2014-10-12
50524 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-10-12 02:51 | 2014-10-12 05:22 | 2014-10-17 | AUTOMATIC REACTOR SCRAM DUE TO DECREASING REACTOR WATER LEVEL "Today at approximately 0250 (EDT) [on 10/12/14], during a planned reactor power ascension with reactor power at approximately 1% of rated thermal power, reactor water level began lowering. Operators inserted a manual SCRAM at 0251 (EDT) in accordance with station procedures. The cause of the lowering reactor level is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. The plant is currently shutdown and plant parameters are stable. "This event is reportable per 10CFR50.72(b)(2)(iv)(B) - 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" Decay heat is being released to the main condenser and normal offsite power is being maintained. The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JOSH MCGUIRE TO JEFF ROTTON AT 1520 EDT ON 10/17/2014 * * * "An automatic SCRAM occurred at 0251 EDT, moments before operators inserted a manual SCRAM in accordance with station procedures." The licensee notified the NRC Resident Inspector. Notified R1DO (Cook). | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-10-12
50523 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-10-10 17:17 | 2014-10-11 00:03 | 2014-11-18 | MISSING FIRE BARRIER "During a Fire Penetration walkdown, an opening less than 1 [inch] tall under a duct was identified between the Train B Aux Feedwater Pump (AFWP) Room (Unit 1 side) and the Bus150/160 room. This constitutes a missing fire barrier between Fire Area (FA) 32 and FA 37 such that the required degree of separation for redundant safe shutdown trains is lacking. "A firewatch has been established on the Unit 1 side of the AFWP Room and Bus 150/160 room. The compensatory fire watch will remain in place per F5 Appendix K until the fire barrier is returned to full functional status. "The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(B). "The protection of the health and safety of the public was not affected by this issue. "The licensee has notified the NRC Resident Inspector of this event." * * * RETRACTION FROM DOUG LARSON TO DANIEL MILLS AT 2118 EST ON 11/18/2014 * * * "Northern States Power Company (NSPM) has determined that the opening under the duct is not separating redundant equipment and no longer meets the regulatory definition of an unanalyzed condition. This was identified when it was determined that the redundant pressurizer heater cables credited for safe shutdown were routed through the same fire area. This was reported under EN 50531 (Unanalyzed Condition Due To Missing Fire Barrier). Since the missing fire barrier does not separate redundant equipment, the condition does not degrade plant safety, and is no longer reportable. "The protection of the health and safety of the public was not affected by this issue. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Peterson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-10-11
50522 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-08 15:30 | 2014-10-09 11:30 | 2014-10-09 | FITNESS FOR DUTY - NON LICENSED SUPERVISOR IN VIOLATION OF THE FITNESS FOR DUTY POLICY A non-license supervisor has been found in violation of the Duke Energy Fitness for Duty Policy. The individual's access to the plant has been suspended. The NRC Resident Inspector has been informed. The licensee will be notifying State and Local authorities. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2014-10-09
50521 | 0 | SHAW PIPELINE SERVICES, INC. |  |  |  |  | 2014-10-08 16:00 | 2014-10-08 18:53 | 2014-10-11 | LOST RADIOGRAPHY CAMERA DURING SHIPMENT The licensee had two SPEC-150 radiography cameras shipped from their job site in Morgan Hill, California on 9/30/2014 to their office in Broken Arrow, Oklahoma. One of the radiography cameras arrived at the destination, but as of 10/1/14, the last known location of the second camera was in Memphis, Tennessee. The licensee contacted the common carrier's customer service and the dangerous goods department to locate the shipment. According to the dangerous goods department supervisor, the common carrier is investigating a radiation alarm at one of their dumpsters which may contain the radiography camera. The licensee will follow up with the common carrier on the morning of 10/9/14 to receive a status of their search. The lost SPEC-150 radiography camera contains less than 57 curies of Ir-192. The licensee has notified the State of Oklahoma. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, Nuclear SSA, FEMA National Watch Center, and DNDO-JAC. * * * UPDATE FROM SHANE OWENS TO HOWIE CROUCH (VIA EMAIL) ON 10/9/14 AT 0902 EDT * * * The licensee provided the shipper's declaration for dangerous goods, the shipping label, and tracking information from the shipper. They will continue communications with the common carrier and provide updates as necessary. The State of Oklahoma has notified the Tennessee State Radiation Protection Program. Notified R4DO (Allen), NMSS (Dudes), ILTAB (Bunch), IRD (Stapleton) and FSME Events Resource email. * * * UPDATE FROM SHANE OWENS TO DONALD NORWOOD ON 10/9/2014 AT 1214 EDT * * * The licensee was informed by the common carrier that the search of their dumpster revealed that the radiography camera was not in the dumpster. The common carrier told the licensee that they had enlisted more personnel and had stepped up their search for the package containing the radiography camera. Notified R4DO (Allen), NMSS (McCartin), ILTAB (Hahn), IRD (Stapleton) and FSME Events Resource email. * * * UPDATE FROM KEVIN SAMPSON TO DONALD NORWOOD ON 10/9/2014 AT 1402 EDT * * * The following information was received via e-mail from the Oklahoma Department of Environmental Quality: "On September 30, 2014, a package containing 57 Ci of Ir-192 was shipped from California to Shaw Pipeline Services, OK license OK-23193-02. The package was scheduled to arrive in Oklahoma on October 3, 2014. On October 6, 2014, it was discovered that the package still had not arrived. On October 6, 2014, Shane Owens [licensee RSO] contacted [the common carrier] to start looking for the package. On October 7, 2014 [the common carrier] began a search. [The common carrier] identified that the package entered Memphis [common carrier's] Hub on October 1, 2014, but did not leave. [The common carrier] identified a dumpster that caused radiation alarms to alert. At that time, [the common carrier] did not have the proper tools or personnel to handle the package, but they will contact Shaw Pipeline on October 9, by 0900 CDT to announce their findings. "Object in the dumpster has been identified and is not the missing radiographic device." Notified R4DO (Allen), NMSS (McCartin), ILTAB (Hahn), IRD (Stapleton) and FSME Events Resource email. * * * UPDATE FROM SHANE OWENS TO DONALD NORWOOD ON 10/11/2014 AT 1653 EDT * * * The radiography camera has been found at the common carrier's facility in San Jose, California where it had been originally dropped off for shipment. As of 1300 PDT on 10/11/2014, Shaw Pipeline Services has retaken possession of the radiography camera and verified that the radioactive source is in a safe condition. Notified R4DO (Allen), NMSS (Dudes), NMSS (McCartin), ILTAB (Hahn), IRD (Stapleton) and FSME Events Resource email. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, Notified the following via E-mail only: FDA EOC, Nuclear SSA, FEMA National Watch Center, and DNDO-JAC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/MISSING CAT 2 RAD MATL IN TRANSIT | [9 empty] | NON EMERGENCY | 4 | OK | OTH |  | 37.81(b) |  |  |  | 0 | 2014-10-16
50520 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-10-08 10:40 | 2014-10-08 17:54 | 2014-10-08 | POTENTIAL LEAK FROM A PIPE COULD RESULT IN DAMAGE TO BOTH TRAINS OF ELECTRICAL POWER SYSTEMS "This is a non-emergency notification. "At approximately 10:40 AM on October 8, 2014, with the Harris Nuclear Plant operating at 100% power, a condition was discovered where a potential leak from a pipe supplying water to the fire suppression system in the diesel fuel oil storage tank building could result in damage to equipment in both trains of the onsite electrical power system. "Neither the leak from the piping nor the damage to equipment actually occurred, so there are no actual safety consequences and no impact to public health and safety or the environment due to this condition. "The condition was discovered during a Harris staff evaluation in the corrective action program. The condition will be fully investigated, including the extent of condition, and corrective actions taken to resolve the issue. Compensatory actions have been taken as interim actions to ensure safety systems are not impacted by the potential pipe leak. "This event is reportable per 10 CFR 50.72(b)(3)(v). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2014-10-08
50519 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2014-10-08 10:35 | 2014-10-08 15:39 | 2014-10-08 | POTENTIAL FIRE INDUCED CABLE FAILURE IN MULTIPLE FIRE ZONES "INPO-IER-L4-14-33 (Direct Current Circuits Challenge Appendix R Fire Analysis) was reviewed to determine applicability to ANO Unit 1 & 2. It was determined that 2P-21, Turbine Generator Emergency Seal Oil Pump, control cables are not fused and are routed through multiple fire zones containing safe shutdown equipment. A potential fire induced cable failure in any of these fire zones could result in a secondary fire or damage adjacent cables along the path of the unprotected cable. The concern is that under fire safe shutdown conditions, it is postulated that a fire in one zone can cause short circuits potentially resulting in secondary fires or cable failures in other fire zones where the cables are routed. The secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected zones of the plant. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation |  | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-10-08
50518 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-10-08 04:45 | 2014-10-08 07:24 | 2014-10-08 | SODIUM HYPOCHLORITE LEAK WITH POTENTIAL TO ENTER THE ENVIRONMENT "This notification is being made as a result of notifications to other government agencies. A sodium hypochlorite leak occurred on site at Limerick Generating station on 10/7/14, that had the potential to enter the environment. The leak has been isolated. A flow control valve in the U1 cooling tower chemical treatment system caused the leak. The sodium hypochlorite that leaked was deposited into the onsite Holding Pond. The Holding Pond was being discharged at the time of the leak in accordance with procedures to support normal plant operations. The leak was discovered at 2110 hours [EDT on 10/7/14] and isolated at 2115 hours. The Holding Pond discharge was secured at 2125 hours. Sampling of the Holding Pond confirmed the presence of sodium hypochlorite. Since the Holding Pond was being released at the time of the leak, there is a potential that greater than 67 gallons of sodium hypochlorite could have been released to the Schuylkill River. This report is being made due to the potential that a reportable quantity of sodium hypochlorite could have discharged to the Schuylkill River while the Holding Pond was releasing during the sodium hypochlorite leak. Evaluations are being performed to quantify this actual volume of sodium hypochlorite that was discharged as a result of the leak." The licensee has notified the NRC Resident Inspector and state and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-08
50517 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-07 19:00 | 2014-10-07 21:22 | 2014-10-07 | ULTRASONIC TESTING REVEAL DEGRADED CONDITION ON ONE CONTROL ROD DRIVE MECHANISM PENETRATION "In accordance with 10 CFR 50.72(b)(3)(ii)(A), this notification reports a degraded condition on Byron Station Unit 2 that occurred on October 7, 2014, when it was determined that the results of planned ultrasonic testing (UT) examinations performed on one CRDM penetration of the reactor vessel head would not meet the applicable acceptance criteria. Byron Station Unit 2 is presently in day eight of a refueling outage. The examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1 to ensure the structural integrity of the reactor vessel head pressure boundary. The UT examinations continue for the remaining CRDM head penetrations. The repairs are currently being planned and will be completed prior to unit start-up. "The NRC Resident Inspector has been notified of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-10-07
50516 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-04-22 | 2014-10-07 15:42 | 2014-10-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was obtained from the State of New Jersey via facsimile: "TCNJ [The College of New Jersey] reported the loss of up to 63 radioluminescent exit signs. The signs had been removed from a building slated for demolition and were stored until proper disposal could be arranged. Each Safety Light corporation sign contained between 278 and 851 GBq of H-3. TCNJ was not sure of the actual total of signs possessed by them. They believe that a box containing up to 51 signs was accidentally picked up on 1/8/14 by a contractor removing electronic waste." New Jersey Incident Number: 04-22-14 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-10-15
50515 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-04-12 | 2014-10-07 15:42 | 2014-10-07 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was obtained from the State of New Jersey via facsimile: "One gauge (Berthold LB-7444-D-CR) containing 3.7 GBq Co-60 source was stuck in the closed position. One gauge (Berthold LB-7444-CR) containing 18.5 GBq Co-60 source was stuck in the open position. These malfunctions were discovered during the routine NJDEP [New Jersey Department of Environmental Protection] inspection and survey." New Jersey Incident Number: 512693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-10-15
50514 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-09-23 | 2014-10-07 15:42 | 2014-10-07 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATOR The following information was obtained from the State of New Jersey via facsimile: "A static eliminator (NRD P-2021-8101, S/N A2PH963/048648) was likely stolen. It contained 0.37 GBq Po-210 source (assayed on 4/18/11). "New Jersey Incident Number: 9/23/2011" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-10-15
50513 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2014-10-07 12:20 | 2014-10-07 15:40 | 2014-10-07 | INADVERTENT SIREN ACTUATION "At approximately 1230 EDT on October 7, 2014, Seabrook Station was notified by Rockingham County Dispatch that an inadvertent activation of the Public Alert Notification System (PANS) sirens in Newtown, NH occurred at 1220 EDT. The activation was caused by an apparent human error during procedure review by a town of Newton employee. The sirens sounded, reset, and are functional. This event is being reported as it may generate media interest. No press release is planned at this time. "The NRC Senior Resident Inspector and Region I have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-07
50512 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-10-06 | 2014-10-06 16:32 | 2014-10-06 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following was received from State of California via email: "On October 6, 2014, at approximately 1245 [PDT], [Deleted], RSO [Radiation Safety Officer] of RMA Group, RML [Radioactive Materials License] #2700-36, contacted RHB [Radiological Health Branch] Brea concerning the moisture/density gauge, Troxler, model 3430, serial number 28356 (Cs-137, 0.3 GBq, Am-241, 1.50 GBq) that had been stolen from a transport vehicle in front of a private residence in El Monte at approximately 0700 [PDT]. [The RSO] has contacted the Local Law Enforcement officials in El Monte to request an investigation of the private residence where the Troxler radioactive gauge was taken and to take the report of the authorized user that was in possession of the gauge prior to the theft. A copy of the theft report will be sent to RHB Brea as part of this report. [The RSO] will utilize local papers to attempt to retrieve the stolen gauge as well as notifying local servicing vendors of radioactive gauges to be alert of the serial number of the stolen gauge in case it turns up for any of their services. The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. This is being reported to the NRC Operations Center as a 24-hour report under 10CFR30.50(b)(2) since the radioactive gauge has been stolen and it cannot be determined what condition the sources are currently in." California Event No.: 100614 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-10-14
50511 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-10-06 10:59 | 2014-10-06 15:35 | 2014-10-06 | OFFSITE NOTIFICATION DUE TO FISH FOUND DEAD AFTER ZEBRA MUSSEL TREATMENT "At 1059 CDT on October 6, 2014, the State of Minnesota and Environmental Services were notified that approximately 100 fish were found dead against the trash racks of the plant screen house. The licensee had completed zebra mussel treatment several days prior to this event and the fish deaths are attributed to this treatment. "This is reportable under 10 CFR 50.72 (b)(2)(xi), News Release or Notification of Other Government Agency. "The protection of the health and safety of the public was not affected by this issue. "The licensee has notified the NRC Senior Resident Inspector." | 84 | 99 | 0 | 84 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-10-06
50510 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-10-06 13:36 | 2014-10-06 15:00 | 2014-10-06 | ALERT DECLARED - FIRE IN A DIESEL GENERATOR POTENTIAL TRANSFORMER At 1336 CDT, Wolf Creek declared an Alert due to a fire. The fire in the "B" Emergency Diesel Generator potential transformer was extinguished using a portable CO2 fire extinguisher. Plant personnel were exposed to the smoke and were evaluated with no injuries noted. The plant continued to operate at 100% power throughout the event. The licensee notified the NRC Resident Inspector, State of Kansas Division of Emergency Management, and the Coffey County Sheriff Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email. * * * UPDATE AT 1648 EDT ON 10/6/2014 FROM AARON LUCAS TO MARK ABRAMOVITZ * * * The Alert was terminated at 1542 CDT because the fire had been terminated within fifteen minutes and a walkdown of the area was clear. The licensee notified the NRC Resident Inspector. Notified the R4DO (Allen), IRD (Grant), NRR (Lee), DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email.. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-10-06
50509 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-10-04 14:08 | 2014-10-04 22:02 | 2014-12-02 | CONTAINMENT LEAK RATE EXCEEDS ACCEPTANCE CRITERIA "The total as-found Minimum Pathway Leakage Rate for the Primary Containment exceeded Level 1 acceptance criteria. Acceptance criteria of 321 (Standard Liters per Minute) SLM was not met. This criteria is equivalent to 1.0 La, the maximum allowable Primary Containment Leakage rate as prescribed by Technical Specification 5.5.6.c.1. "This is reportable under 10CFR50.72(b)(3)(ii)(A) as 'The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded .. ' All other Level 1 acceptance criteria were met. "All as-left containment leakage requirements for startup have been met." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM DUSTIN SCURLOCK TO DANIEL MILLS AT 1646 EST ON 12/02/2014 * * * "On October 4, 2014, FitzPatrick reported that the total as-found containment minimum pathway leak rate exceeded the maximum allowable containment leak rate per the containment leakage rate testing program. This was primarily due to the drywell exhaust Penetration X26A/B. Penetration X26A/B Local Leak Rate Testing (LLRT) results were initially indeterminate, and therefore conservatively assumed to exceed the primary containment leakage acceptance criteria. "The excessive leakage was assumed for Penetration X26A/B due to LLRT results for two (2) containment isolation valves (CIV). The subject CIVs are installed in series on Penetration X26A/B. The upstream valve is not isolable from primary containment, therefore, LLRT testing for these two CIVs is performed simultaneously via pressurization through a test connection between the two valves. During the LLRT, Penetration X26A/B was pressurized to 44.42 psig. The required test pressure for this penetration is 45.3 psig. As the required test pressure was not achieved, the LLRT results were initially indeterminate. Excessive leakage was conservatively assigned to the penetration resulting in the failure of the primary containment leakage acceptance criteria. This condition (failure of the primary containment leakage acceptance criteria) was determined to be reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) as a condition of the nuclear power plant, including its principle safety barriers, being seriously degraded. "A subsequent engineering evaluation addressed the leakage for Penetration X26A/B, and concluded that the LLRT test results did not reflect failure of the primary containment leakage acceptance criteria. "The installed configuration prevents testing these valves individually; however, troubleshooting activities indicated no detectable leakage through the downstream valve. The upstream valve was removed and inspected. The results of the inspection confirmed that all LLRT leakage was attributable to the upstream valve. Following maintenance activities, the valve was reinstalled and Penetration X26A/B was retested. The post-maintenance LLRT resulted in a total leakage of 0.078 SLM for Penetration X26A/B. "The resultant total primary containment leakage rate determined on a minimum pathway basis was below the operability limits of 192 and 321 SLM (0.6 La and 1.0 La, respectively). Primary containment remained operable throughout Cycle 21; no degraded condition existed. Therefore, this [event notification] is being retracted." The licensee has notified the NRC Resident Inspector. Notified R1DO (Dentel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-10-04
50508 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-10-03 13:40 | 2014-10-03 17:44 | 2014-10-03 | FITNESS FOR DUTY - CONTRACT SUPERVISOR IN VIOLATION OF FITNESS FOR DUTY POLICY "A Supplemental Supervisor failed a random Fitness For Duty test as determined by the Medical Review Officer. Unescorted access has been revoked pending review. Work performance investigation will be conducted. This event is being reported in accordance with 10CFR26.719(b)(2)(i)." The licensee will notify the State of New Jersey and Delaware. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2014-10-03
50507 | 0 | AREVA INC. |  |  |  |  | 2014-08-28 | 2014-10-03 16:48 | 2014-10-03 | PART 21 - DEFECT IN THE INPUT TO CALCULATE THERMAL LIMITS The following was received via email by Areva Inc.: "(i) Name and address of the individual or individuals informing the Commission. Alan B. Meginnis, AREVA Inc., 2101 Horn Rapids Road, Richland, WA 99354. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. The defect is in the input to a program that calculates the minimum critical power ratio (MCPR) and linear heat generation rate (LHGR) thermal limits for Browns Ferry Unit 2 Cycle 18. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. AREVA Inc. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. This issue is a defect as defined in 10 CFR 21.3. The error is an omission in the POWERPLEX core monitoring software system input that could result in the application of non-conservative nuclear fuel operating thermal limits when the reactor is operated at 25 to 30% power. In the event of an abnormal operational occurrence while operating in this power range, a fuel thermal safety limit could be exceeded. "(v) The date on which the information of such defect or failure to comply was obtained. August 28, 2014 "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. The defect exists only for Browns Ferry Unit 2 Cycle 18. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. AREVA Inc. recommended plant operations be restricted to provide enough margin to the MCPR and LHGR thermal limits anytime power is in the range 25% < P < 30%. AREVA has also provided revised POWERPLEX input to TVA for Browns Ferry Unit 2 Cycle 18 to correct the error permanently. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. This defect only had the potential to exceed the safety limit minimum critical power ratio (SLMCPR) and/or one of the Specified Acceptable Fuel Design Limits if an AOO [anticipated operational occurrence] occurred during the brief periods the plant was at power levels in the range 25% < P < 30% during Cycle 18. The plant has not had any such events in Cycle 18. The identified defect is a human performance error impacting only Browns Ferry Unit 2 Cycle 18. It does not affect other operating cycles, Browns Ferry Units, or other nuclear plants." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-10-03
50506 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-10-02 22:51 | 2014-10-03 13:53 | 2014-10-03 | INITIATION OF MATERIAL CONTROL AND ACCOUNTABILITY ALARM RESOLUTION PROCEDURE "10 CFR 74.57(f)(2) requires notification within 24 hours that a Material Control & Accountability (MC&A) alarm resolution procedure has been initiated. In the Solvent Extraction Area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure was initiated, this notification is being made. The MC&A investigation quickly resolved the alarm per the criteria in the NFS [Nuclear Fuel Services] Fundamental Nuclear Material Control Plan (FNMCP). No material loss has occurred. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 1 | 2014-10-17
50505 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-09-30 14:35 | 2014-10-03 12:22 | 2014-10-08 | AGREEMENT STATE REPORT - PRELIMINARY REPORT ON A CONTAMINATED EMPLOYEE The following was received from the State of Tennessee via email: "Not much information is known at present, but on September 30th, an employee at Siemens was involved in some type of exposure that resulted in a skin dose contamination. No other spread of contamination has been noted. REACT/s was notified via Siemens and is being used for additional consultation. Awaiting more information from the licensee on [the type of] isotopes involved, a full detailed report of the incident, and their plan of action for the employee. Will update accordingly." TN ID NO.: TN-14-186 * * * UPDATE ON 10/6/14 AT 1539 EDT FROM SABRINA ROBERTSON TO DONG PARK * * * The following report from the licensee was received from the State of Tennessee via email: "Description of the Event "On 9/30/2014 at approximately 2:35pm, [an employee] was drawing activity to manufacture line sources out of a stock vial of Ge-68. She drew up the required activity into a syringe and when she removed the syringe from the rubber septum of the Ge-68 DTPA stock solution vial, the vial evidently became pressurized and sprayed liquid on to her nasal facial area. Another employee in the area immediately notified the Radiation Safety Officer (RSO). "Mitigation "The Radiation Safety Department responded and assisted with decontamination of the affected areas. Decontamination was started approximately 15 minutes after notification of the incident. A water lavage of the facial area was performed and washing of the affected area with hand soap and shaving cream. Wet nasal swabs were used to remove contamination from the nasal passage. After decontamination it was determined that the contamination was confined to the area around her nose and mouth, including inside her nasal passage. Since that time she has collected all nasal excretions and any sputum, as well as wipes of her skin in the affected area. Radiation surveys are done several times per day to ascertain activity reduction. We are continuing to perform surveys, nasal swabs and urine bioassays until all contamination is removed. To date all urine bioassay samples have been within the range of background. REAC/TS was contacted on October 2, 2014 to determine if they had any further ideas for contamination removal. They recommended the use of make-up removal pads on the face, but did not have any further ideas for removal of contamination from the nasal passage. "Dose Estimation "Using the surveys and an initial estimated activity for the contamination event of 76 microCuries in the highest affected area, VARSKIN was used to calculate dose to the skin. Initial calculations estimated the dose to remain below regulatory limits. On October 2, 2014 the Health Physicist running the VARSKIN program noticed that it was not calculating the dose from both Ge-68 and its daughter Ga-68. The calculations were revised and the results exceeded the regulatory limits. The RSO notified the State of Tennessee Division of Radiological Health on October 3, 2014. As of October 3, the calculations showed that skin dose is approximately 132 rem, which exceeds the regulatory limit of 50 rem. [The employee] has been notified of her estimated dose levels and has been involved with decontamination procedures. We will continue to adjust the total dose daily as surveys are performed. We will submit the final dose number when all contamination is removed and calculations are completed. Our current estimated dose at 10 days from today with no further removal of contamination is 240 rem to the skin." Notified R1DO (Bower) and FSME Events Resource via email. * * * UPDATE FROM SABRINA ROBERTSON TO HOWIE CROUCH (VIA EMAIL) AT 0825 EDT ON 10/8/14 * * * The following update was received from the State of Tennessee via email: "Summary of the long-term plan for monitoring the employee We will continue to monitor the employee's nasal facial area daily, collect and count wipe samples from skin in the affected area and nasal secretions, collect and count urine bioassay samples for at least the next week (October 14, 2014) unless all measurements are within the range of background before that date. We will assess the value of continued measurements at that time. "Contamination and projected 10-day calculated skin dose for Monday, October 6 and Tuesday, October 7, 2014. The two areas from which skin dose is being estimated are the bridge of the nose (#1) and the tip of the nose (#2). Measurements are taken using a pancake GM detector (Ludlum 44-9). Skin dose is calculated using VARSKIN. "October 6 - contamination readings: #1 = 840 cpm; #2 = 4940; calculated skin dose @10 days = 229, 934 mrad "October 7 - contamination readings: #1 = 740 cpm; #2 = 6040 cpm; calculated skin dose @ 10 days = 239, 070 mrad "[Licensee staff] are trying to determine a more realistic efficiency for the Ludlum 44-9 GM detector, as we believe it is closer to that of P-32 than to F-18. The use of a higher efficiency will substantially reduce the calculated dose. As you suggested, we have contacted REAC/TS about conduct an independent verification of our skin dose calculation. They informed us they are not able to conduct independent verification. However, they did provide us with consultants who are able to provide this service. "Finally, as we discussed [with the State of Tennessee], Siemens will provide you with a daily update of the contamination readings and 10-day projected skin dose." Notified R1DO (Bower) and FSME Events Resource email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-10-13
50504 | 0 | ELECTROSWITCH |  |  |  |  | 2014-09-30 | 2014-10-03 10:15 | 2014-10-03 | PART 21 REPORT - SERIES 20 MODULE MAY ALLOW THE SIDE COVER TO TOUCH THE WIRE INSULATION The following information was excerpted from report received via email: "The orientation (90 degrees) of the placement (soldering) of the internal wire on the resistor terminal used in the above referenced Series 20 modules may allow the side cover screw to touch the wire insulation. The engineering drawing nor manufacturing assembly instructions did not clearly describe the correct orientation. "On the basis of our evaluation, it was determined on September 30, 2014, that Electroswitch does not have the capability to perform the evaluation to determine if a defect, which could create a substantial safety hazard, exists. "Purchasers are being advised to perform testing to verify operation or return the product to Electroswitch. "The following personnel may be contacted regarding this notification: Larry Friedman Quality Assurance Manager 781-607-3309 Ed Reszenski Engineering Manager 781-607-3341" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-10-03
50503 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-08-01 | 2014-10-02 13:55 | 2014-10-02 | AGREEMENT STATE REPORT - LOCKING MECHANISM FAILURE The following information was received via facsimile: "On October 2, 2014, during a complaint investigation, the Agency [Texas Department of Health Services] confirmed allegations that on August 1, 2014, one of the licensee's industrial radiography crews had experienced a mechanical failure on an INC Model IR-100 exposure device that contained a 34 curie Iridium-192 source. Following the last exposure of the day, the source failed to retract into the locked and secure position within the device. The locking mechanism had tripped while the ball stop was outside the lock. The source was inside the s-tube but not in the locked position. The source could not be cranked out of the guide tube either. The key was removed and the radiographer was unable to unlock the camera when the key was re-inserted to retract the source. The radiographer was able to manipulate the locking mechanism so that the lock reset and the source was fully retracted. The licensee reported that its investigation [had determined] no one had exceeded any dose limits as a result of this event. The licensee did not believe it was a reportable event and did not notify the Agency. The exposure device was cleaned and returned to service by the licensee. Further information will be reported in accordance with SA-300 as it is obtained." Texas Incident #: I-9241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-10
50502 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2014-10-01 01:24 | 2014-10-01 15:07 | 2014-10-27 | PARTIAL LOSS OF COMMUNICATIONS IN EMERGENCY OPERATIONS FACILITY AND JOINT INFORMATION CENTER "At 0750 EDT on October 1, 2014, the Shift Manager was notified that site Information Technology (IT) personnel were being mobilized to investigate a potential voice and network loss at the Emergency Operations Facility (EOF) and Joint Information Center (JIC). Site IT personnel were notified by offsite IT resources at 0727 EDT on October 1, 2014 of the issue that was first identified by IT monitoring software at 0124 on October 1, 2014. "The site IT personnel that responded to the EOF and JIC reported to site Control Room and Emergency Preparedness (EP) personnel at 0845 that connectivity to the Exelon network and the internet was unavailable at both the EOF and the JIC. This loss of connectivity would prevent the ability of the EOF Emergency Response Organization (ERO) personnel to directly monitor key plant parameters via the site's Plant Process Computer (including the Site Parameter Display System) and other network-based plant parameter display systems. "Site IT and EP personnel determined that the following communications equipment was not impacted by the connectivity issue: - Dedicated Offsite Agency Phones (primary method for contacting state and local agencies) - Commercial Phones and dedicated bridge line (primary method for contacting other site Emergency Response Facilities) - FTS-2001 Phones (e.g., ENS and HPN lines) - ERDS "Additionally, EP personnel verified with Dose Assessment Office personnel that dose assessment and dose monitoring functions from the EOF could still be performed without delay. "Site IT personnel reported to the Control Room at 1135 that connectivity to the Exelon network and the internet had been restored to a fully functional status. "While site and fleet IT personnel continue to address and verify all appropriate corrective actions have been taken to prevent recurrence of the connectivity issue, the site has employed appropriate compensatory measures to ensure that the verbal transmission of key plant parameters from the site (Technical Support Center or Control Room) to the EOF is recognized and maintained. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM TIM HUBER TO JEFF ROTTON AT 1208 EDT ON 10/27/2014 * * * "This update retracts Event Report #50502, which reported that a loss of connectivity to the Exelon network and internet at the Emergency Operations Facility (EOF) and Joint Information Center (JIC) had impacted the ability of staff in these facilities to directly monitor key plant parameters via the site's Plant Process Computer and other network-based plant parameter display systems. "Subsequent to the identification of this event, further investigation by site and fleet staff determined that adequate direction was included in applicable Emergency Response Organization (ERO) procedures to respond to data display system failures of this type. Specifically, the checklist (procedure) for the Operations Communicator in the EOF provided adequate direction for this ERO member to obtain required plant data from the Operations Communicator located in the Control Room via alternate methods (e.g., over the phone - phone lines remained functional throughout the time that the loss of computer connectivity condition existed). "Therefore, this event did not result in a major loss of emergency assessment capability and was not reportable to the NRC under 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." Notified R1DO (Bickett) and Cyber Assessment Team via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-10-01
50501 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-30 | 2014-10-01 14:43 | 2014-10-01 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Texas via email: "On October 1, 2014, the Agency [Texas Department of State Health Services] received notice that on September 30, 2014, a radiography source disconnect had occurred at a temporary field site in east Houston. The camera was a Sentinel 880D (s/n D6746) with 68.3 curies of selenium-75 (s/n SE3877). The port cover had not been opened and the source had not been connected to the drive cable. Upon crank-out, the source was stopped at the port cover and could not be retracted. Retrieval was done by pushing the source back in via another drive cable from the other side. The person doing the retrieval received 38 mR to the body and 98 mR to the hand according to pocket dosimeters. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-09
50500 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-24 10:00 | 2014-10-01 13:05 | 2014-12-04 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Arkansas via email: "Mistras Group, Inc., ARK-1034-03310, reported the inability to retract a 2.738 TBq (74 Ci) Ir-192 source (Source QSA Global Model A424-9, Serial 10270G) into the radiography exposure device (QSA Global, Model 880 Delta, Serial D9086) on 9/24/2014. "During the morning of September 24, 2014, the radiographer's written statements indicated that a piece of pipe shifted and rolled onto the guide tube during an exposure. This action caused a crimp in the guide tube and the source was not retractable. "The radiography crew reset the boundaries to 2.0 mR/hr and contacted the home office. The RSO of the Baton Rouge, Louisiana office responded to the site. "The RSO reported that upon arrival, the radiography crew had reset the boundaries to 2.0 mR/hr. The source was located in the collimator and the crimp location was 6 inches from the collimator. The RSO placed 50 pounds of lead shot over the collimator and placed a metal plate under the crimp. The RSO then used a hammer to 'round out' the guide tube allowing the source to be retracted into the camera. The guide tube was removed from service and the crank-out was inspected for any damage. "The RSO stated that he wore an SRD [self-reading dosimeter] with a 0-200 mR range and this was found to be off-scale. The RSO was instructed by the State to submit the dosimetry badge for immediate processing. "The pocket dosimeters for the radiography crew were reported to read 1 mR and 0 mR respectively. "No other survey readings, other than the 2 mR/hr boundary, have been reported. "The State is tracking this event under Arkansas Event Number AR-2014-007 and is continuing to investigate this incident." * * * UPDATE FROM STEVE MACK TO JOHN SHOEMAKER AT 1245 EST ON 12/04/14 * * * The following report was received from the State of Arkansas via email: "The State of Arkansas is providing the following update to event 50500. "Dosimetry results for the individual performing the source retrieval were received and indicated that a dose of 1.0 millirem had been received. A dose reconstruction performed by the licensee indicated that the highest possible dose received during the source retrieval was 4.538 millirem. "The State of Arkansas agrees that there was no overexposure as a result of this source retrieval. The licensee provided corrective actions that included review of the licensee's source retrieval procedures and reporting procedures. "The [State of Arkansas] Department considers this event to be closed." Notified R4DO (Kellar) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2014-10-09
50499 | 0 | HIGH ENERGY DEVICES, LLC |  |  |  |  | 2014-09-26 16:00 | 2014-09-30 15:44 | 2014-10-07 | RELEASE OF KRYPTON -85 The licensee received 125 millicuries of Krypton-85 in a cylinder that was in excess of their license limit. The license limit is 5 millicuries. During an experiment to transfer the Krypton-85 to an evacuation chamber, the chamber did not pressurize as expected, and all 125 millicuries of Krypton-85 was evacuated to atmosphere. The licensee is still investigating the incident and will provide additional information when it becomes available. * * * UPDATE PROVIDED BY JOSEPH KOCH TO JEFF ROTTON AT 0835 ON 10/07/2014 * * * Licensee provided correction to the original report. Event date was 09/26/2014 at 1600 CDT. Notified R3DO (Orlikowski), FSME (McIntosh) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXCESSIVE RELEASE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2202(b)(2) |  |  |  | 0 | 2014-10-08
50498 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-09-28 08:30 | 2014-09-28 10:55 | 2014-09-28 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTIVATION OF AN EMERGENCY SIREN "On 9/28/14 at approximately 0830 EDT, the Operations Shift Manager was made aware that the Berrien County Sheriff's Department (BCSD) had been notified of an Emergency Siren that had actuated. BCSD was notified by local residents. BCSD reset the emergency siren and a local police officer verified the siren was no longer actuating. "The cause of the actuation is under investigation at this time. The siren remains in service pending further investigation. There are a total of 70 sirens and all remain functional. "This notification is being made under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report. "The licensee notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-09-28
50497 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-09-27 16:16 | 2014-09-27 20:09 | 2014-09-27 | REACTOR COOLANT SYSTEM SAFETY INJECTION LINE ULTRASONIC TEST INDICATION "On Friday, September 26, 2014, while performing planned inspections of Reactor Coolant System piping welds, one flaw indication was identified on each of two 1.5 inch Safety Injection Line connections to the Reactor Coolant System piping. On Saturday, September 27, 2014, after confirmatory inspections and evaluation, both of the flaw indications were determined to not meet the acceptance criteria specified in ASME Code Section XI. As such, these indications are reportable under 10 CFR 50.72(b)(3)(ii) as a Degraded Condition. A repair plan is being developed. There is no impact on current Unit 1 refueling operations while defueled and in No Mode. This condition and repair have no impact to the health and safety of the public or employees. "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-09-27
50496 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-09-25 22:00 | 2014-09-26 02:53 | 2014-11-20 | CONTAINMENT ISOLATION DECLARED INOPERABLE DUE TO RELAY AGE "At 2200 CDT on September 25, 2014, the Duty Shift Manager was notified that Agastat relays associated with Primary Containment Isolation valves on the Hydrogen-Oxygen Analyzing System are beyond the analyzed shelf life for relays that are in the normally energized state and are considered INOPERABLE. This affected both primary containment isolation valves for a containment penetration on multiple flow paths. This issue was determined to be reportable under [10 CFR] 50.72 (b)(3)(v)(C) & (D) for an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material and mitigate the consequences of an accident. "Additionally, the required actions involved isolating six flow paths via manual isolation valves. This action rendered the Hydrogen-Oxygen Analyzers non-functional for both trains and constitutes a loss of Emergency Preparedness and Accident Assessment Capability. This is reportable under [10 CFR] 50. 72(b)(3)(xiii). "The Primary Containment Isolation Valves have been, and remain, in their closed position to satisfy their Primary Containment Function and protect the health and safety of the public. "The NRC Senior Resident Inspector has been notified." The licensee will notify the State of Minnesota. The relays of concern were manufactured 19 years ago and have been in operation for 11 years, versus a manufacturer assumption of a 10 year operational lifespan. * * * UPDATE FROM SCOTT CHRISTOS TO DONALD NORWOOD AT 1430 EST ON 11/20/2014 * * * "Partial retraction for EN 50496. This is an update of Emergency Notification System (ENS) report 50496 that was submitted at 0253 EDT on Friday, September 26, 2014. "ENS notification was made due to four relays associated with the sampling valves on the Hydrogen-Oxygen Analyzing (HOA) system that perform Primary Containment Isolation Valve (PCIV) functions. These relays were discovered installed beyond their manufacturer qualified service life, which called operability into question. "The portions 10 CFR 50.72 (b)(3)(v)(C) & (D) are being retracted after subsequent bench testing and investigation of system operability. Based on the past operability evaluation, all four relays associated with PCIV functions on the HOA system would have performed their specific safety function of primary containment isolation, as required by the facility's technical specifications. Therefore, this event does not meet the threshold of an event or condition that would prevent fulfilment of a safety function. "The loss of emergency preparedness and accident assessment capability previously reported under 10 CFR 50.72 (b)(3)(xiii) remains unchanged. "The NRC Resident Inspector has been notified." Notified R3DO (Peterson). | 69 | 0 | 0 | 69 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  | 0 | 2014-09-26
50495 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-09-23 15:55 | 2014-09-25 16:35 | 2014-09-25 | PART 21 REPORT - ELECTROMATIC RELIEF VALVE EXCESSIVE WEAR The following report was received via e-mail: "This is a non-emergency notification from Oyster Creek Nuclear Generating Station (OCNGS) required under 10 CFR Part 21 concerning the design of Electromatic Relief Valve (EMRV) actuators. "On June 20, 2014, during as-found bench (stroke) testing of the EMRV actuators removed from the plant during refueling outage 1R24 (October 2012), two of five EMRV actuators failed to operate. Subsequent inspection of these actuators found unexpected wear of the posts (grooves approximately 1/2 inch from the top), springs (thinned and broken at the top), and guides (grooves inside), with one spring having a piece axially wedged between the post and the guide. "The root cause of this failure was determined to be the inadequate design of the EMRV actuators in that when placed in an environment where the actuator is subject to the vibration associated with plant operation, the allowed installation tolerances between posts and guides can create a condition where the springs can jam the actuator plunger assembly by wedging between the guides and the posts. If the EMRV actuators are set up in a condition where the posts are not optimally aligned, preferential wear of the post is observed due to interaction of the post, spring, and guide. Additionally, the vendor guidance for refurbishment of the EMRV actuator does not provide the necessary acceptance criteria for alignment of the posts to guides to ensure that the springs, posts, and guides do not interact in a way that causes preferential wear of the post allowing the jamming mechanism to exist. "By OCNGS process, the EMRV actuators are refurbished with new springs, posts, guides, and microswitches every 24 months during refueling outages due to the known wear of these parts. The actuator inspection/refurbishment frequency of 24 months exceeds the manufacturer's (i.e., Dresser Industries) recommended frequency of 36 months (per Vendor Manual VM-OC-0030, Installation and Maintenance Manual for Electromatic Relief Valves, Revision 1, Section VII, Ref. 4.5). In addition, in 2008, the station implemented the manufacturer's recommended material changes intended to minimize part wear, and prevent potential actuator failures. "Identification of Facility and Component: Oyster Creek Nuclear Generating Station / Electromatic Relief Valve Actuator, Dresser Valve Type 6 inches Model 1525-VX "Identification of Component Manufacturer and/or Supplier: Dresser Industries. "Nature of Defect: Inadequate design of the EMRV actuators in that when placed in an environment where the actuator is subject to the vibration associated with plant operation, the allowed installation tolerances between posts and guides can create a condition where the springs can jam the actuator plunger assembly by wedging between the guides and the posts. "Safety Significance (e.g., substantial hazard that is or could be created): Identified condition is a Substantial Safety Hazard since it could cause EMRV to be inoperable, which could result in a loss of safety function. "Date of Discovery of Initial Condition (taken from the IR): 06/20/14 "Date of Discovery of the Substantial Safety Hazard (date of approval of the technical evaluation): 09/22/14 "Recommended Actions: Change the design to mitigate the cause of the actuator parts (i.e., springs, guides and posts) interacting which results in unexpected wear due to vibration induced fretting. "Number and Locations of All Defective Components: Two EMRVs located in the Drywell on the Main Steam piping. "Any Advice Related to the Defect: Consider actuator design change if vibration conditions at the valve location results in unexpected wear of the EMRV actuators. Perform actuator as-found stroke testing before removal for refurbishment to determine in situ operability of the component. With current design, ensure posts are aligned such that preferential wear does not occur. Spring should be optimally centered on the guide and the post and guide should be equidistant around the full circumference of the bushing. "Contacts (Name, Title, Location, Phone Number, etc.): Sylvain L. Schwartz, Senior Staff Engineer, Oyster Creek Nuclear Generating Station, Phone: (609) 971-4558, Email: sylvain.schwartz@exeloncorp.com" The licensee notified the NRC Resident Inspector. Plants with similar Dresser EMRVs: Nine Mile Point, Quad Cities, and Dresden. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-25
50494 | 0 | MALLINCKRODT |  |  |  |  | 2014-09-18 | 2014-09-25 10:57 | 2014-09-25 | LOST DEPLETED URANIUM SHIELDS Mallinckrodt reported the loss of six (6) depleted Uranium shields used as shielding for Tc-99m generators. The licensee believes that the shields were lost in transit between 5/2013 and 9/2013. Five of the shields were in transit between Mallinckrodt and Triad Isotopes (locations in Texas and Hicksville, NY) shipped by "Associated Couriers." One of the shields was in transit between Mallinckrodt and Cardinal Health (Plainville, NY) shipped by "Medical Delivery Services." Each shield is roughly 12 inches in height, 8 inches in diameter, 65 pounds in weight, and contains 8.1 mCi of Uranium. The dose rate on contact would be roughly 3.1 mrem/hr, and the dose at 1 foot would be roughly 1.2 mrem/hr. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-10-03
50493 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-09-23 11:50 | 2014-09-25 09:27 | 2014-09-25 | AGREEMENT STATE REPORT - FAILURE OF A PROCESS GAUGE SHUTTER The following was received from the State of Nebraska via email: "The Nebraska Department of Health and Human Services, Radioactive Materials Program, was notified at 0803 CDT on 9/25/2014 by a representative of the Omaha Public Power District that a Kay Ray fixed gauge Model Number 7080 source shutter failed to close. The device contains approximately 6 millicuries of Cesium-137 originally installed in 1984 with approximately 50 millicuries. The gauge is mounted between two fly ash hoppers approximately 20 feet above the floor. The source closure mechanism on the gauge is connected to a handle located at floor level by a flexible cable. The closure cable is secured so that when the floor handle is operated, the control cable slides inside of the sheath opening/closing the shutter. The outer sheath for the cable became separated from the capture mechanism at the source. The handle on the floor would move but the linkages at the source would only move approximately « inch and then the sheath would move away from the compression fitting. The reason for operating the source shutter was to perform the semiannual function check. "This type of failure has been seen in the past and is easily fixed by tightening the screw which secures the end of the cable to the structure. This requires a scaffold to be built up to the source level." NE Incident ID #: NE140005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2014-10-03
50492 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-09-24 15:33 | 2014-09-25 00:04 | 2014-10-06 | UNIT 1 TRAIN B RVLIS AND ICCM INOPERABLE DUE TO DATA ERRORS "At 1533 CDT on September 24, during a Past Operability review for the Unit 1 Train B Inadequate Core Cooling Monitor (ICCM), it was discovered that due to data errors, the as left VDC [voltage DC] value for the Remote Display Power Supply was outside of acceptance criteria during the last performance of SP 1213B 'Inadequate Core Cooling Monitor Calibration,' completed on 8/25/2014. The Reactor Vessel Level Instrumentation System (RVLIS) and the Core Exit Thermocouples (CETs) are subsystems of the ICCM System and were determined to be inoperable during this timeframe. Therefore Tech Spec 3.3.3 Condition A for Train B RVLIS and Tech Spec 3.3.3 Condition B for CETs were not met. Also during this time, Unit 1 Train A ICCM was out of service from 1110 [CDT] on 9/8/2014 to 1530 [CDT] on 9/12/2014 for calibration. Thus, both trains of Core Exit Thermocouples and RVLIS were inoperable during this 4 day, 4 hour and 20 minute time period. "ICCM System indication is used for Safety Injection Termination and Reinitiation criteria in the Emergency Operating Procedures (EOPs). During the time when both trains of ICCM were inoperable, B Train remained in service and was thought to be operable. This provided the potential for operators to perform an untimely SI Termination or Reinitiation during an accident based on inaccurate information. The Emergency Response Computer System was available to provide accurate backup information to the operators and for timely Emergency Action Limit classification "This is reportable under 10 CFR 50.72 (b)(3)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function to Mitigate the Consequences of an Accident. "Based on new information currently being received from Westinghouse, the ICCM Remote Display Power Supply only functions to communicate data to the display and has no effect on the data values. Thus the ICCM System may have been functioning properly. An update to this information will be provided once it is available "The protection of the health and safety of the public was not affected by this issue. "The Unit 1 Train B ICCM System was returned to operable status at 2300 [CDT] on 9/24/2014. "The license has notified the NRC Senior Resident Inspector." * * * RETRACTION AT 1408 EDT ON 10/6/2014 FROM NATHAN BIBUS TO DONG PARK * * * "Based on further analysis and input from Westinghouse, the remote display 12V power supply is operable as long as data is still updating on the display. It was determined that the tolerance acceptance criteria within our procedure was conservative. For this application, the power supply can function at much less than 12V. The acceptance criteria within surveillance procedures were incorrect and procedure changes have been submitted to correct the tolerance. Therefore, there was no loss of safety function. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Orlikowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-09-25
50491 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2014-09-24 16:25 | 2014-09-24 22:45 | 2014-09-25 | OFFSITE NOTIFICATION FOR NON-CREDIBLE BOMB THREAT "This report is being made pursuant to the reporting requirement 10CFR50.72(b)(2)(xi). At approximately 1625 MST on September 24, 2014, a PVNGS [Palo Verde Nuclear Generating Station] employee received a bomb threat via a company telephone. PVNGS Security Department informed Unit 1 control room that a bomb threat had been received for the North Annex (Building G). The bomb threat, which is not considered credible at this time, resulted in no emergency classification. The Maricopa County Sheriff's Office was notified by PVNGS Security at approximately 1647 MST. The notification of the Maricopa County Sheriff's office was determined to be reportable under 10CFR50.72(b)(2)(xi) as a notification to a government agency. "The NRC Resident Inspector has been notified of the event. "[PVNGS Security is in a heightened state of awareness and] maintaining the same security posture since the initiating event and will continue until all searches have been completed. Nothing has been found and the threat is considered non-credible." The licensee also notified the FBI. * * * UPDATE FROM CHUCK COLES TO DONALD NORWOOD AT 0045 EDT ON 9/25/2014 * * * The following is a brief timeline of activities that have occurred since the initial report: 1720 MST - Maricopa County Sheriff's office personnel and bomb sniffing dogs arrived on-site. 1933 MST - Bottom to top search of Building G began using two canine teams, Maricopa County Sheriff's deputies, and plant security personnel. 2045 MST - Search of Building G completed with negative findings. Building declared safe. 2112 MST - Exited security color code of orange and stepped down to code yellow. As a precaution, security will remain in a heightened state of awareness at code yellow, probably throughout the night. The Maricopa County Sheriff's report number for this incident is: MC14-179941. Notified R4DO (Drake) and ILTAB (Totterer). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2014-09-24
50490 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-22 | 2014-09-24 16:53 | 2014-09-24 | AGREEMENT STATE REPORT - STUCK SOURCE The following report was received from the State of Texas via email: "On September 24, 2014, the Agency [Texas Department of State Health Services] received notice that on September 22, 2014, there had been a radiography source retraction failure at a temporary field site. A pipe had fallen from a stand onto the guide tube, causing a crimp. The source was retrieved by squeezing the crimp with pliers, allowing retraction. The individual performing the retrieval received 387 mrem according to a pocket dosimeter. The camera was a SPEC 150 (sn 1599) with an Ir-192 source at 49 Ci (sn VG010). Additional information will be supplied as it is received in accordance with SA-300." Texas Incident #: I-9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-02
50489 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-09-23 19:00 | 2014-09-24 16:37 | 2014-09-24 | AGREEMENT STATE REPORT - STUCK SOURCE The following report was received from the State of Colorado via email: "Event description: The department [Colorado Department of Public Health and Environment] was notified via phone on 9/23/2014, at approximately 1845 [MDT] by the Radiation Safety Officer [RSO] of Premier NDT Services, Inc. (license # CO 1162-01) that a radiography crew was unable to retract the source assembly to its fully shielded position and secure it in this position at a temporary job site. "At approximately, 1900 [MDT] on 9/23, the RSO reported to the department [Colorado Department of Public Health and Environment] that the source had been retracted to it fully shielded position by working the crank back and forth a few times. It was about a quarter turn to get the source into position and have the exposure device lock engage. The source was not fully extended outside of the camera but was in the camera enough to close the outlet port cover. "The radiography camera was surveyed and it was determined that the source was in fact in its fully shielded position prior to transporting the camera back to the licensee facility. "The department [Colorado Department of Public Health and Environment] visited the licensee facility on 9/24/14, at approximately 0930 [MDT] and interviewed licensee staff including the radiography crew. "It was determined that the radiography assistant had not properly surveyed during the approach to the camera to verify that the source was in fact in its fully shielded position and that he disconnected the guide tube prior to realizing that the source was not fully shielded. When he attempted to disconnect the drive cable he realized that the exposure device lock was not engaged properly and the crew retreated to a safe distance. "There were two assistant radiographers and a radiographer present and their pocket dosimeters read 10, 9 , and 20 mrem after the event. It appears unlikely that this is an overexposure event. The time in which the crew was in close proximity to the camera with the source out of its secured position was less than 5 minutes total and the time in which the crew member was in contact with the camera was less than a second to disconnect the guide tube and close the outlet port cover and another second when he attempted to disconnect the drive cable. "It is suspected that this was a malfunction of the device. The camera (QSA 880 Delta), drive cables, and guide tube are being sent back to the manufacturer for diagnosis. "The department [Colorado Department of Public Health and Environment] is preparing a Notice Of Violation for multiple items and is expecting a full report from the licensee within 30 days including dose estimates." Event Report ID No.: CO14-I14-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-10-02
50488 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-23 | 2014-09-24 12:34 | 2014-09-24 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE LOST THEN FOUND The following was received from the State of Texas via email: "On September 23, 2014, the Agency [State of Texas] was notified by the licensee of the loss of a Troxler Model 3411 moisture density gauge, serial #6329, containing a 1.48 GBq (40 mCi) Am-Be source, serial #47-2502, and a 0.3 GBq (8 mCi) Cs-137 source (serial #40-3459). The licensee stated a technician was traveling when his tailgate fell open and the container holding the locked gauge fell off the truck. The gauge was improperly secured in the back of the truck. He turned around to go back to the intersection but the gauge was missing. "On September 24, 2014, a company called the licensee informing them that they found the gauge in the road. The gauge was returned to the licensee. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-10-02
50487 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-09-24 07:28 | 2014-09-24 08:41 | 2014-09-24 | SHIELD BUILDING VENT GAS RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0728 CDT on 9/24/2014, 2R-22 Shield Building Vent Gas Radiation Monitor was removed from service for planned maintenance. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs) - NUE (Notification of Unusual Event) and Alert classifications - when out of service. It is also used for offsite dose projection calculations. This results in a Loss of Emergency Assessment Capability while 2R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 2 Shield Building Ventilation Stack is also monitored by high range monitor, 2R-50, which is used for the same purpose in Site Area or General Emergency classifications. 2R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 2R-22 prior to its removal from service. The duration of this maintenance is scheduled for 1 hour and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-24
50486 | 0 | CARBOLINE COMPANY |  |  |  |  | 2014-09-23 | 2014-09-23 19:36 | 2014-09-23 | PART 21 REPORT - CARBOLINE SG BASE NOT CURING PROPERLY The following report was received via facsimile: "This letter serves to notify of a potential safety related noncompliance deviation in a basic component as defined in 10CFR Part 21. The noncompliance involves a batch of Carbozinc 11 SG Base that is not curing properly. "A customer notified Carboline of concerns regarding the cure of a particular batch of Carbozinc 11 SG. Our salesman was contacted by the customer and the salesman initiated a report to our Technical Service group. The internal report was opened and investigation began on Friday 9/19/2014. Analysis of the retain sample by our plant Quality Control was requested, the results show a slower than normal cure. Material was then sent into Saint Louis R&D for additional analysis. On Tuesday, September 23, 2014, the analytical evaluation was reviewed by the product chemist and the batch cure issues were confirmed. "The batch has been placed on hold and reports have been run to determine where the batch has shipped. "We are notifying customers to review their use and stock of Carbozinc 11 SG, to discontinue use of this batch, 14FN6228L and return any material with the batch number of 14FN6228L. "Please contact our Customer Service Department at 1-800-848-4645 to obtain a Returned Goods Authorization. We will credit your account for this material, if you need replacement material, Customer Service can make the necessary arrangements at that time. "Further work is being done to determine the cause of cure issues with this batch of Carbozinc 11 SG. At this time, we have confirmed that this material is not curing properly. "If you have any questions or need additional information please contact me. "Respectfully submitted, "Marikay Speckert - Corporate Quality Manager - Carboline Company 2150 Schuetz Road - Saint Louis, MO 63146 - 314-644-1000 Ext. 2456" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MO | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-23
50485 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-09-08 | 2014-09-23 17:42 | 2014-09-23 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DELIVERED TO WRONG ADDRESS The following information was obtained from the Commonwealth of Massachusetts via email: "Boston University Medical Center's (BUMC) Radiation Safety Officer (RSO) reported by telephone to the Massachusetts Radiation Control Program (MA RCP) on 9/23/2014 that a shipment of Iridium-192, in the form of brachytherapy sealed sources containing approximately 10 curies, was delivered by [the shipping company] to the wrong address, a non-BUMC address at [redacted], Boston, MA on 9/8/2014. "The RSO reported that the package, a yellow III package, was accepted by a mail room employee of the non-BUMC address on 9/8/2014; that BUMC was contacted on 9/8/2014; and that BUMC transferred the package to BUMC less than one hour after the package was delivered to the wrong address. "The RSO reported that BUMC is conducting an investigation and attempting to contact [the shipping company] and that all radioactive materials that were supposed to have been in the package were accounted for. "The MA RCP plans to perform inspection upon this event. This event is considered by MA RCP to be open." THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-10-01
50484 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-09-23 | 2014-09-23 16:30 | 2014-09-24 | AGREEMENT STATE REPORT - THERMAL EVENT SUFFICIENT TO TRIGGER SPRINKLER SYSTEM The following report was received from the State of Tennessee via email: "Event description: Tennessee Division of Radiological Health (DRH) was notified on September 23, 2014, by a representative from [Manufacturing Science Corporation] MSC that there had been a thermal incident in the chip/turnings oxidizer that triggered the sprinkler system. The Oak Ridge [OR] Fire Dept. responded. The sprinkler system released ~200 gallons of water which was contained within the bermed area. The incident was contained sufficiently that the OR fire department left the facility prior to 1000 [EDT]. MSC changed pre-filters upstream of the HEPA filters, the HEPAs did not appear to need changing. MSC felt that this incident is required to be reported per TN State Regulations for Protection Against Radiation (SRPAR) 0400-20-05-.141(2)(c)4, in that the event potentially involved 'an unplanned fire or explosion damaging any licensable material or any device, container or equipment containing licensable material when: (i) The quantity of material involved exceed five times the lowest annual limit of intake specified for the material in Schedule RHS 8-30 in Rule 0400-20-05-.161, and (ii) The damage affects the integrity of the licensable material or any device, container or equipment containing licensable material.' "There was no release to the environment, no personnel contamination, and no injuries. "Notifications: [State] Oak Ridge Fire Department. Press release has not been issued at this time. TN DRH has not received any media inquiries at this time." No fire or smoke was observed. State Event Report ID #: TN-14-181 UPDATE FROM BILLY FREEMAN TO DANIEL MILLS AT 0921 EDT ON 9/24/14: The following was received via email: "Tennessee Division of Radiological Health (DRH) was notified on September 23, 2014 by a representative from MSC that there had been a thermal incident in the depleted uranium (DU) chip/turnings oxidizer that triggered the sprinkler system. The Oak Ridge Fire Dept. responded. The sprinkler system released ~200 gallons of water which was contained within the bermed area. The incident was contained sufficiently that the OR fire department left the facility prior to 1000 EDT. MSC changed pre-filters upstream of the HEPA filters the HEPAs did not appear to need changing. MSC felt that this incident is required to be reported per TN State Regulations for Protection Against Radiation (SRPAR) 0400-20-05-.141(2)(c)4. in that the event potentially involved 'an unplanned fire or explosion damaging any licensable material or any device, container or equipment containing licensable material when: (i) The quantity of material involved exceed five times the lowest annual limit of intake specified for the material in Schedule RHS 8-30 in Rule 0400-20-05-.161, and (ii) The damage affects the integrity of the licensable material or any device, container or equipment containing licensable material.' "They are not certain of the quantity of DU involved. There was no release to the environment, no personnel contamination and no injuries. "Notifications: [State] Oak Ridge Fire Department. Press release has not been issued at this time. TN DRH has not received any media inquiries at this time." Updated information: The material involved was Depleted Uranium. Notified R1DO (Gray), FSME MOC (Dudes), FSME Events Resource (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-10-01
50483 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-09-23 08:19 | 2014-09-23 13:59 | 2014-09-23 | RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "[Millstone] U2 High Range Stack Radiation Monitor, RM-8168 was removed from service for pre-planned maintenance. This action is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). RM-8168 was restored to operable status on 9/23/14 at 1212 [EDT]." The licensee has notified the NRC Resident Inspector and state and local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-23
50482 | 0 | SAN ONOFRE | 1 | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2014-09-23 02:50 | 2014-09-23 11:10 | 2014-09-23 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Decommissioned | Defueled |  | Decommissioned | Defueled |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-09-23
50481 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2014-08-27 | 2014-09-22 17:34 | 2014-09-22 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL RELEASE EXCEEDING EMISSION LIMIT The following report was received from the State of Washington via email: "Event Narrative: Notification [was given] to [Washington] State by the licensee for exceeding the allowable total abated emission limit for this unit [Cardinal Health 414, LLC]. The limit is 7.4 mRem to the MEI [Maximally Exposed Individual] while the licensee acknowledges a release so far in 2014 of a total of 23.7 mRem (21.5 from Fluorine 18 and 2.2 from Carbon 11). The licensee believes the problem is a combination of errors including both human and engineering. Proposed corrective actions include changes in procedures as well as changes in the air discharge system components." NMED Report Number: WA-14-039. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-09-30
50480 | 0 | QUALTECH NP |  |  |  |  | 2014-09-22 | 2014-09-22 17:17 | 2014-12-30 | PART 21 NOTIFICATION - DISCREPANCY BETWEEN QUALIFICATION REPORT AND INSTALLATION INSTRUCTIONS The following information was obtained from the vendor via facsimile: "To whom it may concern: "This letter is issued to provide notification of a documentation defect concerning QualTech NP Generation 3 Quick Disconnect Connectors (Gen 3 QDC). Specifically, there is a discrepancy concerning o-ring replacement between the 1/2 Inch Gen 3 QDC Qualification Report (EGS-TR-23009-14, through Revision B) and the Instructions for Installation (EGS-TR-23066-04, Revision Original), the 3/4 Inch Gen 3 QDC Qualification Report (EGS-TR-23067-01, Revision A) and the 1-1/2 Inch Gen 3 QDC Qualification Report (EGS-TR-23068-01, Revision A). "Section 5.0 of the 1/2 Inch Qualification Report (EGS-TR-23009-14, through Revision B) states in part that 'whenever the connector is disconnected after one week or more installed service, the used o-ring must be discarded and a new o-ring installed prior to reconnection.' Contrary to this requirement, Section 9.0 of the Instructions for Installation (EGS-TR-23066-04, Revision Original) states in part that, 'whenever the QDC is disconnected after one week or more installed service, it is recommended that the o-ring be discarded and a new o-ring installed prior to reconnection. This action, while not mandatory, will maintain the o-ring seal in a superior condition' and Section 6.0 of both the 3/4 Inch Qualification Report (EGS-TR-23067-01, Revision A) and 1-1/2 Inch Qualification Report (EGS-TR-23068-01, Revision A) states in part that, 'whenever the connector is disconnected after one week or more, it is recommended that the used o-ring be discarded and a new o-ring installed prior to reconnection.' "To prevent confusion and inconsistency between the 1/2 Inch Qualification Report (EGS-TR-23009-14), the 3/4 Inch Qualification Report (EGS-TR-23067-01), the 1-1/2 Inch Qualification Report (EGS-TR-23068-01) and the Instructions for Installation (EGS-TR-23066-04), the documents have been revised to require that the o-ring must be discarded and a new o-ring installed prior to reconnection. The new revision level of each document is as follows: - EGS-TR-23067-01, Revision B - 3/4 Inch Qualification Report - EGS-TR-23068-01, Revision B - 1-1/2 Inch Qualification Report - EGS-TR-23066-04, Revision A - Instructions for Installation "The revised Qualification Reports and the Instructions for Installation have been or will be distributed to all customers who have received 1/2 Inch, 3/4 Inch, and/or 1-1/2 Inch Gen 3 QDC connectors. "Should any Gen 3 QDC connectors be currently installed in service, it is required that a determination be made as to whether or not the connector has been disconnected after one week of installed service and if the o-ring was replaced. If the o-ring was replaced, no further action is required. If the connector was disconnected and the o-ring was not replaced, the o-ring must be discarded and a new o-ring installed. "QualTech NP will provide replacement o-rings, free of charge, to customers who identify replacement o-rings are required for Gen 3 QDC connectors that have been installed in service. "As a point of interest, please note that this notification does not apply to the original EGS QDC connectors (Gen 1 QDC). QualTech/EGS QDC connectors certified to Qualification Reports PEI-TR-880701-04, Revision A (1/2 Inch Gen 1 QDC), EGS-TR-913601-01. Revision B (3/4 Inch Gen 1 QDC) and/or EGS-TR-913602-01, Revision B (1-1/2 Inch Gen 1 QDC) are not impacted by this notification as these Qualification Reports require the o-ring be discarded and replaced if the connector is disconnected after one week of installed service. "If you require additional details or would like to discuss this further please contact the undersigned or Tony Gill (QualTech NP Quality Assurance Manager) at 256-924-7438 (office), 256-426-4558 (mobile) or tgill@curtisswright.com. "Jim Tumlinson Products Engineering Manager QualTech NP, Huntsville Operations Curtiss-Wright Corporation 256-924-7429 (office) 256-425-8037 (mobile) jtumlinson@curtisswright.com" * * * UPDATE ON 12/30/14 AT 1528 EST FROM JIM TUMLINSON TO DANIEL MILLS * * * The following information was obtained from the vendor via facsimile: "To whom it may concern: "This letter provides for the formal close out of notification QTHuntsville 10 CFR 21-2014-05. The initial notification was made on September 22, 2014 . All corrective actions have been completed and revised documents have been provided to customers of Generation 3 Quick Disconnect Connectors (Gen 3 QDC) and 3/8 Inch QDC. "The corrective actions include revision of the following documents to clarify O-ring replacement: "EGS-TR-23067-01 - 3/4 Inch Qualification Report EGS-TR-23068-01 - 1-1/2 Inch Qualification Report EGS-TR-23066-04 - Instructions for Installation (Gen 3 QDC) EGS-TR-23062-0002-01 - 3/8 Inch QDC Qualification Report EGS-TR-23062-04 - 3/8 Inch QDC Generic Qualification Report EGS-TR-23062-06 - Instructions for Installation (3/8 Inch QDC) "The revised Qualification Reports and the Instructions for Installation have been distributed to all customers who have received 1/2 Inch, 3/4 Inch and/or 1-1/2 Inch Gen 3 QDC connectors as well as the customers for 3/8 Inch QDC connectors. Based on the above information and corrective actions, this Part 21 file is considered closed. If you would like to discuss this further, please contact the undersigned or Tony Gill (QualTech NP Quality Assurance Manager) at 256-924-7438 (office), 256-426-4558 (mobile) or tgill@curtisswright.com. "Jim Tumlinson Products Engineering Manager QualTech NP, Huntsville Operations Curtiss-Wright Corporation 256-924-7429 (office) 256-425-8037 (mobile) jtumlinson@curtisswright.com" Notified R1DO (Dimitriadis), R2DO (Hopper), R3DO (Cameron), R4DO (Hay), Part 21 Group (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-22
50479 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-09-20 12:30 | 2014-09-22 13:06 | 2014-09-22 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following report was received from the State of Colorado via email: "The State of Colorado received a report this morning from a medical licensee of a misadministration. The licensee reported that at 1230 [MDT] on Saturday 9/20/14, the technologist injected a patient with a bulk dose of Tc-99m instead of a [smaller] patient dose. The initial estimate for the amount injected is 140 mCi. The initial potential whole body dose is 6-7 rem with 30 rad as the highest potential organ dose (upper intestine). The investigation is ongoing." Additional information regarding the intended patient dose will be provided when available. The attending physician and patient will be informed by the licensee. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-09-30
50478 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2014-09-22 10:00 | 2014-09-22 09:34 | 2014-09-23 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "On September 22, 2014, at 1000 EDT, the Technical Support Center (TSC) will be unavailable due to pre-planned maintenance impacting the TSC ventilation envelope. The TSC is expected to be restored to operational status on September 23, 2014. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures, and the TSC staff will assemble at a preplanned alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency response facility (ERF). An update will be provided once the TSC has been restored to operational status. The NRC Resident Inspector has been notified." The maintenance is expected to be completed within 36 hours. * * * UPDATE FROM TIMOTHY MILLER TO HOWIE CROUCH AT 1638 EDT ON 9/23/14 * * * "The TSC ventilation envelope has been restored. The TSC is returned to operational status on September 23, 2014 at 1600 EDT. The NRC Resident Inspector has been notified." Notified R2DO (Widman). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-22
50477 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-20 | 2014-09-21 09:09 | 2014-09-22 | AGREEMENT STATE REPORT - VEHICLE FIRE INVOLVING TWO DENSITY GAUGES The following report was received via e-mail: "On September 20, 2014, the licensee notified the Agency [Texas Department of State Health Services] that two nuclear gauges, Thermo Fisher Scientific Model 5190 density gauges containing a 200 milliCurie cesium (Cs) - 137 source, were inside a large fire that occurred in the early morning hours. The fire at an oil field temporary job site in Dimmit County, Texas burned over twenty vehicles and the two gauges stored in Type A containers were in the fire. Status of the gauges is unknown. An additional two similar gauges were at the site but not in the area of the fire. An investigation is ongoing and additional information in accordance with SA-300 will be reported. There was no public or worker exposures due to the incident as no one was on site at the time of the fire. "Gauge Serial Numbers are B6610 and B7600." Texas Incident #I-9236 * * * UPDATE FROM KAREN BLANCHARD TO JOHN SHOEMAKER AT 1247 EDT ON 9/22/14 * * * The following event report update was received from the State of Texas via email: "[The State was informed by the licensee at 1345 CDT on 9/22/14, that] the licensee surveyed and inspected the two Thermo Fisher Scientific Model 5190 gauges that were in a fire on September 20, 2014. Radiation measurement of 7 R/hr on contact with the outer surface of one of the gauges was detected, indicating that the lead shielding had been compromised (gauge SN: B7500). There were no elevated radiation levels detected on the second gauge. The licensee has secured all four gauges that were at the site and set up appropriate barrier while it awaits permission to remove them from the site. The cause of the fire is still under investigation. The manufacturer is sending a transport container. The licensee reported it will add external lead around the compromised gauge for transport. Upon receipt, the manufacturer will inspect/evaluate all four gauges." Notified R4DO (Drake), FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-29
50476 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-09-19 23:59 | 2014-09-20 07:42 | 2014-09-20 | LOSS OF SECONDARY CONTAINMENT INTEGRITY "At approximately 2359 EDT a temporary modification plug was found to be removed from a floor drain in the Outboard MSIV Room (Trunnion Room). The purpose of the temporary modification plug is to ensure that secondary containment remains intact during outages where the trunnion room door is required to be open. The trunnion room door was open when the plug was found to be removed. The plug was immediately reinstalled, restoring the safety function of the secondary containment. "Per [10 CFR] 50.72(b)(3)(v)(C), Oyster Creek is reporting an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-09-20
50475 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-09-19 13:53 | 2014-09-19 17:54 | 2014-11-18 | UNANALYZED CONDITION DUE TO MISSING FIRE BARRIERS "As part of an extent of condition review related to ENS report 50362 (Unanalyzed Condition Due to Lack of Appropriate Fuse Protection), it was identified that, within the past three years, three additional examples existed of missing fire barriers that could have impacted separation of redundant safe shutdown trains. For the affected areas associated with each of the three missing barriers, compensatory measures (hourly fire watches) had been in place for three years prior to the discovery of the condition. However, it was determined the missing barriers met the reporting criteria for 10 CFR 50.72(b)(3)(ii)(B) as unanalyzed conditions that significantly degraded plant safety. "The first condition was the use of rodofoam material in Auxiliary Building seismic joint seals. Rodofoam is a combustible foam material and does not provide a fire rating equivalent to the barriers in which it was used. This issue was corrected in a plant modification. "The second condition is the lack of required fire dampers in ventilation supply ducts to the Aux. Feedwater (AFW) Pump Rooms (Fire areas 31 and 32). An engineering change package has been approved to implement a plant modification to install the required dampers as part of the NFPA-805 transition. "The third condition is a gap where the ventilation duct passes through the wall from the Bus 150/160 room into the AFW pump room. An engineering change package has been approved to implement a plant modification to correct this condition as part of the NFPA-805 transition. "The protection of the health and safety of the public was not affected by this issue. In all cases, compensatory measures existed to ensure the protection of safe shutdown equipment. "The licensee has notified the NRC Senior Resident Inspector." * * * UPDATE FROM DOUG LARSON TO DANIEL MILLS AT 2122 EST ON 11/18/14 * * * "Northern States Power Company (NSPM) has determined that the missing fire damper and the wall gap (the second and third identified conditions) are not separating redundant equipment and no longer meet the regulatory definition of an unanalyzed condition. This was identified when it was determined that the redundant pressurizer heater cables credited for safe shutdown were routed through the same fire area. This was reported under EN 50531 (Unanalyzed Condition Due To Missing Fire Barrier). Since the missing fire barrier does not separate redundant equipment, the condition does not degrade plant safety, and is no longer reportable. "The protection of the health and safety of the public was not affected by this issue. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Peterson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-09-19
50474 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-09-19 11:34 | 2014-09-19 16:35 | 2014-09-19 | UNANALYZED CONDITION DUE TO A POSTULATED HOT-SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "From review of Event Notification 50468 made by Wolf Creek Nuclear Operating Company on 9/18/2014, which in turn was based on review of INPO Event Report 14-33, 'Direct Current Circuits Challenge Appendix R Fire Analysis,' it was determined that portions of the control circuits for the main turbine-generator direct-current (DC) Emergency Lube Oil Pump and the Emergency DC Seal Oil Pump at Callaway Plant are not properly fused to prevent overload and possible secondary fires. The review found that a fire at the motor starter cabinet in the turbine building could cause specific 'smart' hot shorts that could cause overheating of the control cable and result in secondary fires outside the turbine building, including the Control Building, thereby potentially affecting safe shutdown capability for the plant. Based on this information, it has been determined that this condition is unanalyzed, and on a conservative basis, is reportable per 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "As compensatory measures, hourly fire watches are in place in the affected areas of the Turbine Building and Control Building. These compensatory measures, in addition to automatic fire detection and suppression capability in these fire areas, ensure protection of the potentially affected equipment. "The NRC Resident Inspector has been notified." The licensee continues to evaluate other control circuits to identify if this condition exists elsewhere. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-09-19
50473 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-17 | 2014-09-19 14:12 | 2014-09-19 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURES TO TWO RADIOGRAPHERS The following information was obtained from the State of Texas via email: "On September 18, 2014, the Agency [Texas Department of Health] was notified by the Licensee's Radiation Safety Officer (RSO) that two radiographers working at a field location may have received exposures in excess of the annual whole body exposure limit. The RSO stated two qualified radiographers were working at a temporary field site using an INC IR-100 exposure device containing a 55 curie iridium-192 source. One radiographer (RA) was performing the exposures and the other (RB) was developing the film. The RSO stated RA walked out of the darkroom and saw the camera setting on the truck's tailgate. The radiographer also observed the dose rate meter sitting on the truck's tailgate was reading pegged high. The radiographers picked up the crankout device and cranked the handle approximately one-half turn which locked the source in the fully shielded position. The RSO stated RA read their self-reading dosimeter (SRD) and it was off scale. The RSO stated RB was not wearing a SRD or OSL [optically stimulated luminescence] dosimeter. The RSO stated RB was wearing an alarming rate meter, but they are hard to hear and with the background noise of the generator they did not hear it alarming. "The RSO stated RB was five feet from the exposure device for about 20 minutes. The RSO stated the calculated dose to RB is 12.8 rem based on their current information. The RSO stated RA was near the camera for about 30 seconds and his dose was calculated to be 10.8 rem. Both radiographers' dosimeters have been sent to the licensee's processor for reading. The RSO stated they have not calculated the dose to RA's hand yet. The RSO stated they are reenacting the event on September 19, 2014, to help calculate the dose to both workers. The licensee has contracted a consultant (Bruce Bristow) to aid in the dose calculations. The RSO stated the cause for the high exposures was failure of RA to fully retract the source. The RSO stated the exposure device was working properly. No other individuals received any exposure due to this event. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-9235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-29
50472 | -1 | MONONGALIA GENERAL HOSPITAL |  |  |  |  | 2014-09-19 | 2014-09-19 13:56 | 2015-10-05 | BRACHYTHERAPY PATIENT RECEIVED 54% OF PRESCRIBED DOSE The authorized user determined that, due to scar tissue from a previous procedure, the patient received only 54% of the intended dose during a I-125 prostate brachytherapy treatment. The patient was implanted with 72 seeds (nominal 0.269 mCi each), some of which were inadvertently implanted in the scar tissue. The authorized user/physician expects no adverse effects on the patient and does not intend to repeat the treatment. The patient has been notified. The investigation into the event is ongoing. * * * RETRACTION FROM MARK PENA TO HOWIE CROUCH AT 1458 EDT ON 9/30/15 * * * Upon investigation of the details surrounding the event, it was determined that the patient received greater than 80% of prescribed activity. Therefore, this event no longer meets any regulatory reporting criteria and is being retracted. Notified R1DO (Bower) and NMSS Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-09-29
50471 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-09-19 | 2014-09-19 10:09 | 2014-10-10 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The state of New Jersey provided notification that a licensee (French and Parrello) reported a Troxler moisture density gauge (Model 3430, Serial #38931) stolen. The gauge was in the possession of a contractor (employed by Aerotek staffing agency) who has not shown up for work for several days. Attempts have been made to contact the contractor. New Jersey instructed the licensee to contact local law enforcement. The gauge contains 40mCi Am-241 and 8mCi Cs-137. NJ EVENT: 14-09-19-1107-54 * * * UPDATE FROM JACK TWAY TO HOWIE CROUCH (VIA EMAIL) ON 9/19/14 AT 1231 EDT * * * The gauge operator contacted the Wall Township Police Department to inform them that he was in possession of the gauge and would be returning it to the licensee today. Notified R1DO (Lilliendahl), FSME Events Resource (email), and ILTAB (email). * * * UPDATE FROM JACK TWAY TO HOWIE CROUCH (VIA EMAIL) ON 10/10/14 AT 1019 EDT * * * The gauge was, in fact, returned to the licensee on 9/19/14. The State of New Jersey received a written report of the event from the licensee and considers this case closed. Notified R1DO (Bower), FSME Events Resource (email) and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-09-29
50470 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2014-09-18 12:35 | 2014-09-18 18:43 | 2014-09-18 | OFFSITE NOTIFICATION - FAILURE TO SUBMIT REQUIRED SEMI-ANNUAL AND ANNUAL SAMPLES AND REPORTS PER NPDES "Today, at 1235 [PDT], San Onofre made the decision to notify offsite agencies (San Diego Regional Water Quality Control Board and Environmental Protection Agency if directed by SDRWQCB). Initial contact made with the San Diego Regional Water Quality Control Board was at 1333 [PDT] on 9/18/14. The subject of the report is listed below: "On September 15, 2014, during a review of the NPDES [National Pollutant Discharge Elimination System] self-monitoring reports, SCE SONGS [Southern California Edison San Onofre Nuclear Generating Station] environmental staff discovered annual and semi-annual samples and required reports due in 2014 were not submitted on time and are now past due: "- The missed samples and associated reports are non-radiological in nature "- All parameters (physical and analytical data) in past Semi-annual and Annual reports have been in compliance with the NPDES permit." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-09-18
50469 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-02-01 | 2014-09-18 14:24 | 2014-09-18 | AGREEMENT STATE REPORT - DISCOVERY OF THREE LEAKING SOURCES The following information was received from the state of Colorado via email: "The following is a notification not previously identified to NRC. "On or about April 24, 2014, during licensing renewal activities, the [Colorado Radiation Control Program] Agency licensing staff received information that Colorado specific licensee Analytical Instrument Recycle, Inc. (AIR, 15860 West 6th Ave., Golden, CO 80401; CO License #974-01) had reportedly discovered that three generally licensed (GL) electron capture devices (ECDs) in their possession that had failed a leak test approximately two months prior (in ~February 2014). (The licensee refurbishes and resells analytical instruments containing ECDs, although the licensee performs leak tests, it is not authorized to work on or open ECDs or the sources contained within them.) "The licensee's Radiation Safety Officer (RSO) indicated that he had previously sent notification regarding the leaking sources to the Agency (Colorado Department of Public Health and Environment) in early February, 2014 and provided a copy of an undated letter during the investigation. "The licensee reported the leak test results/analysis data as follows: 1) Hewlett-Packard/Agilent model 19233 serial number L4716 (Contamination level of 0.064uCi) 2) Hewlett-Packard/Agilent model G1533A serial number K3545 (Contamination level of 0.013uCi) 3) Hewlett-Packard/Agilent model G1223A serial number F1219 (Contamination level of 0.008uCi) "Each of the leaking devices contains a nominal activity of 15 mCi of Ni63, although the devices are authorized to contain up to 18 mCi of Ni63. "The licensee reported that areas where the devices were handled had been surveyed and indicated that no contamination above background present in the work area or facility. The licensee reported to the Agency that the leaking ECDs were returned to the manufacturer on March 7, 2014. "No further action is required and the Agency considers this matter closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-09-26
50468 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-09-18 11:55 | 2014-09-18 14:05 | 2014-09-18 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "During a review of INPO Event Report 14-33, Direct Current Circuits Challenge Appendix R Fire Analysis, it was determined that portions of the control circuits for the Turbine Generator DC Emergency Lube Oil Pump and the Emergency DC Seal Oil Pump are not properly fused to prevent overload and possible secondary fires. The review found that a fire at the motor starter cabinet in the turbine building could cause specific smart hot shorts that could cause overheating of the control cable and result in secondary fires outside the turbine building. Based on this information, it was determined that this condition is unanalyzed and is potentially reportable per 10 CFR 50.72(b)(3)(ii)(B). "Hourly fire watch compensatory measures are in place in the affected areas of the Turbine Building. The presence of compensatory measures in addition to automatic fire detection and suppression in these fire areas ensures protection of the equipment." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-09-18
50467 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2014-09-18 11:50 | 2014-09-18 13:01 | 2014-09-18 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO MISALIGNED CONTROL ROD "During the performance of PT-Q89, Control Rod Exercise Test, Rod G-3 in Shutdown Bank 'B' misaligned (stepped in) to approximately 195-200 steps indicated with group demand at 217 steps. The movable gripper fuse was suspect, found not blown [so further] troubleshooting required. At 1150 [EDT], the decision was made to reduce power to approximately 70% within two hours per I.T.S. [Improved Technical Specification] 3.1.4.b.2.2. The plant is currently stable at 68% power. I.T.S. 3.1.5.b.1 was also entered for Shutdown Bank 'B' less than allowable insertion limits at time 1228 [EDT] to be in Mode 3 in 6 hrs. (1828 [EDT])." The licensee notified the New York Independent System Operator, the New York Public Service Commission and the NRC Resident Inspector. | 68 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-09-18
50466 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-09-16 | 2014-09-18 10:35 | 2014-09-18 | AGREEMENT STATE REPORT - FIXED GAUGE WITH A STUCK OPEN SHUTTER The following was received via email: "The licensee's radiation safety officer called the Agency [Illinois Emergency Management Agency] to advise that on 9/16/14, an Ohmart Vega, m/n SH-F1-45 fixed gauge containing 15 milliCi of Cs-137 (as of April 2002) had a shutter which could not be closed. They became aware of the situation during the performance of routine 6 month operability checks. The manufacturer was immediately contacted to schedule an evaluation in the coming weeks and for advice. The licensee was advised to lubricate the shutter pinion and allow it to sit overnight before attempting to close the shutter again the next day. The licensee intends to have the manufacturer's field engineer come on site to inspect the device. "The gauge is located on a vessel which is still in active use for sulfur production and is exposed to ambient weather conditions. The gauge is located approximately 15 feet overhead on a platform which is not a routine work location for day to day operations. A lock out/tag out procedure is actively in use at the site should any work on/in the vessel be necessary before repairs can be affected. Notifications to the acting RSO are part of that procedure. The licensee is aware of the 30 [day] written reporting requirement." This is the second time that the shutter has stuck open recently. Illinois Event #: IL14019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-09-26
50465 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-09-17 09:13 | 2014-09-17 13:59 | 2014-09-17 | OFFSITE NOTIFICATION DUE TO OIL TANKER TRUCK SPILL "At approximately 0913 CDT, the Callaway Plant Control Room was notified that an oil tanker truck overturned on plant property. The location of the incident was inside the owner controlled area but outside of the protected area. The truck was making a delivery to the plant. The Callaway County Emergency Operation Center was contacted at approximately 0930 to request an ambulance for the driver. The driver of the truck was transported offsite for medical treatment. The drivers injuries are not life threatening. The incident has resulted in a slow leak of diesel fuel that is being contained onsite. "Missouri Department of Natural Resources was notified of the spill. "The Missouri Highway Patrol is onsite assisting with the incident and restoration efforts. "Both NRC Resident Inspectors were notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-09-17
50464 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-09-17 08:00 | 2014-09-17 09:21 | 2014-09-17 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "This telephone notification is provided in accordance with 10CFR50.72(b)(3)(xiii), 'Major Loss of Emergency Preparedness Capabilities.' "On September 17th, 2014, at 0800 [CDT], the Exelon LaSalle Station Technical Support Center (TSC) ventilation system was removed from service for planned TSC ventilation system maintenance. "The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The ventilation system is expected to be out of service for approximately 4 hours. "The licensee has notified the [NRC] Senior Resident Inspector of the issue." * * * UPDATE PROVIDED BY WAYNE CLAYTON TO JEFF ROTTON AT 1741 EDT ON 09/17/2014 * * * The scheduled TSC ventilation system maintenance is expected to be out of service for approximately an additional 7 hours. The licensee has notified the NRC Senior Resident Inspector of the issue. Notified R3DO (Dickson) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-17
50463 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-09-16 19:05 | 2014-09-16 23:20 | 2014-09-16 | LOSS OF DIVISION 3 OF SHUTDOWN SERVICE WATER REQUIRES HPCS TO BE DECLARED INOPERABLE "At 1905 hours (CDT), during surveillance testing of the Division 3 Shutdown Service Water (SX) system, the Division 3 SX pump tripped for unknown reasons. The Division 3 SX system was declared inoperable and in accordance with Technical Specification 3.7.2, Action A, the High Pressure Core Spray (HPCS) system was declared inoperable. Since the HPCS system is a single train safety system, this event is reportable under 10CFR50.72(b)(3)(v)(D). An investigation is underway to determine the cause of SX pump to trip. "The NRC Resident [Inspector] has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-09-16
50462 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-09-16 15:19 | 2014-09-16 16:34 | 2014-09-16 | OFFSITE NOTIFICATIONS AND PRESS RELEASE REGARDING ONSITE FATALITY "At approximately 1420 [EDT] on September 16, 2014, a worker collapsed in an office building inside the protected area. Initial response by on-site responders found the person unresponsive. Subsequent response by off-site medical responders determined the person had died. Licensee was notified of fatality at 1519 [EDT]. The fatality was due to an apparent personal medical issue and not work related. The individual was not contaminated. "The individual was transported off-site via Medic One, a local ambulance. "The NRC Senior Resident Inspector was notified. Plant operation was not impacted by the event. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies. The Licensee plans to make a press release." The licensee also notified Michigan OSHA, and other local authorities. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-09-16
50461 | 0 | DOWL HKM |  |  |  |  | 2014-09-16 | 2014-09-16 14:13 | 2014-10-14 | TROXLER MOISTURE/DENSITY GAUGE DAMAGED ON CONSTRUCTION SITE The licensee [Dowl HKM] Radiation Safety Officer (RSO) reported that a Model 34/40 Troxler Moisture/Density Gauge, containing 8 mCi Cs-137 and 40 mCi Am/Be sources, was damaged at a construction site near Evanston, Wyoming. A roller inadvertently backed over the gauge, however the sources are intact and in the stored position. There is no indication of contamination or exposure to personnel. The gauge has been returned to the appropriate storage container and the container has been locked. The storage container has been placed in the back of a pickup truck and the truck has been parked in a roped off area to minimize the possibility of exposure. The licensee RSO has been dispatched and will provide additional details as they are acquired. * * * UPDATE AT 1740 EDT ON 10/14/14 FROM MICHAEL NEZWORSKI TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On 9/16/14, a DOWL HKM technician was operating a portable nuclear Densometer (Troxler model 3440 s/n: 30263) on an asphalt paving job near Evanston, WY. The nuclear gauge came in contact with a steel drum roller on the roadway surface, which caused the gauge to be slightly damaged. The outer case was cracked, and the base of the gauge was bent. Both sources within the gauge were still intact and proper shielding was still in working order. The gauge was placed in the safe position and locked in its storage box. The box was placed in a pickup truck and properly locked and then quarantined until a leak test and survey could be performed later that evening. The DOWL HKM RSO was contacted in Billings, MT, and dispatched to the jobsite immediately after the event. As he traveled, Qai-Tek associates were also contacted to perform leak testing and survey of the gauge and surrounding area. At approximately 2100 EDT, a Qai-Tek associate arrived and performed an on-site leak test of the gauge, and the gauge case. The leak test passed, no exposure occurred, so no survey of the jobsite was performed. Mr. Wilson secured the gauge in his vehicle, and returned it to Qai-Tek's office in Idaho Falls, ID. Repairs were made to the damage gauge and it was returned to DOWL HKM on 10/13/14." Notified the R4DO (Haire) and FSME Events Resource (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-09-24
50460 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2014-09-15 | 2014-09-15 17:55 | 2014-09-15 | AGREEMENT STATE REPORT - IODINE 131 SPILL IN PHARMACY The following information was provided by the State of South Carolina via email: "Shertech Pharmacy (SC Radioactive Material License No. 531) in Spartanburg, SC, reported a spill of 100mCi of I-131. A pharmacist dropped the iodine vial on the pharmacy floor. Most of the contamination was on the floor and the shoes of the pharmacist. The Radiation Safety Officer and pharmacist began clean-up procedures. Clothes and shoes were placed in zip lock bags. The floor was cleaned with Radiac wash and the cleaning items were placed in zip lock bags. Activated charcoal was placed on the floor. The four individuals present did take Lugol's solution. Zip lock bags containing the contaminated items were placed in the fume hood. No contamination was found on the skin of any of the individuals involved. Readings of 0.6 mR/hr are measured outside of the closed room. The licensee will perform bioassays at 24, 48, and 72 hours on the four individuals present during the spill and clean up. The primary contamination appeared to be on the shoes themselves." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2014-09-23
50459 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-09-15 13:09 | 2014-09-15 17:57 | 2014-09-15 | LOSS OF EMERGENCY SIREN ACTIVATION CAPABILITY "At 1309 Eastern Daylight Time (EDT) on September 15, 2014, it was determined that the ability to activate the thirty-eight (38) emergency sirens within the 10 mile emergency planning zone (EPZ) radius of the plant was lost. Subsequently, activation capability was restored when a loose modem cable was discovered and remedied. By approximately 1450 EDT, the ability to activate the emergency sirens had been satisfactorily tested. Activation capability of the emergency sirens was restored in approximately 1 hour and 41 minutes. This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a major loss of communications capability. "This event did not result in any adverse impact to the health and safety of the public. The Brunswick Nuclear Plant and State of North Carolina Emergency Response Plans include back-up processes to provide warning to affected areas, if required, in the event of the loss of sirens. "The cause of the loose modem cable will be investigated. "The NRC Senior Resident [Inspector] has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-15
50458 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-08-06 | 2014-09-15 15:12 | 2014-09-15 | AGREEMENT STATE REPORT - MANUFACTURING DEFECT RESULTING IN EQUIPMENT TO NOT PERFORM AS DESIGNED The following information was provided by the Commonwealth of Massachusetts via email: "On 9/15/2014, Massachusetts Radiation Control Program (MA RCP) was notified by licensee (QSA Global, Inc.) in accordance with 105 CMR 120.142(B)(2) of manufacturing defect of a model 95020 radiographic guide tube resulting in equipment that failed to function as designed. The licensee reported that its customer (Team Industrial Services of South Roxana, Illinois) informed the licensee on 8/6/2014 that the end stop of the guide tube had come off during a radiographic exposure performed 7/25/2014, that the source was able to be returned to the shielded/stored position in the exposure device using normal retraction with the control assembly, and that there was no excessive personnel exposure related to the part failure. "The licensee reported that its examination of the model 95020 assembly failed part showed that the end fitting had not been swaged to the guide tube housing as is required by the design. "The licensee reported that upon learning of the part failure, it immediately performed a visual inspection of all guide tube and control assemblies accepted into stock for distribution and that there were no other instances of unswaged fitting or improper manufacture identified for accepted stock. Licensee further reported that it believes that the instance to be an isolated occurrence and that no other assemblies containing this defect remain in the field. "Licensee reported that manufacturer failed to swage end stop fitting to guide tube and manufacturer failed to perform pull test of end stop fitting to guide tube and check connection for slip using inspection gauge. "Licensee reported that corrective actions include changes that will be implemented in the production process to increase inspection and review of quality critical operational steps to ensure this type of manufacturing defect is not accepted and released to customers in the future. "Model 95020 guide tubes are approved for use with QSA Global, Inc. model 880 series radiographic exposure devices described by Sealed Source and Device Registration No. MA-1059-D-334-S. "Licensee reported that it conducted a review to determine if this type of condition had occurred previously and identified one instance from 2012 where a different model guide tube, model 48906, had not been properly swaged and tested prior to distribution to an international customer. "MA RCP plans to perform inspection to include evaluation for any generic implications." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-09-23
50457 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-09-15 09:00 | 2014-09-15 14:54 | 2014-09-30 | FAILED FUEL ASSEMBLY IDENTIFIED DURING CORE OFF-LOAD "With North Anna Unit 2 in Mode 6 during a scheduled refueling outage, discharged assembly 4Z9 was identified as a failed fuel assembly by In-Mast Sipping. The fuel assembly was located in core location B11. Initial inspection of the fuel assembly identified two (2) visibly split fuel pins of eight (8) to ten (10) inches long with visible damage to the top of the pins. The internals of the affected pins are visible and the springs from the top of each pellet stack are touching the top nozzle. The fuel assembly has been placed into its designated location in the Spent Fuel Pool. No abnormal increase was noted on any radiation monitor either after or during fuel assembly movement. This fuel assembly had been used during three (3) previous operating cycles and is not scheduled for reuse. "On September 15, 2014, at 0900 [EDT], subsequent video inspection of the fuel assembly identified that the top springs of the two (2) fuel pins were dislodged. Video inspection of the reactor vessel identified debris that has the potential to be fragments of fuel pellets resting on the core plate. Additional investigations are in progress. "Due to the fact that the failure exceeded expected conditions, this event is being reported per 10 CFR 50.72(b)(3)(ii)(A), as any event or condition that results in the condition of the nuclear plant, including its principle safety barriers, being seriously degraded." The licensee has notified the NRC Resident Inspector and will notify local county authorities. * * * UPDATE FROM PAGE KEMP TO HOWIE CROUCH AT 1227 EDT ON 9/30/14 * * * "Event Notification #50457 was provided on September 15, 2014, at 1454 hours, pursuant to 10 CFR 50.72(b)(3)(ii)(A), to provide notification that North Anna Unit 2 discharged assembly 4Z9 had two visibly split fuel pins and debris on the core plate that had the potential to be fuel pellet fragments. "Detailed video inspections estimated that fifteen (15) fuel pellets were dislodged from fuel assembly 4Z9. For reference, the reactor core contains approximately 15 million fuel pellets. Efforts to identify and recover the fuel pellets were performed. Debris fragments, estimated to represent five (5) fuel pellets, were located within the damaged fuel assembly that is currently in the spent fuel pool. In addition, an estimated three (3) pellets worth of material was retrieved by the foreign object search and retrieval (FOSAR) efforts in the reactor vessel. The remaining seven (7) fuel pellets have already or are expected to granulate into fine particles that will remain in low flow areas of the primary plant systems or be removed by normal purification processes. However, since the specific location of the seven (7) fuel pellets is undesignated, a report is being made pursuant to 10 CFR 74.11(a) for the loss of special nuclear material. "The seven (7) fuel pellets contain licensed material in a quantity greater than 10 times the quantity specified in Appendix C of 10 CFR 20; therefore a report is also being made pursuant to 10 CFR 20.2201(a)(ii). "The cause of the fuel clad degradation is understood and is being addressed. It has been evaluated that the dispersion of fuel pellet material will pose no threat to the integrity or operation of the reactor fuel and primary system components. Reactor Coolant System activity will remain below Technical Specification limits during power operation. In addition, there are no adverse radiological consequences to the public as a result of this issue." The licensee will be notifying the state of Virginia, local authorities in Louisa County and has notified the NRC Resident Inspector. Notified R2DO (Vias) and IRD (Stapleton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | LOST/STOLEN SNM | LOST/STOLEN LNM>10X |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) | 74.11(a) | 20.2201(a)(1)(ii) |  | 0 | 2014-09-15
50456 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-09-14 02:26 | 2014-09-14 11:03 | 2014-11-10 | OPERATION IN UNANALYZED REGION OF THE POWER TO FLOW MAP "At 0226 CDT on September 14, 2014, MNGP [Monticello Nuclear Generating Station] experienced a trip of the 12 Reactor Recirc Pump. The subsequent power drop and lowering of recirculating water flow resulted in the plant being outside of the analyzed region of the Power to Flow Map. Operators promptly restored operation within the analyzed region per procedural guidance. This event has been determined to be a condition where the plant was in an unanalyzed condition that significantly degrades plant safety and is reportable under 50.72(b)(3)(ii). The plant is in stable condition at 51% power and the health and safety of the public were not affected. The investigation of the cause of this event is in progress." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM SCOTT CHRISTOS TO HOWIE CROUCH AT 1433 EST ON 11/10/14 * * * "Further analysis has determined that the condition did not significantly degrade plant safety. "General Electric Hitachi was requested to review the event and confirm the SIL653 guidance remains applicable for MELLLA+ [Maximum Extended Load Line Limit Analysis] operation. This review was completed and the conclusions of SIL653 remain valid . The SIL states that: 'unplanned events that result in the plant exceeding the licensed upper boundary do not constitute a safety concern. The consequences of such unplanned events are bounded by the GE safety analysis of limiting events initiated from within the licensed operating domain. "Stability monitoring and protection using Detection and Suppression Solution Confirmation Density remained available throughout the event (oscillating power range monitors). "The NRC Resident Inspector has been notified." Notified R3DO (Hills). | 51 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-09-14
50455 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-09-13 03:07 | 2014-09-13 09:53 | 2014-09-13 | FIRE PENETRATION DID NOT MEET APPENDIX R REQUIREMENTS "A fire penetration on the Unit 1 reactor building 158 foot elevation was discovered to be degraded such that the associated wall would not meet Appendix R requirements as a 3-hour barrier. In the event of a postulated fire in either of the affected fire areas, separated by the affected penetration, both Unit 1 safe shutdown paths could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were established in accordance with the plant's Fire Hazard Analysis (FHA). The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition can be corrected. "Condition Report: 865615" The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-09-13
50454 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2014-09-12 15:47 | 2014-09-12 20:42 | 2014-09-12 | STORED FUEL MAY NOT MEET FUEL SPECIFICATIONS OR LOADING CONDITIONS FOR HI-STORM 100 CASK SYSTEM "Arkansas Nuclear One (ANO) identified the potential for stored fuel that does not meet the fuel specifications or loading conditions of the Certificate of Compliance (CoC) for the HI-STORM 100 Cask System. Investigation into the cause of a Control Room Emergency Ventilation System (CREVS) actuation on the morning of 9/12/2014 led to sampling of helium circulating through the Multi-Purpose Canister (MPC-24-060) as part of the Forced Helium Dehydration process in the final stages of cask loading. Sample results indicated the presence of Kr-85. Kr-85 is a fission product that indicates the potential for the fuel that does meet the selection criteria for the HI-STORM 100 Cask System. "All fuel assemblies loaded into MPC-24-060 were checked to confirm their intact status (a cask Certificate of Conformance requirement) as part of the selection process. Each assembly's status as intact is based on in-mast sipping and/or ultrasonic testing performed subsequent to their final operating cycle. Results of these sipping and ultrasonic test campaigns are maintained in a comprehensive engineering report used to verify assembly status during cask fuel selection. "Per the CoC for the Hi-STORM 100 Cask System, Appendix B, Section 1.0, the definition of 'INTACT FUEL ASSEMBLY' is a fuel assembly without known or suspected cladding defects greater than pinhole leaks or hairline cracks, and which can be handled by normal means. Given the presence of Kr-85 along with the fuels history, it cannot be confirmed that all fuel assemblies meet the definition of 'Intact' and would not meet the CoC Requirements for Fuel to be stored in the HI-STORM 100 SFSC System (Section 2.1.1)." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW | [5 empty] | 0 | 2014-09-12
50453 | 0 | NOVELIS |  |  |  |  | 2014-09-12 11:30 | 2014-09-12 16:30 | 2014-09-15 | FIXED GAUGE SHUTTER STUCK IN CLOSED POSITION The licensee RSO (Radiation Safety Officer) reported that the shutter on a fixed gauge was stuck in the closed position. An authorized technician was able to repair the shutter and the gauge has been returned to service. There were no exposures involved with this event. The gauge is an ABB/IRMS, source model S18 containing a Y-90 300 mCi source. This report is being made per 10CFR30.50(b)(2)(i). * * * UPDATE FROM MICHAEL ROSSANA TO JOHN SHOEMAKER AT 1250 EDT ON 9/13/14 * * * The licensee RSO reported that around 0000 EDT on 9/13/14, an electrician performing routine checks found the gauge shutter stuck in the open position. The technician who performed maintenance on the previous day had caused the shutter to stick in the open position because of a mis-positioned screw. Repairs were completed and the gauge shutter is now functioning normally. This gauge is scheduled to be replaced during the upcoming Christmas shutdown. There were no exposures involved with this event. Notified R1DO (Jackson) and FSME Events Resource via email. * * * UPDATE FROM MICHAEL ROSSANA TO JOHN SHOEMAKER AT 1224 EDT ON 9/15/14 * * * The following report was received from the Novelis Corporation RSO via email; "This email serves as [the licensee's] formal notification to follow up the two telephone notifications made by [the licensee's RSO] on September 12, 2014. Both occurrences were related to shutter failures on the same thickness gauge. These notifications were made to satisfy the NRC Regulation 10 CFR 30.50 reporting requirement. "On Friday, September 12, 2014, at approximately 1300 [EDT], the shutter on the Novelis Fairmont #1 Mill thickness gauge failed in the closed position. An employee who has received non-routine maintenance training per NUREG-1556, Volume 4, Appendix G & N, took it upon himself to remove the side of the gauge and perform an investigation and repair the stuck shutter. It was determined that the pneumatic cylinder for the shutter was not functioning properly and replaced. A radiation survey was performed and the surrounding area was taped off with caution tape. There was no over exposure to radiation. The gauge was put back into service at approximately 1400 [EDT] that same afternoon. "On the same night, Friday, September 12, 2014, at approximately 2330 [EDT], the shutter on the same thickness gauge failed again. This time the shutter failed in the open position. Once the shutter was determined to be in the open position, the foreman on shift notified [the RSO]. [The RSO] spoke with the shift electrician and had him perform a radiation survey and tape off the area with caution tape. The shift electrician has received non-routine maintenance training per NUREG-1556, Volume 4, Appendix G & N. [The RSO] was on site at approximately 0030 [EDT] Saturday morning, September 13, 2014. [The RSO] verified that the shutter was in the open position by performing a radiation survey. Additionally, the light identifying the shutter position was RED indicating the shutter was open. The same individual that replaced the pneumatic cylinder was on site and he investigated the failure. It was determined that the shutter appeared to be on a bind and the screws that hold the pneumatic cylinder in place were adjusted and the shutter was free to move as intended. "With the side off of the gauge, next to the shutter assembly, at 6 inches, the measured mR/H was approximately 1 mR/h. Directly beside the shutter mechanism approximately 2 mR/h was measured. The employee worked for about 30 minutes to adjust the shutter mechanism. During this repair, there was no over exposure to radiation." Notified R1DO (Lilliendahl) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-09-22
50452 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-07-26 16:48 | 2014-09-12 12:05 | 2014-09-12 | INVALID SPECIFIED SYSTEM ACTUATION "The following information is provided as 60 day telephone notification to the NRC in accordance with 10 CFR 50.73(a)(1) reported under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of Division 1 Shutdown Service Water (SX) and an invalid actuation signal for Division 1 Containment Isolation Group 12. This event occurred on July 26, 2014, at 1648 CDT. As allowed by 10 CFR 50.73(a)(1) this notification is made via telephone. "(a) The specific train(s) and system(s) that actuated were: On July 26th, during lightning strikes on the switchyard grid system, the Division 1 SX (Shutdown Service Water) auto-started as a result of momentary loss of power to the Low Pressure Auto Start Relay. A lightning strike causing voltage transients also caused a Division 1 Group 12 Containment Isolation signal affecting DIV 1 Hydrogen monitor. "(b) Whether each train actuation was complete or partial. Upon receiving the invalid signal from momentary loss of power, for Division 1 SX and Group 12 Containment Isolation signal, the systems responded as expected for existing plant conditions. For group 12 isolation, [Containment Monitoring] 1CM011/12/47 and 48 valves closed from their normally open position. For DIV 1 Shutdown Service Water (SX), the start of the Shutdown Service Water (SX) pump and alignment of valves operated as expected. The actuation was considered a complete Division 1 SX and Division 1 Group 12 Containment Isolation actuation. "Containment Isolation Signals: The following Group 12 valves closed and associated shunt trips occurred on a loss of power to [Radiation Monitors] 1RIX-PR001A/1C: 1CM011, 1CM012, 1CM047, and 1CM048. "(c) Whether or not the system started and functioned successfully. Upon receiving the invalid signal from momentary loss of power, Division 1 SX and Containment Isolation signals started and functioned successfully. "The NRC Senior Resident Inspector has been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-09-12
50451 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-11 12:00 | 2014-09-12 10:42 | 2014-09-12 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK OUTSIDE THE CAMERA The following information was received via e-mail: "On September 11, 2014, at 1241 hours [CDT], the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that one of their radiography crews reported they were unable to fully retract a 46 curie iridium - 192 source into a SPEC 150 exposure device. The RSO stated the radiographers had completed an exposure and cranked the source back to the exposure device. The radiographer picked up their dose rate meter and observed the reading was 30 millirem an hour. The radiographer also observed that the locking mechanism had not tripped. The radiographer contacted the RSO. An individual qualified to perform source retrieval was sent to the scene. The radiographer did not approach the exposure device. The RSO stated the source retrieval person should reach the location in about an hour. Awaiting information from RSO. Update will be provided in accordance with SA-300." Texas Report #: I-9232 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-22
50450 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-07-26 13:13 | 2014-09-12 10:12 | 2014-09-12 | ELECTRICAL TRANSIENT CAUSES AN INVALID SYSTEM ACTUATION "At 1313 [EDT] on 7/26/14, the plant experienced an electrical transient on bus EK-1-B1 (safety-related 120 volt AC distribution panel) that resulted in partial Balance of Plant Division 2 isolation signals and alarms received in the Control Room. "The following component actuations occurred: valve 1P50F140 closed, resulting in a trip of Containment Vessel Chilled Water C; valve 1G41F140 closed, isolating the Fuel Pool Cooling and Clean-up return from the containment building upper pools; valve 1B33F019 closed, isolating Reactor Water sampling; valve 1D17F071B closed, isolating the Drywell Atmosphere Radiation Monitor; valve 1D17F081B closed, isolating the Containment Atmosphere Radiation Monitor; valves 1G61-F030, 1G61-F150, 1G61-F075, and 1G61-F165 closed, isolating the Containment and Drywell Floor and Equipment drain sumps; valve 1G50-F272 closed isolating the Reactor Water Cleanup Backwash Receiving Tank: 1M25F020B, Control Room HVAC Inboard supply damper, closed and Division 2 indicated an auto initiation (M25-S12, Auto Initiate Active amber light was on). "This event is considered an invalid system actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. Therefore, this notification is provided via a 60 day optional phone call in accordance with 10 CFR 50.73(a)(1) instead of submitting a written Licensee Event Report. "The event meets reporting criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation valve signal affecting containment isolation valves in more than one system. All affected systems functioned as expected in response to the electrical transient on bus EK-1-B1 that resulted in the partial Balance of Plant Division 2 isolation signals. The valves were reopened in accordance with plant procedures. The failure mechanism that caused the electrical transient was a failed capacitor in regulating transformer EFB1B2. The capacitor was replaced and tested with satisfactory results. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-09-12
50449 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-09-11 14:00 | 2014-09-11 18:10 | 2014-09-11 | FITNESS FOR DUTY - PROGRAMMATIC FAILURE "On September 11, 2014, at 1400 hours, it was determined that four (4) personnel in the Emergency Response Organization (ERO) were not subject to random testing requirements of the Fitness for Duty (FFD) Program. The personnel involved do not have unescorted access to the Protected Area, but they do respond and perform duties as a member of the ERO. The affected individuals are now included in the random FFD testing pool. "10CFR26.4(c) requires all persons who are required by a licensee in 10CFR26.3(a) and, as applicable, (c) to physically report to the licensee's Technical Support Center or Emergency Operations Facility by licensee emergency plans and procedures shall be subject to an FFD program that meets all of the requirements of this part. "This event is a 24-hour reportable event per 10CFR26.719(b)(4) - Any programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within the protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2014-09-11
50448 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-09-11 14:00 | 2014-09-11 18:00 | 2014-09-11 | FITNESS FOR DUTY - PROGRAMMATIC FAILURE "On September 11, 2014, at 1400 hours, it was determined that four (4) personnel in the Emergency Response Organization (ERO) were not subject to random testing requirements of the Fitness for Duty (FFD) Program. The personnel involved do not have unescorted access to the Protected Area, but they do respond and perform duties as a member of the ERO. The affected individuals are now included in the random FFD testing pool. "10CFR26.4(c) requires all persons who are required by a licensee in 10CFR26.3(a) and, as applicable, (c) to physically report to the licensee's Technical Support Center or Emergency Operations Facility by licensee emergency plans and procedures shall be subject to an FFD program that meets all of the requirements of this part. "This event is a 24-hour reportable event per 10CFR26.719(b)(4) - Any programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within the protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2014-09-11
50447 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-09-10 | 2014-09-11 11:59 | 2014-09-11 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received from the Tennessee Department of Environment and Conservation Division of Radiological Health via email; "The licensee and gauge service representative called [the Tennessee Department of Environment and Conservation Division of Radiological Health] to report a gauge shutter stuck in the open position. The gauge is an Ohmart Model SHRM, SN 3307, with a 35 mCi Cs-137 Model A-5771 source. The gauge remains in the installed position. It will be replaced in the future by the service representative. The gauge will be shielded as needed if the shutter is not able to be closed before transport." There were no over exposures and additional information will be provided, as it is received, from the State of Tennessee. Tennessee Event Number: TN-14-172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-09-19
50446 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-09-11 10:09 | 2014-09-11 11:32 | 2014-09-11 | SHIELD BUILDING VENT GAS RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "At 1009 CDT on September 11, 2014, 1R-22 Shield Building Vent Gas Radiation Monitor was removed from service for planned maintenance. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs) - NUE (Notification of Unusual Event) and Alert classifications when out of service. It is also used for offsite dose projection calculations. This results in a Loss of Emergency Assessment Capability while 1R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 Shield Building Ventilation Stack is also monitored by high range monitor, 1R-50, which is used for the same purpose in Site Area or General Emergency classifications. 1R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 1R-22 prior to its removal from service. The duration of this maintenance is scheduled for 8 hours and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-11
50445 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-09-10 | 2014-09-10 14:16 | 2014-09-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received via E-mail: "On September 8, 2014, at approximately 0845 PDT, the RSO of Sladden Engineering, RML #6318-33, was contacted by RHB Brea concerning a moisture/density gauge, CPN, model MC1DRP, serial number MD40807529 (Cs-137, 0.370 GBq, Am-241, 1.85 GBq) that had been damaged when run over by construction equipment at a building site located at 123 N. Palm Canyon Drive, Palm Springs, California, on September 3, 2014, at approximately 1400 PDT. The authorized user at the construction telephoned the RSO. They then went through the radiation safety plan over the phone, and after an initial inspection of the radioactive gauge it was determined that the gauge was heavily damaged but since the source remained in the shielded position, the RSO authorized transport back to the office in the Type A transport container. A closer inspection of the radioactive gauge was conducted by the RSO on the following morning, September 4, 2014, at which time it was determined that the source rod was broken. The RSO contacted the RHB South Brea office and left voice mail messages, then contacted the emergency number and was transferred to a telephone number in Sacramento RHB and left another voice mail message. The RSO performed a leak test on the radioactive gauge and sent it to PNT Company for analysis on September 4, 2014, and received notification that the sources were negative for leakage on September 5, 2014. The RSO performed a follow-up investigation of the incident at the location of the accident and has contacted Maurer Technical Services for disposal of the radioactive gauge since it is beyond repair. "This is being reported to the NRC Operations Center as a 24-hour report under 10CFR30.5(b)(2) since the radioactive gauge cannot be locked in the shielded position (due to the source rod being broken ) despite the fact that the Cs-137 source is in the shielded position as that was the configuration at the time of the accident." California Report #: 5010-090314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-09-18
50444 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-09-10 11:06 | 2014-09-10 14:20 | 2014-09-10 | RADIATION MONITOR OUT OF SERVICE "Loss of assessment capability due to pre-planned maintenance affecting a radiation monitor for supplementary leakage collection and release system. [Monitor] (3HVR*RE19A/B) will be out of service. The condition is reportable per 10CFR50.72(b)(3)(xiii). The equipment is expected to be restored within 48 hours." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-10
50443 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-09-10 04:53 | 2014-09-10 11:55 | 2014-09-10 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO FIRE ALARM "This is a non-emergency eight hour notification for a loss of Emergency Preparedness Capabilities. This event is reportable in accordance with 10 CFR50.72(b)(3)(xiii) as the condition affects the functionality of an emergency response facility. "At approximately 0453 EDT on September 10, 2014, a fire alarm in an area near the primary Technical Support Center (TSC) triggered an automatic shutdown of the TSC ventilation system. The system was restored at 0755 EDT. The alternate TSC was available at all times. "This condition does not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-10
50442 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-03-13 08:00 | 2014-09-10 11:51 | 2014-09-10 | WELDING PROGRAM DEVIATIONS DURING CONSTRUCTION "This is a 10CFR50.55(e) initial notification for a significant breakdown in the Quality Assurance (QA) program of Chicago Bridge & Iron (CB&I) Lake Charles facility, a sub-supplier of CB&I. CB&I Lake Charles supplies safety-related structural sub modules for the Virgil C. Summer Units 2 and 3 construction project. "In March, 2014, CB&I Lake Charles issued a root cause analysis report for welding program deviations associated with the fabrication of sub-modules being supplied to domestic AP1000 construction projects. An evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10CFR50.55(e)(4)(iii) and 10CFR50.55(e)(5)(i)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY | [9 empty] | NON EMERGENCY | 2 | SC | POW |  | 50.55(e) |  |  |  | 0 | 2014-09-10
50441 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-03-13 08:00 | 2014-09-10 11:24 | 2014-09-10 | WELDING PROGRAM DEVIATIONS DURING CONSTRUCTION "This is a 10CFR50.55(e) initial notification for a significant breakdown in the Quality Assurance (QA) Program of Chicago Bridge & Iron (CB&I) Lake Charles facility, a sub-supplier of CB&I. CB&I Lake Charles supplies safety-related structural sub-modules for the Vogtle 3 and 4 construction project. "In March, 2014, CB&I Lake Charles issued a root cause analysis report for welding program deviations associated with the fabrication of sub-modules being supplied to domestic AP1000 construction projects. An evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10CFR50.55(e)(4)(iii) and 10CFR50.55(e)(5)(i)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 50.55(e) |  |  |  | 0 | 2014-09-10
50440 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-09-09 19:36 | 2014-09-10 10:24 | 2014-09-10 | FAILURE OF THE AUTO-START FEATURE ON TWO CONTAINMENT COOLERS "This is a non-emergency notification in accordance with 10 CFR 50.72(b)(3)(v)(D) which requires a report when any event or condition at time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "On 9/9/14, FPL discovered the automatic feature associated with the swing 4A emergency containment cooling (ECC) unit was inoperable due to a design change inadequacy. During breaker replacement activities performed on 9/3/14, a one hour shutdown action statement pursuant to TS 3.6.2.2.b was exceeded due to two ECC's being unable to automatically start on an SI [Safety Injection] signal. [This was not known until the 4A was declared inoperable on 9/9/14 at 1936 EDT]. "The 4A ECC was declared inoperable at 1936 EDT on 9/9/14, and in accordance with TS 3.6.2.2.a, must be returned to OPERABLE status within 72 hours from the time of discovery." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-09-10
50439 | 0 | CAMERON MEASUREMENT SYSTEMS |  |  |  |  | 2014-09-09 | 2014-09-09 18:37 | 2014-09-09 | PART 21 REPORT - DEFECTIVE BARTON DIFFERENTIAL PRESSURE SWITCHES The following is a synopsis of information received via facsimile: Cameron Measurement Systems has issued a product advisory concerning nuclear qualified versions of Barton Model 288A, 289A, 580A and 581A differential pressure indicating switches and blind switches and spare switch assemblies shipped from the Cameron factory. The defect being reported is an out of specification thread on the screws that depress the switch operating plunger which can cause a change in the switch setpoint. The maximum change in screw position observed during testing equates to a switch set point change of approximately 8.4 percent of the instrument's factory calibrated span. The screws of concern did not enter the Cameron stock before February of 2014 for the ones used in the Model 580A and 581A instruments and not before June of 2014 for the ones used in Model 288A and 289A instruments. Cameron recommends that new switch actuator arm assemblies be replaced on any unit that is evaluated to be a concern by their customers. Notification to NRC provided by ISAAC RAMSINI, Manager Quality and Safety, (562) 321-9158. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-09
50438 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-09 | 2014-09-09 18:10 | 2014-09-09 | AGREEMENT STATE REPORT - STUCK SHUTTERS ON TWO PROCESS GAUGES The following information was received via E-mail: "On September 9, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee that while taking a tank out of service for repairs, it was unable to close the shutters on two Ohmart Vega model SH-F2 level gauges, each containing 500 milliCuries of Cesium-137. The shutters are stuck in the open position, which is the normal operating position for the gauges. The licensee has contacted a service provider who will be on site on September 10, 2014 to make repairs to the gauges. The gauges do not create an exposure hazard to any individual. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-17
50437 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-09-09 | 2014-09-09 17:52 | 2014-09-09 | AGREEMENT STATE REPORT - HUMBOLDT MOISTURE DENSITY GAUGE IN VEHICLE INVOLVED IN A TRAFFIC ACCIDENT The following information was provided by the State of Texas via email: "On September 9, 2014, the Agency [Texas Department of State Health Services] was notified by the Woodlands Fire Department that they were at the scene of a traffic accident [on roadway FM 2978 near Magnolia, TX] involving a vehicle transporting a gauge containing radioactive material. The gauge was a Humboldt 5001 EZ moisture/density gauge containing a 10 millicurie Cesium-137 source and a 40 millicurie Americium-241 source. The licensee contacted the Agency and stated one of their trucks was stopped behind a tractor trailer when it was struck from behind by a truck. Neither the gauge nor the transportation package was damaged in the event. No injuries to individuals involved in the event were reported. Traffic on the road the vehicles were traveling on was closed for more than 1.5 hours. The licensee stated the dose rate on contact with the transportation container was 0.5 millirem per hour, which is normal. The Transport Index for the container was 0.2. The licensee stated the gauge would be taken back to their facility and inspected. No individual received any significant exposure to radiation due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-17
50436 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-09-08 11:30 | 2014-09-08 18:28 | 2014-09-08 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE The following information was received via E-mail: "On September 8, 2014, at approximately 1130 to 1245 PDT, an authorized user of radioactive gauges who is the ARSO [assistant radiation safety officer] of Calwest Geotechnical, RML #5539-56, contacted RHB [Radiation Health Branch] Brea concerning a moisture/density gauge, Troxler model 3440, serial number 15195 (Cs-137, 0.333 GBq, Am-241, 1.63 GBq) that had been stolen from a transport vehicle in front of a restaurant in Santa Monica during the lunch break period of 1130 to 1245 PDT. The ARSO has contacted the local law enforcement officials in his area and has filled out a theft report which will be copied and sent to RHB Brea as part of this report. The ARSO will utilize local papers to attempt to retrieve the stolen gauge. The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. This is being reported to the NRC Operations Center as a 24-hour report under 10CFR30.50(b)(2) since the radioactive gauge has been stolen and it cannot be determined what condition the sources are currently in." California Report No.: 5010-090814 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-09-16
50435 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-09-08 16:00 | 2014-09-08 18:27 | 2014-09-08 | AGREEMENT STATE REPORT - CONTAMINATED CD-109 SEALED SOURCE The following information was obtained from the Commonwealth of Massachusetts via email: "The Agency (Massachusetts Radiation Control Program) was notified on 9/8/2014, by Thermo Scientific Portable Analytical Instruments, Inc. (MA RAM License # 55-0238), that a leak test result for a Cd -109 sealed source was above the leak test limits of 185 Bq (0.005 microCi). The wipe test showed that the removable activity was 486 Bq (0.0131 microCi), which is above the regulatory limit. "The licensee provided the following information about the sealed source: The source manufacturer is Eckert and Ziegler (formerly/aka Isotope Products Laboratories). The model number is FXB-3 and intended for use in a handheld XRF analyzer. Total activity on the source is 40 mCi. The wipe test was done in a controlled environment in their production source room as they were taking the source out of its original packing material. The licensee did survey the area after discovering the wipe test and did not find any signs of contamination elsewhere. The package (not the sources within) was received on August 21, 2014 and wipe tested clean at that time, so there is no indication that contamination has spread anywhere beyond the source itself. "There were no personnel contaminations or area contamination from this contaminated sealed source. The licensee will file a report to our agency within 5 days of this leak test. "The Agency considers this matter to still be OPEN pending further review of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-09-16
50434 | 0 | UNDERWATER CONSTRUCTION CORPORATION |  |  |  |  | 2014-06-18 | 2014-09-08 16:41 | 2014-09-08 | PART 21 - FAILURE TO MEET SPECIFIED IRRADIATION DURING TESTING OF COATED TEST PANELS The following information is a synopsis of information received via facsimile: Underwater Construction Corporation (UCC) was notified by Steris Isomedix Services (SIS) that test panels coated with Bio-Dur 560Blue epoxy coating, which SIS had been contracted to irradiate to a minimum accumulated dose of 1000 Mrad, could possibly have received a dose of only 949 Mrad due to a variance of 5.1 percent not previously reported on the Steris Component Irradiation Certificate. Bio-Dur 560Blue is a Service Level I coating. Failure to meet irradiation requirements for qualifying Service Level I coatings could result in the coating disbonding from the substrate, thus clogging Emergency Core Cooling Strainers during a postulated Loss of Cooling Accident (LOCA). Bio-Dur 560Blue was used to reline the toruses at Peach Bottom Units 2 and 3. Also, 588 square feet of Bio-Dur 560Blue was applied to the liner of the suppression pool at Limerick Unit 1. UCC notified Exelon concerning the irradiation failure and provided the following recommendations: - Perform evaluation of their Safety Analysis Report to determine if 949 Mrad meets licensing commitments. - Perform a review and determine if Supplemental Test Report per Exelon Contract 00045628, Release 00735, whereby irradiation testing of Bio-Dur 560Blue was performed to 1000 Mrad by University of Massachusetts will provide reasonable assurance that coating will not fail during a LOCA. Notification to NRC provided by Les Ayer, UCC QA Manager, 860-767-8256, x-169. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-08
50433 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-09-04 | 2014-09-08 16:37 | 2014-09-08 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO MISADMINISTRATION OF Y-90 THERASPHERES The following information was received via email: "A Y-90 TheraSphere liver therapy procedure resulted in delivered doses to the liver and lungs that differed from the prescribed dose. The revised Lung Shunt Fraction (LSF) value was used to recalculate the actual radiation dose to lungs and LT liver lobe. The results are that the lungs received 34.5 Gy (instead of 3.7 Gy) and the LT liver lobe received 67 Gy (instead of 117 Gy). Also, it is calculated that the LT liver lobe was implanted with a Y-90 activity dose of 0.82 GBq (22.2 mCi) while the lungs received a Y-90 activity dose of 0.69 GBq (18.64 mCi) since the patient was implanted with 1.50 GBq (40.53 mCi) of Y-90. The patient's family was notified. UVA staff are meeting to analyze the root cause of the event. RMP [Virginia Radioactive Materials Program] staff will review UVA's findings and determine what further actions are necessary." Virginia Event Report ID No.: VA-2014-16 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-09-16
50432 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-09-08 09:17 | 2014-09-08 10:42 | 2014-09-08 | STACK RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "Millstone site Stack Radiation Monitor, RM-8169, was removed from service for scheduled maintenance. This is reportable as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). Expected return to service time is at 1600 [EDT] on 9/8/14." The licensee has notified Waterford township, the State of Connecticut and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-08
50431 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-09-06 06:13 | 2014-09-06 13:17 | 2014-09-06 | TECHNICAL SUPPORT CENTER AIR CONDITIONING CONDENSING UNITS OUT OF SERVICE "At 0613 [CDT] on 9/6/2014, Technical Support Center roof mounted condensing units were found tripped by operations personnel. An attempt was made to restart both condensing units, neither condensing unit would restart. This caused a loss of Technical Support Center cooling capability. Technical Support Center Air Handling system is in service and required filtration remains available. Wet bulb temperature of the TSC, taken at 0950 [CDT] is 78.0 degrees F. Corrective action process has been initiated. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 3, since this condition affects an emergency response facility." The NRC Resident Inspector has been notified. * * * UPDATE FROM DAVE CIHA TO DONALD NORWOOD AT 1822 EDT ON 9/10/14 * * * "Braidwood Generating Station TSC ventilation was repaired to available status at 1700 CDT on September 10, 2014. During troubleshooting, it was discovered that two of three fuses leading to the controller for a fan had cleared. The fuses were replaced and the station is currently monitoring the voltage and current of the fan controller." The licensee notified the NRC Resident Inspector. Notified R3DO (Riemer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-06
50430 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-09-06 09:51 | 2014-09-06 11:18 | 2014-09-07 | OFFSITE NOTIFICATION DUE TO ONSITE OIL SPILL "At 0951 EDT on September 6, 2014, it was determined that Beaver Valley Unit 2 had experienced an oil spill to the catch basin system that progressed to the Ohio River, requiring notification of: National Response Center (incident report #1094523), Pennsylvania (PA) Department of Environmental Protection, Beaver County Emergency Management Agency, PA Emergency Management Agency and, Downstream water authorities (Midland Water Authority, Allegheny Ludlum, East Liverpool Water Co.) "This notification is a required 4-hour report per 10CFR50.72(b)(2)(xi). "Oil was inadvertently pumped from a transformer spill catch area during routine seasonal water removal efforts. Oil was not expected in the catch area and the spill catch area had tested negative for oil during pre-removal testing. An oil sheen has been detected on the Ohio River immediately surrounding the outfall. The source of the spill has been terminated, however some residual oil is washing out of the catch basin system into the river. It is estimated that less than 5 gallons entered the river. "Clean up efforts for the catch basins are currently underway and containment efforts for the oil in the river are being evaluated. A press release is currently being planned. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BLASE BARTKO TO HOWIE CROUCH AT 1025 EDT ON 9/7/14 * * * The licensee has decided not to issue a press release concerning this event. The licensee will notify the NRC Resident Inspector. Notified R1DO (Ferdas). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-09-06
50429 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2014-09-04 | 2014-09-05 16:07 | 2014-09-05 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of Washington via email: "On Thursday, September 4, 2014, [Washington State] Emergency Response Duty Officer received a call from the Radiation Safety Officer of GeoResources, LLC. She informed [Washington State] that a portable gauge was run over by heavy equipment in a construction area. The gauge operator was within a few feet of the gauge and tried to stop the driver of the front end loader but could not and had to jump out of the way for his own safety. Because of the circumstances, there will be no citations of the radiation safety program. [A Washington State inspector] drove to the location and assisted the RSO and gauge operator. The mangled gauge was put into a 55 gallon drum surrounded by soil. The highest external surface of the drum was 80 mR/hr. For health and safety purposes and the short distance to transport the drum from the construction site to the licensee's facility, a decision was made to transport the drum without DOT Yellow III package labeling and vehicle placarding, while escorted by the state inspector. The drum was put into a secured room while waiting for the consultant to come the next day (today). A consultant from Northwest Technical Services is communicating with Instrotek and R.L. Carriers for transport and disposal." WA Incident # WA-14-037 The gauge contained 0.050Ci AM-241 and 0.010Ci Cs-137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-09-15
50428 | 0 | SCHULZ ELECTRIC |  |  |  |  | 2014-09-04 | 2014-09-05 11:08 | 2014-09-30 | POTENTIAL PART 21 ISSUE ON MOTOR DEDICATIONS PERFORMED PRIOR TO JUNE 2002 The following information was obtained via fax: "Pursuant to the 10 CFR Part 21 requirements, this letter is to notify the NRC of a potential Part 21 condition. "While performing research on questions regarding acceleration presented by First Energy/Davis Besse, Schulz Electric identified that the acceleration calculation used to determine acceleration times for new motors which it dedicated before June 7, 2002 (at which time Schulz developed a shop instruction for calculating acceleration using the proper calculation) was incorrect. The use of this incorrect calculation could potentially cause misleading acceleration times, and therefore motors which may not perform as required by First Energy/Davis Besse and/or other customers. "Schulz Electric will perform an evaluation to identify: 1. All projects that had acceleration calculations performed as part of a motor dedication prior to June 7, 2002. 2. The methodology used to perform the calculations. 3. Whether the actual acceleration times meet the acceleration/performance requirements of the applicable customers. "Schulz Electric has the capability and chooses to perform the evaluation to determine if a defect exists. It is the responsibility of Schulz Electric to inform the purchaser(s), and any affected licensees. "Schulz Electric will complete the specified evaluation of the circumstances within sixty (60) days of discovery of the potential defect. The NRC will be provided a copy of Schulz Electric's evaluation report. "If you have any questions, please feel free to contact me [Charles 'Bill' Eldredge] by phone 203.562.5811, by fax 203.562.1082, or email me at Eldredge@schulzelectric.com." * * * UPDATE FROM CHARLES ELDREDGE TO DONALD NORWOOD AT 0922 ON 9/30/2014 * * * The following is a synopsis of information received via facsimile: FINAL EVALUATION RE: EVENT # 50428 Customer: First Energy / Davis Besse. Parts: 3 AC Motors - 1) 400 HP, 1) 450 HP, 1) 600 HP. All located at First Energy / Davis Besse. Description of Defect/Nonconformance: Schulz Electric identified that the methodology for determining acceleration for the subject motors was incorrect. When the acceleration times were calculated using the correct methodology, it was determined that the three motors will not meet the acceleration requirements for 70% voltage as required by the purchase order. Corrective Action: The customer has been informed of the nonconformance and Schulz has worked with the customer to generate performance curves at various voltage levels and pump head requirements. Other Plants Affected: None. Notified R1DO (Krohn), R2DO (Widmann), R3DO (McCraw), R4DO (Whitten) and Part 21 Reactors Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-09-05
50427 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-09-04 19:05 | 2014-09-05 00:27 | 2014-10-23 | CONTROL ROOM EMERGENCY VENTILATION (CREV) SYSTEM INOPERABLE "On September 04, 2014, at 1905 hours [CDT], the Control Room Emergency Ventilation (CREV) system was declared inoperable due to the Air Handling Unit (AHU) tripping upon restoration of Control Room Ventilation following testing of Reactor Building Ventilation instrumentation. Troubleshooting is in progress at this time. "Technical Specification 3.7.4, Condition A, was entered which requires the CREV system to be restored to an operable status in seven (7) days. Additionally, Technical Specification 3.7.5, Condition A, was entered which requires CREV AC to be restored to an operable status in 30 days. "This notification is being made in accordance with 10CFR50.72(b)(3)(v)(D), '[any] event or condition that could have prevented fulfillment of a safety function,' because the CREV system is a single train system required to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY MARK BRIDGES TO JOHN SHOEMAKER AT 1721 EDT ON 10/23/2014 * * * "The purpose of this notification is to retract the ENS notification made on September 4, 2014 (ENS 50427). Upon further investigation it was verified that the function of Control Room Emergency Ventilation System was not affected as discussed in Chapters 6 and 15 of the Updated Final Safety Analysis Report. Therefore, the threshold for reporting the issue as an event or condition that could have prevented the fulfillment of a safety function was not met (NUREG 1022 Revision 3 - Event Report Guidelines Section 3.2.7)." The licensee has notified the NRC Resident Inspector and applicable State authorities. Notified R3DO (Pelke) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-09-05
50426 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-09-04 18:37 | 2014-09-04 19:49 | 2014-10-30 | DISCOVERY OF UNPROTECTED VITAL AREA Discovered vulnerability in a safeguard system that could allow access to a vital area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. The licensee has notified the Minnesota State Duty Officer and the Sheriff Departments for Wright and Sherburne Counties. * * * RETRACTION FROM MICHAEL BURTON TO HOWIE CROUCH AT 1841 EDT ON 10/30/14 * * * After further evaluation, the licensee determined that a vulnerability did not exist and is retracting this event. The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-09-04
50425 | -1 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-09-04 11:00 | 2014-09-04 16:49 | 2014-09-18 | UNANALYZED CONDITION RELATED TO POTENTIAL MATERIAL TRANSFER CART TIPPING "I. EVENT DESCRIPTION: On September 4, 2014 at approximately 1100 [EDT], a Nuclear Criticality Safety (NCS) engineer identified a safety concern. While working to consolidate information in the safety basis for the safe geometry storage and transport carts, it was determined that an unanalyzed condition existed that did not meet the performance requirements of 10 CFR 70.61. Tipping or impact of a cart during transport had not been considered as a credible upset condition. "II. EVALUATION OF THE EVENT: At B&W's NOG-L [Nuclear Operations Group] facilities, safe geometry storage and transport carts are used to transfer uranium bearing materials between radiologically controlled areas. The carts are typically used to transfer scrap and waste materials in favorable volumes less than or equal to 2.5 liter containers to the Drum Count Area for 235U assay. Because the 235U content of such containers is not known until they have been assayed, they are referred to as 'unknowns' and are subject to a net weight limit. These containers are limited to a maximum of 7,000 grams net weight (approximately 15 pounds) of uranium bearing material in any form. "There are forty storage locations on a cart, twenty per side. The locations on each side are arranged in an array of 4 columns, each column contains 5 storage locations. During transport each column of storage locations is protected by closure of a door. The four column doors on each side of the cart are secured by a common locked bar. "The NCS evaluation of the safe geometry storage and transport carts did not address possible tipping during transit. Although unlikely, it is believed at this point the event is credible. If a cart were to tip, no controls were identified to retain the containers on the cart. Although the doors on the cart are secured by a robust locking bar, this action is taken for security purposes and is not credited as an IROFS [Item Relied On For Safety]. Assuming the containers on the cart were fully loaded (7 kg net weight) with a U-metal water mixture at optimum H/X and the cart tipped over, and more than three containers fell out of the cart, a configuration could result that would exceed the keff safety limit of 0.95 in NRC License SNM-42 for a single contingency. "The requirement of 10 CFR 70.61 (d) states in part: '... the risk of nuclear criticality accidents must be limited by assuring that under normal and credible abnormal conditions, all nuclear processes are subcritical, including use of an approved margin of subcriticality for safety.' "Therefore the performance requirement of 10 CFR 70.61 (d) would not be maintained during this credible abnormal condition. "The as-found condition had no actual safety significance. There was no immediate risk or threat to the safety of the workers, the public, or the environment as a result of this condition. The safe geometry storage and transport carts did not contain any uranium bearing materials. There was no actual tipping event. The carts were immediately removed from service. "Ill. NOTIFICATION REQUIREMENTS: B&W is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1)--Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. "IV. STATUS OF CORRECTIVE ACTIONS: The carts have been removed from service. An investigation of the root causes of this condition is ongoing. Corrective actions will be determined as a result of the investigation." The licensee notified the NRC Resident Inspector and will be notifying the facility NMSS Project Manager (Baker). * * * RETRACTION FROM KENNY KIRBY TO HOWIE CROUCH AT 1634 EDT ON 9/18/14 * * * "The initially identified abnormal condition was not analyzed in the Integrated Safety Analysis. A conservative approach was taken in evaluating the condition in order to ensure compliance with the specified time period established in the regulations for reporting. Further analysis has determined the condition is not credible. Although unlikely, should more than three containers fall from the cart, it is not credible that a configuration could occur that would exceed the keff limit of 0.95 in NRC License SNM-42 for a single contingency. The performance requirements of 10 CFR 70.61 would be maintained. Following the guidance of FCSS ISG-12, Rev 0, '10 CFR Part 70, Appendix A- Reportable Safety Events', B&W is correcting Event Notification #50425 in accordance with 10 CFR 70.74(a)(4) and withdrawing the 10 CFR 70, Appendix A, (b)(1) notification." The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes), NMSS EO (Gonzalez) and Fuels OUO Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2014-09-12
50424 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-09-04 08:43 | 2014-09-04 09:50 | 2014-09-04 | 1R-50 SHIELD BUILDING HIGH RANGE VENT GAS RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0843 CDT on September 4th, 2014, 1R-50 High Range Shield Building Vent Gas Monitor was removed from service for planned maintenance. This monitor provides indication of release of gaseous radioactivity to the environment. There is not a compensatory measure that will allow timely classification of two Emergency Action Levels when out of service: General Emergency Event RG1.1 and Site Area Emergency Event RS1.1. This results in a loss of emergency assessment Capability while 1R-50 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 Shield Building ventilation stack is also monitored by radiation monitor 1R-22 that is used for the same purpose in Alert or Unusual Event Emergency classifications. 1R-22 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 1R-50 prior to its removal from service. The maintenance is scheduled for ten hours or will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-09-04
50423 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-08-20 | 2014-09-03 15:16 | 2014-09-04 | AGREEMENT STATE REPORT - LOST FLOOD SOURCE "A Co-57, 4 mCi flood source was reported missing. The source was first noticed missing two weeks ago. It was possible source was shipped back to vendor with another flood source that was mailed recently. They are currently checking with their vendor Eckert & Ziegler Isotope Products, Inc. to verify their shipment. Jacksonville inspection office contacted to perform site inspection." Florida incident: FL14-075 * * *UPDATE PROVIDED BY KELLIE ANDERSON TO JEFF ROTTON AT 1313 EDT ON 09/04/2014 * * * The following is a summary of information provided by the State of Florida via email: The State of Florida was notified today by the [licensee's] RSO, who made the initial report, that the licensee had found the source and it had been accidently mailed back to their supplier along with another source. The State of Florida will still send an investigator to look into the matter and provide recommendations, otherwise the State of Florida is considering this incident closed. Notified R1DO (Ferdas), ILTAB (Wray) and FSME Events Resource group via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-09-11
50422 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-06-06 | 2014-09-03 11:25 | 2014-11-17 | AGREEMENT STATE REPORT - ELEVEN MISSING PO-210 SOURCES The following was received from the Commonwealth of Massachusetts via email: "On 9/3/14, Agency [Commonwealth of Massachusetts] determined, through inventory reconciliation, the general licensee is missing eleven Model 2021 Nuclecel Ionizers each originally containing up to 10 mCi Po-210. Agency further determined that six devices contained material with calculated current activity well below the immediate report level (0.1 mCi for Po-210), three devices contained material with calculated current activity of 0.12 mCi, and two devices contained material with calculated current activity of 0.77 mCi. The Agency did not receive specific lost source notification from the licensee. No other details from the licensee at this time. The devices are designed to be rugged, require no special handling procedures, and intended for use in neutralization of static charge in environmental tests. The current exposure rate for each device is expected to be considerably less than the initial maximum exposure rate of less than 0.2 mR/hr. "Agency inspector to conduct site visit. "Agency considers this event to still be OPEN and Agency review is ONGOING" The devices were manufactured by NRD Inc., Model P-2021, three were manufactured 4/13/12, and two were manufactured 4/10/13. The serial numbers are A2JB491, A2JB496, A2JB500, A2JM622, and A2JM624. The sources were Po-210 10 mCi each. * * * UPDATE ON 10/7/14 AT 1438 EDT FROM ANTHONY CARPENITO TO DONG PARK * * * The following was received from the Commonwealth of Massachusetts via email: "Agency initiated inspection 9/3/14. Licensee written report received 9/22/14. Two devices were subsequently found by licensee during search within facility. Agency [Commonwealth of Massachusetts] determined that all nine devices still missing will each individually have, on 10/17/14, calculated activities below the immediate report level (0.1 mCi for Po-210). Notice of Violation to be issued related to loss of control of licensed material and not immediately reporting missing licensed material. Causes and corrective actions included in this update. Agency considers this event to be CLOSED." Notified R1DO (Bower), ILTAB and FSME Events Resource via email. * * * UPDATE ON 11/17/14 AT 1633 EST FROM ANTHONY CARPENITO TO DONG PARK * * * The following was received from the Commonwealth of Massachusetts via email: "Notice of Violation [NOV] issued 10/16/14. In response to NOV, licensee included report that another of the missing devices was found. Additional licensee corrective actions not previously reported included retraining of employees and implementing a monthly device inventory check. Licensee to also systematically phase out its use of said device. Agency [Commonwealth of Massachusetts] still considers this event to be CLOSED. "On 10/26/14, the licensee reported another device previously reported missing was found: SN A2JB491, NRD Model P-2021, 10mCi, 4/13/12 Manufactured and Assay Date." Notified R1DO (Jackson), ILTAB and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-09-11
50421 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2014-08-27 | 2014-09-02 16:40 | 2014-09-02 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED AT CONSTRUCTION SITE "Our [Froehling & Robertson] technician was using the gauge to test compaction of soils placed for wall backfill. [The technician] placed the nuclear gauge on the sloped hill next to the backfill area and stepped away from the gauge to check on the concrete pour that was happening at the top of the hill. As she was walking away, the backfill crew started using the two drum walk-behind roller. The roller was in vibratory mode and, as it approached the area near the nuclear gauge, the gauge slid down the slope into the path of the roller. The gauge was hit with the roller on the end opposite the rod, damaging the casing and the instrument panel. [The technician] and the roller operator moved the gauge to assess the damage and, when they realized it was damaged, [the technician] cordoned off the area. "Exposure Readings and Visual Damage Assessment: "[The RSO] arrived on-site with the survey meter (CD V-700 calibrated 5/9/2014) and checked the area for radiation exposure. No significant readings were recorded (less than 0.1 mrem/hr 5 feet from the gauge). The source rod was fully retracted into the casing and did not appear to be damaged other than the handle was twisted. The gauge appeared to be intact in the vicinity of the Americium source. The gauge was packed and secured in its storage case and transported to Northeast Technical Services for a leak test and damage evaluation. "Assessment of Cause: "[The RSO] interviewed the client and [technician] to try to assess a cause for the incident. The client had asked [the technician] to go check on the concrete pour before performing another density test and, instead of properly securing the gauge in the truck or keeping it within arm's reach, [the technician] left the gauge unattended while she walked up the slope. In talking with [the technician], she was aware of the proper procedures for securing the gauge and maintaining control of the gauge but failed to do so in this case. "Corrective Measures: "As this is a first offense for [the technician], she will be issued a written warning stating that if involved in another incident like this, she will be terminated. Additionally, she will be asked to take another refresher course on using and transporting nuclear density gauges. [The RSO] will also be holding a safety meeting with all technicians to review this incident and review the F&R Nuclear Gauge Safety material regarding maintaining control of gauges." Sources: 0.37 GBq Cs-137 and 1.48 GBq Am-241:Be Make/Model: Troxler 3400 Serial #: 23898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2014-09-10
50420 | -1 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2014-08-29 16:00 | 2014-08-30 16:00 | 2014-09-04 | UNPLANNED CONTAMINATION INCIDENT IN THE RESEARCH REACTOR FACILITY At approximately 1600 EDT on 08/29/14, a 60 nanocurie Pu-239 wafer source dropped from its holder during change out following neutron irradiation in building 235 (Research Reactor Test Facility). The wafer struck the floor and cleaved in half. Radiation surveys confirmed alpha contamination of approximately 200 counts per minute. The area was decontaminated, resurveyed and released. The licensee will notify their NMSS PM (Naquin) and the State of Maryland Department of Environment as a courtesy. * * * UPDATE AT 1840 EDT ON 08/30/14 FROM TOM O'BRIEN TO STEVE SANDIN VIA EMAIL * * * "Follow-up to the dropped source (Pu-239 RS# 87-0039(4) on 8/29/14)) at NG-6MAll personnel involved have been evaluated, with the exception of two nasal swipes, on two separate individuals not directly involved with the incident, but near the location, reporting about 0.17 dpm alpha each, all surveys find the personnel to be clear of contamination. It is believed the two 0.17 dpm nasal swipes are statistically not different than zero, follow-up measurements will be done to confirm this. Even if we assume them to be positive, the resulting estimated dose from these measurements would be on the order of 10 mrem. "The NG-6M instrument area has been surveyed and cleared for normal use. All contamination swipe surveys of the floor, tools, furniture and equipment potentially involved in this incident have been found to be clean. With the exception of one alpha instrument survey, all surveys with alpha and beta/gamma survey instruments have found levels less than or equal to background. The one survey where positive indication was found was performed at the source drop location, directly underneath where the source fell. This survey was done after the source was retrieve. Initially measured about 200 cpm alpha contamination and very localized, the spot was carefully deconned and subsequent surveys found to be less than or equal to background. All swipes of this spot were also found to be clean. "The source has been safely retrieved, secured and is locked in our safe in A134. No removable contamination was found on the source containers or during retrieval of the source. Gamma spectrum measurements of the retrieved source, detecting the Am-241 trace nuclide, and correlating this activity by know nuclide ratios find that the Pu-239 activity of the source is within good agreement of the original activity of the source (2190 Bq). While this confirmation has many errors incorporated into it, it is the best measurement we can make at this time, that along with the negative findings of any removable contamination to speak of, and visual inspections of the source, I conclude that to the best of my knowledge, the source material is intact on the broken source substrate pieces, inside the source container. Careful follow-up measurements would need to be performed to confirm this for certain, but based on the info I have at present this is my conclusion." Notified R1DO (Mangan), NMSS EO (Stablein) and NMSS PM (Naquin). * * *RETRACTION PROVIDED FROM TOM O'BRIEN TO JEFF ROTTON AT 1425 EDT ON 09/04/2014 * * * "Upon detailed review of the incident data NIST is requesting retraction of this notification on the basis that 70.50 (b)(1)(i) and (ii) are not applicable to this event and therefore no 24 hour (or other notification) was required. Access to the contaminated area was restricted for less than 24 hours. Additionally, at the time of initial reporting on 8/30/2014, the most conservative annual limit on intake (ALI) was used as the chemical composition was not yet known. As of today, 9/3/2014, we have confirmed that the radioactive material is in the form of PuO2. This additional information indicates that the involved quantity of radioactive material was less than five times the lowest ALI for Pu-239. "Since the initial report of 8/30/2014, there has been no other contamination detected. The nasal-swab measurements were analyzed for a longer time period and have been determined to be less than the minimum detectable activity. "NIST is evaluating the incident for lessons learned and extent of conditions and will advise [NRC] Region I and our [NRC] Project Manager of the outcome. "Licensee also requested that the first sentence of the [original] Event Text be corrected as indicated below as the source was not subjected to neutron irradiation. 'At approximately 1600 EDT on 08/29/14, a 60 nanocurie Pu-239 wafer source (that was going to be used to calibrate an instrument detector) dropped from its holder during transfer in building 235 (Research Reactor Test Facility).'" Notified R1DO (Ferdas), NMSS EO (Smith) and NMSS PM (Naquin). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 70.50(b)(1) |  |  |  | 0 | 2014-08-30
50419 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-08-28 09:30 | 2014-08-29 11:33 | 2014-08-29 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received via facsimile: "At approximately 0950 MST on August 28, 2014, the Agency [Arizona Radiation Regulatory Agency] was informed that the licensee had a Troxler Model 3430, portable moisture/density gauge damaged at a construction site. The damage occurred at approximately 0930 MST on August 28, 2014. The gauge was in use and was run over by construction equipment. The sealed sources were not damaged and were intact. The damaged gauge was leak tested and will be returned to Troxler for repairs. The Troxler gauge, serial number 35809, contains 8 mCi of Cesium-137 and 40 mCi of Am:Be-241. "The Agency continues to investigate the event. The Governor's Office and US NRC are being notified of this event." Arizona First Notice #: 14-021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-09-08
50418 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-08-29 14:57 | 2014-08-29 16:23 | 2014-08-29 | NOTIFICATION TO STATE OF VIRGINIA REQUIRED BY SITE DISCHARGE PERMIT "On 08/29/2014 at 1457 hours [EDT], Surry Power Station notified the State of Virginia Department of Environmental Quality (DEQ) that two of the three turbine building sumps, required to be sampled by the discharge permit VA00004090, indicated an out of specification condition for oil and grease parameters. The laboratory supervisor reviewed the analysis and found no discrepancies. Sample methods and sample locations were reviewed and were unchanged from previous samples. A review of the operation of the sump oil skimmers indicated that they have been operating properly. In addition, there have been no oil spills or maintenance that would cause elevated readings in the sumps. "Backup samples of both sumps were obtained on 08/27/14 and 08/28/14. The results of the backup samples were received on 08/29/2014 and all samples indicated a less than the detectable levels. "Based upon an initial review of the issue, the results of the backup samples, and at least 5-year history of less than detectable oil and grease levels in the sump, the original samples for the sumps are considered anomalous. The results, however, are being reported in accordance with the permit requirements. This report is being issued in accordance with 10 CFR 50.72(b)(2)(xi), any event or situation related to the protection of the environment for which notification to other government agencies has been made. "The Surry NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-29
50417 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-08-29 09:32 | 2014-08-29 16:15 | 2014-08-29 | DIGITAL RADIATION MONITORING SYSTEM OPERATING INTERMITTENTLY "At 0932 EDT on August 29, 2014, Beaver Valley Power Station (BVPS) Unit 2 determined that the Digital Radiation Monitoring System (DRMS) was operating intermittently. This resulted in an intermittent loss of radiation monitor capability to alarm and indicate in the control room. BVPS Unit 2 DRMS was declared non-functional. Repair efforts were initiated and compensatory measures were established. "At 1556 EDT on August 29, 2014, following initial investigation and repairs, BVPS Unit 2 DRMS was declared functional. "Since the BVPS Unit 2 DRMS was non-functional, this event resulted in a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." The cause was attributed to an automatic reboot of the computer based on lack of disk space. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-29
50416 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-08-29 14:04 | 2014-08-29 15:52 | 2014-10-31 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM NATHAN BIBUS TO HOWIE CROUCH AT 1610 EDT ON 10/31/14 * * * Compensatory measures are in place for the subject areas. The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa) and 73.71 Group (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-29
50415 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2014-08-29 15:01 | 2014-08-29 15:06 | 2014-08-29 | UNACCOUNTED FOR SPECIAL NUCLEAR MATERIAL "This is a non-emergency Event Notification being made in accordance with 10CFR74.11 for a loss of special nuclear material (SNM). In accordance with Entergy's procedure for Special Nuclear Materials Program (EN-NF-104), this notification relates to information considered commercial or financial within the meaning of 10CFR9.17(a)(4) as correspondence and reports which contain information concerning the licensee's material control and accounting program for special nuclear material not otherwise designated as Safeguards Information or classified as National Security Information or Restricted Data and is therefore requested to be withheld from public disclosure in accordance with 10CFR2.390(d)(1). "During the physical inventory of SNM at IPEC in August, 2014, an irradiated Moveable In-core Detector (MID) could not be accounted for. The MID contained 0.0041 grams of U-235 prior to irradiation when it was initially installed in the plant, and thus is required to be tracked as SNM. A portion of the MID drive cabling, approximately the same size as the MID, was stored in a container and appears to have been incorrectly tracked as the MID following its removal from operation. The condition is being recorded in the IPEC corrective action program (CAP) and will be evaluated to identify the cause and corrective actions to prevent recurrence." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 74.11(a) |  |  |  | 1 | 2014-09-08
50414 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-08-29 | 2014-08-29 14:51 | 2014-08-29 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received via facsimile: "On August 29, 2014, the licensee made a telephone notification of a medical event which occurred during a skin treatment using a Nucletron microSelecton 106.990 HDR. The Radiation Safety Officer indicated that a decay corrected value for the source activity was used during data entry for the treatment plan. The licensee discovered, after the administration of the treatment fraction, that the software also corrected for decay in determining the exposure time for the fraction. The extra decay correction resulted in a dose approximately twice the prescribed fraction dose of 600 cGy. The licensee has informed the referring physician and held a staff meeting to discuss the circumstances. Any future treatment fractions for the patient will be reviewed and the licensee will review its nine previous skin treatment procedures to determine if additional medical events may have occurred. Additional information, including the administered dose, will be provided by the licensee in its written report." Event Report ID No.:VA-2014-005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-09-08
50413 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-08-28 12:27 | 2014-08-28 18:26 | 2014-08-28 | AUXILIARY ELECTRIC EQUIPMENT ROOM HVAC INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), 'Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident.' While the 'B' train of Auxiliary Electric Equipment Room HVAC was inoperable and out of service for emergent repairs due to an oil leak, the 'A' train of Auxiliary Electric Equipment Room HVAC became inoperable due to a failure of the liquid line solenoid valve. The Main Control Room Envelope consists of the Main Control Room and the Auxiliary Electric Equipment Room. Both the Control Room HVAC and the Auxiliary Electric Equipment Room HVAC systems are required to be operable in the current mode. "This is a loss of safety function for a system that is intended to mitigate the consequences of an accident and is discussed in Chapter 6 of the UFSAR and is Tech Spec required and is safety related. Also, the system, structure, or component (SSC) is inoperable in a required mode in the Tech Spec applicability and there is no redundant equipment in the same system that is operable. "The required actions of Tech Spec 3.7.5 were entered for this event. Online Risk remains Green. The station is currently pursuing repairs to both trains." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-08-28
50412 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-08-28 12:00 | 2014-08-28 15:30 | 2014-08-28 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE STOLEN FROM PICKUP TRUCK A Georgia Department of Transportation crew stopped for lunch at 1200 EDT on 08/28/14 at a Sam's Club in McDonough, GA. A Troxler Model 3430, S/N 31643, containing two sources: 10 mCi of Cs-137 and 40 mCi of Am241/Be, was stolen from the unattended vehicle. The Troxler was not properly secured as required. The State of Georgia is conducting an investigation into the incident. The Henry County Police Department is investigating. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-09-05
50411 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-08-28 09:00 | 2014-08-28 10:09 | 2014-08-28 | BOTH DISCHARGE CANAL RADIATION MONITORS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "Planned preventive maintenance will render both divisions of discharge canal radiation monitors non-functional. As a result, this represents a loss of emergency assessment capability and is reportable under 10 CFR 50.72(b)(3)(xiii). The planned maintenance is expected to last two hours. During this time, alternate plant parameters will be monitored and sampling performed if needed. The health and safety of the public remains protected as the plant is operating in a normal condition. "The NRC Resident Inspector was notified prior to removing the discharge canal radiation monitors from service." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-28
50410 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-08-27 05:30 | 2014-08-27 13:35 | 2014-08-27 | 26 OF 40 EP SIRENS COULD NOT BE VERIFIED FUNCTIONAL "At 0645 CDT on August 27, 2014, Exelon was notified that during the daily test at 0530 CDT of the offsite sirens, the vendor received an alarm on Clinton Power Station siren communications. This Emergency Preparedness (EP) siren communications issue results in 26 of the 40 EP sirens not being verified as functional, which affects 84.4% of the EPZ population. The loss of communications represents more than 25% of the EPZ population for greater than 1 hour and is therefore reportable under 10 CFR 50.72(b)(3)(xiii). "The cause of issue has been isolated to a microwave link at Clinton Power Station that communicates via radio frequency to each siren. The siren vendor is currently investigating to repair the issue. "The DeWitt County Emergency Manager has been notified. DeWitt County has implemented the Emergency Message System through 'Code Red' notification in lieu of siren communications. "The NRC Senior Resident has been notified." * * * UPDATE FROM RICH CHAMPLEY TO CHARLES TEAL AT 1755 EDT ON 8/27/14 * * * "The DeWitt County Emergency Manager has been notified. DeWitt County has implemented the backup means of notification called 'Route Alerting' in lieu of siren communications. Route Alerting consists of vehicles and public address systems. "At 1400 CDT only 2 sirens remain not fully functional. These 2 sirens represent 0.7% of EPZ population. Work continues to restore these 2 sirens. "The NRC Senior Resident has been informed." Notified R3DO (Stone). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-27
50409 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-08-25 15:30 | 2014-08-27 13:44 | 2014-08-27 | AGREEMENT STATE REPORT - AUTOMOTIVE ACCIDENT INVOLVING AN IR-192 CAMERA The following was received from the State of Arizona via email: "At approximately 9:00 AM [MDT] on August 26, 2014, the Agency [State of Arizona] was informed that the licensee had a company truck involved in a rollover accident. The truck was transporting an Iridium-192 gamma camera used for industrial radiography. The camera was not damaged in the accident and was transported by the licensee back to their Phoenix office. The gamma camera was leak tested. The accident occurred at approximately 3:30 PM on August 25, 2014. The Delta 880, Serial Number D9783, radiographic camera contains approximately 100 Ci of Ir-192. "The Agency continues to investigate the event. "The Governor's Office and U.S. NRC are being notified of this event. " Arizona First Notice: 14-020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-09-04
50408 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-08-25 09:00 | 2014-08-27 12:23 | 2014-08-27 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED AT CONSTRUCTION SITE The following from the State of Arizona via email: "At approximately 9:00 AM [MDT] on August 26, 2014, the Agency [State of Arizona] was informed that the licensee had a Troxler Model 3430 portable moisture/density gauge damaged at a construction site. The damage occurred at approximately 9:00 AM on August 25, 2014. The gauge was in use and was run over by construction equipment. The sealed sources were not damaged and were intact. The damaged gauge was leaked tested and will be returned to Troxler for repairs. The gauge, serial number 29852, contains 10 mCi of Cesium-137 and 40 mCi of Am:Be-241. "The Agency continues to investigate the event. "The Governor's Office and U.S. NRC are being notified of this event." Arizona First Notice: 14-019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-09-04
50407 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-08-27 08:05 | 2014-08-27 12:24 | 2014-08-27 | LOSS OF COMMUNICATIONS DUE TO POWER SUPPLY FAILURE "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a loss of communications capability. On August 27, 2014 at 0805 hours CDT the internal phone system, Emergency Notification System (ENS), and Emergency Response Data System (ERDS) became nonfunctional because of a power supply failure. "The ERDS has been restored to service and work is currently in progress to restore the internal phone system and ENS. It has not been determined at the time of this notification as to when the internal phones system and ENS will be restored to a fully functional status." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-27
50406 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-08-27 08:39 | 2014-08-27 09:56 | 2014-08-27 | PROCESS RADIATION MONITORS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "Loss of assessment capability due to preplanned maintenance affecting radiation monitors. Normal ventilation and 'HI' range process radiation monitors (3HVR & RE10A/10B) will be out of service. This condition is reportable per 10 CFR 50.72(b)(3)(xiii). The equipment is expected to be restored within 9 hours." The NRC Resident Inspector has been notified. The licensee will notify the state and local governments. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-27
50405 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-08-27 02:48 | 2014-08-27 09:13 | 2014-08-27 | SAFETY INJECTION PUMP FAILED TO START "At 0243 [EDT on 8/27/14] the '11' Safety Injection pump breaker was tagged for scheduled maintenance on the 11SJ34, and the control room entered TSAS 3.5.2.b, action 'A' - a 72 hr LCO. The control room recognized the time line for the repair would require filling the '14' SI Accumulator prior to work completion. The CRS [Control Room Supervisor] decided to perform the '14' SI Accumulator makeup prior to commencing work on the 11SJ34, and directed the NCOs [Nuclear Control Operators] to start the '12' SI pump and make up to the '14' SI Accumulator in accordance with procedure SI.OP-SO.SJ-0002. At 0248, TSAS 3.0.3 was entered when the '12' Safety Injection pump failed to start on demand. At 0301, the '11' Safety Injection pump was restored to service and declared operable and TSAS 3.0.3 was exited. TSAS 3.5.2.b, action 'A' remains in effect due to the '12' Safety Injection pump being inoperable. "This event is being reported under the requirements of 10 CFR 50.72(b)(3)(v) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to perform mitigation of the consequences of an accident.''' "Licensee has notified the NRC Resident Inspector. No one was injured as a result of the failure of the '12' Safety Injection pump breaker." The licensee will notify the Lower Alloways Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-08-27
50404 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-08-26 17:30 | 2014-08-26 21:24 | 2014-08-26 | TURBINE GENERATOR NEUTRAL OVERVOLTAGE CAUSES A REACTOR SCRAM "At 1730 CDT on August 26, 2014, Browns Ferry Unit 1 experienced a turbine trip resulting in an automatic reactor scram. The cause of the turbine trip was a control valve fast closure signal that was generated by a turbine trip on generator neutral over voltage signal. The Main Steam Isolation Valves (MSIVs) remained open with the main turbine bypass valves controlling reactor pressure. The Reactor Feedwater Pumps are in service to control reactor water level. "Primary Containment Isolation Systems (PCIS) Groups 2, 3, 6, and 8 isolation signals were received. Upon receipt of these signals, all required components actuated as required with the exception of Standby Gas Treatment (SBGT) train A, which is under a clearance for planned maintenance. Neither High Pressure Coolant Injection (HPCI) nor Reactor Core Isolation Cooling (RCIC) initiation signals were received. Initially, three Main Steam Relief Valves (MSRVs) opened to control the pressure surge and subsequently reclosed. "This event requires a 4 hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including reactor scram or reactor trip, and (2) General containment Isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).' "The NRC Resident Inspector has been notified. "Service Request 926468 was initiated in the Corrective Action Program." The plant is in its normal shutdown electrical lineup. The licensee is investigating the cause of the generator neutral overvoltage signal. There was no impact on units 2 and 3. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-08-26
50403 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2014-06-02 18:30 | 2014-08-26 18:29 | 2014-08-26 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following was received from the State of Utah via email: "[The licensee was unable] to retract and secure a radiographic source to its fully shielded position. [The] licensee's RSO was able to disassemble the locking mechanism and retract the source. The exposure device was then locked and the source verified to be in the fully shielded position." There were no overexposures as a result of this event. Event Report ID No.: UT140003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2014-09-03
50402 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-08-21 | 2014-08-26 17:59 | 2014-08-26 | AGREEMENT STATE REPORT - GAUGE FOUND AT RECYCLING FACILITY The following was received from the State of California via email: "On August 21, 2014, . . . Henkle Aerospace contacted . . . RHB to report that one of their generally licensed fixed gauges (NDC, Model 103, S/N 4331 containing Am-241) had been found at a recycling facility. The recycling facility had contacted the manufacturer of the gauge (NDC) and it was returned to NDC. NDC contacted Henkel to notify them of the gauge was found at the recycling center. The source was intact and NDC has performed a leak test which indicated no contamination. "On 08/26/14, . . . Henkel called RHB and provided the following information: The gauge contained 150 mCi of Am-241 (as of late 90s) and it was acquired by Henkle in 2006. This gauge was replaced by a licensed vendor in February 2010, and was set aside to be transferred to the vendor. Eventually, they lost track of the gauge, and it ended up at the recycling center with the rest of the metal Henkel had shipped to the scrap yard. "Corrective actions by Henkle: After this incident they have revised their policies and procedures to keep track of the two gauges they currently possess (Sr-90 containing 250 mCi each, GL units licensed by Mahlo). "Note: As of now, RHB does not have the information on current activity of the Am-241 source in the gauge." California 5010 #: 082114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-09-03
50401 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-08-26 09:48 | 2014-08-26 16:25 | 2014-08-26 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RUN OVER BY A SKID-STEER The following was received from the State of Colorado via email: "At 0948 MDT on the morning of August 26, 2014, [the State of Colorado] was notified by the ARSO at Terracon, Inc (Colorado License # 664-02) that a Troxler 3430 moisture/density gauge had been run over by a skid-steer at a temporary job site. The source was locked in the shielded position when the gauge was hit. Surveys taken at the site confirmed that the source remained shielded. "The gauge was placed in its transport case (Transport index confirmed) and taken to Instrotek for leak testing and analysis. Final results should be available within a week and initial results show no evidence of leakage. "The investigation is still ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-09-03
50400 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-08-26 07:59 | 2014-08-26 11:54 | 2014-08-26 | UNIT 2 HIGH RANGE STACK RADIATION MONITOR TAKEN OUT OF SERVICE FOR PRE-PLANNED MAINTENANCE Millstone removed their unit 2 high range site radiation monitor, RM-8168, from service for pre-planned maintenance. RM-8168 was restored to service at 1012 EDT on 8/26/14. The licensee notified the NRC Resident Inspector, the State of Connecticut, and the town of Waterford. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-26
50399 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-08-25 | 2014-08-25 17:21 | 2014-08-25 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE OF RADIOGRAPHER The following was received from the State of Texas via email: "On August 25, 2014, the Agency [State of Texas] received notice that a dosimetry badge for a radiographer trainee had come back with an exposure of 8.6 roentgen for the period of July 5 to August 4, 2014. The individual has stated that he dropped his badge during work and picked it up later. The trainer working with the trainee received 210mR for the same period. The trainee worked 10 days with the company in all. Currently awaiting written statements from trainee and trainer and further reports from dosimetry provider. Additional information will be provided in accordance with SA-300." Texas Incident #: I-9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-09-02
50398 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2014-08-25 08:12 | 2014-08-25 09:51 | 2014-08-25 | UNUSUAL EVENT DECLARED DUE FIRE ALARM IN REACTOR BUILDING "At 0757 CDT on 8/25/14, LaSalle Main Control Room received a fire alarm from the Unit 2 Reactor Building 807 foot elevation. Operators dispatched and confirmed no fire at 0817 CDT (20 min). At 0812 CDT (15 min) an unusual event (HU3) was declared due to not having verified no fire within 15 minutes of the alarm. No fire was confirmed and plans are in progress to terminate event." The NRC Resident Inspector has been notified. The licensee notified the Illinois Emergency Management Agency. Notified DHS SWO, FEMA Operation Center, FEMA National Watch Center, NICC, Nuclear SSA via email. * * * UPDATE PROVIDED BY ALAN MCLAUGHLIN TO JEFF ROTTON AT 1046 EDT * * * "At 0915 CDT on 8/25/2014, the LaSalle Shift Emergency Director terminated the Unusual Event (HU3) which had been declared at 0812 CDT. No fire present was verified at 0817 CDT and required hourly firewatch is in place. Maintenance Department has begun efforts to locate and replace faulted detector or other degraded component." The licensee notified the NRC Resident Inspector and the Illinois Emergency Management Agency. Notified R3DO(Passehl), NRREO (Hiland), IRD (Gott). Notified DHS SWO, FEMA Operation Center, FEMA National Watch Center, NICC, Nuclear SSA via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-08-25
50397 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-25 05:00 | 2014-08-25 04:10 | 2014-08-29 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "On 8/25/2014, planned preventive maintenance activities are being performed on the Braidwood Generating Station Technical Support Center (TSC) Ventilation System. The work will be completed within approximately 42 hours. This activity includes preventive maintenance on the TSC condensing unit which affects the TSC ventilation. During the planned maintenance, the TSC condensing unit will be rendered non-functional. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff as necessary. This planned maintenance will not impact the emergency filtration capability of the TSC. "This event is reportable per 10CFR50.72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The planned maintenance will not be able to restore the TSC condensing unit to service within the facility activation time specified in the emergency plan (1 hour) in the event of an accident. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1526 EDT ON 08/29/14 FROM ANNE MATHEWS TO S. SANDIN * * * "Braidwood Generating Station TSC ventilation was restored to available status at 1200 CDT on August 29th, 2014. "The previously reported system preventative maintenance has been completed." The licensee informed the NRC Resident Inspector. Notified R3DO (Stone). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-25
50396 | -1 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-08-24 | 2014-08-24 03:23 | 2014-10-01 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO POST ACCIDENT MONITORING INSTRUMENTATION OUT OF SERVICE "At 0039 [CDT] on 8/19/14, Point Beach Nuclear Plant, Unit 2 identified that 2TE-451A and 2TE-451C Cold Leg Temperature RTDs were out of service. Technical Specification 3.3.3, Post Accident Monitoring (PAM) Instrumentation, Action Condition C for one or more functions with two required channels inoperable was entered. Action Condition C requires one channel to be restored to OPERABLE status within 7 days. If completion time in Action Condition C cannot be met, Action Condition D will be entered, which requires entry into Action Condition E. Action Condition E would require Unit 2 to be in Mode 3 in 6 hours and Mode 4 in 12 hours thereafter. "Unit 2 is being shut down to effect repairs within the 7 day required action completion time for Action Condition C. This event is reportable under 10 CFR 50.72(b)(2)(i), Plant Shutdown Required by Technical Specifications. The Resident Inspector has been informed." * * * RETRACTION FROM ALEX RIVAS TO HOWIE CROUCH AT 2337 EDT ON 10/1/14 * * * "Point Beach is retracting EN# 50396 made on August 24, 2014 at 0323 EDT. Technical Specification 3.3.3. Post-Accident Monitoring (PAM) Instrumentation, Action Condition C for one or more functions with two required channels inoperable was entered. Action Condition C requires one channel to be restored to OPERABLE status within 7 days. The Unit 2 TE-451A and TE-451C Cold Leg Temperature RTDs inoperable condition was corrected and the plant returned to power before expiration of the 7 day period specified in Condition C of Technical Specification 3.3.3. Reference example (3) Failure that was or could have been corrected before shutdown was required, of Section 3.2.1, Plant Shutdown Required by Technical Specifications of NUREG-1022, Rev. 3, Event Report Guidelines 10 CFR 50.72 and 50.73." The licensee has notified the NRC Resident Inspector. Notified R3DO (McCraw). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-08-24
50395 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-08-23 13:00 | 2014-08-23 20:19 | 2014-08-23 | LOSS OF SAFETY FUNCTION "At 13:00 [EDT] on Saturday, August 23, 2014, both trains of the Peach Bottom Atomic Power Station (PBAPS) Emergency Service Water (ESW) System were declared inoperable on Unit 2 and Unit 3, due to a pin-hole, through wall piping leak. In accordance with 10CFR 50.72(b)(3)(v), this event is being reported as an event or condition that could have prevented the fulfillment of the safety function of systems that are needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat and mitigate the consequences of an accident. "At 19:22 [EDT], the station received verbal approval of a Notice of Enforcement Discretion (NOED) request. Simultaneously, the station is preparing an evaluation to support an emergent-relief request. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2014-08-23
50394 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-08-21 | 2014-08-22 16:41 | 2014-08-22 | AGREEMENT STATE REPORT - NUCLEAR GAUGE STUCK OPEN SHUTTER The following was received via email: "On August 21 the Agency [Illinois Emergency Management Agency] received a call from a representative of Clark Dietrich Building Systems (CDBS), Rochelle, IL (reg no 9223802) concerning findings made by their contractor for a generally licensed gauging device at their facility. A Gamma Instruments model GR100 device (s/n 930-706) with a 1000 milliCi Am-241 source was found to have a stuck [open] shutter during maintenance/operability checks being performed by a field engineer from Advanced Gauging Technologies. Repairs were made by the contractor and the gauge subsequently returned to service with no additional issues noted. The field engineer reported that apparently dirt and debris had accumulated from the rolling operations line in such a manner as to prevent proper closure. The caller from CDBS indicated that the gauge had just been last checked by their own staff on July 8, 2014 and no issues with the shutter were detected at that time. He went on to say that he expected a full report from the contractor to be provided in a few days and would forward that information when it became available. "Until the full report from the registrant and the field engineer are received, this matter will remain open. However, based on the information provided at this time no on-site investigation is warranted." No personnel exposures resulted from this event. Illinois Incident Number: IL-14014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-09-01
50393 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-08-22 12:57 | 2014-08-22 14:11 | 2014-08-22 | DISCOVERED A POTENTIAL SECURITY VULNERABILITY A past security vulnerability was identified for which compensatory measures were not employed. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-22
50392 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-08-22 06:45 | 2014-08-22 13:37 | 2014-08-22 | LOSS OF ASSESSMENT CAPABILITY BECAUSE THE METEOROLOGICAL TOWER COMPUTER FAILED "This notification is being made due to a loss of emergency assessment capability in accordance with 10CFR50.72(b)(3)(xiii). At 0645 (CDT), on 8/22/2014, the meteorological tower computer system failed which resulted in a loss of meteorological data to the plant for greater than 1 hour. Proceduralized compensatory measures for dose assessment include use of National Weather Service followed by historically determined default values. Information Technology personnel have reported to the plant for investigation. The NRC Resident Inspector has been informed. The issue has been put into the corrective action process for further evaluation." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-22
50391 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-08-21 09:10 | 2014-08-21 14:31 | 2014-08-21 | CONTAMINATED INJURED INDIVIDUAL "An employee with an injured knee reported to the on-site dispensary this morning. First aid was administered. A whole body survey of the employee and plant clothing was performed; the maximum amount of contamination present was on the employee's work boots, 96,000 dpm/100cm2. All contaminated clothing was removed from the employee. An additional whole body survey of the employee was performed prior to leaving the restricted area; no contamination above background levels was detected. The employee was sent to an offsite medical facility for further evaluation and/or treatment." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-08-21
50390 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2014-08-21 08:50 | 2014-08-21 12:04 | 2014-08-23 | INADVERTENT ACTUATION OF ONE EMERGENCY SIREN "One of the 37 Prompt Notification System sirens surrounding the James A Fitzpatrick (JAF) / Nine Mile Point (NMP) sites spuriously activated at 0850 EDT. The Oswego County Emergency Operations Center notified Nine Mile Point via RECS [Radiological Emergency Communications System] that siren #13 had inadvertently activated. Repair technicians have de-activated and silenced the faulty siren as of 0943 EDT. Siren #13 is currently out of service and the backup method for siren #13 has been verified to be functional. The cause of the inadvertent siren activation is believed to be a lightning strike. "The issue has been entered into the site's Corrective Action Program. "The Oswego County Emergency Management Office issued a News Release identifying the inadvertent actuation of the emergency siren. "The NRC Resident Inspector has been notified. * * * UPDATE AT 1247 EDT ON 8/23/14 FROM MARK GREER TO MARK ABRAMOVITZ * * * "As of 0928 EDT on 08/23/2014, siren #13 has been repaired and returned to service. The NRC Resident Inspector has been notified." Notified the R1DO (McKinley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-21
50389 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-08-21 08:50 | 2014-08-21 12:00 | 2014-08-23 | INADVERTENT ACTUATION OF ONE EMERGENCY SIREN "The purpose of this report is to provide a telephone notification under 10 CFR 50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of one Oswego County emergency notification siren at approximately 0850 [EDT] on 08/21/14. Thunderstorms in the area are believed to have caused a lightning strike and the spurious activation. Siren repair personnel have been dispatched to isolate the siren and begin repair work. The siren has since been silenced. Alternate notification of the public in the area is through Hyperreach. "The Oswego County Emergency Management Office issued a news release identifying the inadvertent actuation of the emergency siren. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1145 EDT ON 8/23/2014 FROM HENK VERWAY TO MARK ABRAMOVITZ * * * "As of 0928 EDT on 08/23/2014, siren #13 has been repaired and returned to service." The licensee notified the NRC Resident Inspector. Notified the R1DO (McKinley). | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-21
50388 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-08-12 | 2014-08-21 10:25 | 2014-08-21 | AGREEMENT STATE REPORT - LEAKING ELECTRON CAPTURE DEVICE SEALED SOURCE The following report was received from the State of Colorado via email: "Event description: The Department [Colorado Department of Public Health and Environment] was notified via e-mail on 8/13/2014, by TestAmerica Laboratories Inc (license # CO 486-03), that a leak test result for a Ni-63 Electron Capture Device [ECD] source had shown counts exceeding 185 Bq. "The licensee has removed the source from service, decontaminated the instrument that the ECD was mounted on and sent the unit, containing the source, to the manufacturer for repair and source replacement. "The email was sent to the department pursuant to Section 4.58 of the Colorado Regulations. "The Department has requested a few additional details regarding specifics of the source (serial Number, manufacturer, etc.) at this time and will populate the NMED database as soon as they are received." Colorado Event Report ID No.: CO14-I14-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-08-29
50387 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-21 02:59 | 2014-08-21 04:58 | 2014-10-16 | ATTEMPTED INTRODUCTION OF A FIREARM INTO THE PROTECTED AREA A plant employee inadvertently attempted the introduction of a firearm into the protected area. The licensee will notify the NRC Resident Inspector. * * * RETRACTION PROVIDED BY MIKE NIEMEYER TO JEFF ROTTON AT 1449 EDT ON 10/16/2014 * * * "Investigation of the event determined the contraband was inadvertently sent through the PA search process. The absence of malevolent intent establishes the event as loggable under 10 CFR 73, Appendix G, (ll)(b)." The licensee notified the NRC Resident Inspector. Notified R4DO(Haire) and Part 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-21
50386 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-21 02:10 | 2014-08-21 04:03 | 2014-08-22 | OFFSITE NOTIFICATION DUE TO SUSPECTED FUEL OIL LEAK TO THE ENVIRONMENT "At 0210 EDT on August 21, 2014, D.C. Cook made notifications to the State of Michigan, local authorities and the National Response Center due to a suspected release of approximately 8,700 gallons of diesel fuel oil to the environment. The level in the buried fuel oil storage tank for the Train B Emergency Diesel Generator was found to be approximately 8,700 gallons less than measurements taken within the last 24 hours. The tank is located within the plant protected area. At this time the suspected fuel oil plume has not left the site. "The NRC Resident Inspector was notified. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) and NUREG 1022 section 3.2.12, due to notification of offsite agencies." * * * UPDATE FROM JAMES SHAW TO VINCE KLCO ON 8/22/14 AT 1342 EDT * * * "An event investigation determined that no spill occurred. The discrepancy in level was due to maintenance activities that caused an error in level indication. No actual loss of inventory from the fuel oil storage tank occurred. Offsite agencies have been notified that this spill event is being retracted [to the State and Offsite agencies]. "The NRC Resident Inspector was notified." Notified the R3DO (Passehl). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-21
50385 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-20 19:05 | 2014-08-20 19:52 | 2014-08-20 | UNAUTHORIZED PROTECTED AREA ACCESS Actual entry of unauthorized person into the protected area. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-20
50384 | -1 | PORTSMOUTH AMERICAN CENTRIFUGE |  |  |  | URANIUM ENRICHMENT FACILITY | 2014-08-20 08:20 | 2014-08-20 18:21 | 2014-09-08 | AN ISOLATION VALVE DID NOT CLOSE DURING A MAINTENANCE EVOLUTION "On 8/20/2014, 0820 hrs [EDT], the Plant Shift Superintendent was notified of the following condition: "During a maintenance evolution to change the machine drive unit (MDU) software, one of the four primary isolation valves comprising the machine isolation valve (MIV) set did not close as required. Specifically, the purge vacuum (PV) isolation valve did not close. All other isolation valves did close as required. "This event is being reported as a loss or degradation of an IROFS [Item Relied on for Safety] that results in a failure to meet the performance requirements of Section 70.61 [and is reportable per 70.50(b)(2)]." The licensee will notify the NRC Resident Inspector. * * * RETRACTION PROVIDED BY ERIC SPAETH TO JEFF ROTTON AT 1543 EDT ON 09/08/2014 * * * "On 09/08/2014, the Plant Shift Superintendent, with concurrence of USEC-ACP RO [Regulatory Oversight] determined that this event can be retracted. "Engineering Evaluation, EE-2101-0053 Rev. 0, establishes the basis for retracting Event Number 50384. The retraction is based upon an analysis showing that failure of the purge vacuum (PV) isolation valve in the machine isolation valve (MIV) IROFS does not create a condition that results in a failure to meet the performance requirements of 10 CFR 70.61." The licensee will notify the NRC Resident Inspector. Notified R2DO (Seymour) and NMSS EO (Habighorst). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2014-08-20
50383 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-08-20 03:00 | 2014-08-20 09:50 | 2014-08-20 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee, with dust in his eye, reported to the on-site dispensary this morning. First aid was administered. A whole body survey of the employee, in his plant clothing, was performed; the maximum amount of contamination present was on the employee's work boots, 44,441 dpm/100cm2. The employee was able to return to work following treatment. The employee remained inside the Restricted Area over the entire course of the event." There was no contamination in the employee's eye. The licensee has informed the NRC Region II Senior Fuel Facility Inspector (Hartland) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-08-20
50382 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-08-20 07:47 | 2014-08-20 09:23 | 2014-08-20 | SERVICE WATER RETURN RADIATION MONITOR NONFUNCTIONAL FOR PLANNED MAINTENANCE "On August 20, 2014, at 0747 hours CDT, Kewaunee Power Station rendered the Auxiliary Building Service Water Return Monitor (R-20) nonfunctional for planned maintenance. R-20 is used for Emergency Action Level (EAL) classification of an unplanned release of liquid radioactivity to the environment that would result in an Alert or Unusual Event and is being conservatively reported under 10CFR50.72(b)(3)(xii) as a loss of emergency assessment capability. "R-20 is planned to be restored to functional by 1400 CDT today, 08/20/2014. "The NRC Regional Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-20
50381 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-08-18 19:25 | 2014-08-19 14:29 | 2014-08-20 | SHIELD BUILDING BOUNDARY DOOR FAILED TO LATCH "At 1925 EDT on 08/18/2014 an equipment failure prevented a boundary door to the Shield Building Negative Pressure Area to latch closed upon egress, thereby preventing fulfillment of the Station Emergency Ventilation System safety function. Necessary door repairs per normal station practices were completed at 1935 EDT to establish full safety system function. "This event was previously considered not reportable. Subsequent review determined the event reportable. The NRC Resident has been notified of the event. The failure to meet the 8-hour reporting requirement has been entered into the Corrective Action Program." The licensee will notify the State, Ottawa, and Lucas counties * * * UPDATE FROM THOMAS COBBLEDICK TO JOHN SHOEMAKER AT 1027 EDT ON 8/20/14 * * * "At approximately 0413 [EDT] on 8/20/14, the boundary door to the Shield Building Negative Pressure Area again failed to latch closed upon egress. The door was able to be closed and latched at 0419, restoring the Station Emergency Ventilation System safety function. Door use will be limited to essential activities until final repairs to the door closure and latching mechanism are complete. The NRC Resident has been notified of the event." The licensee will notify the State of Ohio and local authorities. Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-08-19
50380 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-08-19 07:33 | 2014-08-19 14:14 | 2014-08-19 | LOSS OF ASSESSMENT CAPABILITY "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0733 (PDT), on 08/19/2014, PRM-RE-18, Reactor Building Stack Monitor - Intermediate Range Detector, failed downscale. PRM-RE-1A and PRM-RE-1C, the Reactor Building Stack Monitor - low and high range detectors, both remain operable and fully functional. Compensatory measures are being implemented per plant procedures at this time." The NRC Resident Inspector has been notified. | 47 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-19
50379 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-08-15 | 2014-08-19 10:08 | 2014-08-25 | AGREEMENT STATE REPORT - IODINE-125 SEEDS POSITIONED INCORRECTLY DURING IMPLANTATION The following information was received via E-mail: "On August 18, 2014, the licensee notified the Agency [Texas Department of State Health Services] that on August 15, 2014, it discovered that a medical event had occurred. One of the licensee's patients had iodine-125 seed implantation in July 2014 and on August 7, 2014, a post-plan computed tomography scan was performed. During the post-plan evaluation, the licensee discovered that the seeds had not been positioned in the target tissue as prescribed during implantation. The licensee believes that approximately 30 percent of the prescribed dose was delivered to the target tissue. The licensee is evaluating the data to determine actual dosimetrics and will report its calculated dose to the intended and other tissue to the Agency upon completion. The Agency will provide further information in accordance with SA-300." This event occurred at the Baylor All Saints Medical Center in Fort Worth, Texas. Texas Incident #: I-9221 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM KAREN BLANCHARD TO CHARLES TEAL AT 1706 EDT ON 8/25/14 * * * The following was received from the State of Texas via email: "The licensee for this event was initially reported as Texas Oncology, license L-05545. It has been determined that Baylor All Saints Medical Center Radiology Department, license L-02212, is the actual licensee the implantation procedure in this event was licensed under. The licensees are continuing their investigation and will submit a written report within the required 15 days." Notified R4DO (Pick) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-27
50378 | 0 | WATERFORD | 3 |  |  | [3] CE | 2014-08-18 08:53 | 2014-08-18 17:23 | 2014-08-18 | ULTIMATE HEAT SINK SYSTEM INOPERABLE "Conditions were met that require immediate NRC notification per 10 CFR 50.72(b)(3)(v)(B) and 10 CFR 50.72(b)(3)(v)(D) due to both trains of the Ultimate Heat Sink (UHS) system being inoperable for approximately 83 minutes. This condition resulted from a planned system outage of train B Component Cooling Water (CCW), as a subsystem of the Train B UHS, and an unexpected trip of a Train A Auxiliary Component Cooling Water (ACCW) Wet Cooling Tower (WCT) fan, which is also a subsystem of the Train A UHS. "CCW Train B was declared inoperable at 0820 CDT and removed from service for a planned relay replacement, resulting in entry of 72 hour shutdown Technical Specification (TS) LCO 3.7.3, and associated cascading TS on Train B, including TS LCO 3.7.4 Action a. Subsequently, at approximately 0853 [CDT], the 6A ACCW WCT fan tripped, rendering the redundant Train A UHS inoperable, causing entry into 1 hour TS LCO 3.7.4 Action b, which states, 'With both UHS trains inoperable, restore at least one UHS train to OPERABLE status within 1 hour or be in at least HOT STANDBY within the next 6 hours and COLD SHUTDOWN within the following 30 hours.' "At approximately 0948 CDT the WCT Fan 6A electric motor thermal overload relays were reset, the fan restarted, and operated properly. At 1016 CDT, CCW train B had been restored from the planned maintenance and was declared operable, exiting TS LCO 3.7.3 and associated cascading TSs on Train B. Although a plant shutdown was not commenced following expiration of the one hour specified in TS LCO 3.7.4 ACTION b, Operations was preparing for a power reduction and TS required plant shutdown. "During this reported condition, an outside air intake valve of the Control Room Emergency Filtration system was inoperable for planned maintenance, for which TS 3.7.6.1 mitigating actions were in place. This valve was restored to Operable at 1210 CDT. Other safety systems remained available. The plant remained stable at 100% during this time." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-08-18
50377 | 0 | PATRIOT ENGINEERING AND ENVIRONMENT |  |  |  |  | 2014-08-15 16:30 | 2014-08-18 15:28 | 2014-08-18 | DAMAGED MOISTURE/DENSITY GAUGE A moisture/density gauge was run over by a bulldozer at a construction site in Indianapolis, Indiana. The RSO performed surveys of the gauge and no abnormal dose rates were observed. The gauge was leak tested and the data has been sent to Seaman Nuclear Products for analysis. The gauge has been removed from service and is secured at the licensee's facility. The gauge is a Seaman Model C-75 moisture/density gauge and typically contains 8 mCi of Cs-137 and 40 mCi of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-08-26
50376 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-17 04:00 | 2014-08-17 11:21 | 2014-08-17 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION SYSTEM INOPERABLE "On 8/17/2014 at 0400 EDT, the Technical Support Center (TSC) emergency ventilation system was identified as inoperable. Troubleshooting of this equipment found a blown control power fuse. The system has been restored to operational status as of 0555 EDT on 8/17/2014. "If an emergency had been declared and TSC activation was required, the TSC would have been staffed and activated unless the TSC became uninhabitable due to ambient temperatures, radiological or other conditions. The station Emergency Director would assess habitability in accordance with station procedures. TSC relocation of personnel would be directed as required until such time that the TSC emergency ventilation system was returned to service." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-17
50375 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-08-15 12:18 | 2014-08-15 18:02 | 2014-09-16 | STANDBY GAS TREATMENT SYSTEM INOPERABLE "On 8/15/2014 at 1218 CDT, the 'B' Standby Gas Treatment (SBGT) System was undergoing its monthly surveillance testing. With the 'B' fan running, as part of the surveillance, the 'A' Standby Gas Treatment Mode Select Switch was taken to Manual. This renders the 'A' SBGT subsystem inoperable. Almost simultaneously the 'B' fan Flow Indicating Controller went blank and flashed an error message although indicated flow through the 'B' train remained at 4073 SCFM. Based on the indication seen on 'B' controller, regardless of flow, the 'B' SBGT subsystem was also declared inoperable. In accordance with the surveillance the 'A' SBGT mode switch was placed back in the AUTO position on 8/15/2014 at 1220 CDT, restoring that train to operability. The 'B' SBGT was still considered inoperable based on its flow indicating controller being blank and flashing an error message. For a period of two minutes both SBGT subsystems were considered inoperable which is a condition that could have prevented the fulfillment of the safety function of SBGT system to control the release of radioactive material. This is considered a 8-hour reportable event per 50.72(b)(3)(v)(C) 'Any event or condition that at the time discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "During the 2 minutes that 'A' SBGT was in Manual, the 'B' SBGT train maintained 4073 scfm train flow which is at the required flow rate per STP 3.6.4.3-01B. In addition, the 'A' train could have been initiated manually at any time during that 2 minutes by the operator who was stationed at the panel performing the surveillance." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY BOB MURRELL TO DANIEL MILLS AT 0835 EDT ON 09/16/2014 * * * "The purpose of this notification is to retract a previous report made on 08/15/2014 at 1802 (EDT) (EN 50375). Notification of the event to the NRC was initially made as a result of declaring both trains of the Standby Gas Treatment (SBGT) System inoperable. Specifically, during performance of planned surveillance testing required by Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.3.2, with the 'B' train of SBGT running as part of the testing, the 'A' SBGT train's mode switch was taken to manual. This action renders the 'A' train inoperable. Simultaneously with this action, the 'B' SBGT Flow Indicator Controller went blank and flashed an error message. This resulted in the 'B' train being declared inoperable. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that TS SR 3.6.4.3.2 contains a note that states, 'When a SBGT subsystem is placed in an inoperable status solely for the performance of VFTP testing required by this Surveillance on the other subsystem, entry into associated Conditions and Required Actions may be delayed for up to 1 hour.' The 'A' SBGT train mode switch was in manual for approximately 2 minutes; therefore, entry into the associated conditions and actions was not required. "Therefore, this event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Senior Resident Inspector has been notified." Notified R3DO (Dickson) | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-08-15
50374 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2014-08-15 | 2014-08-15 17:04 | 2014-08-15 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED INDUSTRIAL GAUGE The following was received from the State of Oklahoma via email: "Phillips 66 Co. (OK-07402-12) has reported the failure of the shutter mechanism on one of their fixed gauges. Earlier today the shutter was closed while the licensee collected a leak test sample. The RSO noted that the shutter was difficult to operate. When they returned the shutter handle to the 'open' position, the control room which monitors the gauge readings reported that the readout briefly returned to its normal level, then dropped back to zero when the shutter was supposed to be fully open. Repeated attempts showed that the gauge only operated when the shutter was approximately 75% of the fully 'open' position. The licensee has contacted the gauge manufacturer but they won't be able to supply a replacement for approximately 6 weeks. The licensee has requested permission to leave the gauge in service until a replacement is available. The gauge is installed on a stand pipe 18 feet above ground level in an oil refinery in Ponca City, OK. It is only accessible by catwalk which the RSO is going to cordon off. Material in the gauge is Cs-137, 25 mCi when new in 1993. We[State of OK] have told the RSO they may leave the gauge in operation pending the results of the leak test. If these show the source to be leaking they must immediately remove the gauge from service." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2014-08-25
50373 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-08-15 14:33 | 2014-08-15 15:21 | 2014-08-15 | INADEQUATE COMPENSATORY MEASURES A security related system was removed from service and has been returned to service. During the time that the system was not in service, compensatory measures were implemented. Follow-up review determined the compensatory measures were not performed in accordance with the applicable Security Implementing Procedure. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-15
50372 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-08-14 | 2014-08-15 14:53 | 2014-08-15 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE TO LIVER The following was received from the State of Ohio via email: "The licensee prepared and delivered a therapeutic dose of TheraSpheres to a patient's liver on August 14, 2014. The written directive was for 120 Gy to the liver with 27 mCi of Y-90 TheraSpheres. On August 15, 2014, the licensee discovered that 20% of the dose that was supposed to be administered to the patient was still in the bottom of the vial. Although the licensee prepared the vial in accordance with the manufacturer's instructions, 20% of the TheraSpheres remained in the bottom of the vial and did not go into suspension. "The patient and referring physician have been notified. "The Bureau [Ohio Bureau of Radiation Protection] will be conducting a follow-up investigation regarding this event." The patient received 96 Gy to the liver instead of the prescribed 120 Gy. Ohio incident # OH140010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-08-25
50371 | 0 | ABB, INC |  |  |  |  | 2014-08-15 | 2014-08-15 11:00 | 2014-09-12 | NOTICE OF DEVIATION REGARDING K-LINE CIRCUIT BREAKER SECONDARY CLOSE LATCH The following information was excerpted from a facsimile received from ABB, Inc: "This letter provides notification of a failure to comply with specifications associated with a secondary close latch, part number 716610K01, used in K-Line 225/800 and 1600/2000 amp electrically operated Model 7 circuit breakers. This does not affect previous models of these same breakers that have not been upgraded to include the interlocking primary and secondary close latches. It also does not affect manually operated Kline breakers or K3000/4000 circuit breakers. Information is provided as specified in 10CFR21 paragraph 21.21(d)(4). "Notifying individual: Jay Lavrinc, Vice President & General Manager, ABB (Medium Voltage Service), 2300 Mechanicsville Road, Florence, SC 29501 "Identification of the Subject component: ABB part number 716610K01 secondary close latch. This secondary close latch is used on new legacy K-Line Model 7 electrically operated circuit breakers. It is also used during breaker refurbishments when a secondary close latch is required to be replaced because of damage or wear. The secondary close latch is available as a component part and is also used in K-Line Model 7 up-grade kits. "If a breaker is sent in for refurbishment the primary and secondary latches are replaced unless it is required in the customer PO that they not be replaced unless they are damaged or worn. "Nature of the deviation: During outgoing inspection a breaker went trip free during the operational phase of the testing procedure. The inspector found that the cam attached to the top of the secondary close latch, 716610K01, was not properly riveted in place. The head of the rivet was not pushed down flush against the side of the cam. Since the rivet was not seated properly, the other end of the rivet did not project through the other side of the latch and therefore the bradded end of the rivet was not deformed in a manner to sufficiently apply the required holding force to keep the cam in its proper and secure operating position. "Corrective actions include: a. Perform 100% inspection all part number 716610K01 secondary close latches in inventory to identify the nonconforming latches. (Action complete) b. Trained inspectors and breaker assemblers on identifying this condition (Action Complete) c. Contact primary vendor to investigate cause and correct on future orders. (Action Complete) d. Verified that this is the only assembly with bradding that this vendor provides. (Action complete) e. Notification of the potential existence of this deviation to affected customers (Action to be completed by 18 August 2014) "Affected Customers: Constellation Energy, DTEEnergy, Entergy Operations, Exelon Corporation "Recommendations: It is recommended that affected Licensees that have received latches that were identified as having been provided from parts that fall under this notification take the following actions: "If the latch is in their inventory as a component, in a kit or in a breaker that is not currently in use it is suggested that the secondary trip latch be inspected for this condition. Inspection should include visual inspection of the rivets to confirm they are properly seated and bradded and physical manipulation of the cam to determine that it is securely held in place in the assembly. "If a suspect latch is installed in a breaker that is currently installed and energized we recommend that at their next maintenance cycle, the secondary close latch in the breaker be inspected for this condition. "We currently cycle Kline breakers that are refurbished approximately 55 close/open operations before they ship from the Florence facility. New breakers get at least that many operations or more. If a breaker has shipped out of the Florence facility during this period it is unlikely that the breaker would get through inspection without failing with a latch that is improperly riveted. ABB cannot guarantee that no latch on a breaker that shipped is affected but we do not see it as a likely occurrence with the testing that the breaker is subjected to prior to shipment. There have been no field failures reported that were attributed to this manufacturing issue." * * * UPDATE FROM DAVID BROWN TO JOHN SHOEMAKER ON AT 1654 EDT ON 9/12/14 * * * The following information was received from ABB Inc. via email; "This amendment is being issued to correct 2 errors in the original notification: 1. This 'secondary close latch' was mistakenly referred to as a 'secondary trip latch' in Section 7 [of the report]. 2. The manner in which the problem was detected was described improperly as a breaker 'went trip free' when in fact, the breaker 'failed to close'. This is from Section 5 [of the report]. "This [amendment] letter is being submitted to ensure accurate information has been reported. There have been no reported field failures and affected customers have been notified." For questions, contact; David Brown QA Engineer, ABB Inc. Ph: (843) 413-4782 Notified R1DO (Jackson), R2DO (Shaeffer), R3DO (Riemer), R4DO (Azua), and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-08-15
50370 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-14 16:31 | 2014-08-15 01:19 | 2014-08-15 | UNIT 2 TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO MULTIPLE INOPERABLE EMERGENCY DIESEL GENERATORS "While performing scheduled maintenance on Unit 2 Emergency Diesel Generator (EDG) 2-2, Diablo Canyon Power Plant (DCPP) identified a failed capscrew on engine cylinder 1L. As part of subsequent inspections to determine whether a similar condition existed on any of the other Unit 1 or Unit 2 EDGs, a degraded capscrew was identified on EDG 2-3 cylinder 8L at 1631 PDT on 08/14/2014. No capscrew issues were identified on the Unit 1 EDGs or on Unit 2 EDG 2-1. Although all operational tests of the diesels up to the time of discovery were satisfactorily performed with no indication of degraded performance, the EDG 2-3 was declared inoperable. "Because two Unit 2 EDGs were inoperable concurrently, this is being reported as a condition that could have prevented fulfillment of a safety function per 10 CFR 50.72(b)(3)(v). Per the requirements of TS 3.8.1, with two EDGs inoperable, a plant shutdown was commenced at 2031 PDT on 08/14/2014. Therefore, this condition is also being reported in accordance with 10 CFR 50.72(b)(2)(i). "Offsite power remained available throughout this condition. EDG 2-2 remains out of service as part of its scheduled maintenance window. "This condition did not result in any adverse impact on the health and safety of the public. "A press release is planned. "The licensee informed the NRC Resident Inspector." The licensee also reported event notifications for 10 CFR 50.72(b)(3)(v)(C) - Control of Rad Release and 10 CFR 50.72(b)(3)(v)(D) - Accident Mitigation. The licensee plans to continue the shutdown to Mode 3 and is developing plans to return one of the two inoperable EDGs to operable status by the time the unit reaches Mode 5. | 0 | 63 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | OFFSITE NOTIFICATION | POT UNABLE TO SAFE SD | POT RHR INOP | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(xi) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 0 | 2014-08-15
50369 | 0 | BOTSFORD HOSPITAL |  |  |  |  | 2014-07-10 13:20 | 2014-08-14 17:17 | 2014-08-14 | PATIENT RECEIVED LESS THAN PRESCRIBED DOSE A patient undergoing High Dose Rate Brachytherapy using Ir-192 was prescribed 700 cGy per fraction and only received 700 cGy to 60% of the planned volume. The patient was scheduled for two treatments. The first treatment was successfully administered to the patient on 6/26/14. When the patient returned for the second treatment on 7/10/14 the HDR afterloader was loaded with the treatment plan for the original treatment instead of the second treatment. This resulted in the patient not receiving the full prescribed treatment. The licensee discovered the problem during an audit when the number of catheters did not match. There are no adverse health effects expected as a result of this treatment. The licensee has contacted the vender to determine a way to remove old treatment plans from the machine to ensure this does not happen in the future. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2014-08-22
50368 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-08-14 14:45 | 2014-08-14 17:16 | 2014-08-14 | AGREEMENT STATE REPORT - INOPERABILITY OF THE ACCESS CONTROL SYSTEM The following was received from the State of Colorado via email: "CDPHE [Colorado Department of Public Health] received telephone notification of an inoperability of the access control system on 8/14/2014 at approximately 1445 [MDT]. Colorado State University, a research licensee, reported that a radiation monitor provided to detect the presence of high radiation levels in the radiation room of a panoramic irradiator was alarming when there was no [abnormal] radiation level present. One of the irradiator users noticed the audible alarm when their work was complete and they were leaving the area. The RSO responded and suspected a stuck source. Using a hand held radiation detection instrument, the irradiator door was opened and the irradiator room was entered. As the RSO entered the room there was no indication of radiation levels above what was expected when the source is in its shielded position, and as a result, it was determined that the source was in its shielded position. The room radiation monitor was reset but shortly after again alarmed without any [abnormal] radiation field present. The irradiator has been taken out of service and the monitor has been removed for repair." Colorado event report ID: CO14-I14-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-08-22
50367 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-08-11 | 2014-08-14 14:16 | 2014-08-14 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following was received from the State of Massachusetts via email: "Thermo Scientific received a total of 15 sealed sources, Model XFB-3, manufactured by Eckert & Ziegler Isotope Products, containing Cd-109, each with an activity of 40 mCi. As part of Thermo's inspection protocol, individual sealed sources were leak tested, and one source, serial number TR3042 tested greater than the leak test limit of 0.005 microcuries. "Following the initial leak test, two additional leak test measurements were made and all three measurements were found to be in excess of the 0.005 microcurie limit, with measurements ranging from 0.0126 to 0.0184 microcuries. "Eckert and Ziegler was notified immediately by Thermo Scientific, a return authorization was provided, and Thermo returned the sealed source via [common carrier] to Eckert and Ziegler on 08/11/14. "The licensee reports that the area where the leaks tests were obtained was surveyed thoroughly and no contamination was found. "The Agency [State of Massachusetts] considers this event open." MA Docket #: 20-1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-08-22
50366 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-08-13 | 2014-08-14 11:07 | 2014-08-14 | AGREEMENT STATE - RADIOGRAPHY CAMERA SOURCE WOULD NOT RETRACT The following information was provided by the State of Texas via email: "On August 14, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that on August 13, 2014, a radiography crew using a 50 foot crank out device could not retract a 54 curie iridium-192 source to the fully retracted and locked position in a QSA 880D exposure device (camera). The RSO stated the radiographer had completed an exposure at a temporary field site and was retracting the source when he felt the resistance to movement in the crank out handle disappear and he could no longer move the source. The radiographer noted the dose rates were still higher than those for a fully shielded source. The radiographer contacted the RSO and increased the control area. The radiographer placed two bags of lead on the guide tube where he believed the source was located. The RSO stated the radiographer was in the area of the source for just a few seconds. The radiographer checked his self reading dosimeter after placing the lead at the source and found it off scale. "The RSO and a recovery team went to the location to retrieve the source. The RSO had additional lead placed on the guide tube and the dose rates at the crank out device dropped to less than 2 millirem per hour. The RSO disconnected the drive cable housing from the broken in two at crank out device. The RSO grabbed the drive cable inside the drive cable housing with a set of pliers and was able to pull the drive cable and return the source to the fully shielded position. "The personnel dosimeter for the radiographer who had approached the guide tube was sent to the licensee's dosimetry processor for processing and the radiographer has been removed from all work involving exposure to radiation until the results for their badge has been received. The RSO stated that based on the exposure rates and the time the radiographer was in the area of the source he did not believe the radiographer received a significant exposure from the event. The RSO received 8 millirem by pocket dosimeter from the event. No other individuals received any significant exposure in this event. "The crank out and drive cable will been sent to the manufacturer for inspection. The RSO stated he examined the drive cable, but did not see anything that would indicate why the cable failed. The RSO stated they performed a flex test of the drive cable and it passed. The RSO stated the camera and guide tube were inspected and returned to service. Additional information will be provided in accordance with SA-300." Texas Incident #: I-9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-22
50365 | 0 | UNION ELECTRIC DBA AMEREN MISSOURI |  |  |  |  | 2014-08-13 10:30 | 2014-08-14 09:40 | 2014-08-14 | PROCESS DENSITY GAUGE DAMAGED BY FIRE AND/OR HEAT "On the morning of August 13, 2014 while cleaning up from a fire event on coal handling conveyer belt #2 at the Ameren Missouri (Ameren) Rush Island Energy Center it was observed that the nucleonic gauge located outside of the area of the original fire had some indications of potential damage. The gauge is located approximately 12 feet above the walkway near the ceiling of the room in an area that was not easily accessible. The gauge is a Ronan Engineering Model SA1-C10 containing 100 mCi of CS-137 in sealed solid form. Ameren contacted R. M. Wester (NRC Licensed maintenance vendor) to evaluate the nucleonic gauge on August 13, 2014 to determine if the gauge had been damaged due to the fire. "R. M. Wester examination of the source housing showed the exterior to be in good condition with some minor scorching. The shutter check performed showed smooth operation and good beam strength with the shutter open (greater than 200 mR/hr) and good shielding with the shutter closed (1.5 mR/hr). Wipes of the source and the area below the source indicated no contamination or leakage from the source. "An area radiation survey did indicate that some of the lead inside of the source housing had potentially melted and shifted. The on contact readings of the back (0.2 mR/hr), sides/bottom (0.3 mR/hr), and shutter (1.5 mR/hr) were all consistent with expected readings. The 30 cm readings from the source back, sides, and bottom were also as expected (approximately 0.03 mR/hr). The readings on top of the source were higher than expected with a reading of 6 mR/hr on contact and 0.4 mR/hr at 30 cm. These readings on the top of the source do not present an immediate radiological hazard due to their low intensity and the fact that the source is mounted very close to the ceiling in the room. The ceiling support beam and water deflection shield make it difficult to even get a reading 30 cm from the top of the source. "R. M. Wester's recommendation was that the gauge is functional and it could continue to be use until a replacement device could be procured and installed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2014-08-22
50364 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-08-14 07:55 | 2014-08-14 08:58 | 2014-08-14 | SERVICE WATER RADIATION MONITOR NONFUNCTIONAL FOR PLANNED MAINTENANCE "The service water radiation monitor system will be rendered nonfunctional during planned preventive maintenance. As a result, this represents a loss of emergency assessment capability and is reportable per 10CFR50.72(b)(3)(xiii). The planned maintenance is expected to last 4 hours. During this time, plant parameters will be monitored and sampling will be performed which will support sustaining the health and safety of the public during this planned maintenance activity. "The NRC Resident Inspector will be notified prior to removing the service water radiation monitor from service." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-14
50363 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2014-08-13 23:18 | 2014-08-14 01:16 | 2014-08-14 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "Nine Mile Point Unit 1 (NMP1) had a momentary loss of Secondary Containment due to both Reactor Building Airlock doors being opened at the same time. "At 2318 [EDT] on 8/13/2014, both Reactor Building Airlock doors at NMP1 were open simultaneously for less than 5 seconds. This results in a momentary loss of Secondary Containment operability (TS 3.4.3). The doors were closed and operability was restored. "Secondary Containment being inoperable is an 8 hour notification per 10 CFR 50.72(b)(3)(v)(C), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Senior Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-08-14
50362 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-08-08 10:26 | 2014-08-13 17:40 | 2014-08-13 | UNANALYZED CONDITION DUE TO LACK OF APPROPRIATE FUSE PROTECTION "Based on industry operating experience, a drawing review was performed and it was determined that the control circuits for the DC Emergency Turbine Oil Pumps for both Unit 1 and Unit 2 are not fused properly. Therefore an overload within the control circuit could result in a fire that could propagate to multiple fire areas affecting safe shutdown equipment that could be compromised, which affects the Appendix R safe shutdown analysis. Based on this information, the determination was made that this condition meets the reporting criteria for 10 CFR 50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with F5 Appendix K, Fire Protection system minimum requirements, for impaired fire protection equipment. Hourly fire watches are in place in the affected locations as a result of previous conditions. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensures the protection of the equipment. "The protection of the health and safety of the public is not affected by this issue. "The license has notified the NRC Senior Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-08-13
50361 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2014-08-13 11:57 | 2014-08-13 13:06 | 2014-08-13 | AUTOMATIC REACTOR TRIP "On August 13, 2014 at 1157 EDT, the Indian Point Unit 3 Reactor Protection System automatically actuated at 100% power due to Over Temperature Delta Temperature logic. At the time of the trip, pressurizer pressure Channel 1 was in test for maintenance, though testing was suspended at this time for lunch. All control rods fully inserted on the reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators, and normal heat removal through the condenser via condenser steam dumps. There was no radiation released. Indian Point Unit 2 was not affected by this event and remains at 100% power. "A post trip investigation is in progress. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-08-13
50360 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-08-13 | 2014-08-13 11:23 | 2014-08-13 | CONTROL ROOM BOUNDARY DOOR FAILED TO LATCH "A Control Room Boundary Door failed to latch and maintain the Control Room boundary. This condition was reportable in accordance with 10CFR50.72(b)(3)(v)(D). The door was repaired and the Control Room boundary was restored on 8/13/14 at 0552 [EDT]." The licensee notified the NRC Resident Inspector, State of Connecticut, and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-08-13
50359 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2014-08-01 | 2014-08-01 15:16 | 2016-02-03 | POTENTIAL ISSUE REGARDING INCORRECT INDUSTRIAL IRRADIATION DOSE The following information was received via facsimile: Nutherm International, Inc. was notified by Steris Isomedix Services that the applied radiation dose reported on their Component Irradiation Certificates did not account for all uncertainties involved (i.e. density of unrelated products in carriers, off-carrier location within the irradiator and Cobalt-60 source decay). This issue was originally identified as part of NRC Inspection Report No. 99901445/2014-201. "Nutherm International, Inc. is conducting an evaluation to determine whether a defect as defined by 10 CFR Part 21 exists. The impact of this failure to account for all uncertainties will be evaluated for all projects that required data from any sample irradiated by this supplier. "At the conclusion of the evaluation, any customer impacted by this issue will be notified and the U.S. Nuclear Regulatory Commission will be notified in accordance with the requirements of 10 CFR Part 21.21. "If you have any questions regarding this issue please do not hesitate to contact Adrienne Smith, Quality Assurance Manager at 618-244-6000, adrienne.smith@nutherm.com." The supplier will update this report when the evaluation is complete. This event report was originally received by the NRC Operations Center on 08/01/2014 * * * UPDATE AT 1727 ON 8/31/2015 FROM THOMAS STERBIS TO MARK ABRAMOVITZ * * * The following information was received via fax: "Nutherm has identified one customer where there is a potential impact to the conclusions of the equipment qualification that Nutherm does not have the capability to perform further evaluations to determine if a defect exists. "Nutherm International, Inc. performed equipment qualification testing for SOR, Inc., Lenexa, KS under SOR, Inc. Purchase Order number 166984 which included irradiation performed by Steris Isomedix. Based on the location of the sample during the irradiation and the total variability for this location provided by Steris Isomedix, Nutherm has verified that the test specimens received a minimum irradiation dose that meets the customer's TID requirement but does not meet the customer's TID requirement with the 10 percent IEEE 323 margin. "In accordance with the requirements of 10 CFR Part 21.21, SOR Inc. has been notified regarding this issue to allow them to evaluate this deviation or failure to comply." Notified the R4DO (Werner), NMSS Events Resource (via e-mail), and the Part-21 Group (via e-mail) * * * UPDATE FROM NUTHERM INTERNATIONAL, INC. AT 1658 EST ON 2/3/16 * * * The following information is summarized from the information received from Nutherm International, Inc. via fax: Nutherm has completed their evaluation of past equipment qualifications and identified that the following U.S. facilities may be impacted: Cooper Nuclear Plant, Oconee Station, J.A. Fitzpatrick Station, Point Beach Nuclear, Brunswick Nuclear, Susquehanna Nuclear and Electric Power Research Institute. Nutherm has notified the affected facilities. Notified R1DO (Rogge), R2DO (Musser), R3DO (Kozak), R4DO (Pick) and the Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-08-13
50358 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-08-12 12:48 | 2014-08-12 16:43 | 2014-08-12 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTUATION "At approximately 1248 CDT, on August 12, 2014, Emergency Planning was notified by the siren vendor that Pierce County inadvertently actuated sirens at 1239 [CDT] while performing a cancel test. Fifty two (52) of the 123 sirens were actuated county wide for approximately 15 seconds before Pierce County could cancel activation. Per F3-5.2, Response to a False Siren Activation, this requires a 10 CFR 50.72(b)(2) 4 hour non-emergency report. Capability to notify the public was never degraded during this time. The sirens remain in service. No press release is planned at this time. "The license has notified the NRC Senior Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-12
50357 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-08-12 13:19 | 2014-08-12 15:58 | 2014-08-12 | SITE STACK RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE Millstone removed their site stack radiation monitor, RM-8169, from service for scheduled maintenance. Expected duration of maintenance is 8 hours. The licensee notified the NRC Resident Inspector, the State of Connecticut, and the town of Waterford. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-12
50356 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2014-08-12 02:38 | 2014-08-12 10:32 | 2014-10-03 | HPCI POTENTIAL INOPERABILITY DISCOVERED DURING POST MAINTENANCE TESTING "At 0238 hours [EDT] on Tuesday, August 12, 2014, with Pilgrim Station at 100 percent power in the Run Mode with reactor coolant pressure at approximately 1025 psig and the High Pressure Coolant Injection (HPCI) System previously removed from service for maintenance, a condition with the potential to impact the operability of the HPCI System was discovered. The HPCI System was being operated in accordance with plant procedures to complete post maintenance test requirements. Upon HPCI initiation, the indicated flow on HPCI Flow Indicator FI-2340-1-1 was 0 Gallons Per Minute (GPM) with the flow controller in the manual mode. The indicated flow on HPCI Flow Indicator Fl-2340-1-1 remained at 0 GPM throughout the duration of the surveillance. Alternate flow indication indicated the expected HPCI flow rate. The flow controller in manual was capable of controlling at the demanded HPCI turbine speed. The HPCI turbine speed was manually varied with a corresponding change in the HPCI flow computer point reading. Activities to restore the flow indicator capability are in progress. "The plant is in a safe condition and plant personnel are investigating the cause of the flow indicator issue. "The NRC Resident Inspector has been informed of this notification. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(B) and 10 CFR 50.72(b)(3)(v)(D)." The licensee will be notifying the state. * * * RETRACTION FROM O'ROURKE TO KLCO ON 10/03/2014 AT 1254 EDT * * * "Subsequent investigation determined that HPCI Flow Instrument SQRT-2340-10 output signal was 0 mA and did not change in response to the actual HPCI flow rate. With the SQRT-2340-10 output signal at 0 mA, the HPCI Flow controller would demand maximum HPCI injection flow in the AUTOMATIC control mode. Circuitry within the control system limits the maximum HPCI flow to 5250 GPM at a turbine speed of 4165 RPM. Engineering analysis has concluded that the HPCI pump operating limits (net positive suction head and low pressure suction trip) would not be exceeded in a maximum HPCI flow state. Therefore, the HPCI System was operable and capable of performing its residual heat removal and accident mitigation functions. "Therefore, the initial 50.72(b)(3)(v)(B) and 10CFR50.72(b)(3)(v)(D) report is being retracted. "The [NRC] Resident Inspector has been informed of this notification retraction." Notified the R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-08-12
50355 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-12 04:32 | 2014-08-12 05:04 | 2014-08-12 | UNUSUAL EVENT FOR A HALON RELEASE NEAR THE TSC AND EOF The licensee declared an Unusual Event because of a halon discharge in the simulator. This potentially affects access and habitability of the Technical Support Center (TSC) and the Emergency Operations Facility (EOF). The Unusual Event was declared under HU3.1 "toxic, corrosive, asphyxiate, or flammable gases in amounts that have or could have adversely affected normal plant operations." The fire brigade has been dispatched to determine whether a fire actually exists. The licensee informed State and local agencies and the NRC Resident Inspector. Notified other FEDS (FEMA Ops Center, DHS NICC Watch Officer, DHS SWO) and (Nuclear SSA, FEMA NWC) via email. * * * UPDATE AT 0707 EDT ON 8/12/2014 FROM DAVID FASCHER TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 0700 EDT. "Halon discharged into the plant simulator. There was no actual fire. Offsite assistance was requested. Local fire department and ambulance are on site. The TSC and EOF have been activated. "The halon discharge into the simulator building is not impacting normal plant operations where the ERO [Emergency Response Organization] capabilities and staffing are still required. Therefore, activation for UE [Unusual Event] is being terminated." The Incident Commander released the building for normal access at 0717 EDT. The licensee informed State and local agencies and the NRC Resident Inspector. Notified the R2DO (Nease), IRD (Gott), and NRR (Thomas). Notified other FEDS (FEMA Ops Center, DHS NICC Watch Officer, DHS SWO) and (Nuclear SSA, FEMA NWC) via email. * * * UPDATE AT 1218 EDT ON 8/12/14 FROM CRAIG OLIVER TO JOHN SHOEMAKER * * * "EVENT DESCRIPTION: This is an update of a previous notification which was made by telephone to the [NRC] Operations Center at approximately 0504 EDT per Event Number 50355. "At approximately 0421 EDT on 08/12/2014, the Halon fire suppression system in the Plant Simulator actuated by releasing the Halon. A Notification of Unusual Event (NOUE) was declared at 0432 EDT on the basis that a release of toxic or asphyxiating gas had occurred on site (Emergency Action Level HU3.1). Emergency response personnel reported to the site and prepared to perform emergency response activities. "The site fire brigade was dispatched. The local fire department was called and emergency personnel were dispatched to the site. "The reason for the Halon discharge is not known at this time and is under investigation. No actual fire was observed. The Plant Simulator is located in the same building with the primary Technical Support Center (TSC) and primary Emergency Operations Facility (EOF). Since the Halon discharge occurred in this building, the site incident commander restricted access to these two primary Emergency Response Facilities, rendering them unavailable for use. The NOUE was terminated at 0700 EDT. Normal access to the TSC and EOF was restored at 0717 EDT. "INITIAL SAFETY SIGNIFICANCE EVALUATION: This event had no effect on the operating units, and there was no adverse impact on nuclear safety or on the health and safety of the public. "The NRC Resident Inspector has been notified. "CORRECTIVE ACTIONS: Offsite fire department personnel assisted by on site fire brigade have validated that no fire condition existed. The building has been ventilated and normal access restored. The failure of the Halon System is being tracked for restoration in accordance with station fire protection documents." Notified R2DO (Hopper) and NRR Daytime EO (Thomas). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-08-12
50354 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2014-08-11 10:20 | 2014-08-11 14:20 | 2014-08-11 | MANUAL REACTOR TRIP ON LOSS OF INSTRUMENT AIR FOLLOWED BY SAFETY INJECTION "This is an non-emergency notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to auxiliary feedwater (AFW) initiation , safety injection (SI) initiation, and emergency diesel generator (EDG) auto start. "On 8/11/14 at 1028 EDT, Unit 3 experienced a manual reactor trip due to a loss of instrument air. Auxiliary feed water automatically initiated as expected. Unit 3 is currently in Mode 3 and stable. Instrument air has been restored. "At 1305 a safety injection signal [SI] occurred due to main steamline high differential pressure during a plant cooldown to 470 degrees Fahrenheit. High head safety injection (HHSI) pump, residual heat removal (RHR) pumps, and emergency diesel generators (EDGs) auto started as expected due to the safety injection signal. Based on plant conditions, the HHSI and RHR pumps did not inject into the reactor coolant system." The plant was stabilized after the reactor trip, however, the loss of instrument air resulted in a loss of letdown and PZR level continued to slowly increase to approximately 91%. All rods fully inserted and normal offsite power was maintained. Operators initiated a plant cooldown to stabilize and lower PZR level using the S/G atmospheric steam dumps. Unequal opening of the S/G atmospheric steam dumps caused the SI to occur due to main steamline high differential pressure. No RCS injection occurred and all SI equipment operated as expected and has been subsequently secured. Unit 3 is stable in mode 3 at 490 degrees Fahrenheit and RCS pressure is 1940 psig. There was no effect on Unit 4 which continues to operate at 100% power. The loss of instrument air is being investigated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-08-11
50353 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2014-08-11 | 2014-08-11 14:12 | 2014-08-11 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to monitoring and protection of site perimeter. Compensatory actions taken. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | MA | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2014-08-11
50352 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-08-09 07:40 | 2014-08-09 15:21 | 2014-08-09 | UNPLANNED ONSITE MEDICAL TREATMENT OF A CONTAMINATED WORKER "An employee experienced a minor thermal burn to the leg and reported to the on-site dispensary this morning. The plant nurse administered first aid. A whole body survey of the employee's plant clothing was performed; the maximum amount of contamination present was on the employee's work boots, 15,949 dpm/100cm2. The plant nurse allowed the employee to return to work following treatment. The employee remained inside the Restricted Area over the entire course of the event. "Contamination due to uranium ore concentrates." The licensee will notify their NRC Region 2 Inspector (Hartland) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-08-18
50351 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-07 17:07 | 2014-08-07 20:00 | 2015-04-20 | UNANALYZED CONDITION DUE TO DISCOVERY OF DEGRADED FIRE BARRIER WALLS "During a fire inspection activity involving inspection of fire walls that serve as Appendix R barriers, degradation of some fire walls was identified that was sufficient to prevent these walls from meeting Appendix R requirements as 3-hour fire barriers. In the event of a postulated fire in the affected areas, both safe shutdown paths on the affected unit could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded penetrations in these same fire areas. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded conditions can be corrected. "Condition Reports: 850802, 850819" In addition to automatic fire protection features, the licensee has posted fire watches as a compensatory measure. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM STANLEY STONE TO DONALD NORWOOD AT 1814 EST ON 11/24/2014 * * * "As part of the 'extent of condition' corrective action for the condition identified in EN 50351, an inspection activity is in progress to inspect the remaining fire walls for conditions similar to those reported on 8/7/2014. During this inspection, another condition was identified involving some degradation of the fire wall between Fire Area 1023 - RPS MG Set Room and Fire Area 1015 - Annunciator Room. In the event of a postulated fire in the affected areas both safe shutdown paths on Unit 1 could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded penetrations in these same fire areas and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. The inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS update report and will be documented in a revised LER at the end of the inspection activity. "Condition Report: 898908." The licensee will notify the NRC Resident Inspector. Notified R2DO (Ehrhardt). * * * UPDATE FROM KENNY HUNTER TO DANIEL MILLS AT 1758 EST ON 11/25/2014 * * * "As part of the 'extent of condition' corrective action for the condition identified in EN 50351, an inspection activity is in progress to inspect the remaining fire walls for conditions similar to those reported on 8/7/2014. During this inspection, another condition was identified involving some degradation of the fire wall between Fire Area 1016 - 600 Volt Switchgear Room 1C and Fire Area 1017 - 600 Volt Switchgear Room 1D. In the event of a postulated fire in the affected areas, both safe shutdown paths on Unit 1 could be compromised. Given this information the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded penetrations in these same fire areas and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. The inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS update report and will be documented in a revised LER at the end of the inspection activity." The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes). * * * UPDATE FROM SCOTT BRITT TO DONALD NORWOOD AT 1706 EST ON 12/4/2014 * * * "As part of the 'extent of condition' corrective action for the condition identified in EN 50351, an inspection activity is in progress to inspect the remaining fire walls for conditions similar to those reported on 8/7/2014. During this inspection, additional conditions were identified involving multiple fire barriers in the control building that affected both safe shutdown paths on Unit 1 and Unit 2 based on the respective inspection results. In the event of a postulated fire in the affected areas both safe shutdown paths on Unit 1 and 2 could be compromised. "Given this information the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded penetrations in these same fire areas and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. The inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS update report as required and will be documented in a revised LER at the end of the inspection activity." The licensee will notify the NRC Resident Inspector. Notified R2DO (Freeman). * * * UPDATE AT 1842 EST ON 12/12/2014 FROM G.S. GRIFFIS TO MARK ABRAMOVITZ * * * "As part of the 'extent of condition' corrective action for the condition identified in EN# 50351, an inspection activity is in progress to inspect the remaining fire walls and associated penetrations for conditions similar to those reported on 08/07/2014. During this inspection, nonconformances of multiple fire barriers were identified that bring into question the functionality of the affected fire barriers that can compromise safe shutdown paths on Unit 1 and 2 based on the respective inspection results. Since additional time is required to further evaluate each nonconformance to conclusively determine if the nonconformance is sufficient to consider the barrier nonfunctional, interim conservative fire actions were taken by considering these fire barriers as nonfunctional. Based on this conservative conclusion, in the event of a postulated fire in the affected areas both safe shutdown paths on Unit 1 and 2 could be compromised. Given this information the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded penetrations and fire walls in most of these same fire areas and will remain in place until the barrier(s) are repaired. Additional fire actions were taken as required to address the additional fire areas identified. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. The inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report and will be documented in a revised LER at the end of the inspection activity. "Unit 1 is entering a planned outage due to unrelated activities." Condition Report: 10000607 The licensee notified the NRC Resident Inspector. Notified the R2DO (Desai). * * * UPDATE FROM STANLEY STONE TO DONALD NORWOOD AT 2315 EST ON 1/15/2015 * * * "As part of the 'extent of condition' corrective action for the conditions identified in EN# 50351, an inspection activity was performed of a fire wall for conditions similar to those reported on 12/12/2014. During this inspection, another condition was identified involving some degradation of the fire wall between Fire Area 1008 - Unit 1 AC Inverter Room and Fire Area 0001 to consider the barrier nonfunctional. In the event of a postulated fire in the affected areas both safe shutdown paths on Unit 1 could be compromised. Given this information the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded fire barriers in these same fire areas and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. The inspection activity is continuing and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report and will be documented in a revised LER at the end of the inspection activity." Condition Report: 10013077 The licensee notified the NRC Resident Inspector. Notified the R2DO (Musser). * * * UPDATE FROM JOHN MITCHELL TO JEFF HERRERA AT 2025 EST ON 1/21/2015 * * * "During review and closeout of fire barrier and penetration seals work orders and surveillance procedures performed as part of the 'extent of condition' inspection activity initially described in Event # 50351, the following conditions were identified that in the event of a postulated fire in the respective fire areas listed both safe shutdown paths could be compromised. "Unit 2 Control Bldg. el. 130', gap in the grout around conduit penetration between fire areas 2013 and 2015 "Unit 1 Reactor Bldg. el. 130', open conduit between fire areas 1203C and 1105 "Given this information the determination was made that this condition meets the reporting criteria of 10 CFR 50.72(b)(3)(ii)(B). Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded fire barriers in the Unit 2 fire area and will remain in place until the affected barrier areas are repaired. Compensatory measures were established for the Unit 1 areas and will remain in place until the affected barriers areas are repaired. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded condition is repaired. Subsequent similar condition(s) found when performing remaining inspections that meet the reporting requirements will be included in an ENS Update Report and will be documented in a revised LER at the end of the inspection activity. "Condition Report 10015417 "Condition Report 10015437" The licensee notified the NRC Resident Inspector. Notified the R2DO (McCoy). * * * UPDATE FROM G.S. GRIFFIS TO HOWIE CROUCH AT 1714 EST ON 2/4/15 * * * "During the review of fire barrier surveillance procedures performed as part of the 'extent of condition' inspection activity for the event initially identified in EN# 50351, some degradation was observed on the east wall of fire area 2006. These nonconforming issues observed on the affected fire wall were identified as affecting both safe shutdown paths for Unit 2. Therefore, in the event of a postulated fire for the affected area, both safe shutdown paths on Unit 2 could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire area and will remain in place until the wall is repaired. The presence of the compensatory measures, in addition to portable fire protection equipment located in adjacent areas, ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The extent of condition inspection activity is continuing, and this, and any subsequent similar condition(s) that meets the reporting requirements, will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity." CR 10021623 Notified R2DO (HAAG). * * * UPDATE FROM JOHN MITCHELL TO DANIEL MILLS AT 1823 EST ON 2/18/15 * * * "During performance of work package closeouts to support the 'extent of condition' inspection activity for the event initially identified in EN# 50351, the following fire barriers were identified as failing to meet the procedure acceptance criteria: - Three penetrations separating Unit 1 Fire Areas 1013 and 0040 - A fire wall deficiency in the wall separating Unit 1 Fire Areas 1015 and 1013 "These nonconforming issues observed on the affected penetrations and fire wall were identified as affecting both safe shutdown paths for Unit 1. Therefore, in the event of a postulated fire for the affected area, both safe shutdown paths on Unit 1 could be compromised. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire area and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The extent of condition inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10028364 "CR 10028366" The NRC Resident Inspector has been notified. Notified R2DO (Rose). * * * UPDATE AT 2035 EST ON 02/25/15 FROM SCOTT BRITT TO S. SANDIN * * * "During the review and closeout of a work package performed as part of the 'extent of condition' for the inspection activity initially described in EN #50351, a fire penetration seal was identified as failing to meet the procedure acceptance criteria. This penetration seal is located in the 2C Diesel Generator (DG) room and passes between Fire Area 2407 and 2408. "The nonconforming issue observed on the affected penetration was identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were established for the Unit 2 Areas and will remain in place until the affected barriers areas are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The extent of condition inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10032202" The licensee will inform the NRC Resident Inspector. Notified R2DO (Seymour). * * * UPDATE FROM SCOTT BRITT TO HOWIE CROUCH AT 2000 EST ON 3/4/15 * * * "During an expanded scope inspection, two deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - Small imperfections and a hole through Penetration 1Z43-H116C that passes between Fire Area 1101G (Unit 1 Reactor Building Closed Cooling Water (RBCCW) Room) and Fire Area 1006 (Unit 1 Water Analysis Room), and - Gaps in a civil/architectural joint at the top of the south wall leading from Fire Area 1006 (Unit 1 Water Analysis Room) to Fire Area 0007A (East Corridor in the Control Bldg.). "These nonconforming conditions observed for the affected penetration and fire barrier were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire area and will remain in place until the wall is repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS update report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10035730" The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Sykes). * * * UPDATE FROM SCOTT BRITT TO DANIEL MILLS AT 2047 EDT ON 3/16/15 * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - Imperfections in three penetration seals (2Z43-H037C, 2Z43-H038C, and 2Z43-H177C) located in the 2A Battery Room separating Unit 2 Fire Areas 2004 and 2005 - Imperfections in fire penetration seal 2Z43-H644C located in the U2 Water Analysis Room separating Fire Area 2006 and 0007A - Imperfections in the grout between two tiers of concrete masonry wall and at the intersection of the walls in the upper northeast corner of the U2 Water Analysis Room separating Fire Areas 2006 and 0007A "The nonconforming conditions observed for the affected penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10041392, CR 10041394, and CR 10041397" The NRC Resident Inspector will be notified. Notified R2DO (Shaeffer) * * * UPDATE FROM JOHN MITCHELL TO HOWIE CROUCH AT 1619 EDT ON 3/17/15 * * * "During an expanded scope inspection, a fire penetration seal was observed to contain imperfections that did not meet acceptance criteria. Penetration seal 1Z43H542C is located between the U1 Corridor, Fire Area 0001, and the Unit 1 AC Inverter Room, Fire Area 1008, in the Unit 1 Control Building. "The nonconforming issue observed on the affected penetration was identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until all associated non-functional fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The extent of condition inspection activity is continuing and this, and any subsequent similar condition(s) that meets the reporting requirements, will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10041766" The licensee notified the NRC Resident Inspector. Notified R2DO (Desai). * * * UPDATE FROM GUY GRIFFIS TO HOWIE CROUCH AT 1648 EDT ON 3/18/15 * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - Gap in the concrete masonry wall at penetration seal 1Z43-H547C located between the Unit 1 AC Inverter Room (Fire Area 1008) and the Unit 1 Corridor (Fire Area 0001) - Gap in the annulus around the 2 inch continuous run penetration seal located between the Unit 1 AC Inverter Room (Fire Area 1008) and the Unit 1 Corridor (Fire Area 0001) - Gap in penetration seal 1Z43-H059C located between the Unit 1 AC Inverter Room (Fire Area 1008) and the Unit 1 Corridor (Fire Area 0001) "The nonconforming conditions observed for the affected penetrations and barrier were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10042532; CR 10042530; CR 10042526" The licensee has notified the NRC Resident Inspector. Notified R2DO (Desai). * * * UPDATE FROM JOHN MITCHELL TO DANIEL MILLS AT 1814 EDT ON 3/31/15 * * * "During an expanded scope inspection, a fire wall was observed to contain a gap behind a 3 inch square plate attached to the thru-bolt anchor that did not meet acceptance criteria and caused the affected barrier to be considered nonfunctional. The affected fire barrier is located between the U2 RPS MG Set Room (Fire Area 2013) and the U2 Annunciator Room (Fire Area 2015). "The nonconforming issue observed on the affected fire barrier was identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until all associated non-functional fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The extent of condition inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10048449" The licensee will notify the NRC Resident Inspector. Notified R2DO (Walker). * * * UPDATE FROM KEN HUNTER TO VINCE KLCO ON 4/13/15 AT 1722 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - Gap around penetration 1Z43H805D located between the Unit 1 East DC Switchgear Room 1D (Fire Area 1017) and the Unit 1 Transformer Room (Fire Area 1019). - Gaps in a fire barrier around a unistrut, below penetration 1Z43H012D, that are approximately 7 deep and into the CMU core located between the Unit 1 East DC Switchgear Room 1B (Fire Area 1020) and the Unit 1 130' Elevation Control Building Working Floor Hallway (Fire Area 0014K) - Gap in the top corner of the wall, above 1Z43H842D that protrudes into the CMU approximately 7 deep located between the Unit 1 East DC Switchgear Room 1B (Fire Area 1020) and the Unit 1 130' Elevation Control Building Working Floor Hallway (Fire Area 0014K) - Two anchor bolt holes east of penetration 1Z43H810D located between the Unit 1 East DC Switchgear Room 1B (Fire Area 1020) and the Unit 1 East DC Switchgear Room 1D (Fire Area 1017) "The nonconforming conditions observed for the affected penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Heissierer). * * * UPDATE FROM GUY GRIFFIS TO CHARLES TEAL ON 04/14/15 AT 1728 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - A 1/16" wide x 4" long x 5" deep gap was identified at the top of the wall, above penetration 1Z43H646D, in the west wall in Unit 1 East 600V Switchgear Room (separating Fire Area 1017 and Fire Area 1016). - A 1/16" wide x 4" long x 7" deep gap was identified at the top of the wall, above penetration 1Z43H646D, in the east wall in the Unit 1 West 600V Switchgear Room (separating Fire Area 1016 and Fire Area 1017). - A «" wide x 2" long x 7" deep gap was identified at the top of penetration 1Z43H522D located between the Unit 1 West 600 V Switchgear Room (Fire Area 1016) and U1 East 600 V Switchgear Room (Fire Area 1017). "The nonconforming conditions observed for the affected penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10055316; CR 10055377" The licensee will notify the NRC Resident Inspector. Notified the R2DO (Bartley). * * * UPDATE FROM SCOTT BRITT TO JOHN SHOEMAKER AT 2000 EDT ON 4/16/15 * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - A 1" wide x 2" long x 7" deep gap was identified at the top of penetration 1Z43H622D in the west wall of the Unit 1 RPS MG Set Room (separating Fire Area 1013 and Fire Area 0014K). - A 1/4" wide x 1/4" long x 7" deep gap was identified near a ground wire, above penetration 1Z43H595D, at the top of the east wall of the Unit 1 East DC Switchgear Room (separating Fire Area 1020 and Fire Area 1104). - A 3" wide x 1/4" tall x 7" deep gap was identified at penetration 1Z43H617D on the south wall of the Unit 1 Working Floor (separating Fire Area 0014K and Fire Area 1013). "The nonconforming conditions observed for the affected penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10056548; CR 10056555; CR 10056582" The licensee will notify the NRC Resident Inspector. Notified the R2DO (Bartley). * * * SEE EN #50998 FOR CONTINUATION OF UPDATES * * * | 100 | 90 | 0 | 100 | 90 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-08-07
50350 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-07 09:25 | 2014-08-07 17:26 | 2014-08-07 | EMERGENCY OPERATIONS FACILITY AIR CONDITIONING OPERATING AT REDUCED CAPACITY "At 0925 [CDT] on 08/07/14, a Condition Report was initiated identifying that one of the two air conditioning condenser coil fans for the CPNPP [Comanche Peak Nuclear Power Plant] Emergency Operations Facility (EOF) air conditioner was damaged. With low outside air temperatures, the air conditioner can adequately maintain habitability of the EOF with one of the two air conditioning fans not working. However, outside air temperatures at CPNPP are forecast to reach 100 degrees F later today, and it is believed that the air conditioner will likely trip due to the increased load. With the air conditioner out of service and outside air temperatures near 100 degrees F, the EOF may no longer have the capability for protracted operation under emergency conditions. Compensatory measures are currently in place to staff and activate the Alternate EOF in the event of a declared emergency. Repair of the damaged air conditioning condenser coil fan is scheduled to be completed by the end of the day on 08/08/14. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-07
50349 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-08-06 | 2014-08-07 11:35 | 2014-08-07 | AGREEMENT STATE REPORT - LOST RADIOACTIVE GAUGE The following information was obtained from the Commonwealth of Pennsylvania via email: "Event Description: On July 18, 2014 the Department [PA Department of Environmental Protection] performed a routine license inspection and discovered that a gauge was unaccounted for. The licensee believed the gauge was transferred to their Philadelphia plant and began to check records to try and verify its location. On August 6, 2014 the licensee reported to the Department that the gauge could not be located and is considered missing. "Gauge Information: Model: Filtec FT-50B Serial Number: 2398 Isotope: Am-241 Activity: 100 mCi "Cause of the Event: Human error. No records were kept as required regarding the gauge. "Actions: The Department plans to issue a Notice of Violation and also provide assistance in locating the gauge." Pennsylvania Event Report ID No.: PA140019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-08-15
50348 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2014-08-07 07:30 | 2014-08-07 06:59 | 2014-08-07 | RADIATION MONITORING COMPUTER SYSTEM INOPERABLE DUE TO PRE-PLANNED MAINTENANCE "On August 7, 2014 at 0730 EDT, the Unit 2 Radiation Monitoring Computer System will be inoperable and unavailable due to pre-planned maintenance to implement an upgrade to the system. Alternate methods for monitoring are being utilized. The Radiation Monitor Computer System is expected to be restored to available status at approximately 2000 EDT on August 7, 2014. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii), as an event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update will be provided once the Radiation Monitoring Computer System has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE AT 1925 EDT ON 8/7/14 FROM JOHN REXRODE TO S. SANDIN * * * "The Unit 2 Radiation Monitoring Computer System has been restored to an operable status as of August 7, 2014 at 1733 EDT. "The NRC Resident Inspector has been notified." Notified R2DO (Nease). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-07
50347 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-08-06 05:16 | 2014-08-06 05:36 | 2014-08-07 | TSC HVAC AND FILTRATION REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "This is a non-emergency notification per Vogtle U1 & U2 Technical Requirements Manual (TRM) 13.13.1, Emergency Response Facilities, Action 8.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities on the TSC support systems. Alternate facilities are available to provide emergency response functions, and, actions are proceeding to return the TSC to functional status with high priority. A 10 CFR 50.54(q) evaluation has been prepared and approved for this planned maintenance activity. The NRC Resident Inspector has been notified." * * * UPDATE FROM RUDY JOHNSON TO DONALD NORWOOD AT 1132 EDT ON 8/6/14 * * * As of 1124 EDT maintenance has been completed and the TSC has been returned to service. The NRC Resident Inspector has been notified. Notified R2DO (Nease). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-06
50346 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2014-08-05 17:34 | 2014-08-05 22:20 | 2014-08-06 | AUTOMATIC REACTOR SCRAM "This notification is being provided pursuant with SAF 1.6 10CFR50.72(b)(2)(iv)(B) and SAF 1.7 10CFR50.72(b)(3)(iv)(A). "At 1734 CDT on August 5, 2014, LaSalle Unit 2 automatically scrammed due to an RPS actuation. The MSIVs isolated on a Group 1 signal, the cause is under investigation. The reactor water cleanup system isolated during the transient. The plant is stable with Reactor Pressure Control being maintained by the Reactor Core Isolation Cooling System and SRVs and level being controlled by the Low Pressure Core Spray System. The plant is planned to remain in hot shutdown pending investigation of the trip." The Unit 2 electric plant is in a normal shutdown lineup. All control rods inserted fully on the scram. Unit 1 was not affected by the Unit 2 transient. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY MICHAEL FITZPATRICK TO JEFF ROTTON AT 1650 EDT ON 8/6/2014 * * * The initial notification to the NRC stated that the reactor water cleanup system had isolated during the transient. The actual status is being corrected to state that the reactor water cleanup pump tripped during the transient. The licensee has notified the NRC Resident Inspector. Notified R3DO (Stone). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-08-05
50345 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-08-05 14:46 | 2014-08-05 20:53 | 2014-08-05 | BOTH TRAINS OF CONTROL ROOM EMERGENCY FILTRATION SYSTEM INOPERABLE "The Division 1 Control Room Emergency Filtration System (CREF) was inoperable for scheduled replacement of charcoal. During the scheduled maintenance, Division 2 CREF was placed into service. Approximately 5 minutes after startup (1446 CDT on 8/5/2014), the Division 2 CREF recirculation fan tripped off for unknown reasons. This rendered both trains of CREF inoperable. This required entry into Technical Specification TS 3.0.3. "This is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to (D) Mitigate the consequences of an accident. "At 1707 CDT on 8/5/2014, the Division 1 CREF train maintenance was completed and the Division 1 CREF was declared operable. TS 3.0.3 was exited at this time. "Investigation is in progress to determine the cause of the Division 2 CREF trip. "The control room boundary was not challenged during this time period with any change in radiation levels as plant operation was unaffected. Thus, the health and safety of the public was not affected." The licensee notified the NRC Resident Inspector and the State of Minnesota Duty Officer. | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-08-05
50344 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-08-05 | 2014-08-05 18:06 | 2014-08-06 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON FIXED GAUGE The following report was provided from the State of Texas via Email: "On August 5, 2014, the licensee notified the [Texas Department of State Health Services, Investigation Unit, Radiation Branch] Agency that it had discovered it was unable to close the shutter on a Berthold model LB300ML fixed nuclear gauge that contains a 2.5 milliCurie cobalt-60 source. The licensee stated it had experienced a loss of power on August 3, 2014, that resulted in the loss of control of the flow of molten steel. The licensee stated when it was able to get to the gauge on August 5th and discovered that some steel had spilled onto the top of the gauge's knobs and prevented shutter closure. The licensee stated that the source housing was not damaged and the source had not been compromised. The licensee also reported it has not yet been able to get to the shutter on a second gauge (same model and source) due to the steel spillage. It is anticipating the steel will be cleared within the next 1-2 days so it can make a determination on the status of the shutter on the second gauge. The gauges normally operate with the shutter in the open position. There have been no overexposures as a result of this event. Due to the location of the gauges/sources and the steel spillage, there is no risk of overexposure. The licensee stated it had already scheduled a routine service call for August 7th, for its gauges. The licensee will have the technician make needed repairs to the disabled gauge(s) while they are at the facility. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9218 * * * UPDATE FROM KAREN BLANCHARD TO JEFF ROTTON VIA EMAIL AT 1247 EDT ON 8/6/2014 * * * "On August 6, 2014, the licensee notified the Agency that it was finally able to access the second gauge, Berthold LB300ML containing 2.5 milliCurie cobalt-60 source, referred to in the initial report. The licensee reported that the shutter on this second gauge was binding (cause unknown at this time) and they were unable to close it. The gauge normally operates with the shutter in the open position. There have been no overexposures as a result of this event. Due to the location of the gauges/sources and the steel spillage, there is no risk of overexposure. The licensee will include this shutter for evaluation/repair when the service technician comes to its facility on 08/07/2014. More information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Werner) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-13
50343 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-08-05 07:47 | 2014-08-05 13:47 | 2014-08-05 | REMOVAL OF STACK HIGH RADIATION MONITOR FOR MAINTENANCE "Unit 2 high range stack radiation monitor, RM-8168, was removed from service for planned maintenance. This action is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). RM-8168 will be restored to operable status by 1800 EDT. The licensee notified the NRC Resident Inspector, State of Connecticut, and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-05
50342 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2014-05-29 18:30 | 2014-08-05 11:28 | 2014-08-12 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT The following information was received via E-mail: "The Assistant Radiation Safety Officer (ARSO) of Mistras reported to the Division of Radiation Control (DRC) that a radioactive source could not be returned to the shielded position in a radiography camera. The radiography technician failed to connect the guide tube to the stiff extension they were using to make superimposed exposures. When the technician cranked out the source, he cranked the cable past the assembly gear and could not retrieve the source. The technician then roped off the area of the incident to ensure individuals did not enter a high radiation area, and informed personnel at the refinery that an incident had occurred. The ARSO was then contacted and informed of the situation. The ARSO arrived on the scene of the incident and performed surveys near the exposure device to determine what the high and low levels of radiation were. The ARSO selected a spot where he could reach the radiography camera's crank handle that was in an area with a dose rate of 4 mR/hr. "The ARSO used a hack saw to cut the crank handle off of the guide tube. Once the crank handle was removed, the ARSO pulled the guide cable to retract the source back into the camera's shielded position. The camera was then surveyed and returned to the licensee's storage facility. No personnel involved in the incident received exposures in excess of the regulatory limits. "On May 30, 2014, at approximately 5:00 pm [MDT] the DRC inspectors arrived at the Mistras's facility. The inspectors interviewed personnel involved in the event and collected statements. The inspectors took photographs of the exposure device, collimator, and performed surveys of the camera. The inspectors confirmed that the radioactive sealed source was stopped in the camera's shielded position. "Radiography exposure device information: Model INC-100, S/N 4419." The radiography camera contains a 68 Curie Ir-192 source. The event took place at the Chevron refinery located at 2351 North/1100 West, Salt Lake City, Utah. Utah Event Report ID No.: UT140002. * * * UPDATE FROM SPENCER WICKHAM TO JOHN SHOEMAKER AT 1919 EDT ON 8/12/14 * * * The following event update was received from the Utah Department of Environmental Quality, Division of Radiation Control via email: "No personnel involved in the incident received exposures in excess of the regulatory limits. On May 30, 2014, the day after the incident, DRC inspectors interviewed personnel involved in the event and collected statements. The inspectors took photographs of the industrial radiography exposure device and performed surveys of the device. The inspectors confirmed that the radioactive sealed source was stopped in the device's shielded position." Notified R4DO (Campbell) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2014-08-13
50341 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-08-04 17:01 | 2014-08-05 00:57 | 2014-08-08 | RADWASTE BUILDING RADIATION MONITORING SAMPLE RACK DECLARED NONFUNCTIONAL "At 1701 hours PDT on August 4, 2014, the Rad Waste Building process radiation monitoring sample rack was declared nonfunctional. The cause of the equipment malfunction is under investigation. Field team assessment function is unaffected and remains available if required. "This event is being reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE FROM NICHOLAS RULLMAN TO HOWIE CROUCH AT 1501 EDT ON 8/8/14 * * * "At 1501 PDT on 8/7/14, the Rad Waste Building process radiation monitor sample rack was declared functional. "The NRC Resident Inspector has been notified." Notified R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-08-05
50340 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-08-30 | 2014-08-04 14:49 | 2014-08-04 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received via email from the State of California: "The current corporate RSO (will also to be assigned as the future RSO for this license) contacted RHB [California Radiologic Health Branch] to report incident that happened on 08/30/13. The RSO was conducting an audit of the program and learned that one of their gauges (Troxler model 3411, S/N 4089, containing 9 mCi of Cs-137 and 44 mCi of Am-241 was run over by a compactor at the Lower Butte Creek Levee Project on 08/30/13. The field technician had reported the incident to the RSO [at the time of the incident]. The rod was broken, however, the source was contained within the shielded part of the gauge assembly. The technician brought the damaged gauge back to the licensee's storage facility and it was stored there until it was picked up by PNT on July 24, 2014. The RSO failed to inform the incident to RHB within 24 hrs. and the incident was reported to RHB almost a year later. The licensee is in the process of changing the RSO to the corporate RSO. Recently, the new RSO has provided refresher training to all the gauge users. The facility will be cited for failure to report the incident per CCR 30295 (b) and 10 CFR 30.50 (b) and for failure to follow procedures." CA Report No: 072414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-08-12
50339 | 0 | MONTANA STATE UNIVERSITY |  |  |  |  | 2014-07-03 | 2014-08-04 11:57 | 2018-03-27 | MISSING NICKEL-63 SOURCE "On July 3, 2014, Montana State University's Radiation Safety Officer (RSO) went to remove the Ni-63 sealed source (14 mCi) from a Varian Model 3400, Serial #13762 (Source Serial #A1059), Gas Chromatograph/Electron Capture Detector (GC/ECD) that was in storage. The RSO is in the process of disposing of all unwanted/unused sources. Upon arriving, the RSO found that the GC/ECD was no longer in CB 28 [Chemistry/Biochemistry Room 28] as it was three months earlier during the semi-annual sealed source leak test inspection. None of the individuals occupying the space had any idea what happened to the device. "An email, including a picture of the device was sent to all personnel in both the transferor (Land Resources/Environmental Science) and transferee (Chemistry/Biochemistry) departments. In addition a lab by lab search of all chemistry labs was conducted by the RSO. As of this date, the GC/ECD has not been found. The RSO is in the process of continuing the search on the rest of the campus. "Ni-63 is a low energy (67 keV) beta emitter. The beta energy necessary to penetrate the skin is 70 keV. Therefore, it is very unlikely for anyone to receive a dose from it unless it was broken open and injected, ingested, or inhaled. "Corrective actions: 1. Two other unused GC/ECDs were picked up by the RSO and taken to his secure lab for removal of the Ni-63 sources to prevent the incident from happening again. 2. The three remaining GC/ECDs are being required to be put on active protocols. 3. During the search for the missing GC/ECD, another GC/ECD was revealed to be in another lab which has not been registered with the RSO. Therefore, the RSO has requested that all Principal Investigators (PIs) report all radiation producing equipment to him immediately. 4. The RSO is also currently meeting with each PI using radioactive material to verify they do not have the missing GC/ECD nor are there any other unreported radiation producing devices on campus. 5. The RSO has also placed a notice on all GC/ECDs stating, the RSO must be contacted prior to relocating this device. 6. All personnel in labs containing radiation producing equipment will be trained to report to the RSO any relocation of these devices. 7. The RSO has been placed under disciplinary action by the Director of the Office of Research Compliance. 8. The RSO will be conducting a search of the remainder of the MSU campus to locate the missing GC." * * * UPDATE FROM NICHOLAS CHILDS TO DONALD NORWOOD AT 1351 on 3/27/2018 EDT * * * "In August of 2014, Montana State University's (MSU's) previous RSO [Radiation Safety Officer] reported that a Ni-63 sealed source with a serial number of A1059 (15 mCi on 4/1/2004) was missing. The current RSO, as of October 2014, conducted a thorough review of MSU's sealed source inventory and located the source A1059. "The source was leak tested with results indicating less than 0.005 microCi of removable contamination and subsequently added to MSU's sealed source inventory. The source was removed from MSU through the Source Consolidation And Threat Reduction Program (SCATR) on July 1, 2015." Notified R4DO (Gaddy). Notified via E-mail: ILTAB (Whitney) and NMSS Events Notifications. Notified via fax: Canada. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-03-27
50338 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-08-03 15:49 | 2014-08-03 20:01 | 2014-08-03 | OFFSITE NOTIFICATION DUE TO INADVERTENT PAGER NOTIFICATION SYSTEM MESSAGE "This event is being reported per 50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' "At 1549 CDT, August 3, 2014, the National Weather Service inadvertently issued a Civil Emergency Message over their pager notification system during preparations for an upcoming [Cooper Nuclear Station] Emergency Drill. A follow up message was issued by the National Weather Service at 1601 CDT stating that the Civil Emergency Message was a test message and should be disregarded. "A media/press release is planned." The licensee has notified the NRC Resident Inspector, State, and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-08-03
50337 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-08-01 21:42 | 2014-08-02 03:39 | 2014-08-02 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE DUE TO TEST RETURN VALVE LEAKAGE "River Bend Station personnel declared the High Pressure Core Spray system inoperable at 2142 [CDT] on 8/1/2014. "The High Pressure Core Spray (HPCS) system at River Bend Station includes a test return line to the Condensate Storage Tank (CST). The test return line is isolated by two motor operated valves (MOVs) with both having a safety function to close on an ECCS [Emergency Core Cooling System] initiation signal to ensure that injection flow is directed to the reactor vessel. While the HPCS pump is normally aligned to the CST, the credited source of water for the pump is the suppression pool. Accordingly, the pump suction is realigned to the suppression pool on low level in the CST or when suppression pool level rises to a certain point. Station personnel identified leakage past the test return valves to the CST. In evaluating this condition, engineering personnel noted that the observed leakage past the two MOVs might be sufficient to deplete suppression pool inventory such that it would not be capable of performing its specified function for the duration of the 30 day mission time. The issue of concern is that once HPCS is aligned to the suppression pool post-LOCA, pool inventory would be lost to the CST through the leaking test return valves. "Based on that concern, the HPCS pump suction valve from the suppression pool was disabled in the closed position to preserve pool inventory. This action caused the HPCS system to be declared inoperable at 2142 [CDT]. This action results in a 14 day shutdown LCO and is reportable to the NRC in accordance with 10 CFR 50.72(b)(3)(v)(D). "The HPCS pump remains available with its suction aligned to the CST. Assuming normal makeup water supplies are available, the HPCS system can be realigned to the suppression pool if necessary. "This condition continues to be evaluated and rework options are being developed. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-08-02
50336 | 0 | CRANE NUCLEAR, INC. |  |  |  |  | 2014-08-01 | 2014-08-01 17:00 | 2014-08-01 | PART 21 REPORT - SAFETY-RELATED VALVES ASSEMBLED WITH NON-SAFETY RELATED LEVERS Crane did not provide safety related levers, for manual type safety valves, on a recent shipment. Crane was advised by their customer that valves provided for AP1000 PV10 Scopes (VDS 101 and VDS 150) should have had safety-related levers. Crane believes the only affected valves are those that have been provided on the AP 1000 project. If you have questions please contact; Rosalie Nava, Director Safety and Quality Phone 630-226-4940 Fax 630-226-4646 Email RNAVA@cranevs.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-08-01
50335 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-09-12 | 2014-08-01 11:22 | 2014-12-12 | AGREEMENT STATE REPORT - ALPHATRON IONIZATION VACUUM GAUGE FOUND IN LOAD OF SCRAP METAL The following information was obtained from the Commonwealth of Massachusetts via email: "On 9/12/12, a scrap metal load shipped by ECO Recycling of Brockton, MA, was rejected by Metal Recycling of Providence, RI, for triggering the site's radiation detectors. The highest vehicle radiation reading was < 0.2 mR/hr. The vehicle returned to Brockton where, on 9/13/12, one device (described as an Alphatron ionization vacuum gauge containing approximately 500 microCuries Radium-226 manufactured by National Resources of Newton, MA approximately 40 years ago) was located and removed from the load by an independent consultant and isolated in secure storage on-site in Brockton for future disposition. The consultant indicated < 0.5 mR/hr readings in accessible areas near the storage container. The original owner not determined. The device continues to be secured at Brockton site as of 8/1/14. "The Agency [Massachusetts Radiation Control Program] considers this event to still be OPEN." Event Docket #: 19-1408 * * * UPDATE AT 1441 EDT ON 9/2/2014 FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "9/12/14 Update - Agency conducted on-site inspection 8/1/14. No significant change to previously reported information. Agency [Massachusetts Radiation Control Program] review ongoing. "The Agency considers this matter to still be OPEN." Notified the R1DO (Ferdas) and FSME Event Resources (via e-mail). * * * UPDATE ON 10/7/14 AT 1512 EDT FROM ANTHONY CARPENITO TO DONG PARK * * * The following was received from the Commonwealth of Massachusetts via email: "ECO Recycling in process of soliciting / collecting quotes from waste brokers for proper disposal. "Agency review ongoing. Agency considers this event to still be OPEN." Notified R1DO (Bower) and FSME Events Resource via email. * * * UPDATE ON 11/6/14 AT 1151 EDT FROM ANTHONY CARPENITO TO DONG PARK * * * The following was received from the Commonwealth of Massachusetts via email: "ECO Recycling continuing process of soliciting / collecting quotes from waste brokers for proper disposal. "Agency review ongoing. Agency considers this event to still be OPEN." Notified R1DO (Gray), FSME Events Resource, and NMSS Events Resource via email. * * * UPDATE ON 12/12/14 FROM ANTHONY CARPENITO TO HOWIE CROUCH VIA EMAIL ON 12/12/14 AT 1424 EST * * * "ECO Recycling arranged for source to be removed by registered waste broker. Upon Agency [State of Massachusetts] contact and inquiry, waste broker confirmed source pick-up scheduled for third week in January 2015. Agency considers this event to still be OPEN. Agency will close this event when source is removed from Brockton site." Notified R1DO (Rogge) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-08-11
50334 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-31 17:29 | 2014-07-31 23:49 | 2014-09-24 | UNANALYZED CONDITION "On 07/31/2014 at 1729 PDT, Diablo Canyon Power Plant (DCPP) identified an unanalyzed condition involving the three class 1E 4160 volt buses on Unit 1 and on Unit 2. Following a postulated main steam line High Energy Line Break (HELB) in the Turbine Building, steam could enter the 4160 volt bus rooms through ventilation ducts that exhaust to the turbine deck where the steam lines are located. New analysis identified that the relative humidity (RH) of the 4160 volt bus rooms could reach 100%, which exceeds the design RH used in the analyses for the protective devices in the room. The high-humidity could possibly prevent the protective devices from operating as intended and could therefore result in the unavailability of the 4160 volt buses to supply power to engineered safety feature systems. "This concern is being reported as an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B) and as a condition that could have prevented fulfillment of a safety function per 10 CFR 50.72(b)(3)(v). "Compensatory measures were taken to isolate the ventilation ducts between the 4160 volt bus rooms and the turbine deck, thereby preventing steam entry into the 4160 volt bus rooms, assuring the protective devices would not be subjected to conditions exceeding the design RH. With this compensatory measure all three 4160 buses on each unit are assured of performing their expected design function following the postulated main steam line break. "This concern did not result in any adverse affect on the health and safety of the public. "The licensee informed the NRC Resident Inspector." In addition to the 10 CFR sections listed in the header of this event notification, the licensee is also reporting this under 10 CFR 50.72(b)(3)(v)(D). * * * RETRACTION RECEIVED FROM BOB KLINE TO JOHN SHOEMAKER AT 1839 EDT ON 09/24/14 * * * "Diablo Canyon Power Plant is retracting this event notification based on the following: "Subsequent to the identification of this event, PG&E conducted additional analysis and testing to support a past operability evaluation. Testing and analysis was completed successfully, demonstrating that the full population of associated components would perform their design safety function in 100% relative humidity conditions during a postulated high energy line break. "Based on these analysis and testing results, PG&E concludes that the associated equipment remained operable, and did not represent an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B) or a condition that could have prevented fulfillment of a safety function per 10 CFR 50.72(b)(3)(v). Therefore, PG&E retracts its notification of 7/31/2014. "The licensee has notified the NRC Resident Inspector." Notified the R4DO (Drake). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2014-08-01
50333 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-07-31 14:30 | 2014-07-31 19:02 | 2014-07-31 | TRITIUM AND COBALT DETECTED IN GROUND WATER MONITORING WELL "Voluntary notification per the NEI Groundwater Protection Initiative. "On July 31, 2014, Callaway Plant received results of a sample from a new ground water monitoring well. The sample was taken on July 25, 2014. The sample results indicated a tritium concentration of approximately 1.6 E6 picocuries/liter and a Co-60 concentration of approximately 12 picocuries/liter. "The new monitoring well is located within the plant's property and is adjacent to a manhole where the plant's discharge piping joins with the cooling tower blowdown piping. Both the plant discharge piping and the cooling tower discharge piping are buried. "Releases from the plant discharge line have been suspended. A backup sample taken on July 25, 2014, will be sent to a lab for analysis. Another sample will be taken on August 1, 2014. "There is no effect on drinking water, and therefore, no dose to the general public or plant staff." The licensee will notify the Missouri State Department of Natural Resources and Callaway County officials. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-31
50332 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-07-29 | 2014-07-31 16:22 | 2014-07-31 | AGREEMENT STATE REPORT - MOISTURE/DENSITY GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received from the State of Arizona via email: "This first notice constitutes early notice of events of possible safety or public interest significance. The information is as initially received without verification or evaluation, and is basically all that is known by the [State of Arizona] Agency Staff at this time. "On July 29, 2014, during an inspection, the inspectors noted that a moisture density gauge had a shutter mechanism that was stuck open with the handle in the closed position. The gauge is a Troxler Model 3440, Serial Number 29505, containing 10 millicuries of Cesium-137 and 50 millicuries of Am-241. The licensee is scheduling to have a service company come out to service the gauge. "The investigation into this event is ongoing pending the licensee servicing the gauge." Arizona State Report Number: 14-018. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-08-08
50331 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2014-06-04 | 2014-07-31 15:51 | 2014-07-31 | PART 21 INTERIM REPORT - TEMPERATURE SWITCH SET POINTS OUT OF CALIBRATION On June 19, 2014, United Controls International (UCI) issued a Return Material Request to Florida Power and Light, Turkey Point. It was discovered that a tool used in the verification of the temperature switch set points was out of calibration during the impact analysis of the out of tolerance condition these switches were identified as needing to be returned for adjustment and re-testing. At this time, UCI is unable to complete our evaluation into the possible effects the out-of-calibration tool had on the temperature switches. Florida Power and Light has not returned the items to UCI for evaluation and rework. June 4, 2014, is the date on which the information of such defect or failure to comply was obtained. If you have any questions or wish to discuss this matter or this report, please contact: Jim Garrison Engineering Manager, Seismic and Equipment Qualification jgarrison@unitedcontrols.com 770-496-1406 X 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-07-31
50330 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-07-30 | 2014-07-31 13:07 | 2014-07-31 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE The following report was received from the California Department of Public Health via email: "[The licensee reported to the State of California that a] patient [was] receiving Y-90 treatment to the right lobe of liver with Theraspheres. (10CFR35.1000). The prescribed dose was 100-150 Gray, actual dose received was 63.4 Gray. The targeting vessel was 'flowing slowly' causing Theraspheres to 'settle out' prior to reaching target. Preliminary findings suggest that the underdose was due to the physical condition of patient, not through any fault of the medical physicist or licensee. "No adverse outcomes are expected for the patient. Medical physicist and physicians [are] evaluating whether or not retreatment is necessary." California Report Number: 073014. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-08-08
50329 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-07-31 08:25 | 2014-07-31 11:08 | 2014-07-31 | HIGH RANGE STACK MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE At 0825 EDT, Millstone Station Unit 2 removed the Stack High Range Radiation Monitor RM-8168 from service for planned maintenance. Maintenance was completed and operability was restored at 0937 EDT. The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 83 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-31
50328 | 0 | FROEHLING & ROBERTSON, INC. |  |  |  |  | 2014-07-30 14:00 | 2014-07-31 10:26 | 2014-07-31 | DAMAGED MOISTURE/DENSITY GAUGE A moisture/density gauge was damaged by Lullr construction equipment at the Civil Affairs Battalion Complex on Fort Bragg Military Base. The source rod was not damaged and the damage was mostly to the electronics portion. The RSO performed surveys of the gauge and no abnormal dose rates were observed. The gauge is a Troxler Model 3430 moisture/density gauge and typically contains 8 mCi of Cs-137 and 40 mCi of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-08-08
50327 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-07-31 07:20 | 2014-07-31 08:21 | 2014-07-31 | SERVICE WATER RADIATION MONITOR OUT OF SERVICE FOR MAINTENANCE "Planned preventative maintenance on the Service Water Radiation Monitor (SWRM) strainer will remove the SWRM from service. As a result, this represents a loss of emergency assessment capability since the SWRM is used to assess NUE and ALERT thresholds. The activity is expected to last 6 hours. During this time, the site will be monitoring alternate indications to detect leakage and the Chemistry Department will perform grab samples as required to ensure the ability to detect NUE levels of radioactivity in a timely manner and protect the health and safety of the public. "The NRC Resident Inspector has been notified prior to removing the SWRM from service." | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-31
50326 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-07-30 16:07 | 2014-07-30 18:05 | 2014-07-30 | IMPROPER CONTROL OF SAFEGUARDS INFORMATION Safeguards information was scanned and emailed to one Exelon employee without proper safeguards controls. The recipient immediately notified his supervisor and subsequently deleted the email. The electronic information is being purged from the LAN and Network data. The licensee will notify the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-07-30
50325 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-07-29 | 2014-07-30 13:07 | 2014-07-30 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following was received via facsimile: "The licensee reported on July 29, 2014, that a portable density gauge had been damaged by a compaction roller at a temporary job site in Loudoun County, Virginia. The gauge was a CPN Model MC with a 10 millicurie Cesium-137 source and a 50 millicurie Americium-241 source. Investigation by the licensee's radiation safety officer indicated there was no damage to the gauge casing and that the sources were in their shields when the accident occurred. The control rod for the Cesium source was slightly bent as a result of the accident, but both sources remained in their shielded positions. The gauge was returned to the licensee's office and a leak test wipe was sent for analysis. The licensee plans to transport the gauge to an authorized repair facility after the leak test results are received. A written report is required within 30 days." Virginia Event Report ID Number: VA-2014-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-08-07
50324 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-07-30 09:40 | 2014-07-30 13:27 | 2014-07-30 | ULTIMATE HEAT SINK IN AN UNANALYZED CONDITION "On July 30, 2014, at [0940 CDT], with the plant operating at 100% power, a review of an engineering analysis of the ultimate heat sink (UHS) determined that the UHS had been in an unanalyzed condition that degraded plant safety. This condition was the result of a design basis deficiency for the UHS that did not account for the adverse effects of system leakage on compliance with the 30-day inventory required by Regulatory Guide 1.27. The system design basis requires that 30-day inventory be maintained, with the assumption that no replenishment of the UHS occurs for the entire duration of the postulated event. "In support of the development of the engineering analysis, compensatory measures have been implemented which provide adequate assurance that the UHS will perform its design safety function. Corrective actions to restore full compliance with design basis requirements are in development. "This event is being reported in accordance with 10 CFR 50.72 (b)(3)(ii) as an unanalyzed condition that degraded the safety function of the UHS." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-07-30
50323 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-07-29 | 2014-07-30 12:06 | 2014-07-30 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received from the State of Texas by facsimile: "On July 29, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee that a Humboldt Scientific Inc. model 5001 moisture density gauge containing a 10 millicurie Cesium-137 and a 40 millicurie Americium-241 source was damaged at a field site. The technician had placed the device at a sample location and extended the cesium source into the inspection hole. The area had been compacted and the technician did not believe there was any heavy equipment in the area he was working. While waiting for the results of the sample, the technician received an email. The technician needed his glasses to read the email so he walked 70 feet to his truck to get his glasses. While at the truck, the device was run over by a soil compactor (steam roller). The technician went to the gauge and restricted access to the area. He then contacted his Radiation Safety Officer (RSO). The licensee's RSO contacted a service provider (SP) who responded with the RSO to the scene. The device case was severely damaged, but the licensee was able to return the Cesium source to the shielded position and secure it in position. The SP's technician verified the Americium source was still in the device. The SP's technician surveyed the device and did not find any abnormal dose rates. The SP took the damaged device to their facility for disposal. No individual received any significant additional exposure due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-07
50322 | 0 | BLEVINS ASPHALT CONSTRUCTION CO. |  |  |  |  | 2014-07-30 08:30 | 2014-07-30 11:50 | 2014-07-30 | DAMAGED MOISTURE/DENSITY GAUGE With the moisture/density gauge still on the ground after performing a standard count, the licensee Radiation Safety Officer backed over the gauge with his pickup truck. The source was not exposed at the time and the source remained shielded. Damage noted to the gauge was a broken shaft that sets the depth of test which is also part of the handle along with some surface scarring to the gauge housing. The gauge was checked with a survey meter for leakage from the sources. At one meter the survey meter reading was less than 0.2 mrem/hr which is comparable to a non-damaged gauge. A leak test wipe was also performed and sent to Humboldt Mfg. for measurement. The gauge was transported and placed in its secure storage location until a determination has been made on how repairs will be accomplished. The gauge is a Humboldt Model 5001 moisture/density gauge containing 10 mCi Cs-137 and 40 mCi Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-08-07
50321 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-07-28 | 2014-07-30 10:48 | 2014-08-29 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION DUE TO TREATMENT GIVEN TO WRONG PATIENT The following information was obtained from the state of Texas via email: "On July 30, 2014, the Agency was notified by the licensee that a patient had received a portion of a treatment intended for a different patient. The licensee's Risk Compliance Officer (RCO) stated two patients had arrived for treatment. Both patients were female of similar size. Both were to receive treatment to the brain, one patient to the right side and the other to the left side. The treatment head frame had been placed on both patients. It was decided that patient two would be treated first. This information was not provided to the individual entering the program into the treatment system so the program for patient one was entered into the treatment system. Patient two was placed on the treatment table and the treatment started. About two minutes into the treatment, a physician reviewing the treatment realized the wrong plan for the patient was being used and halted the treatment. "The licensee determined the patient received 3.7 gray to 0.5 cc of brain tissue during the treatment. The patient and the patient's physician were notified of the error. The RCO stated the patient's doctor evaluated the event and stated the patient should not experience any adverse effects from the exposure. The patient was later treated using the correct treatment plan. "The licensee has implemented several corrective actions as a result of the event. They include adding a second time out prior to treatment and requiring multiple staff to identify. "The device was a Leksell Gamma System Model 24001 containing about 1800 curies of cobalt-60. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9217 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1508 EDT ON 8/29/2014 * * * The following information was received via E-mail: "On July 30, 2014, the Agency [Texas Department of Health Services] was notified by the licensee that a patient had received a portion of a gamma knife treatment intended for a different patient. The incident was investigated at the facility and confirmed that a patient received a portion of a fractional treatment dose intended for another patient. The treatment time was for 2.68 minutes with a calculated total dose of 3.5 gray to the centerpoint maximum with 50% to the isodose lines at 1.75 gray to the wrong patient. The error occurred due to rescheduling patient one who had a much longer treatment time than patient two. The health physicist and radiation oncologist lacked communication with nursing staff regarding the switch to treat patient two before patient one. This communication error along with a lack of patient identification played a major role in the unintended treatment process. The facility completed a root cause analysis of the problem and self-reported the incident. Corrective actions have been implemented to include new policies and procedures incorporating better scheduling, patient identification practices to include 'time outs' during the treatment process and limiting distractions during the treatment procedure. No violations were cited." Per the Texas Department of State Health Services, this event was not an Abnormal Occurrence as initially reported on 7/30/2014. Notified R4DO (Pick) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-07
50320 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-29 10:40 | 2014-07-30 08:16 | 2014-07-30 | FITNESS FOR DUTY POLICY VIOLATION "A non-licensed employee contractor foreman had a confirmed positive test result for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. "This notification is being made under 10 CFR 26.719 (b)(2)(ii), significant FFD policy violations or programmatic failures, as a twenty-four (24) hour report. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2014-07-30
50319 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-07-29 09:00 | 2014-07-29 15:53 | 2014-07-29 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL PACKAGE ON CONTACT RADIATION READING ABOVE LIMIT The following information was provided by the State of Tennessee via email: "[State of Tennessee Division of Radiological Health] was notified on 7/29/2014 by the Radiation Safety Officer of Energy Solutions [Oakridge, TN] that a package (55 gallon drum) [on flat bed truck] was delivered above the 200 millirem an hour non-exclusive use limit. This drum was surveyed with an ion chamber and it was determined to be 300 millirem an hour. Tennessee Division of Radiological Health inspector also surveyed this drum and found it to be 300 millirem an hour on contact." TN Event ID Number: TN-14-147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-08-06
50318 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2014-06-25 | 2014-07-29 11:59 | 2014-07-29 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received from the State of Washington via email: "On June 25, 2014 at 1600 PDT, a CPN portable gauge (model MC1-DR, SN: MD00405577) containing 50 mCi of Am-241/Be and 10 mCi of Cs-137 was damaged by a front end loader. An AllWest employee was [performing] an in-place moisture/density test in a parking lot at the URM warehouse project in Spokane, Washington. A front end loader was brought into the same parking lot to work on another part of the project. The AllWest employee walked 20 feet away from the gauge to direct the loader operator. The loader made a hard right turn while backing up to do a line up for a proof roll. The AllWest employee realized the loader was traveling in the direction of the portable gauge. The AllWest employee tried to get the loader operators attention by yelling and waving his hands. The operator noticed and stopped the loader just as the tire bumped the portable gauge. The employee looked at the gauge and did not notice any obvious damage until the loader was moved away. The AllWest employee noticed the gauge guide tube was slightly bent. The employee was able to retract the source rod (which was at 2 inch depth at the time of the accident) and verified the slide plate was in the safe position. The loader was checked for contamination and none was found. The AllWest employee notified the office manager at the time of the accident and was told to return to the office since there was no major damage to the gauge. The office manager contacted the company RSO to report the incident and to report that a leak test would be performed before the gauge would be sent to CPN/Instrotek for repairs. The leak test showed no sign of leaking sources. The gauge was sent to CPN/Instrotek on July 1, 2014 and on July 14, 2014, AllWest was notified that the source rod was also slightly bent and could not be repaired and needed to be disposed of." Incident Number: WA-14-030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-08-06
50317 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-07-26 | 2014-07-29 08:16 | 2014-07-29 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following information was obtained from the state of Texas via email: "On July 28, 2014, the Agency [Texas Department of State Health Services] received notice that a radiography source retraction failure had occurred at a temporary field site [Houston] on July 26, 2014. The guide tube had separated at the crimp between the flexible portion and the fitting to the camera. The flexible portion had pushed out when the source was cranked out. The source was retrieved by manually pulling the drive cable back through the camera. The guide tube was removed from service and replaced. The camera was a Sentinel 880 Delta with about 40 curies of selenium-75. No overexposures resulted from this event. An investigation into this event is ongoing. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident #: I-9215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-08-06
50316 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-29 05:00 | 2014-07-29 05:05 | 2014-07-29 | TECHNICAL SUPPORT CENTER HVAC REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. Planned maintenance activities are being performed on 07/29/2014 to the Technical Support Center (TSC) HVAC. "The work includes performance of breaker inspections and corrective/preventative AHU [Air Handling Unit] maintenance. The planned work activity duration is approximately 48 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The NRC Resident Inspector has been notified. "This condition does not affect the health and safety of the public or station employees." The licensee will be notifying state and local authorities. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-29
50315 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2014-07-28 01:18 | 2014-07-28 05:06 | 2014-07-28 | LOSS OF METEOROLOGICAL DATA TO THE SITE "At 0118 [EDT] on 7/28/2014, meteorological data was lost to both Salem and Hope Creek. At the time, there were storms in the vicinity which [were] the apparent cause of the temporary loss of data. Both Salem and Hope Creek lost wind direction information. This event is being reported under 10CFR50.72(b)(3)(xiii), major loss of emergency assessment capabilities. "At 0130, meteorological data was restored to the control rooms. Plant operations at Hope Creek and both Salem Units 1 and 2 were not affected. All three units remain at full power. "The licensees notified the NRC Resident Inspectors." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-28
50314 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-07-27 14:09 | 2014-07-27 15:22 | 2014-07-27 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEED PUMP DURING TESTING "VEGP [Vogtle Electric Generation Plant] Unit One was at 100 percent power, with a Main Feed Pump (MFP) Turbine A trip mechanism test in-progress, when MFP A Trip alarm was received in the Main Control Room. Control Room crew identified MFP A speed and steam generator levels lowering and initiated a manual reactor trip. All control rods fully inserted and nothing unusual was noted. Auxiliary feed water and feedwater isolation actuated as expected. The unit is currently stable in MODE 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the MFP A trip and determine restart criteria and time of restart." The unit is in a normal shutdown electric plant lineup. No effect on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-07-27
50313 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-07-26 14:11 | 2014-07-26 15:14 | 2014-07-26 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO TURBINE DRIVEN AFW PUMP FAILURE "At 1458 [EDT] on 7/26/14, the [Technical Specification] 72 hour action statement for TDAFWP [Turbine Driven Auxiliary Feedwater Pump] inoperable expires (LCO 3.7.1.1 Action C). Per Technical Specification Action Statement, plant is required to be in HOT STANDBY by 2058 on 7/26/14 (6 hours) and in HOT SHUTDOWN by 0858 on 7/27/14 (additional 12 hours). MPS [Millstone Power Station] Unit 2 shutdown (using normal procedures) has commenced at 1411 when troubleshooting and repairs were unable to determine and correct cause of low pump recirculation flow. Additional activities will continue to correct issue." Unit 3 is not affected by this event. All safety-related systems and equipment required for safe plant shutdown are available. The licensee notified the NRC Resident Inspector, Waterford Dispatch, and State of Connecticut Department of Energy and Environmental Protection. | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-07-26
50312 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-07-26 04:00 | 2014-07-26 10:44 | 2014-07-26 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "[A Honeywell] employee with dust in his right eye reported to the on-site dispensary this morning. The plant nurse administered first aid. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination present was on the employee's work boots, 331,597 dpm/100 sq.cm. The plant nurse allowed the employee to return to work following treatment. The employee remained inside the Restricted Area over the entire course of the event." The licensee will notify the NRC Resident Inspector and Region 2 (David Hartland via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-07-26
50311 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-06-25 | 2014-07-25 10:09 | 2014-07-25 | AGREEMENT STATE REPORT - STOLEN GENERAL LICENSED MATERIAL The following information was provided by the State of Colorado via email: On July 21, 2014, the State of Colorado was made aware of a stolen generally licensed device. The general license holder was contacted on July 24, 2014 to gather additional information. The general license owner, Rocky Mountain Recycling was planning to perform a demonstration for a company in Dallas, Oregon. During the night of June 25, 2014, the analyzer was stolen from a vehicle parked overnight in Dallas, Oregon. A police report for the stolen material was filed in the city of Dallas, Oregon. The device manufacturer is Thermo Niton, model XLp, serial number 6199, containing 30 milliCuries of Am-241. The investigation is ongoing. No report was made to the Oregon Radiation Protection Services. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-08-04
50310 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2014-07-25 11:29 | 2014-07-25 14:02 | 2014-07-26 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO A SAFETY INJECTION VALVE DEFECT "On July 25th, 2014 at 1129 EDT, during investigation of a small leak inside Saint Lucie Unit 2 containment, a defect was identified on a valve (V3811, Safety Injection Tank 281 Outlet Vent Valve). This valve is within the Q-Group A (ASME Class 1 equivalent) boundary of the safety injection line. The leak is currently isolated from the reactor coolant system by a Technical Specification credited isolation check valve. The affected Safety Injection Tank has been declared inoperable and the unit has entered 24 hour shutdown [Technical Specification] action statement 3.5.1.b. Unit shutdown is currently being planned for repair of the flaw. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(A)." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JOHN REXRODE TO VINCE KLCO AT 0053 EDT ON 7/26/14 * * * "On July 26, 2014 at 0002 EDT, Saint Lucie Unit 2 commenced shutdown to repair the identified leak. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(A) and 10 CFR 50.72(b)(2)(i). "The NRC Resident Inspector has been notified." Unit 2 current power is 88% at 0105 EDT and expect to trip the unit at approximately 0400 EDT. Notified the R2DO (Musser). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | PLANT S/D REQD BY TS |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(2)(i) |  |  | 0 | 2014-07-25
50309 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2014-07-25 09:50 | 2014-07-25 13:24 | 2014-07-25 | TECHNICAL SPECIFICATION VIOLATION DUE TO CONTROL ROOM STAFFING "This morning around 9:45 a.m. (CDT), a reportable occurrence under Section 1.28.f of the NSC [Nuclear Science Center] Technical Specifications was documented at the Texas A&M University Nuclear Science Center (NRC License No. R-83). The incident involved leaving the control room unstaffed by a licensed operator (Section 6.1.3.a.2 of the NSC Technical Specifications) for approximately 2.5 minutes while the 1 MW TRlGA reactor was operating at full power. "The text below presents a brief description of the event: "On the morning of July 25, 2014, during steady state operation at 1 MW [full power], Reactor Operator (RO) trainee [Deleted] was in the control room, along with a Senior Reactor Operator on Duty (SRO) [Deleted] and electronic technician [Deleted]. Senior Reactor Operator [Deleted] and Reactor Operator (RO) [Deleted] were signed in as the operators on duty during the duration of the incident. "Duty SRO and RO were elsewhere in the facility performing Operations tasks, and RO (Licensed) [Deleted] had remained in the Control Room to fulfill the requirement set forth in TS (Staffing) 6.1.3.a.2. At approximately 0948, NSC Radiation Safety Officer (RSO) [Deleted] entered the control room and requested the use of RO [Deleted] key to access a building on site. RO offered to open the building and left [control room] leaving RO trainee and electronic technician alone in the control room. At 0950, RO trainee noted that there was no licensed reactor operator in the control room. RO Trainee paged RO over the intercom and shutdown the reactor via manual SCRAM. "Manager of Reactor Operations [also SRO] heard the reactor SCRAM from his office above the control room and went to the control room to investigate. [Duty] SRO was notified and immediately returned to the control room. It was determined by SROs that during the 2.5 minutes that RO was absent from the control room, the requirements outlined in Technical Specification 6.1.3.a.2 were not fulfilled. NSC Director was informed of the incident and NSC Form 590 (Unscheduled Scram Recovery Form) was filled out after the unscheduled shutdown. Manager of Reactor Operations authorized the restart of the reactor. NSC Director began implementation of Reportable Occurrence reporting procedures according to Technical Specification 1.28.f." Licensee is initiating an internal review to identify and correct any practices and/or procedures that may have systematically contributed to the environment that created this situation. Other corrective actions include the internal suspension of one reactor operator's license privileges pending satisfactory retraining. The unit response during and after the scram was normal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | TX | NPR | [5 empty] | 0 | 2014-07-25
50308 | 0 | KAW VALLEY ENGINEERING, INC. |  |  |  |  | 2014-07-24 10:00 | 2014-07-25 09:30 | 2014-07-25 | LOST TROXLER MOISTURE/DENSITY GAUGE While working at a jobsite on the Fort Riley, Kansas federal reservation, the technician had just finished the standard count on a Troxler moisture/density gauge when he received a telephone call to go to another job site for a meeting. The technician placed the gauge back in its case but did not shut the case or lock the case and left it on the tailgate of the truck. When the technician arrived at the second jobsite, an individual approached the technician and told him that he had observed a yellow case fall off the back of the truck near the Camp Forsythe fire station. The technician immediately went back to the fire station. By the time he arrived, fire department personnel had already secured the case with the gauge inside. The technician estimates that the gauge was out of his possession for approximately 8 - 10 minutes. A leak test was performed with no leakage noted and sent to Troxler for further analysis. The gauge will remain out of use until leak results are received from Troxler. The gauge is a Troxler model 3430 moisture/density gauge containing 9 mCi Cs-137 and 44 mCi Am-241/Be. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | KS | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-08-04
50307 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2014-07-24 23:15 | 2014-07-24 23:41 | 2014-07-25 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "At 2315 EDT on July 24th, 2014, CCNPP [Calvert Cliffs Nuclear Power Plant] U1 identified RCS [Reactor Coolant System] pressure boundary leakage from the instrument line to 1-PDT-123A, 11A reactor coolant pump differential pressure transmitter. Technical Specification 3.4.13, Action B was entered and requires that the unit be placed in Mode 3 within 6 hours and Mode 5 within 36 hours. [CCNPP has] initiated plant shutdown in accordance with this Technical Specification. Therefore, this is reportable under 10 CFR 50.72(b)(2)(i) Plant Shutdown Required by Technical Specifications. This is also reportable under 50.72(B)(3)(ii)(A) as a material defect in the primary coolant system that cannot be found acceptable under ASME Section XI, IWB-3600 or ASME Section XI, Table IWB-3410-1." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JAY GAINES TO VINCE KLCO AT 0320 EDT ON 7/25/14 * * * The licensee reduced reactor power to 10 percent and entered containment. The pressure boundary leak was isolated and the licensee exited the Technical Specification 3.4.13, Action B. The Technical Specification required shutdown was terminated. The licensee is making preparation to increase power to full load. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2014-07-25
50306 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-07-24 16:04 | 2014-07-24 19:43 | 2014-07-24 | OFFSITE NOTIFICATION DUE TO DECEASED AMERICAN CROCODILE "This 4-hour Non-Emergency notification to the NRC is being made based on a notification to another government agency per 10CFR50.72(b)(2)(xi). "On July 24, 2014 at 16:04 [EDT], the control room was notified of a deceased American Crocodile inside the intake well. Based on visual evidence of no physical injury or trauma, the crocodile's death was not caused by plant operations. The Federal Fish and Wildlife Service and the Florida Fish and Wildlife Conservation Commission (FWC) were notified." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-24
50305 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-07-24 12:13 | 2014-07-24 15:38 | 2014-07-24 | OFFSITE NOTIFICATION DUE TO INADVERTENT MESSAGE TRANSMITTED VIA EMERGENCY RESPONSE SIREN "This event is being reported per 10CFR50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' During troubleshooting activities, a pre-recorded message was inadvertently transmitted from one of eight speakers associated with an emergency response siren. At 1213 CDT, Nemaha County Officials were informed that the message transmission was a spurious actuation. A media/press release is planned." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-24
50304 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2010-12-01 | 2014-07-24 13:32 | 2014-07-24 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following was received from the Tennessee Division of Radiological Health via email: "During a routine radioactive materials inspection of GEOServices LLC, a Tennessee Division of Radiological Health inspector found a portable moisture/density gauge, Troxler model 3401-B, containing Cs-137 (8 mCi) and Am-241/Be (40 mCi) that had been struck by a tractor at a construction site located somewhere in Knox County TN. The accident occurred in the month of December 2010. The RSO of GEOServices did not contact DRH about the accident. The RSO did not perform any surveys on the damaged moisture/density gauge. The RSO packaged the damaged moisture/density gauge and returned it to GEOServices' licensed storage location. Once the device was discovered by Tennessee Div. of Radiological Health, surveys were performed. Surveys indicated that the sources were not damaged and were not leaking. The device was packaged by the RSO and returned to Troxler for disposal." Tennessee Incident Number: TN-14-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-08-01
50303 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2014-07-24 08:00 | 2014-07-24 07:44 | 2014-07-24 | RADIATION MONITORING COMPUTER SYSTEM UNAVAILABLE DUE TO PRE-PLANNED MAINTENANCE "On July 24, 2014 at 0800 EDT, the Unit 2 Radiation Monitoring Computer System will be inoperable and unavailable due to pre-planned maintenance to implement an upgrade to the system. Alternate methods for monitoring are being utilized. The Radiation Monitor Computer System is expected to be restored to available status at approximately 1700 EDT on July 24, 2014. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii), as an event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update will be provided once the Radiation Monitoring Computer System has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATED PROVIDED BY TIM KUDO TO JEFF ROTTON AT 1708 EDT ON 7/24/2014 * * * "The Unit 2 Radiation Monitoring Computer System has been restored to an operable status as of July 24, 2014 at 1650 EDT. The NRC Resident Inspector has been notified." Notified R2DO(Musser) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-24
50302 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2014-07-23 20:27 | 2014-07-23 22:48 | 2014-07-23 | COMMON SITE TEMPORARY LOSS OF METEOROLOGICAL DATA "At 2027 [EDT] on 7/23/2014, meteorological data was lost to both Salem and Hope Creek. At the time, there were storms in the vicinity which are the apparent cause of the temporary loss of data. Both Salem and Hope Creek lost wind direction information. This event is being reported under 10CFR50.72(b)(3)(xiii), major loss of emergency assessment capabilities. "At 2036 [EDT], meteorological data was restored to the control rooms. Plant operations at Hope Creek and both Salem Units 1 and 2 were not affected. All three units remain at full power. "The licensees notified the NRC Resident Inspectors." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-23
50301 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-23 19:30 | 2014-07-23 21:32 | 2014-07-23 | UNUSUAL EVENT DECLARED BASED ON SHOTS FIRED IN THE OWNER CONTROLLED AREA "At 1943 CDT on 7/23/14, Braidwood Station declared Unusual Event HU1 due to gunshots fired within the Owner Controlled area (OCA). This was a security condition without a Hostile Action. Both Units remain in Mode 1, 100% reactor power throughout the event. "Local Law enforcement was contacted and investigated. Security stood down from the Security Condition at 1956 CDT." The Control Room was informed at 1930 CDT by Security of fourteen (14) gunshots heard inside the OCA. The licensee informed State and local agencies and the NRC Resident Inspector. Notified other FEDS (FEMA Ops Center, DHS NICC Watch Officer, DHS SWO) and (Nuclear SSA, FEMA NWC) via email. * * * UPDATE AT 2311 EDT FROM JOE CONQUEST TO S. SANDIN * * * "Braidwood Station Terminated an Unusual Event, HU1 at 2134 CDT. Local Law Enforcement Agency called an 'All Clear' and station security restored the normal security posture at 1956 CDT." The licensee informed State and local agencies and the NRC Resident Inspector. Notified R3DO (Orth), NRR (Lund) and IRD (Gott) via email. Notified other FEDS (FEMA Ops Center, DHS NICC Watch Officer, DHS SWO, Nuclear SSA, FEMA NWC) via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-07-23
50300 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2014-07-21 20:30 | 2014-07-23 18:45 | 2014-07-24 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RADIOGRAPHER The following information was received from the State of Washington via email: "At 2030 PDT on July 21, 2014 a Level 2 radiographer doing radiography for QualSpec at the Tesoro Anacortes Refinery in Washington was potentially over exposed to radiation. The individual was conducting an examination in the Catalytic Reformer Unit #10 on 3/4 inch piping on line #L-V6657. The individual noticed the survey meter he had with him was off the 10 Mr/hr scale. He immediately returned to the crank and noticed the source was still out, hence he cranked the source back in. The individual checked his pocket dosimeter and it was also off scale. He then shut down the job and contacted the RSO. An estimated calculated dose was approximately 7 rem, however, his TLD was sent in for emergency processing on Tuesday, July 22, 2014, to determine the actual dose. More information to come including equipment, activity, etc. "Incident Number: WA-14-028" The State of Washington will investigate and has categorized this incident as an Abnormal Occurrence. * * *UPDATE PROVIDED BY STEPHEN MATTHEWS TO JEFF ROTTON VIA EMAIL AT 1751 EDT ON 07/24/2014 * * * "The radiographer approached the source/collimater without cranking the source in. He also did not look at his survey meter during the approach to the source. After arriving at the source (within 2-3 feet) he noticed his survey meter was pegged on the 10 mR/hr scale. The dose on the radiographer's TLD was later determined to be 1.6 rem. The radiographer stated that he did not hear his alarming rate meter due to the noise level where he was working. This was also agreed on by the Tesoro NDE Official. The assistant radiographer was approximately 50 feet away in a lower area looking up at the operation as well as the immediate area. The radiographer's survey meter was an NDS ND2000, serial 21940, calibrated on 6-14-14; pocket dosimeter was an Arrowtech w138, serial 097093, calibrated 4-14-14; and his alarm ratemeter was an NDS RA500, serial N82947, calibrated 5-14-14." The radiography camera was a QSA Global model number: A424-9, serial number 16141C containing a 84.6 Curie Ir-192 source. Corrective Actions: Personnel received additional training to include lessons learned regarding forgetting to crank the source in, and forgetting to watch the survey meter while approaching the source area. Notified R4DO (Miller), FSME Daytime Officer (McIntosh), NSIR (Milligan), and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-07-31
50299 | 0 | SOR INC. |  |  |  |  | 2014-07-16 | 2014-07-23 15:15 | 2015-04-02 | PART 21 REPORT - POTENTIALLY DEFECTIVE PRESSURE & TEMPERATURE SWITCHES The following information was originally received in NRC Region IV on July 16, 2014 via email. Relevant portions of the submittal are provided below without graphs, tables or pictures. "SOR is a supplier of basic components to the nuclear power industry. The components of concern for this notification are SOR nuclear qualified Pressure and Temperature switches with TA housings manufactured from 2004 through 2009. "The defect being reported is a potential out of tolerance condition concerning the machined sealing surface for an environmental seal on the SOR nuclear TA housing. Other switches with a similar defect have the potential to not meet their intended safety function. "Summary: SOR Inc. began a 10CFR21 evaluation on 6/4/14 upon receipt of three SOR pressure switches, model number 5TA-B45-U8-C1A-JJTTNQ (SN's 041100627, 041100628, and 041100629). These were returned from Entergy Nuclear Vermont Yankee (VY) due to inspections which questioned the suitability of the sealing surfaces on the face of the housings where the cover O-ring seals. "The product evaluation was concluded on 6/24/14 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. If the switch housing has an inadequate machined sealing surface, the potential exists for steam permeation into the switch housing during accident conditions. This could result in an increase in set point as well as allow moisture into the housing potentially causing electrical consequences such as current leakage or a short. It is anticipated that the above noted condition represents a small percentage of the total number of housings from this batch of castings. Also, the potential risk is thought to be small due to a second redundant seal on the cover. This condition is being reported as a conservative measure. "Evaluation: There are 2 (redundant) environmental seals on the cover of the nuclear TA housing. One O-ring seals on the undercut of the cover threads (151 O-ring). This seal is not in question and is not part of this evaluation. The other O-ring seals between the face of the enclosure and the O-ring groove on the cover (042 O-ring). This is the seal that is the subject of this evaluation. "Redundant O-ring seals are used on the SOR 'TA' cover to minimize steam permeation into the housing during LOCA or HELB conditions. The consequences of permeation are that it can result in an increase in the set point and also allow moisture into the housing which could have electrical consequences. The returned switches have a suspect sealing surface on the face of the housing where one of the two O-rings (the 042 O-ring) is intended to seal. For the purposes of this Part 21 evaluation, consideration needs to be given to whether this suspect sealing surface could result in increased permeation into the switch enclosure. "Switches #041100627 and 041100628 both have an area on the face of the housing where the casting did not have sufficient material for cleanup when the housing was machined. This area was characterized by use of the SOR CMM and measuring the area where the O-ring is expected to seal. "Switch #041100629 was different from #041100627 and 041100628 in that it had one small indentation in the sealing surface which was immeasurable but does not meet surface finish requirements. "The TA housings on the returned switches are clearly out of tolerance. It is SOR's position that the environmental seals on any switch with a similar defect has the potential to not meet its' intended safety function. . . "Evaluation of Previous Shipments: SOR has validated shipments for a quantity of 56 pressure and temperature switches with the subject TA housing. "Potentially affected customers/utilities include: TVA/Watts Bar, TVA/Browns Ferry, TVA/Sequoyah, Entergy Nuclear/Vermont Yankee, Entergy Operations/River Bend, Southern California Edison, Third Qinshan Nuclear/QSNPP-3-A (TQNPC), Fairbanks Morse Engine, STP Nuclear Operating Co., Hydro Quebec /Gentilly II, Progress Energy/Shearon Harris, Control Components Inc./Korea Hydro Nuclear Shin-Kori & Wolsong, Control Components Inc./KHPN Shin Kori 3 & 4, Korea Hydro & Nuclear/KHPN Yonggwang NPP #5, Konan Engineering/Yonggwang Nuclear, and First Energy/Davis-Besse Nuclear. (Total Potentially Affected = 56. "Root Cause: The returned TA housing castings did not meet print and therefore did not allow enough material for cleanup of the machined sealing surface. "Permanent Corrective Action: SOR internal documentation is being changed to require 100% inspection of the raw casting height. Also, the 1/8 [inch] minimum finish dimension is being added to the housing machining drawings. "Action by Nuclear Power Plant: SOR recommends that the application for each switch noted in the above table be reviewed to determine if it is being used in a LOCA or HELB application. If so, SOR recommends an inspection to visually check for an adequate sealing surface of the housing . This inspection is also recommended for switches that have not yet been installed. The minimum required sealing surface is 1/8 [inch] (0.125 [inch]). After inspection, all units should have the 042 and 151 O-rings replaced if the units do not exhibit the deviation. "SOR will send replacement O-rings at no charge upon request. If units are found that do not meet the acceptance criteria, they will be replaced free of charge by SOR. Contact SOR Director of Customer Service, Greg Barber for the replacements: "Greg Barber "913-956-3059 "gbarber@sorinc.com" * * * UPDATE FROM MELANIE DIRKS TO VINCE KLCO ON 4/2/15 AT 1421 EDT * * * The following information was excerpted from a facsimile: Korea Hydro Nuclear power plants were added to include Shin-Kori 1 & 2; Shin Wolsong 1 & 2. Notified the Part 21 Reactors Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-23
50298 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-07-22 15:00 | 2014-07-23 13:35 | 2014-07-25 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE STOLEN FROM BACK OF A TRUCK The following information was received from the State of Arizona via email: "At approximately 1830 MST on July 22, 2014, the Agency [Arizona Radiation Regulatory Agency] was informed that the licensee had a Troxler Model 3430, SN 35843, portable moisture density gauge stolen from the back of a truck. The theft occurred at approximately 1500 MST. The gauge was locked in a metal box fastened to the bed of the truck which was parked unattended at the Fry's parking lot. The gauge contains 10 mCi of Cesium-137 and 40 mCi Am-241:Be. "Phoenix Police Department [Maryvale] is investigating and has issued report number 20141264003. "The Agency continues to look for the source. "The states of CA, NV, CO, UT, and NM, Mexico, U.S. NRC and FBI are being notified of this event." * * * UPDATE FROM AUBREY GODWIN TO VINCE KLCO AT 1135 EDT ON 7/25/14 * * * Clarification provided that police department is Phoenix (Maryvale). Address of the incident is 4320 West McDowell Road, Phoenix, AZ 85009. Notified R4DO (Miller), FSME and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-07-31
50297 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-07-23 07:48 | 2014-07-23 09:07 | 2014-07-23 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On Wednesday, July 23 at 0748 CDT, the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) Team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service for approximately 2 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "NRC Regional Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-23
50296 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-07-22 13:43 | 2014-07-22 21:36 | 2014-09-02 | DIESEL GENERATOR FOR HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE DURING SURVEILLANCE TESTING "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During the conduct of the Unit 2 Division 3 High Pressure Core Spray (HPCS) Diesel Generator (DG) surveillance test, one of 2 Cooling Water Outlet Valves failed to automatically open. The Division 3 Diesel is supplied by two redundant trains of cooling water one from each Service Water Divisional Header. Although the redundant cooling water supply was fully available and supplied adequate cooling to the diesel generator, the DG was at reduced margin to have adequate cooling water supply, if required during a loss of offsite power. Due to this loss of margin and inoperable condition, it has been determined that this failure could potentially affect the safety function of this system, and is being reported as an 8 hour ENS notification." The licensee has attributed the failure to high resistance in a relay which is currently being replaced. This places Unit 2 in the Technical Specification Action Statement 3.8.1, which requires restoration of Diesel Generator within 72 hours or commence a Reactor Shutdown. All other ECCS Systems have been verified operable. The licensee informed the NRC Resident Inspector and will inform the State of New York. * * * RETRACTION AT 1940 EDT ON 9/2/2014 FROM ANTHONY PETRELLI TO MARK ABRAMOVITZ * * * "This update retracts Event Notification #50296, which reported an event or condition that could have potentially prevented fulfillment of a Safety Function needed to mitigate the consequences of an accident. Upon further review, it was determined that the ability of the HPCS system (single supported train) remained operable and capable of performing its safety function as evaluated by the NMP Unit 2 Safety Function Determination Process (TS 5.5.11). "The NRC Resident Inspector has been notified." Notified the R1DO (Ferdas). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-07-22
50295 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-06-26 | 2014-07-22 18:55 | 2014-07-22 | AGREEMENT STATE REPORT INVOLVING AN UNINTENDED DOSE TO A FETUS On 6/26/14 a 23 year old female patient received 100 mCi of I-131 for a thyroid ablation procedure. Prior to treatment, she tested negative for pregnancy on 6/25/14. Subsequent to the procedure, her physician requested a re-test which confirmed that she was pregnant. The estimated date of conception is 6/23/14. The RSO calculated an estimated dose of 25 Rad to the fetus. This incident was reported to the Florida Bureau of Radiation on 7/22/14. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-07-30
50294 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-07-22 06:35 | 2014-07-22 16:57 | 2014-07-28 | RADIATION MONITORING SAMPLE RACK DECLARED NON-FUNCTIONAL "At 0635 hours PDT on July 22, 2014, Turbine Building Exhaust Air Radiation Indicating Switch (TEA-RIS-13) and the Turbine Building Process Radiation Monitoring Sample Rack (TEA-SR-26) were declared non-functional. The cause of the malfunction is under investigation. Compensatory measures have been implemented to obtain radiation readings from the associated effluent release pathway. Field team assessment function was unaffected and remains available. "This event is being reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM DUANE SALSBURY TO DONALD NORWOOD AT 2018 EDT ON 7/28/2014 * * * "At 1351 PDT on 7/28/2014, Turbine Building Exhaust Air Radiation Indicating Switch (TES-RIS-13) and Turbine Building Process Radiation Monitoring Sample Rack (TES-SR-26) were declared functional. "The NRC Resident Inspector has been notified." Notified R4DO (O'Keefe). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-22
50293 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-07-22 04:14 | 2014-07-22 07:53 | 2014-07-22 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 0414 [EDT on 7/22/2014], VC Summer Nuclear Station automatically tripped due to decreasing water level in the 'C' Steam Generator. The trip occurred when valve XVB-09210 WI System Condensate Bypass Valve failed to open as required while the station was removing the Condensate Polishing System during startup. The Condensate Polishing System is used to purify and filter the condensate from the non-nuclear, secondary side of the plant. This valve failure caused low level in the Deaerator Storage Tank, which consequently tripped all feedwater pumps. This loss of feedwater led to Lo-Lo Steam Generator level in the 'C' Steam Generator. All Emergency Feedwater pumps automatically started on Lo-Lo Steam Generator level and all control rods inserted fully. The Steam Generator levels recovered quickly. "Presently the plant is in Mode 3. Decay heat is being removed by dumping steam to the condenser. A station response team is actively investigating the cause of the event. "The NRC Resident Inspector has been notified." The licensee will notify the State and local governments. | 0 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-07-22
50292 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-07-21 10:03 | 2014-07-21 17:30 | 2014-07-21 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2014-07-21
50291 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2014-06-26 | 2014-07-21 16:35 | 2014-07-21 | PART 21 REPORT - INCORRECT VALVE SOLENOIDS PROVIDED The following is a synopsis of information received via facsimile: Brunswick Nuclear Plant ordered 10 (ten) 120VAC/60Hz valve solenoids on two purchase orders from Fisher Controls International LLC. In February, 2014, Fisher shipped six 125VDC solenoids to Brunswick. All six of those solenoids were identified as non-conforming prior to installation in the plant. The remaining 4 solenoids at Fisher are on a shipping hold. For technical questions or concerns contact: George Baitinger, Manager, Quality, Fisher Controls International LLC, 301 South 1st Ave, Marshalltown, IA 50158, Fax: (641) 754--2854, Phone: (641) 754-2026. Fisher Information Notice: FIN 2014-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-21
50290 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2014-07-21 08:00 | 2014-07-21 08:09 | 2014-07-21 | RADIATION MONITORING COMPUTER SYSTEM INOPERABLE FOR PLANNED MAINTENANCE "On July 21, 2014 at 0800 EDT, the Unit 2 Radiation Monitoring Computer System will be inoperable and unavailable due to pre-planned maintenance to implement an upgrade to the system. Alternate methods for monitoring are being utilized. The Radiation Monitor Computer System is expected to be restored to available status at approximately 1900 EDT on July 21, 2014. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii), as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update will be provided once the Radiation Monitoring Computer System has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM CARLOS SANTOS TO DONALD NORWOOD AT 2038 EDT ON 7/21/2014 * * * "The Unit 2 Radiation Monitoring Computer System is restored to an available status as of July 21, 2014 at 1955 EDT. The NRC Resident Inspector has been notified." Notified R2DO (McCoy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-21
50289 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-07-21 05:25 | 2014-07-21 06:42 | 2014-07-22 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 0525 [CDT] on Monday, July 21, 2014, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system was removed from service for planned preventative maintenance activities on the TSC air handling unit, air compressor units, and TSC air filtration unit. During the maintenance, the TSC Ventilation was shut down. The TSC air filtration fan and dampers are non-functional, rendering the TSC HVAC accident mode nonfunctional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 48 hours. Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning (EP) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with station procedures. "The NRC Resident Inspector has been notified." * * * UPDATE FROM MATT KERCHENFAUT TO DONALD NORWOOD AT 2035 EDT ON 7/22/2014 * * * "At 1540 CDT on July 22, 2014, Dresden TSC Ventilation was restored. The Dresden TSC Ventilation is functional at this time. "The NRC Resident Inspector has been notified." Notified R3DO (Orth). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-21
50288 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2014-07-20 19:53 | 2014-07-20 21:12 | 2014-07-20 | SMALL KEOWEE HYDROELECTRIC STATION OIL DISCHARGED TO THE KEOWEE RIVER "On 7/20/2014, at 1700 hours EDT, a spill of approximately five (5) gallons of Teresstic 68 lube oil was identified in the Keowee Hydroelectric Station (KHS) tailrace. Teresstic 68 oil is used at the station as an equipment lubricant. The KHS tailrace feeds into the Keowee River that leads into Lake Hartwell. The estimated area of the oil sheen is approximately 30x50 feet and a cleanup response is currently in progress. The cause of the spill was attributed to a faulty oil float switch in the KHS unwatering pump that allowed the oil to spill into the KHS tailrace (Keowee River). "South Carolina Department of Health and Environmental Control (SCDHEC) and the National Response Center were notified of the spill on 7/20/2014 at approximately 2002 and 1953 hours [EDT] respectively. "This event was determined to be reportable pursuant to 10CFR50.72(b)(2)(xi) due to the notifications to the SCDHEC and the National Response Center. "The licensee notified the NRC Resident Inspector. "Initial Safety Significance: The oil did not contain any plant produced radiological material and while contained, poses no safety risk with respect to the health and safety of the public. "Corrective Action(s): The oil spill sheen is isolated to an approximate 30x50 foot area of the Keowee River. Because the KHS is currently not operating, the water spill area is stagnant, i.e., there is little or no movement of the water containing the oil sheen. The source of the leak has been contained and an investigation is underway to determine the actual cause of the spill. There was no impact on plant operations. The event was entered into the station's corrective action program." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-20
50287 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-07-20 14:54 | 2014-07-20 20:02 | 2014-08-08 | ULTIMATE HEAT SINK TEMPERATURE EXCEEDED TECHNICAL SPECIFICATION LIMIT "At 1454 EDT on 20 July 2014, Turkey Point Units 3 and 4 entered the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink (UHS). The action was entered because UHS temperature exceeded the limit of 100 degrees F due to a natural event. This report is in accordance with 10CFR50.72(b)(3)(v)(B) because UHS capability to remove residual heat is impacted. At 1800 EDT the NRC verbally approved a natural event Notice of Enforcement Discretion (NOED) which allows the ultimate heat sink temperature to exceed 100 degrees F up to 103 degrees F. Unit power levels have been maintained at Unit 3 100% and Unit 4 95%. "The NRC Resident Inspector has been notified." * * * UPDATE FROM CHRIS TRENT TO DANIEL MILLS AT 2058 EDT ON 7/26/2014 * * * "At 2046 on 7/20/14, Turkey Point Units 3 and 4 exited the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink, when the ultimate heat sink (UHS) temperature decreased below the TS limit of 100 degrees F. "At 1604 on 7/26/14, Turkey Point Units 3 and 4 entered the Action for TS 3.7.4, Ultimate Heat Sink. The action was entered because UHS temperature exceeded the limit of 100 degrees F. This report is in accordance with 10 CFR 50.72(b)(3)(v)(B) because UHS capability to remove residual heat is impacted. Turkey Point is currently complying with NOED No. 14-2-001, which allows a temporary maximum UHS temperature of 103 degrees F. "The NRC Resident Inspector was notified." At 2058 on 7/26/14 the UHS average temperature was 100.3 degrees F and the peak temperature was 100.5 degrees F. Unit 4 is currently operating at 75% power in anticipation of elevated intake temperature in the next several days. Notified R2DO (Musser) * * * UPDATE FROM JOSE VASQUEZ TO DANIEL MILLS AT 1913 EDT ON 7/27/2014 * * * "At 2102 on 7/26/14, Turkey Point Units 3 and 4 exited the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink, when the ultimate heat sink (UHS) temperature decreased below the TS limit of 100 degrees F. "At 1602 on 7/27/14, Turkey Point Units 3 and 4 entered the Action for TS 3.7.4, Ultimate Heat Sink. The action was entered because UHS temperature exceeded the limit of 100 degrees F. This report is in accordance with 10 CFR 50.72(b)(3)(v)(B) because UHS capability to remove residual heat is impacted. Turkey Point is currently complying with NOED No. 14-2-001, which allows a temporary maximum UHS temperature of 103 degrees F. "The NRC Resident Inspector was notified." At 1913 on 7/27/14 the UHS average temperature was 101.1 degrees F and the peak temperature was 101.3 degrees F. Units 3 and 4 are currently operating at 75% power in anticipation of elevated intake temperature in the next several days. Notified R2DO (Musser) * * *UPDATE PROVIDED BY CHRISTOPHER TRENT TO JEFF ROTTON AT 2103 EDT ON 07/28/2014 * * * "At 2212 on 7/27/14, Turkey Point Units 3 and 4 exited the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink, which was entered at 1602 on 7/27/14, when the ultimate heat sink (UHS) temperature decreased below the TS limit of 100 degrees F. "At 1445 on 7/28/14, Turkey Point Units 3 and 4 entered the Action for TS 3.7.4, Ultimate Heat Sink. The action was entered because UHS temperature exceeded the limit of 100 degrees F. This report is in accordance with 10 CFR 50.72(b)(3)(v)(B) because UHS capability to remove residual heat is impacted. Turkey Point is currently complying with NOED No. 14-2-001, which allows a temporary maximum UHS temperature of 103 degrees F. "At 1946 on 7/28/14, UHS temperature decreased below the TS limit of 100 degrees F and Turkey Point Units 3 and 4 exited the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink. 'The NRC Resident Inspector was notified." Peak UHS temperature reached on 7/28/2014 was 101.1 degrees F. Units 3 and 4 are currently operating at 75 percent power in anticipation of continued elevated intake temperatures. Notified R2DO (Musser) * * * UPDATE FROM ADRIAN GONZALEZ TO HOWIE CROUCH AT 2113 EDT ON 8/7/14 * * * "At 1455 on 08/07/14, Turkey Point Units 3 and 4 entered the Action for TS 3/4.7.4, Ultimate Heat Sink. The action was entered because UHS temperature exceeded the limit of 100 degrees F. This report is in accordance with 10 CFR 50.72(b)(3)(v)(B) because UHS capability to remove residual heat is impacted. Turkey Point is currently complying with NOED No. 14-2-001, which allows a temporary maximum UHS temperature of 103 degrees F. "The NRC Resident lnspector was notified." UHS temperature was at 100.4 F at the time of the notification. Notified R2DO (Nease). * * * UPDATE FROM ADRIAN GONZALEZ TO S. SANDIN AT 1900 EDT ON 8/8/14 * * * "At 1445 EDT on 08/08/14 Turkey Point Units 3 and 4 entered Action for TS 3/4.7.4, Ultimate Heat Sink. The action was entered because UHS temperature exceeded the limit of 100 degrees F. On 8/08/14 at 1556 EDT Turkey Point Units 3 and 4 received Amendment No. 261 to Renewed Facility Operating License No. DPR-31 and Amendment No. 256 to Renewed Facility Operating License No. DPR-41 for the Turkey Point Nuclear Generating Unit Nos. 3 and 4 and exited the Action for TS 3/4.7 .4, Ultimate Heat Sink." The licensee informed the NRC Resident Inspector. UHS temperature was at 101.24 F at the time of the notification. Notified R2DO (Nease). | 100 | 95 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2014-07-20
50286 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-07-17 20:50 | 2014-07-18 15:23 | 2014-07-18 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISORY CONTRACT EMPLOYEE A non-licensed supervisory contract employee had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The individual's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2014-07-18
50285 | 0 | ITT ENGINEERING VALVES, LLC |  |  |  |  | 2014-07-18 | 2014-07-18 09:30 | 2014-07-18 | PART 21 REPORT - IMPROPER IRRADIATION OF SAMPLES FOR BALL VALVE SEATS AND DIAPHRAGMS The following information was received from ITT Engineered Valves, LLC by facsimile: ITT is submitting this report based on an NRC Inspection finding at Steris Isometric Services in Whippany, NJ, where samples may have received 3-9% less than the minimum target dosage specified during testing. "ITT is in the process of determining how best to approach our customers with this information, and how to work with them to determine whether a defect as defined by 10 CFR Part 21 does exist. To that end, we are reviewing the impact of the variability on all projects that required radiated samples, particularly ball valve seats and diaphragms including the entire Ml diaphragm product line, and what effect if any this will have on our results and conclusions. We are also reviewing any ongoing projects with radiated samples from Steris, and making the necessary adjustments." Name and address of the individuals informing the Commission: S. T. Donohue ITT Engineered Valves, LLC 33 Centerville Road Lancaster, PA 17603 stephen.donohue@itt.com Senior Principal Engineer (717) 509-2200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-18
50284 | 0 | VELAN INC. |  |  |  |  | 2014-07-17 | 2014-07-18 08:28 | 2014-07-28 | PART 21 REPORT - NOTIFICATION OF DEFECTS ON 2 INCH BONNETS The following information was received from Velan Inc by facsimile: "SUBJECT NOTIFICATION: 2 INCH BONNETS, VELAN PART NUMBER 8943-014 "On May 16, 2014 [Velan] received notification from Westinghouse Electric Co. (WES) that 2 bonnets supplied by Velan to WES in early 2013 for installation at Comanche Peak exhibited the following issues: - The bonnets were intended to be exact replacements for the bonnets built to drawing E73-020 Rev E (OEM is Velan) except for material change to SA-182 FXM-19. Bonnets were visually inspected when received at site. No issues were noted; both bonnets appeared to be identical. - In April 2013, Unit 1 bonnet was installed in valve 1-8109. No issues were noted with the installation. The new bonnet was put into service. -In April 2014, Unit 2 installation was scheduled to begin. After the disassembly of the valve, the old and new bonnets were compared. It was noted that the backseat dimensions are different between the 2 bonnets. The increase in backseat diameter on the new bonnet would cause the stem to not backseat. The decision was made to re-install the old bonnet and send the new bonnet back to the OEM, Velan. "On June 10, 2014 the bonnet, identified in the last bullet above, arrived at Velan Plant 2. "The review by the [Velan] Evaluation Committee was finalized on July 17 and concluded that: -Four similar bonnets were delivered to WES on three different occasions in 1988 and early 90's -The stem head diameter is 01.312 [inches] so, when opening, the stem may pass through the stem bore of the bonnet and not seat on the backseat. -On opening, if the limit switches on the actuator do not function, the stem may enter the packing chamber. The packing may be deformed and a leak may develop. Stem travel is limited by the disc contacting the bonnet and/or the end of the stem thread stopping on the actuator drive nut. -If the actuator and packing flange nuts are removed, there is the potential for the stem to blow out of the valve. -The packing chamber depth will result in more packing being installed in the valve. This may result in a higher packing friction load on the actuator when operating and reduce the actuator margin. -The smaller packing chamber will not affect safety. A different diameter packing may be required. The gland bushing diameter (01.744 inches) is less than the packing chamber diameter and will work correctly. "These bonnets were fabricated against ASME Sec. Ill for installation in Class 2 systems. Not knowing exactly the nature of the application we cannot determine if the [above identified] potential issues may pose a significant safety hazard and therefore we have informed WES by way of a similar letter." * * * UPDATE PROVIDED FROM VICTOR APOSTOLESCU TO JEFF ROTTON AT 1435 EDT ON 07/28/2014 * * * Reporting Organization/Supplier who made the original event report on 07/18/2014 reported to the NRC Operations Center that the Event Notification posted has a typographical error regarding the Velan, Inc part number described in the report. The original documentation provided was concerning Velan Part Number 8943-014 which was mistakenly transcribed as 6943-014 in the original report. This error has been corrected in this updated report. Notified R4DO (Okeefe) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-18
50283 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-07-17 07:30 | 2014-07-17 16:48 | 2014-07-23 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE The following information was received via E-mail: "The RSO for Byer Geotechnical contacted RHB [Radiologic Health Branch] to report that an employee working at a construction site at Colorado Blvd. and Glacier St. in Eagle Rock (a suburb of Los Angeles) had a CPN model MC 1DRP gauge (s/n MD50902828) stolen from the back of his pick-up truck around 0730 PDT. This moisture density gauge contains 370 mBq (10 mCi) of Cs-137 and 1.85 Gbq ( 50 mCi) of Am-241:Be. The security chains attaching the gauge transportation case to the vehicle were cut. The employee notified his RSO asap, who contacted RHB. RHB instructed the RSO to contact the local police dept. to make a report and also place an ad in a local newspaper for return of the gauge with a monetary reward. More information will be obtained from the employee via a written report of the incident." Notified Mexico via E-mail. * * * UPDATE AT 1431 EDT ON 07/23/14 FROM KATHLEEN HARKNESS TO S. SANDIN VIA EMAIL * * * "This CPN gauge was recovered by the licensee on 7/22/2014 at 1500 PDT from the driveway at the same location that it was stolen from. "The RSO notified the RHB inspector on 7/23/2014 at 1000 PDT by phone. "The transportation box's latch was damaged and the padlock missing, but the gauge itself appeared intact. The RSO will be bringing it to a CPN service provider for repair of the case and inspection of the gauge prior to placing it back into service. California will continue to investigate." Notified R4DO (Miller), FSME Events Resource and ILTAB (email) and Mexico (fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-07-25
50282 | -1 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-15 09:42 | 2014-07-15 17:57 | 2014-08-01 | UNANALYZED CONDITION - LOW CONTAINMENT SPRAY FLOW RATE "At 0942 [CDT] on 7/15/2014, the 2A Containment Spray chemical additive flow was found out of tolerance low during surveillance testing. This resulted in an unanalyzed condition in that insufficient chemical additive flow might have resulted in lower than assumed containment spray pH values during past periods. "Based on the above, this is being reported in accordance with 10CFR50.72(b)(3)(ii)(B). Actions are in progress to restore the 2A Containment Spray chemical additive flow to within tolerance. The 2B Containment Spray system is operable per Technical Specification 3.6.6 and is capable of providing required chemical additive flow. "The required flow is 18 to 67 gallons per minute (gpm), however, the measured flow was 17.96 gpm. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM JAMES PETTY TO JOHN SHOEMAKER AT 1729 EDT ON 8/1/14 * * * "The purpose of this report is to retract ENS report #50282 (July 15, 2014). This ENS report was made for the 2A Containment Spray chemical additive flow which was found out of tolerance low during surveillance testing. At the time of reporting, it was concluded that this was an unanalyzed condition in that insufficient chemical additive flow may have resulted in lower than assumed containment spray pH values during past periods. This was reported in accordance with 10CFR50.72(b)(3)(11)(B) as an unanalyzed condition that significantly degrades plant safety. "On Wednesday, July 29, 2014, Braidwood Generating Station concluded that the prior ENS notification could be retracted based on the completion of Engineering Change 398884, 'Evaluation Of 2A CS NaOH Spray Additive Test Results And Discussion of IRs 1682209 and 1683413.' "The Engineering Change concluded that the approval of the alternate source term (AST) license amendment resulted in the elimination of a minimum containment spray (CS) spray pH value. The current containment release analysis does not credit the addition of sodium hydroxide (NaOH) to CS spray for fission product removal from the containment atmosphere. The long-term retention of captured fission products in the sump water assumes the sump water pH is greater than 7. This is established by the transfer of the containment spray additive tank (CSAT) contents to the sump during CS system operation. To transfer the maximum CSAT inventory to the sump within 8 hours, a minimum NaOH eductor flow of approximately 10 gpm is required. The minimum NaOH injection flow for the 2A CS eductor system exceeded 10 gpm so the eductor injection flows meet the criteria to transfer CSAT inventory to the containment recirculation sump within the expected minimum CS system operating time. The out of tolerance flow values recorded at the time of the initial ENS notification are acceptable. "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Lara). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-07-15
50281 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-07-15 09:40 | 2014-07-15 13:20 | 2014-07-15 | STACK HIGH RANGE RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE The Unit 2 stack high range radiation monitor (RM 8169) was removed from service at 0940 EDT for planned maintenance. The monitor was returned to service at 1119 EDT after the completion of maintenance. The licensee notified the NRC Resident Inspector, the Connecticut Department of Energy and Environmental Protection, and the city of Waterford for this event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-15
50280 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2014-07-11 14:00 | 2014-07-14 15:47 | 2014-07-14 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the Commonwealth of Kentucky via email: "KY RHB [Kentucky Radiation Health Branch] was notified by telephone on 7/11/14 by Todd Ramkey, Corporate RSO at Schnabel Engineering Inc. in Glenn Allen, VA, of the fact that a CPN model MC-1 portable moisture/density gauge had been run over and crushed at a coal slurry impoundment belonging to Long Fork Coal Company in Hatfield, KY. The CPN gauge contained 10 mCi of Cs-137 and 50 mCi of Am-241/Be. "Initial surveys performed by the licensee with a RadAlert GM survey instrument indicated the sources were not breached and that there was no contamination on the ground where the incident occurred or on the bulldozer involved. The shattered pieces of the device, including the two sources, were packaged on-site by the licensee into a 55 gallon drum in accordance with guidance provided by the radiation safety staff at Instro-Tek in Raleigh, NC, labeled appropriately and shipped back to the offices of Geo/Environmental Associates, Inc. in Knoxville, TN in a company owned vehicle. The shipment was met by a representative of the TN Division of Radiological Health where follow-on surveys and contamination smears were taken. They also instructed the licensee to send leak test wipes to Instro-Tek for expedited analysis and instructed the licensee to send personal monitoring for those involved in for analysis. "A telephone call to RHB from the CRSO at Schnabel on 7/14/14 at approximately 1500 said indicated leak test results from Instro-Tek were less than the 185 Bq limit and that no breach of the sources had occurred. RHB gave the CRSO permission to release the control of the site and the equipment at Long Fork Coal based on these negative leak test results. The CRSO at Schnabel indicated that hardcopies of the leak test results would be provided to both RHB and TN Div. Rad Health as well as the results of personal monitoring for those involved in the incident including transportation of the gauge back to Knoxville. Reporting criteria defined in 902 KAR 100:040, Section 15(2)(b) [10 CFR 30.50(b)(2)]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2014-07-22
50279 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2014-07-14 | 2014-07-14 13:51 | 2014-07-14 | PART 21 REPORT - POTENTIAL FAILURE OF REACTOR COOLANT PUMP TURNING VANE BOLTS The following was excerpted from a report received via fax from Westinghouse: This issue concerns the potential failure of certain Westinghouse reactor coolant pump (RCP) turning vane bolts that employs turning vane bolts that are 1.0 inch nominal size, made from A286 material. These bolts hold the turning vane diffuser assembly in place inside the RCP, above the pump impeller. Bolt failures have occurred at on plant such that the running vane-diffuser assembly dropped inside three of the four RCPs and in two of these RCPs the assembly contacted the impeller. These bolts are part of the model 93A RCPs delivered to Salem Unit 2 and Surry Units 1 and 2. Name and address of the individual or individuals informing the Commission: James A. Gresham Westinghouse Electric Company Engineering, Equipment and Major Projects 1000 Westinghouse Drive, Suite 310 Cranberry Township, Pennsylvania 16066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-14
50278 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-07-13 19:37 | 2014-07-13 23:13 | 2014-07-13 | MANUAL REACTOR TRIP DUE TO AUTOMATIC FEEDWATER HEATER ISOLATION "On July 13, 2014 at 1937 [EDT], Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to automatic isolation of all low pressure feedwater heaters. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater, steam dumps and the main condenser. The station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident [Inspector] has been notified." Initial indications are that a level switch failed on the #7 heater drain tank which caused the heater drain tank pumps to trip. When the high level tank setpoint was reached, the feedwater system isolated. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-07-13
50277 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-07-13 17:40 | 2014-07-13 21:35 | 2014-07-13 | OFFSITE NOTIFICATION OF A ONE GALLON DIESEL FUEL OIL SPILL "On 07/13/2014 at approximately 1740 [CDT], it was reported that oil sheen was visible in the intake fore bay. Upon further investigation it was determined that a high cold water channel level had caused diesel fuel oil to wash free from an oil drain device from the channel diesel fire pump into the intake fore bay. This oil spill is reportable to the EPA (National Response Center under 40CFR112). Notification to the National Response Center was made at 1750 [CDT]. Notification number is 1088951. "A total of <1 gallon was reported to enter US waters. The source of the leak into the intake fore bay and cold water channel has been stopped. All reportable oil spillage has been contained in the intake fore bay (considered US waters). "Additional notifications have been made to Alabama Emergency Management. "This event requires a 4 hour report pursuant to 10 CFR 50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' "The NRC Resident Inspector has been notified." Notified DOE, EPA, USDA, HHS, and FEMA. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-13
50276 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2014-07-12 17:30 | 2014-07-13 16:10 | 2014-07-13 | ITEMS RELIED ON FOR SAFETY ASSOCIATED WITH THE DRY SCRAP RECYCLE OPERATIONS NOT MEETING REQUIREMENTS "It was determined at 1200 [EDT] on 7/13/14, that one of the Items Relied on for Safety (IROFS) associated with the Dry Scrap Recycle operation failed to meet performance requirements. At approximately 1730 [EDT] on July 12, 2014, a potable water line (1/2 inch poly) failed and resulted in a release of approximately 10 gallons of water into the area. The leak was contained and cleaned up. However, this water release is a failure of IROFS 900-03 for Moderation Restriction. "Although the second IROFS (Process Equipment Barriers IROFS 301) prevented moderation intrusion into equipment and containers, it alone was not sufficient to meet performance requirements. "The affected equipment has been shut down. At no time was an unsafe condition present. Special Nuclear Material (SNM) was not impacted by the leak. No water escaped the area or travelled to non-contaminated areas. While this did not result in an unsafe condition, the event is being reported pursuant with the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours of discovery. "Additional corrective actions, extent of condition, and the cause of the failure are being determined." The licensee will notify NRC Region 2, State of North Carolina Radiation Protection, and New Hanover County Emergency Management. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2014-07-13
50275 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-07-11 15:00 | 2014-07-11 18:00 | 2014-07-11 | OFFSITE NOTIFICATION MADE FOR HAZARDOUS CHEMICAL SPILL "At 1415 [EDT] the Control Room received a report that a refrigeration unit had failed and was spilling coolant (Ethylene Glycol) on the floor of an office building inside the protected area. At 1440 [EDT] the leak was isolated. It is estimated that approximately 10 gallons of Ethylene Glycol was introduced to the floor drains which ultimately lead to the environment. This is not a Reportable Quantity for the Environmental Protection Agency but the Pennsylvania Department of Environmental Protection was notified in accordance with the Pennsylvania Clean Streams Law at 1500 hours. The spill was contained and cleanup is complete. "This condition is being reported pursuant to 10 CFR 50.72 (b)(2)(xi). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-11
50274 | -1 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-07-11 14:00 | 2014-07-11 15:57 | 2014-07-14 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "Tennessee Div. of Radiological Health was notified on 7/11/14, by a representative form Geo/Environmental Associates, that a CPN Model MCI, portable moisture density gauge containing 10 mCi, Cs-137 and 50 mCi, Am-241 was run over by a bulldozer at a construction site in Kentucky while working under reciprocity in that state. Initial surveys performed on the device indicate the source was not damaged and there was no loss of sources from the device. The device is being returned to it's home storage site in Knoxville, Tennessee and will be assessed by state inspectors with further investigation." The gauge was surveyed and is showing 40 mR/hr on contact. Tennessee Report Number: TN-14-138 * * * RETRACTION PROVIDED BY BILLY FREEMAN TO JEFF ROTTON VIA EMAIL AT 0913 EDT ON 07/14/2014 * * * The State of Tennessee is retracting this event due to the fact that this event notification should be made by the Commonwealth of Kentucky where the event occurred. Notified R1DO (Cahill) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-07-21
50273 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2014-07-11 08:23 | 2014-07-11 15:28 | 2014-07-11 | LOSS OF ASSESSMENT CAPABILITY - LOSS OF POWER TO THE PLANT PROCESS COMPUTER "At 0823 EDT on Friday, July 11, 2014, the Pilgrim Nuclear Power Station (PNPS) determined that the plant process computer and, therefore, the in-plant Safety Parameter Display System (SPDS) was not functioning as designed due to a loss of power. The SPDS provides numerous plant parameters, some of which are credited for emergency assessment capability. The site has determined that this constitutes a major loss of assessment capability. Immediate actions were taken to restore the system to functional status and applicable plant procedures were entered to determine temporary mitigating actions. Power was subsequently restored at approximately 1030 EDT via an alternate supply, and SPDS has been restored to normal operation. "This event had no impact on the health and/or safety of the public. "This notification is conservatively being made in accordance with 10 CFR 50.72 (b)(3)(xiii). "There is no impact to plant operations." The licensee notified the NRC Resident Inspector and will notify the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-11
50272 | 0 | NUCLEAR LOGISTICS INC |  |  |  |  | 2014-03-27 | 2014-07-11 14:15 | 2014-07-11 | PART-21 NOTIFICATION - ASSEMBLY ERRORS DURING BREAKER REFURBISHMENT The following is a summary of the information provided via facsimile: "On March 27, 2014, at Exelon-Dresden Station, plant personnel identified that breaker UTC # 1185084 (3B CCSW Pump Breaker) was in the CLOSED condition, but did not indicate CHARGED. The breaker was last CLOSED successfully on March 19, 2014. The breaker charges the closing springs after a CLOSE operation. "The breaker was OPENED and removed from service on 3/28/14, Dresden notified [Nuclear Logistic, Inc.] NLI on 3/28/14 of the issue and the breaker was returned to NLI on RMA 351022093. "NLI performed a failure analysis on the breaker. The spring clamp cam 12mm nylon insert lock nut was not properly tightened on either side, resulting in insufficient clamping force of the cam on the jackshaft. In addition to the lock nuts not being sufficiently tightened, the closing springs were installed on the wrong side. There is a left and a right spring as identified by a red mark on the left spring. The left side spring is the shorter spring, and it was installed on the right side. Further evaluation by NLI determined that this may have been a contributing factor to the failure after the closing spring clamp started to move off the jackshaft. "The presence of the under torque nuts resulted in insufficient clamping force, allowing the clamp to move off the jackshaft. The springs being on the wrong sides began to exert excessive force to the cam as it rotated, and after many operations, it had slipped enough to become partially dislodged from the jackshaft. This bent the spring guide arms, preventing the rotation of the jackshaft to the CHARGED position and did not allow the motor cutoff switch to activate. The result was the breaker did not CHARGE and the motor continued to run until it burned up." Several AHMG breakers (1200 and 2000A) for Dresden and Quad Cities were refurbished by Nuclear Logistics, Inc from 2008 to March 2014. At least one breaker was found with insufficient cam nut spring torque and had the two closing springs installed improperly. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-07-11
50271 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-07-11 | 2014-07-11 13:25 | 2014-07-11 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK IN CLOSED POSITION The following information was received via e-mail: "The licensee reported the malfunction of the shutter mechanism on a fixed gauge. The device is stuck in the closed position. Repair to the shutter will be made by the manufacturer, Ohmart-Vega. A date for their site visit to repair the shutter is pending. Information about the source is shown below: Manufacturer: Ohmart/Vega Model: SH-F2 Serial #: 13549338 Source Serial #: 1224CO Isotope: Cs-137 Initial Activity: 500mCi" Ohio Report Number: OH 2014-019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-07-21
50270 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-07-11 03:14 | 2014-07-11 05:17 | 2014-07-11 | MANUAL SCRAM DUE TO LOSS OF MAIN CONDENSER VACUUM "Today at approximately 0312 [EDT on 7/11/14], during a planned reactor power ascension with reactor power at approximately 55 percent of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 0314 [EDT]. The cause of the degraded vacuum is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The scram was uncomplicated, normal offsite power is available, and plant is being cooled down to cold shutdown. The cause of the degraded condenser vacuum is suspected condenser boot degradation. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-07-11
50269 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2014-07-10 09:59 | 2014-07-10 16:41 | 2014-07-10 | NON-LICENSED EMPLOYEE SUPERVISOR FOUND IN VIOLATION OF FITNESS-FOR-DUTY POLICY "A non-licensed employee supervisor has been found in violation of the Duke Energy Fitness for Duty Policy. The individual's access to the plant has been suspended. The licensee has notified the NRC Region 1 [Hammann]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 1 | FL | POW |  | 26.719 |  |  |  | 0 | 2014-07-18
50268 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-07-08 | 2014-07-10 15:33 | 2014-07-10 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following information was received via fax: "On July 9, the licensee's radiation safety officer called to report a potential medical event had occurred the previous afternoon. The Agency was advised that an interstitial treatment could not be completed involving a High Dose Rate afterloader (HDR) at the University of Illinois at Chicago. As a result of safety features built into the HDR's programming, the first fraction of a four fraction treatment of 300 rad was automatically terminated and the source returned to the safe/stored position after only 6 rad had been delivered when unexpected resistance was detected in the source wire as it moved to the second dwell position. Subsequent attempts to clear the path and reinitiate the treatment were unsuccessful. As a result, an underdose of 98% of the fraction occurred. The HDR unit was subsequently re-run through its quality assurance tests for positioning accuracy with no anomalies noted. The patient was notified of the event immediately. "A week before, the patient had 3 catheters surgically placed near the pelvis and their location relative to the treatment site verified by CT scan with an additional scan just before treatment was initiated. After reviewing the scan the written directive was modified to call for 18 dwell positions in three channels for a duration of 101 seconds. Four fractions were going to be completed on successive days. The scan suggested the possibility of the catheters being moved as a result of distention of some internal organs. Although the 'dummy' wire successfully traversed the initial path, and the active wire reached the first treatment position, after the initial 2 seconds of programmed dwell time, the HDR unit detected an unexpected delay in the wire moving to the second dwell position, presumably due to constriction of the pathway, and automatically retracted the active wire to the safe store position. With the assistance of the manufacturer's off site technical advisor, the error code was cleared and attempts were made to reinitiate the treatment however, the 'dummy' wire could not traverse the path and the treatment abandoned. "In this instance the device performed as designed and subsequent quality assurance tests confirmed the device was operating as expected. Although no effect on the patient is expected from the event, physicians are determining what course of treatment options are available at this time. The licensee was advised of the requirement to submit a written report of the event in accordance with the regulations. Pending additional developments and submission of the report, this matter remains open for now." The HDR Afterloader has a 5 Ci Ir-192 source and was being used to treat a cancer in the pelvic area. Illinois Report Number: IL14011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-07-18
50267 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-11-13 | 2014-07-10 14:35 | 2014-07-28 | AGREEMENT STATE REPORT - BRACHYTHERAPY UNDERDOSE The following information was received via fax: "This medical event (ME) was self-identified by the licensee during an audit. A patient who had undergone an iodine-125 (I-125) prostate brachytherapy procedure was reported to have a 'D90' dose of 43% of the written directive. The licensee radiation safety officer and physician are in contact regarding this ME. It is unknown at this time if the patient has been notified. "The Department [Pennsylvania Department of Environmental Protection] is waiting for the required 15 day written report from the licensee. The Department will then conduct a reactive inspection." PA Event Number: PA140017 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM DAVID ALLARD TO DONALD NORWOOD AT 1641 EDT ON 7/28/2014 * * * The following information was received via facsimile: "Through an internal audit, it was initially thought that a patient who had undergone an iodine-125 (I-125) prostrate brachytherapy treatment in November, 2013 was believed to have had a 'D90' dose of only 43% of the written directive. However, based on a re-assessment by the licensee's Chief Medical Physicist, it appears that greater than 80% of the prostate volume received the prescribed dose. "[The] reported medical event is to be retracted." Notified R1DO (Dimitriadis) and FSME Events Resource via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-07-18
50266 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-07-10 08:38 | 2014-07-10 13:29 | 2014-07-10 | HIGH RANGE SHIELD BUILDING VENT STACK GAS MONITOR REMOVED FROM SERVICE FOR MAINTENANCE "At 0830 CDT on July 10, 2014, 2R-50 High Range Shield Building Vent Stack Gas Monitor was removed from service for planned maintenance. 2R-50 was planned for an out of service time of approximately 8 hours. The clearance order associated with the work isolated the flow path to the sample pump. Subsequent to the execution of the clearance order, it was discovered that the flow path to the alternate sample pump was also unavailable inhibiting the ability to implement compensatory measures. With 2R-50 rad monitor sample pump out of service and no alternate sampling available, timely classification of two Emergency Action Levels (EALs), SAE (Notification of Site Area Emergency) and General Emergency classifications would not be achievable. This results in a Loss of Emergency Assessment Capability while 2R-50 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 2 Shield Building Ventilation Stack is also monitored by the Shield Building Vent Gas Monitor, 2R-22, which is used for the same purpose in NUE (Notification of Unusual Event) and Alert classifications. 2R-22 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 2R-22 prior to removing 2R-50 from service. This planned maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-10
50265 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-07-10 04:45 | 2014-07-10 09:17 | 2014-07-10 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 0445 [CDT] on July 10, 2014, Browns Ferry Unit 2 initiated actions to commence a reactor shutdown to comply with TS LCO 3.0.3. TS LCO 3.0.3 was entered at 0355 [CDT] and was required due to the 'C' Emergency Diesel Generator becoming inoperable after isolating a leak on the Emergency Equipment Cooling Water System. Currently, a 7 day TS LCO Action 3.5.1.A is in effect due to ongoing scheduled Core Spray Loop I maintenance outage. The declaration of inoperability of the equipment supported by the 'C' Emergency Diesel Generator, Core Spray Loop II, along with the redundant Core Spray system inoperable for maintenance resulted in TS LCO 3.0.3 for Unit 2. TS LCO 3.0.3 requires actions to be initiated within one hour; to place the unit in MODE 2 within 10 hours; MODE 3 within 13 hours; and MODE 4 within 37 hours. "This event requires a 4 hour report lAW 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "Actions were taken to restore the Core Spray System to Operable status and LCO 3.0.3 was exited at 0735 [CDT] on July 10, 2014. "The NRC Resident Inspector has been notified. "This event was entered into the Corrective Action Program." Browns Ferry Unit 2 had reduced power to 98% when LCO 3.0.3 was exited, the power reduction was suspended, and preparations are being made to return power to 100%. There is no impact on Units 1 or 3. | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-07-10
50264 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2014-07-08 11:48 | 2014-07-08 14:26 | 2014-07-08 | OFFSITE NOTIFICATION DUE TO DIESEL FUEL OIL LEAK "At 1148 EDT, Fermi-2 Environmental Engineering identified that approximately 2500 gallons of Diesel Fuel Oil was noted to be in a secondary containment collection basin. The Control Room Staff was subsequently notified. Michigan Pollution Control (MPC) has been contacted for cleanup. "DTE Energy notified Michigan Department of Environmental Quality (MDEQ) of the condition. "Fermi-2 is making this 4-hour report to the NRC in accordance with 10CFR50.72(b)(2)(xi) and NUREG-1022 (rev 3) Section 3.2.12. "Investigation regarding the cause is currently in progress. No fuel oil was released to the ground or navigable waters. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-07-08
50263 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-07-08 09:25 | 2014-07-08 10:06 | 2014-07-08 | UNUSUAL EVENT DUE TO SMOKE ALARM INSIDE CONTAINMENT "Unusual Event declared at 0935 EDT on July 8, 2014 due to a single fire alarm in containment. ELA HU4. No abnormal condition or plant impact at this time. The plant remains stable at 100% power." A single smoke detector inside containment alarmed at 0925 EDT. There are no other indications of smoke or fire at this time. Adjacent smoke detectors are not in alarm. A containment entry team is being assembled to verify that there is no fire inside containment. The smoke detector alarm cleared at 1006 EDT. The licensee notified the NRC Resident Inspector. The licensee will make appropriate notifications to state and local government agencies. Notified DHS, FEMA, and NICC via email and phone. Notified FEMA NWC and Nuclear SSA via email. * * * UPDATE FROM CHARLIE STEENBERGEN TO VINCE KLCO ON 7/8/14 AT 1419 EDT * * * "The Unusual Event was terminated at 1328 EDT on 7/8/14. A containment entry was performed and no indications of a fire existed. The fire alarm was spurious and the detector has been disabled. There was no notification of other government agencies and there is no media /press release planned." The plant maintained stable operations at 100% power. The licensee notified the NRC Resident Inspector, the state of Ohio and local officials. Notified R3DO (Hills) NRR EO (McGinty), IRC MOC (Grant). Notified DHS, FEMA, and NICC via email and phone. Notified FEMA NWC and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-07-08
50262 | -1 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-07-08 00:24 | 2014-07-08 07:28 | 2014-09-05 | UNIT 2 SPRAY ADDITION DECLARED INOPERABLE DUE TO TANK INDICATION GREATER THAN 67% "At 0024 CDT on 7/8/2014, Unit 2 Spray Addition was declared inoperable and LCO 3.6.7 (Spray Additive System) not being met, which resulted in a condition reportable pursuant to 10CFR50.72(b)(3)(v)(D). The inoperability was caused by Unit 2 Sodium Hydroxide Tank level indication greater than 67%, at 67.5%. This exceeds a current Prompt Operability Determination compensatory action requirement stating 'level shall be maintained no higher than 67%.' "At 0104 CDT on 7/8/2014, Unit 2 Sodium Hydroxide Tank level was restored to an acceptable level, less than 67%. TSAC 3.6.7B was exited and LCO 3.6.7 met." The licensee informed the NRC Resident Inspector. * * * RETRACTION PROVIDED BY BRADLEY DERINGTON TO JEFF ROTTON AT 1710 EDT ON 09/05/2014 * * * "Point Beach is retracting EN# 50262 made on July 8, 2014 at 0628 CDT. The Operability Determination for this condition has been revised based upon engineering analysis. The event notification is being retracted based upon the subsequent Operability Determination revision that shows the NaOH Injection System was capable of performing its safety function at an observed Spray Additive Tank level of no higher than 77.2 percent." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-07-08
50261 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-07-07 20:40 | 2014-07-07 22:12 | 2014-07-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On July 7, 2014 at approximately [2040 EDT], an issue was discovered with currently removed Electromatic Relief Valves (EMRVs) that calls the operability of the currently installed EMRVs into question. Based on this new information, all 5 of the currently installed EMRVs were conservatively declared inoperable. With the potential of 5 EMRVs inoperable a Technical Specification shutdown is required under Technical Specification 3.4.b, whereby reactor pressure shall be reduced to 110 psig or less within 24 hours. This event is immediately reportable under: "50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "50.72(b)(3)(v)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.'" The licensee notified the NRC Resident Inspector. The licensee will notify the State of New Jersey and issue a press release. * * * RETRACTION AT 1745 EDT ON 7/11/2014 FROM CHARLES SPAGNUOLO TO MARK ABRAMOVITZ * * * "The original concern and July 7, 2014 EN [report] was caused by abnormal wear found on removed Electromatic Relief Valve actuators. However, on July 8, 2014, upon completion of in situ testing as well as visual examination of the installed EMRV actuators, it was determined that the 5 currently installed EMRVs were fully operable and capable of performing their safety function. Therefore, Oyster Creek is retracting the notifications made under 50.72(b)(2)(i) and 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector and the State will be notified. The licensee will be issuing a press release. Notified the R1DO (DeFrancisco). | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-07-07
50260 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-10-17 12:15 | 2014-07-07 14:50 | 2014-07-07 | TRANSPORT OF POTENTIALLY CONTAMINATED INDIVIDUALS FOR OFFSITE MEDICAL TREATMENTS "Based on discussions with NRC on 7/7/2014 at 0800 EDT, it was determined that two (2) previous unplanned medical treatment cases should have been reported to the NRC Operations Center. The unplanned medical treatment cases occurred on 10/17/2013 and 10/29/2013 and involved injured and potentially contaminated individuals. The individuals were injured at the NFS facility and transported to local medical facilities. Due to the extent of the injuries, a full survey for potential contamination on the individuals could not be performed prior to being transported to the offsite medical facilities. Due to the inability to perform full surveys, NFS Medical and Radiological Staff, along with the medical facilities, implemented effective contamination control measures prior to the individuals arriving at the medical facilities, preventing the spread of potential contamination. On 10/17/2013 and 10/29/2013, respectively, NFS determined that reports to the NRC Operations Center were not required; however, notification to the NRC should have been made within 24-hours of the potentially contaminated individuals being transported to the medical facilities. Follow-up surveys and analysis by NFS Radiological Control staff did not identify spreadable radioactive contamination on the individuals or the medical facilities. "There were no actual or potential safety consequences to the public or environment. There were no actual or potential safety consequences to the workers involving exposures to radiation or radioactive materials or hazardous chemicals produced from licensed material. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2014-07-08
50259 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-07-04 02:33 | 2014-07-04 08:22 | 2014-07-04 | TURBINE BUILDING PROCESS RADIATION MONITORING NON-FUNCTIONAL "At 0233 PDT on July 4, 2014, TEA-RIS-13 and the Turbine Building process radiation monitoring sample rack were declared non-functional. The cause of the malfunction is under investigation. Compensatory measures have been implemented to obtain radiation readings from the associated effluent release pathway. Field team assessment function was unaffected and remains available. "This event is being reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-04
50258 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2014-07-03 21:25 | 2014-07-03 21:40 | 2014-07-03 | HURRICANE WITHIN 500 NAUTICAL MILES OF THE FACILITY "A hurricane is within 500 nautical miles from Indian Point Energy Center with wind speed in excess of 87 knots. The National Weather Service has issued a hurricane warning for a hurricane with wind in excess of 87 knots (approximately 100 mph) within 500 nautical miles of the facility. Per Technical Requirement Manual 5.4.A, a prompt report shall be made to the NRC Incident Response Center within 1 hour of receipt of that hurricane warning. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2014-07-03
50257 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-07-03 16:00 | 2014-07-03 22:23 | 2014-07-07 | AGREEMENT STATE REPORT - LOST MOISTURE/DENSITY GAUGE The following was received from the State of Texas via email: "On July 3, 2014, the licensee notified the Agency [Texas Department of Health] that one of its technicians left the licensee's facility in Austin, Texas, to transport a Troxler Model 4640 moisture/density gauge containing an 8 milliCurie cesium-137 source to the licensee's facility in Buda, Texas. The technician failed to properly secure the gauge for transport. When the technician arrived in Buda, he found the tailgate on pickup was down and the gauge was missing. The licensee retraced the technician's route of travel and found a water jug that had also been in the back of the truck near the licensee's Austin facility, but the gauge was not located. The licensee reported that the device (source rod handle) was not locked. The licensee reported that there were no locks on the transport case lid. More information will be provided as it is obtained in accordance with SA-300." * * * UPDATE FROM KAREN BLANCHARD TO VINCE KLCO ON 7/7/2014 AT 1144 EDT * * * The following update was received by the State of Texas by email: "Reporting criteria changed, as the only source in device (8 milliCurie cesium-137) is less than 1,000 times greater than Appendix C values and therefore does not meet 20.2201(a)(1)(i) immediate reporting criteria. The incident does meet 20.2201(a)(1)(ii) and further information will be provided in accordance with SA-300." Notified the R4DO (Kellar) and FSME Event Resource via email. Texas Incident # I-9211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-07-11
50256 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-06-26 | 2014-07-03 17:21 | 2014-07-03 | AGREEMENT STATE REPORT - MISPLACED IODINE 125 SOURCE FOUND IN SHIPPING CASE The following was received from the State of Florida via email: "A well chamber (HDR1000+, s/n A980392) was shipped to University of Wisconsin-Madison from Tallahassee Memorial Cancer Center Tallahassee FL. It arrived inside a case which also contained three source holders and an electrometer. An I-125 source was found on the bottom of the case on the foam inserts. "Due to low exposure rate of the source (about two times background on contact) it was not detected by the monitoring system, but discovered visually. The UWADCL [University of Wisconsin Accredited Dosimetry Calibration Laboratory] received equipment on 6/26/2014. Calibration was completed on 7/2/2014. The shipper has been informed by phone and email." Florida Incident #: FL14-062 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-07-11
50255 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-07-01 14:30 | 2014-07-03 16:46 | 2014-07-03 | AGREEMENT STATE REPORT - TROXLER MOISTURE/DENSITY GAUGE RUN OVER BY BULLDOZER The following was received from the State of Louisiana via email: "On July 2, 2014, the CRSO [Corporate Radiation Safety Officer], for Terracon Consultants (TCI) notified LDEQ [Louisiana Department of Environmental Quality] that a moisture density gauge being used at one of their projects was run over by a bulldozer. "The source was left unattended when a bulldozer ran over the gauge and damaged the housing. They are conducting an investigation to determine the cause of the incident. It appears that it was human error. "The sources were leak tested and TCI is waiting for the results of the test. The unit was surveyed and it appears the sources were not leaking. Results will be forwarded to NMED as an update when the information is obtained. "All equipment involved is isolated and is not a threat to the public. There is no threat to TCI personnel and it appears to be safe. "The damaged gauge was a Troxler, Model 3430, S/N 26346, loaded with 8 mCi of Cs-137 and 40 mCi of Am-241/Be. The gauge housing was damaged, but there was no indication the radioactive sources were compromised or leaking. The sources were isolated and leak tested." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2014-07-11
50254 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-06-28 | 2014-07-03 11:44 | 2014-07-03 | AGREEMENT STATE REPORT - FIXED INDUSTRIAL GAUGES DAMAGED DURING FIRE The following was received from the State of Ohio via email: "On 6/29/14 at 1330 EDT, ODH [Ohio Department of Health] received a call that there was a fire at an oil well location in Hannibal, Ohio, Monroe County. A hydraulic line on a piece of drilling equipment failed, spilling hydraulic fluid onto a hot engine, igniting the fluid. The fluid continued to rapidly leak, which caused the fire to spread. When the fire department arrived on scene, the well pad was reported to be fully engulfed in flames. The drilling company has reportedly lost 20 vehicles in the fire. There were three density gauges on site, two (2) of which were mounted on equipment and one was mounted on the well. There were no detections of radiation at that time. "On 6/30/14 two ODH inspectors were dispatched to the site to verify that the gauges were secure and had not suffered damage from the fire. Upon arrival the ODH inspectors were not allowed to go onto the drilling pad area because it is still being cleared of potentially explosive hazardous chemicals and unexploded ordinance (used in fracking process). The inspectors attended a meeting regarding status of the site and were briefed by representatives from Halliburton (the licensee). The gauges involved were two (2) Model 100-SD, containing 120 mCi of Cs-137 each, and one (1) Model 55-SD containing 66 mCi of Cs-137. "Halliburton was able to conduct an initial visual inspection and survey of the gauges. They stated that there did not appear to be any significant visible damage and the devices appeared to be intact. They recorded readings of 0.5 mR/hr on contact for the Model 100-SD gauges, and 0.3 mR/hr on contact on for the Model 55-SD gauge. Wipe tests were taken by the licensee to check for leakage and the field survey indicated no contamination. The wipes were sent to a laboratory for further analysis. Licensee personnel will put up warning signs and barriers around the gauges once the site is safe for other than emergency operations. It is expected to be several days before the site is determined to be safe enough for any movement or removal of the devices. "On 7/2/14 the licensee was granted permission from the site manager to remove the gauges. All three gauges were removed without incident, and appeared to be intact (although scorched on the exterior from the fire). There were no incidents during the removal and no radiation readings recorded above those originally reported. The three gauges were placed in over packs, with proper labels and shipping papers, and were sent to the Halliburton headquarters in Texas for further evaluation." Ohio Reference Number: ODH 2014-017. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-07-11
50253 | 0 | PREFERRED METAL TECHNOLOGIES, INC. |  |  |  |  | 2014-07-03 | 2014-07-03 14:29 | 2014-07-30 | PART 21 REPORT - INCORRECT INDUSTRIAL IRRADIATOR DOSE The following was received via fax: "Preferred Metal Technologies (PMT) was notified by Steris Isomedix Services that the applied radiation dose reported on their Component Irradiation Certificates did not account for all the uncertainties involved (i.e. density of unrelated products in carriers, off-carrier location within the irradiator and Cobalt-60 source decay). This potential defect was originally identified as part of NRC Inspection Report No. 99901445/2014-201. "After a thorough review of all purchase orders issued to Steris Isomedix Services and PMT Projects that the irradiation test results were utilized on, PMT has determined that there are two projects where the applied radiation dose may have failed to meet the minimum required radiation dose to ensure that the safety related equipment would continue to operate satisfactorily during and after an accident. The details of those two projects are as follows: "N1839 - Tennessee Valley Authority, Browns Ferry - 6 (Six) Electric Spring Return Actuators - Purchase Order #473351. "N1893 - Commission Federal de Electricidad, Laguna Verde - 32 (Thirty Two) Damper Assemblies - Purchase Order #700419016. "Tim Stewart, Vice President Nuclear Preferred Metal Technologies, Inc. 140 East Tower Drive Burr Ridge, Illinois 60527" Preferred Metal Technologies Report Number: 14-01. * * * UPDATE FROM TIM STEWART TO DONALD NORWOOD AT 1636 EDT ON 7/30/2014 * * * The following information was received via facsimile: "In summary, additional radiation exposure testing was performed, post-radiation operability was verified, and it was confirmed that all affected equipment would continue to operate satisfactorily during a design basis event. No equipment upgrades or replacement is required as the supplied equipment was verified to meet the applicable technical requirements." Notified R2DO (O'Donohue), R3DO (Lipa), and the Part 21 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-07-03
50252 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-05-21 03:36 | 2014-07-03 10:34 | 2014-07-03 | CONTROL ROOM OVERHEAD ANNUNCIATOR MALFUNCTION "At 0336 [CDT] on 5/21/14, during activities to isolate the preferred power supply for wiring modification, all control room annunciators cleared and lost power due to a disconnect switch failure associated with the alternate power supply. The normal power supply was restored at 0349 [CDT] to restore the annunciators to functional status. During the brief period of time the annunciators were unavailable, redundant assets as described in existing station documentation and/or the control room alarm typer remained functional along with the station computer alarms and Safety Parameter Display System to provide backup assessment capability. "This event was previously determined to not be reportable, however, following additional review of the significance this is reportable. The NRC Resident has been notified of the event. The late reporting of this event has been entered into the Corrective Action Program." The licensee notified the State of Ohio as well as Lucas and Ottawa counties. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-03
50251 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2014-07-02 13:00 | 2014-07-02 16:23 | 2014-07-02 | AGREEMENT STATE REPORT - UNDERDOSE ADMINISTRATION FOR TREATMENT OF PROSTATE CANCER The following report was received from the New York City Office of Radiological Health (NYC ORH) via facsimile: "Type of Incident: Underdose of Sm-153 administration IV for treatment of prostate cancer. "Location of Incident: Long Island Jewish Medical Center. New York City Radioactive Materials License No. 75-2986-01 "Date and time of Incident: 07/02/14 at 1300 EDT. "Date and time of Report to NYC ORH: 07/02/14 at 1530 EDT. "Date of Investigation by ORH inspector: Inspection will be assigned no later than 24 hours from time of report to the Office of Radiological Health. "Description of event: Patient was being injected with Samarium-153 intravenously [IV], in the arm for treatment of prostate cancer. "In preliminary telephone report by hospital, RSO stated that administration was made into the skin, rather than IV as intended. Physician's prescription was for 100 microcuries (reporting RSO twice stated 'microcuries'). Of the prescribed 100 microcuries, it was estimated that only 39.2 microcuries was delivered. Procedure was stopped in the course of delivery. "Reporting RSO at Medical Center stated that preliminary report would be sent by email later today. Letter with details to follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-07-10
50250 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2014-07-01 15:00 | 2014-07-02 14:49 | 2014-07-02 | FAILURE OF AIR OPERATED SOURCE CALIBRATOR "On July 1, 2014, at approximately 1500 EDT, as a result of an investigation into a report that the electronics associated with the air operated source controller of a J. L. Shepherd Model 149 Neutron Calibrator was not working properly, it was concluded that the electronics for the air operated source controller had failed. The failure would have allowed the source to be withdrawn without the electronic circuit being energized. The original source contained 8.5 Ci of Pu-Be. The calibrator is designed to expose a neutron source on a signal from a control circuit using air to withdraw the source. In this event, source withdrawal was initiated when air was aligned without the control circuit being energized; the air was immediately isolated preventing the source from being withdrawn. The calibrator has been removed from service due to the control circuit failure. The source is in the safe position, tagged and locked with the air line disabled. This failure did not result in any personnel exposure. "This is reportable under 10 CFR 70.50(b)(2) since the circuit is required by design to be operable when the calibrator is used. The cause of the failure has not been determined at this time. "The affected calibrator is not part of any installed plant equipment and has no impact on plant operation." The licensee has notified the NRC Resident Inspector. The licensee will notify the New York Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFETY EQUIPMENT FAILURE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 70.50(b)(2) |  |  |  | 0 | 2014-07-02
50249 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-05-21 | 2014-07-01 21:46 | 2014-07-01 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The following report was received from the Commonwealth of Pennsylvania via facsimile: "Notifications: The DEP [Pennsylvania Department of Environmental Protection and Bureau of Radiation Protection] Southwest Regional Office contacted the licensee upon our DEP Central Office receiving a reciprocity notification for a scheduled repair to be done on a level gauge with a stuck shutter. The RSO from the licensee was unaware that this shutter failure was a reportable event. This event is reportable within 24-hours per 10 CFR 30.50(b)(2). "Event Description: The licensee made a service call to a service provider on May 21, 2014, for a quote on a stuck gauge shutter. This situation was discovered by the licensee during a shutter check and leak test. It is unclear if the shutter was stuck open or closed. However, the licensee does have a 'lock-out/tag-out' procedure, and personnel were restricted from the gauge area. It is also unknown at this time of the actual event date. "Gauge Manufacturer: Ronan Engineering; Model: SA 1-F37; Serial Number: M7255; Source Isotope: Cesium-137; Activity: 10 millicuries (mCi). "Cause of the Event: Unknown at this time. "Actions: The Department plans to do a reactive inspection. More information will be provided when more information is received." PA State Report #: PA140015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-07-09
50248 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-06-30 | 2014-07-01 19:16 | 2014-07-01 | AGREEMENT STATE REPORT - LOST OR STOLEN NUCLEAR DENSITY GAUGE The following report was received from the Commonwealth of Pennsylvania via facsimile: "Notifications: The Department's [Pennsylvania Department of Environmental Protection and Bureau of Radiation Protection] Southwest Office received a phone call on July 1, 2014 regarding a lost nuclear density gauge. This event is reportable per 10 CFR 20.2201(a)(1)(i). "Event Description: The nuclear density gauge in question was last used on Friday, June 27th, at a job site in Mt. Lebanon, PA. The employee who used the gauge, reported returning the gauge (in its case) to the licensee's storage area that afternoon. That same employee reported, at close of business on Monday June 30th, that 'the case was now empty.' An inspection by the licensee [revealed] the case and lock were both intact inside the locked storage area. There were no signs of forced entry and nothing else was missing. The employee has been questioned multiple times and maintains that the gauge was returned to the storage area in the case on Friday, June 27th. The licensee also went back to [search] the job site in Mt. Lebanon, but did not find the gauge. "Gauge Model: Troxler 3411B, Serial # 5434, containing 9 mCi Cs-137 and 44 mCi Am-241 sources. "Cause of the Event: Unknown at this time. "Actions: The local police are being notified and the licensee is offering a reward for the return of the gauge. The Department issued a press release on July 1, 2014, with a photo of the Troxler gauge and noting the reward. The Department's Southwest Regional Office will conduct an reactive inspection. More information will be provided upon receipt." PA Report #: PA140014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-07-09
50247 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-07-01 07:15 | 2014-07-01 12:14 | 2014-07-02 | OFFSITE ALERT AND NOTIFICATION SYSTEM FAILURE "At approximately 0715 (CDT) on 7/1/2014, during the daily morning test, Braidwood Generating Station experienced Offsite Alert and Notification System (ANS) failure of sirens BD10 and BD13 due to a loss of power to the sirens. Loss of power to the sirens was due to the adverse weather conditions experienced on the evening of 6/30/2014. Siren BD10 provides coverage for 20% of Braidwood's Emergency Planning Zone (EPZ) population and siren BD13 provides coverage for 14.1% of the Braidwood EPZ population. "This event is being reported in accordance with 10CFR50.72(b)(3)(viii) for 'any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).' The failure of the sirens resulted in the loss of the capability to alert a large segment of the population in the EPZ (~34%) for more than 1 hour. Per NEI 13-01, Rev 0, a large segment of the population in the EPZ should be taken to mean approximately 25% of the total EPZ population. "Immediate actions taken included placing a portable generator online to restore siren BD10 at 1015 CDT on 7/1/2014. ComEd is currently in the area attempting to restore normal power. Proposed long term corrective actions including an upgrade to the sirens to contain a battery backup are being evaluated. "The licensee has notified the NRC Resident Inspector. The county emergency managers (for Will County - [for siren] BD10 and Grundy County - [for siren] BD13) are aware of the siren outage and the requirements to initiate mobile route alerting (FEMA approved backup) if required." * * * UPDATE FROM MURTAZA ABBAS TO DANIEL MILLS AT 1756 EDT ON 07/02/2014 * * * "Siren BD10 was restored to functional on 7/1/2014 at 1130 CDT. "Siren BD13 was restored to functional on 7/2/2014 at 1145 CDT. "The NRC Resident Inspector has been notified of this ENS update." Notified R3DO (McCraw) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-07-01
50246 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-06-30 19:13 | 2014-06-30 23:54 | 2014-07-01 | AUTO-START OF STANDBY DIESEL GENERATORS DUE TO A GRID DISTURBANCE "This report is being made under 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section' due to an auto start of 'A' and 'B' Standby Diesel Generators. At 1913 CDT, a grid disturbance during a local thunderstorm caused a valid bus undervoltage condition that resulted in the auto start of both the 'A' and 'B' Standby Diesel Generators. The 'A' and 'B' Standby Diesel Generator supply breakers did not close onto their respective buses as they remained powered by their normal power supply, the 1X003 Startup Transformer, during and after the event. NextEra Duane Arnold personnel inspections revealed no issues with breakers in the switchyard. ITC (Iowa Transmission Company) reported a fault on a 161 Kv line in the NextEra Duane Arnold vicinity. Offsite power remained operable during and following the event. "As designed the 'A' and 'B' Emergency Service Water systems auto started when the diesel generators auto started. The Emergency Service Water systems and both Standby Diesel Generators have been returned to standby/readiness condition. All ECCS [Emergency Core Cooling System] systems were available before the event and have remained available following the event." The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-07-01
50245 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-06-30 22:46 | 2014-06-30 23:24 | 2014-08-21 | UNANALYZED CONDITION THAT COULD HAVE RESULTED IN AN INCREASED MAXIMUM FLOOD LEVEL "On June 27, 2014, TVA identified in a reanalyzed hydrologic analysis for Watts Bar Nuclear Plant (WBN) a deviation from the current hydrologic analysis. The flooding analysis in Section 2.4.3 of the WBN UFSAR assumes that the Watts Bar West Saddle Dike fails completely and instantaneously at approximately 1.5 feet of overtopping during a Peak Maximum Flood [PMF]. This assumption exists in the original design basis analysis and the revised analysis which supports WBN-UFSAR-12-01 (Application to Revise Watts Bar Nuclear Plant Unit 1 Updated Final Safety Analysis Report Regarding Changes to Hydrologic Analysis). "The results of recent studies of the West Saddle Dike, conducted as part of the Fukushima Order 2.1 flooding review, indicate that the complete and instantaneous failure of the Watts Bar West Saddle Dike may not be a valid assumption. If the dike does not fail, analyses performed using the codes and methods consistent with those used in original plant design show that the east floodwall of the Watts Bar Dam would overtop. As a result of this overtopping, the east floodwall is assumed to fail. Based on this assumption and analysis, failure of the east floodwall of the Watts Bar Dam would result in an increase in the flood level at the WBN Plant Site. The current licensing basis PMF level for WBN is 734.9 feet as stated in Section 2.4.3.5 of the WBN UFSAR. In addition, it should be noted that by letter dated July 19, 2012, TVA proposed a revised PMF level of 739.2 feet. Introducing non failure of the Watts Bar West Saddle Dike indicated a potential increase of approximately 1.7 feet over the revised PMF level. "TVA performed additional analysis using current industry standard for flooding analysis. Specifically, TVA modeled the condition using the United States Army Corps of Engineers Hydrologic Engineering Center River Analysis System (HEC-RAS) tool. TVA's analysis of the condition using HEC-RAS determined that all required safety equipment for WBN would not be impacted and are considered operable based on a Prompt Determination of Operability completed on June 30, 2014. "This report addresses a condition as described in 10 CFR 50.72 (b)(3)(ii)(B). TVA is making this report consistent with the guidance of NUREG-1022 regarding the application of engineering judgment to the evaluation of reportability of an unanalyzed condition. "The NRC Resident Inspector has been notified of this condition." * * * RETRACTION AT 1705 EDT ON 8/21/2014 FROM MATTHEW ROBERTSON TO MARK ABRAMOVITZ * * * "On June 30, 2014, TVA reported (Event 50245) that during a re-analysis conducted as part of the Fukushima Order 2.1 flooding review, a probable maximum flood (PMF) design assumption that the Watts Bar Dam west saddle dike fails completely and instantaneously at approximately 1.5 feet of overtopping, was determined to be a non-conservative flood model assumption (i.e., invalid). As a result, TVA postulated that Watts Bar Dam's east floodwall would fail, increasing the site flood level at Watts Bar Nuclear Plant (WBN) by 1.7 feet; a condition that was beyond the current licensing basis. "Through subsequent analysis, TVA has demonstrated that although the west saddle dike may not completely and instantaneously fail during a PMF (as previously assumed), the consequential increase in reservoir levels does not result in a failure of the Watts Bar Dam east floodwall and would not result in an increase in the flood level at WBN. "Therefore, the previously reported 10 CFR 50.72(b)(3)(ii)(B) event is being retracted. "The NRC resident Inspector has been informed of this event retraction." Notified the R2DO (Hickey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-30
50244 | -1 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-30 22:46 | 2014-06-30 23:11 | 2014-08-21 | UNANALYZED CONDITION THAT COULD HAVE RESULTED IN AN INCREASED MAXIMUM FLOOD LEVEL "On June 27, 2014, TVA identified in a reanalyzed hydrologic analysis for Sequoyah Nuclear Plant (SQN) a deviation from the current hydrologic analysis. The flooding analysis in Section 2.4.3 of the SQN UFSAR assumes that the Watts Bar West Saddle Dike fails completely and instantaneously at approximately 1.5 feet of overtopping during a Peak Maximum Flood [PMF]. This assumption exists in the original design basis analysis and the revised analysis which supports SQN-TS-12-02, "Application to Revise Sequoyah Nuclear Plant Units 1 and 2 Updated Final Safety Analysis Report Regarding Changes to Hydrologic Analysis". "The results of recent studies of the West Saddle Dike, conducted as part of the Fukushima Order 2.1 flooding review, indicate that the complete and instantaneous failure of the Watts Bar West Saddle Dike may not be a valid assumption. If the dike does not fail, analyses performed using the codes and methods consistent with those used in original plant design show that the east floodwall of the Watts Bar Dam would overtop. As a result of this overtopping, the east floodwall is assumed to fail. Based on this assumption and analysis, failure of the east floodwall of the Watts Bar Dam would result in an increase in the flood level at the SQN Plant Site. The current licensing basis PMF level for SQN is 719.6 feet as stated in Section 2.4.2.2 of the SQN UFSAR. In addition, it should be noted that by letter dated August 10, 2012, as supplemented by letters dated April 5, 2013 and January 16, 2014, TVA proposed a revised PMF level of 722.0 feet. Introducing non failure of the Watts Bar West Saddle Dike indicated a potential increase of approximately 1.5 feet over the revised PMF level. "TVA performed additional analysis using current industry standard for flooding analysis. Specifically, TVA modeled the condition using the United States Army Corps of Engineers Hydrologic Engineering Center River Analysis System (HEC-RAS) tool. TVA's analysis of the condition using HEC-RAS determined that all required safety equipment for SQN would not be impacted and are considered operable based on a Prompt Determination of Operability completed on June 30, 2014. "This report addresses a condition as described in 10 CFR 50.72 (b)(3)(ii)(B). TVA is making this report consistent with the guidance of NUREG-1022 regarding the application of engineering judgment to the evaluation of reportability of an unanalyzed condition. "The NRC Resident Inspector has been notified of this condition." * * * RETRACTION AT 1441 EDT ON 8/21/2014 FROM MATT LEENERTS TO MARK ABRAMOVITZ * * * "On June 30, 2014, SQN reported (Event 50244) that during a re-analysis conducted as part of the Fukushima Order 2.1 flooding review, a probable maximum flood (PMF) design assumption that the Watts Bar Dam west saddle dike fails completely and instantaneously at approximately 1.5 feet of overtopping, was determined to be a non-conservative flood model assumption (i.e., invalid). As a result, TVA postulated that Watts Bar Dam's east floodwall would fail, increasing the site flood level at Sequoyah Nuclear Plant (SQN) by 1.5 feet; a condition that was beyond the current licensing basis. "Through subsequent analysis, TVA has demonstrated that although the west saddle dike may not completely and instantaneously fail during a PMF (as previously assumed), the consequential increase in reservoir levels does not result in a failure of the Watts Bar Dam east floodwall and would not result in an increase in the flood level at SQN. "Therefore, the previously reported 10 CFR 50.72(b)(3)(ii)(B) event is being retracted. "The NRC Resident Inspector has been informed of this event retraction." Notified the R2DO (Hickey). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-30
50243 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-06-30 16:05 | 2014-06-30 17:55 | 2014-06-30 | DISCOVERY OF AN AFTER-THE-FACT UNUSUAL EVENT "This is a one hour report for the discovery of a condition that briefly met the emergency action level (EAL) for an Unusual Event but did not warrant declaration of an emergency classification. A detailed review of the conditions that existed during a thunderstorm that took place today revealed that the backup 50 meter wind speed briefly indicated 95.5 mph, which exceeds the HU 1.3 criteria of 95 mph. The primary 50 meter wind speed indicator did not exceed 89 mph. Operators in the control room did not observe wind speed exceed 80 mph on SPDS. This event is a one hour report based on the guidance in NUREG-1022 for a condition that met an emergency plan EAL and the basis for the emergency classification no longer existed at the time of discovery." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW | [5 empty] | 0 | 2014-06-30
50242 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-30 07:48 | 2014-06-30 17:00 | 2014-07-01 | NON-LICENSED CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL ON A RANDOM FITNESS-FOR-DUTY TEST A non-licensed contract supervisor tested positive for alcohol on a random fitness for duty test. The supervisor's access to the facility has been terminated. The licensee has notified the NRC Resident Inspectors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2014-06-30
50241 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-30 13:10 | 2014-06-30 16:06 | 2014-06-30 | STACK HIGH RANGE RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE The Unit 2 stack high range radiation monitor was removed from service at 1310 EDT for planned maintenance. The monitor was returned to service at 1420 EDT after the completion of maintenance. The licensee notified the NRC Resident Inspector, the Connecticut Department of Energy and Environmental Protection, and Waterford city of this event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-30
50240 | 0 | U.S. AIR FORCE |  |  |  |  | 2014-05-19 | 2014-06-30 15:33 | 2014-06-30 | LOST NICKEL-63 ION SCAN SOURCE "Originally, an Ionscan 400, S/N 10586, was sent to Smith Detection for repair in October 2011. From that time until May 2014, Security Forces personnel believed that the device was still at Smith Detection awaiting repair. In May 2014, [The Air Force] was able to determine that according to Smith Detection records, following repair, the device had been returned to Lackland AFB in October 2012. Security Forces has no record of receiving the device and no notification that the device had been shipped. Thorough searches of Security Forces storage and use areas have been conducted without finding the device. One theory is that the device was sent to an old address for Security Forces. The building at that address has been searched without finding the device." Ionscan 400 contains a NI-63 source with an activity of 15 milliCi. The Ionscan 400 serial number is 10586. The sealed source and device registry number (SS&DR) associated with the Ionscan 400 is NR-0163-D-801-G. The device is used to screen passengers for hazardous material. The licensee will be notifying the NRC Region IV (Cook). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-07-08
50239 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-06-29 17:25 | 2014-06-30 15:30 | 2014-06-30 | AGREEMENT STATE REPORT - INABILITY TO RETRACT RADIOGRAPHY SOURCE TO ITS FULLY SHIELDED POSITION The following information was obtained from the Commonwealth of Pennsylvania via fax and email: "Event type: Inability to retract radiography source to its fully shielded position. "Notifications: The Department's [Pennsylvania Department of Environmental Protection] Central Office was informed of this event on June 30, 2014. This event is reportable within 24-hours per 10 CFR 34.101(a)(2) and 10 CFR 30.50(b)(2). "Event Description: A radiographer and his assistant were performing radiography above ground. During an exposure, the magnet holding the guide tube and collimator in place disengaged and the tube fell between some conduit below. This caused a [sharp] bend in the guide tube [which caused] the source to become lodged in place and un-retractable. The RSO was notified. The area was roped off to prevent unauthorized access and a retrieval team was called in to address the situation. At 5:35 am on June 30, 2014 the retrieval team notified the RSO that the source had been fully retracted. Dosimeter readings indicate no workers were exposed above regulatory limits as a result of this event. All badges are currently being sent for emergency readings. "Manufacturer: QSA Global "Model: 880 Delta "Serial Number: 14678C "Isotope: lr-192 "Activity: 70.2 Ci "Cause of the Event: Undetermined at this time "Actions: The camera and all associated equipment used during this event were removed from service and are currently being sent to the manufacturer for evaluation. The department plans a full reactive inspection. More information will be sent upon notification." PA Event Report ID No: PA140013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-07-08
50238 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-30 07:30 | 2014-06-30 07:50 | 2014-06-30 | PLANNED MAINTENANCE ON TECHNICAL SUPPORT CENTER VENTILATION "At 0730 EDT on Monday, June 30, 2014, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) charcoal filtration system was removed from service for scheduled maintenance. Under certain accident conditions, the TSC may become unavailable due to the inability of the charcoal filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 1500 EDT on Monday, June 30. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM JAMES SHAW TO VINCE KLCO AT 1327 EDT ON 6/30/14 * * * The charcoal filtration system was restored to service at 1245 EDT on 6/30/2014. The licensee will notify the NRC Resident Inspector. Notified the R3DO (McCraw). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-30
50237 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2014-06-28 22:06 | 2014-06-29 01:54 | 2014-06-29 | UNUSUAL EVENT - EARTHQUAKE FELT ON SITE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "An event classification of Unusual Event (HU1.1) was declared at 22:17 MST for the Palo Verde Nuclear Generating Station because of an earthquake that originated 50km NW of Lordsburg, New Mexico at 21:59 MST. Per the USGS website, the magnitude of the earthquake was 5.2 on the Richter scale. Initial walkdowns of plant equipment and review of plant parameters have found no unusual conditions or damage to plant equipment. No abnormalities caused by the seismic event were observed. No reactor protection system (RPS) or engineered safety feature (ESF) actuations occurred and none were required. Palo Verde Unit 1, 2, and 3 are at 100 percent power with all offsite power supplies available. "Initial analysis of the Seismic Monitoring Instrumentation System indicated a seismic event, below the magnitude of the 0.10g spectra Operating Basis Earthquake (OBE) and the 0.20g spectra Safe Shutdown Earthquake (SSE). "The NRC Resident Inspector has been notified of seismic activity and this ENS call." This event time is 2206 MST because this is the time the control room was notified by plant Operators that an earthquake had been felt on site. Notified DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. * * * UPDATE AT 0424 EDT ON 6/29/2014 FROM DENNIS MARTIN TO MARK ABRAMOVITZ * * * "Emergency classification termination was declared at 6/29/14 01:12 MST. All required power block inspections were completed with no deficiencies noted. No other conditions require an emergency classification, there are no challenges to fission product barriers or radiological release, and plant conditions offer no possibility of adverse impact on health and safety of the public." The licensee notified the NRC Resident Inspector, state and local governments. Notified the R4DO (Allen), NRR (Hiland), IRD (Gott), DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-06-29
50236 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-06-28 12:15 | 2014-06-28 14:53 | 2014-06-28 | OFFSITE NOTIFICATION TO THE STATE OF MINNESOTA FOR A FISH KILL "At 1215 PM CDT on June 28, 2014, Xcel Energy notified the Minnesota State Duty Officer that approximately 1000 dead fish of assorted species were discovered in the site's discharge canal. The fish perished due to rising temperatures in the discharge canal caused by an orderly shutdown of Cooling Towers as directed by procedure for response to flooding of the Mississippi River. The discharge canal is a body of water with a barrier from the Mississippi River. The Mississippi River temperature across the site has only risen 0.9F which is well within the permit limit of the maximum of 5F. "There is no impact to the availability of safety systems or safety system performance. This condition has no impact to public health and safety. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The licensee has notified the NRC Resident Inspector [and local authorities]." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-28
50235 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-27 15:35 | 2014-06-27 20:33 | 2014-06-27 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT ACTIVATION OF AN EMERGENCY SIREN "At approximately 1535 Pacific Daylight Time (PDT) the Diablo Canyon Power Plant [DCPP] Emergency Planning Supervisor received a notification from an offsite DCPP employee that one of the emergency plan sirens had inadvertently actuated. The DCPP Shift Manager was notified of the situation by approximately 1545 PDT. "The County of San Luis Obispo was notified of the inadvertent actuation of the single siren. At approximately 1550 PDT the County of San Luis Obispo sent out a county wide alert stating, 'Civil Emergency in this area until [1610] PDT prepare for action'. At approximately 1600 PDT the County of San Luis Obispo sent out another county wide alert stating, 'An early warning system siren was sounded in error. There is no emergency.' "Field technicians have been sent out to the siren location and will shut the siren off. The cause of the inadvertent actuation of the siren is not known at this time." The licensee notified the NRC Resident Inspector and the County of San Luis Obispo. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-27
50234 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-06-27 11:31 | 2014-06-27 16:21 | 2014-06-27 | INDIVIDUAL VIOLATED FITNESS FOR DUTY POLICY "On June 27, 2014, at approximately 1131 hours EDT, it was determined that an individual who is licensed under Part 10 CFR Part 55 to operate a power reactor was in violation of the FENOC [FirstEnergy Nuclear Operating Company] Fitness for Duty policy. "This condition is being reported pursuant to 10 CFR 26.719(b)(2)(ii) . "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2014-06-27
50233 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-06-25 23:48 | 2014-06-27 15:22 | 2014-06-27 | UNPLANNED CONTAMINATION EVENT "Event Text: At approximately 2348 hours (ET) on June 25, 2014, an employee dropped a container of radioactive material solution after removal from a glove box enclosure. The 2-liter poly container split, releasing contents to the floor and surrounding equipment. Operations in the area were placed in a safe condition at the time of the event, radiological controls implemented for personnel protection, and decontamination initiated. Extensive surface contamination surveys were performed to facilitate decontamination and the area was released to normal access by 1615 hours (ET) on June 26, 2014. At this time, the additional radiological controls implemented at the time of the event were removed. At 0245 hours (ET) on June 27, 2014, contamination was discovered to be weeping out of some facility and equipment surfaces in the area of the earlier spill. Radiological controls were reestablished, decontamination efforts resumed, and enhanced monitoring implemented. Since the cumulative time for access restrictions exceeded 24 hours, this is being reported to the [NRC] Operations Center under 10 CFR 70.50 (b)(1). "There were no actual or potential safety consequences to the public or the environment. There were no actual safety consequences to the workers. The potential safety consequences to the workers include exposure to uranyl nitrate solution. "The licensee has notified the NRC Resident Inspector." The radioactive material solution was Uranyl Nitrate containing 540 grams of Uranium-235. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2014-07-01
50232 | 0 | ELI LILLY AND COMPANY |  |  |  |  | 2014-06-26 | 2014-06-27 12:56 | 2014-06-27 | IMPROPERLY DISPOSED OF TRITIUM SIGNS Notified by the licensee that three tritium exit signs were improperly disposed of as trash. The signs were manufactured by SRBT with an estimated source strength of 20 Ci for each sign. The licensee noticed the missing signs following an equipment inventory taken after a renovation. The licensee determined that the three signs were mixed with general construction debris and sent to a landfill. The licensee investigation is continuing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-07-07
50231 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2014-05-08 13:20 | 2014-06-27 11:22 | 2014-06-27 | 60-DAY TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of Emergency Diesel Generator 'B' on May 8, 2014 during the performance of 480v safeguards Bus 16 Under Voltage (UV) testing. Emergency AC Electrical Power system, including Emergency Diesel Generators, is a system named in 50.73(a)(2)(iv)(B). "During testing of the Bus 16 UV cabinet, a human performance error resulted in the simultaneous auto start of the 'B' Emergency Diesel Generator and trip of the Bus 16 normal supply breaker. This is defined as an 'invalid signal' in that the 'B' Emergency Diesel Generator did not start as the result of an actual UV condition on Bus 16. "This start signal is considered an INVALID signal with respect to 50.73(a)(2)(iv)(A), however the system was not fully removed from service. The 'A' train was not affected by this event. The actuation was considered complete since all necessary components responded as would have been expected if there had been a valid UV signal. "The NRC Resident lnspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-06-27
50230 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-26 09:18 | 2014-06-26 15:29 | 2014-06-26 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR IN VIOLATION OF DUKE ENERGY FITNESS FOR DUTY POLICY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to both the McGuire and Oconee plants has been restricted. The NRC Resident Inspectors at both the McGuire and Oconee sites have been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2014-06-26
50229 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-06-19 11:45 | 2014-06-26 15:15 | 2014-06-26 | ONE INCORE DETECTOR CONTAINING U-235 UNACCOUNTED FOR DURING INVENTORY "This is a non-emergency notification regarding a very small amount of Special Nuclear Material (SNM) which is unaccounted for. On May 30, 2014, a discrepancy was found in the V.C. Summer Nuclear Station SNM inventory. After extensive review, it was determined on June 19, 2014 that one nuclear instrumentation incore detector could not be located at V.C. Summer Nuclear Station. Detectors of this type are used to measure incore neutron flux (intensity of neutron radiation) inside the reactor vessel. This is being reported under 10 CFR 20.2201 (a)(1)(ii) Reports of Theft or Loss of Licensed Material. "According to V.C. Summer documentation, there should be 42 such detectors in storage. Only 41 detectors could be physically located. There is no evidence of theft or diversion of the detector. Detectors of this type contain very small amounts of Uranium-235 (.0041 grams/detector), which qualifies them as SNM. The detector is believed to be located in a storage location in the Reactor Building (RB). The RB storage location will be inspected during the next refueling outage. "This event had no effect on plant operations. No impact on public health and safety has been identified. A written report will be made in accordance with 10 CFR 20.2201(b)(1)(i-vi). "The NRC Resident Inspector has been notified by the licensee." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-07-04
50228 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2014-06-23 | 2014-06-26 12:28 | 2014-06-27 | AGREEMENT STATE REPORT - DAMAGED FIXED GAUGE FOUND IN SCRAP METAL SHIPMENT The following information was received by facsimile from the State of Oregon: "Event Description: OR Radiation Protection Services [RPS] was notified by facsimile on June 24, 2014 at 0813 [PDT], by Schnitzer Steel Industries, 12005 N. Burgard Way [Portland, Oregon] of one cesium-137 fixed gauge received in a truckload of scrap from Idaho that triggered their site entry detectors. RPS personnel investigated, found the gauge housing to be severely crushed, shutter damaged and partially open. One side of housing is split but compressed together. Identification plate still attached and mostly legible and given as follows: Manufacturer: Texas Nuclear; Model: 5197; Gauge housing serial number: B7951; Source: Cesium-137; Activity: Currently 65 mCi according to Thermo Fisher Scientific. "Gauge is being stored in secured metal bin in restricted and remote area on company site. Highest exposure reading at bin surface measured at 1.48 mR/hour. Schnitzer personnel reported 60,000 microR/hour (60 mR/hour) at approximately 4 inches from split side of gauge housing surface when first discovered. Schnitzer personnel (one person) used shovel and 4 foot steel rod with hook to move gauge from truck to storage bin on June 23rd. Estimated dose to company person from reconstruction of gauge move is 1.50 mrem based on a 6/25/14 exposure measurement. No other company employees received a dose from this device and RPS personnel did not receive any appreciable dose. "RPS personnel took contamination wipes of gauge housing and found no evidence of exterior contamination after analysis. "The manufacturer, now Thermo Fisher Scientific, was contacted and found the gauge was originally sold to a Martell, California company, Wheelabrator Martell, Inc., on August 23, 1996. Thermo added the last contact for leak test services was December, 1999. RPS is currently investigating further to trace gauge history since 1999 as well as location in Idaho where truck originated. The gauge will not be returned to the manufacturer according to Thermo and classified as waste. A waste broker will be contacted by Schnitzer for packaging and disposal. RPS will be monitoring this process." Oregon State Incident: OR-14-0028. * * * UPDATE FROM DARYL LEON TO VINCE KLCO VIA EMAIL ON 6/27/14 AT 1336 EDT * * * State of Oregon provided clarification of source activity and exposure estimate. Notified the R4DO (Allen) and FSME Resources via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2014-07-04
50227 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-25 15:55 | 2014-06-25 22:59 | 2014-06-25 | POTENTIAL LOSS OF ULTIMATE HEAT SINK CAPACITY DUE TO LOW LEVEL "At approximately 1555 CDT on Wednesday, June 25, 2014, during a review of several station abnormal operating procedures for actions related to low ultimate heat sink (UHS) level, it was discovered that the procedures do not incorporate design assumptions for shutting down the non-essential service water (WS) pumps following a loss of cooling lake dike. The pumps that take suction from the UHS include the WS, circulating water (CW) and fire protection (FP) pumps. Based on current procedural guidance, the only pumps that are secured due to a low ultimate heat sink level are the circulating water (CW) pumps based on low net positive suction (NPSH) "Failing to secure the non-essential pumps on a loss of cooling lake dike failure significantly reduces the 30 day design basis UHS volume to approximately 4 days. "This event is being reported in accordance with 10CFR50.72(b)(3)(ii)(B) for 'any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "Immediate actions taken included issuance of an operations standing order providing direction to secure non-essential pumps on the failure of the cooling lake dike. Proposed corrective actions include procedure revisions. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-25
50226 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-06-24 20:32 | 2014-06-25 11:48 | 2014-06-25 | FITNESS FOR DUTY - CONFIRMED POSITIVE FOR A CONTROLLED SUBSTANCE A non-licensed contract employee had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's plant access has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2014-06-25
50225 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-06-25 | 2014-06-24 15:06 | 2014-06-25 | VARIOUS TELECOMMUNICATION LINES AND ERDS OUTAGE FOR PLANNED MAINTENANCE "Planned preventive maintenance will render parts of telephone system and Emergency Response Data System (ERDS) nonfunctional. As a result, this represents a loss of emergency communications capability and is reportable under 10 CFR 50.72(b)(3)(xiii). The maintenance is scheduled to begin on 6/25/2014 at 00:00 [CDT], and is expected to last approximately 5 hours. During this maintenance window, various communication connections will be intermittently interrupted for short periods of time. Affected communication connections include some local telephone company lines, Federal Telephone System, ERDS, the Monticello's NRC office, and automatic ring down lines to the state of Minnesota's Emergency Operations Center. "During the planned maintenance window, communications to offsite will be available via radios, cell phones, and satellite communications. This ensures that the plant can adequately communicate with the NRC, state, and local agencies to ensure protection of the health and safety of the general public. "The NRC Resident Inspector has been notified of the planned telecommunications maintenance." Licensee also notified the Minnesota State Duty Officer and the Wright and Sherburne County Sheriff dispatchers. * * * UPDATE PROVIDED BY DAMON HESSIG TO JEFF ROTTON AT 1823 EDT ON 06/25/2014 * * * "At 0500 [CDT] on 6/25/2014, planned maintenance on the Monticello telecommunications system was completed. At 1630 [CDT] on 6/25/2014, testing of all telecommunications was completed. All systems are functioning properly. "The NRC Resident Inspector has been notified that the telecommunications system is functional. The Minnesota State Duty Officer and the Wright and Sherburne County Sheriff dispatchers have been notified that the telecommunications system is functional." Notified R3DO (Lara). | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-24
50224 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2014-06-24 11:38 | 2014-06-24 12:24 | 2014-06-24 | INDIVIDUAL PROVIDED FALSIFIED INFORMATION FOR UNESCORTED ACCESS Individual gained unescorted access through falsification of information on personnel history questionnaire. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-06-24
50223 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-24 11:00 | 2014-06-24 10:37 | 2014-06-24 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 1100 EDT on Tuesday, June 24, 2014 the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 16:00 EDT on Tuesday, June 24. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * *UPDATE PROVIDED BY KURT BERAN TO JEFF ROTTON AT 1617 EDT ON 06/24/2014 * * * At 1615 EDT, TSC ventilation systems were restored to service. The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Lara) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-24
50222 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-06-23 15:40 | 2014-06-23 19:55 | 2014-06-23 | REPORTABLE SMALL OIL SPILL INTO U.S. WATERS "On 06/23/2014 at approximately 1540 [CDT], it was reported that an oil sheen was visible in the fore bay. Upon further investigation it was determined that a high cold water channel level had caused diesel fuel oil to wash free from an oil drain device from the channel diesel fire pump into the fore bay. This oil spill is reportable to the EPA (National Response Center) under 40CFR112. Notification to the National Response Center was made at 1551 [CDT]. Notification number is 1086840. "A total of 1 to 2 gallons were reported to enter US waters. The source of leak into the fore bay and cold water channel has been stopped. All reportable oil spillage has been contained in the fore bay (considered US waters). "Additional notifications have been made to Alabama Emergency Management." The licensee has notified the NRC Resident Inspector. | 100 | 93 | 100 | 100 | 93 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-23
50221 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-06-23 11:07 | 2014-06-23 17:02 | 2014-06-23 | EMERGENCY DIESEL GENERATOR AUTO START DUE TO DEGRADED BUS VOLTAGE SIGNAL "At 1107 [CDT] on 6/23/14, Safeguards Bus 15 received a degraded voltage signal that resulted in the bus load shed and the automatic start of the D1 Emergency Diesel Generator (EDG). Bus 15 re-energized to normal voltage after the source breaker from D1 [EDG] automatically closed. This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) for valid actuation of the D1 EDG. "The initiating condition appears to be a failure of the automatic voltage tap changer on the 10-Bank transformer which affected voltage to the normal offsite power supply to the 1R transformer and Safeguards Bus 15. "Currently Bus 15 is powered from offsite via the CT-11 transformer and D1 [EDG] has been shutdown. "When Bus 15 power supply was transferred from D1 [EDG] to CT-11 transformer, a lockout was received on D1 [EDG] due to reverse power. Unit 1 is in TS [Technical Specification] 3.8.1 Condition D for one path inoperable and one EDG inoperable. "At no time during the event were the health and safety of the public challenged. The redundant AC power supply train (Bus 16 and D2 EDG) remained operable and Bus 16 remained powered from offsite power. "The Senior Resident Inspector has been notified." TS 3.8.1 Condition D requires that the one inoperable offsite power path or the D1 EDG be returned to operable status by 2334 CDT or be in Mode 3 in 6 hours. Unit 2 is not affected by this issue. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-06-23
50220 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-06-23 09:00 | 2014-06-23 09:20 | 2014-06-25 | LOSS OF COMMUNICATIONS DUE TO PLANNED MAINTENANCE "A planned maintenance evolution at the Oyster Creek Nuclear Generating Station has removed the dedicated phone line between Emergency Response Facilities and the NARS [Nuclear Accident Reporting System] line from service and will be rendered non-functional during the course of the work activities. Expected out of service time is approximately 82 hours from 0900 [EDT] 6/23/14 to 1900 [EDT] 6/26/14. "If an emergency is declared requiring the use of emergency communication phone circuits a proceduralized alternative method will be used. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) for planned maintenance that impacts the emergency communications capability. An update will be provided when the dedicated phone line between Emergency Response Facilities and the NARS line has been restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JOHN DEVENNEY TO JEFF ROTTON AT 1738 EDT ON 06/25/2014 * * * "At 1700 EDT on 6/25/14 planned maintenance is complete and the dedicated phone line between Emergency Response Facilities and the NARS line has been restored to normal operation." The licensee notified the NRC Resident Inspector. Notified R1DO (Bickett) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-23
50219 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-20 11:00 | 2014-06-20 16:39 | 2014-06-20 | LOSS OF PLANT VENT EFFLUENT MONITORS "This is a non-emergency notification. On June 20, 2014, at 1100 eastern daylight time (EDT), Vogtle Unit 2 identified a loss of emergency assessment capability due to both plant vent effluent monitors being out of service from March 16 to March 26, 2014. This condition was the result of an equipment failure concurrent with planned maintenance activities on the redundant monitor. This event is reportable per 10 CFR 50.72(b)(3)(xiii). "During the time both effluent monitors were out of service Unit 2 was operating at 100% rated thermal power, steady-state conditions. Therefore, this condition does not affect the health and safety of the public or the operation of the facility." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-20
50218 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-06-19 | 2014-06-20 11:11 | 2014-07-01 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following report was received via e-mail: "On June 20, 2014, the Agency [Texas Department of Health] was notified by the licensee of the loss of a Humboldt model 5001EZ moisture density gauge, serial #4772, containing a 1.48 GBq (40 mCi) Am-Be source and a 0.3 GBq (8 mCi) Cs-137 source. The licensee stated a technician was working at a job site on June 19, 2014, when he rushed home for a family emergency. He failed to secure the gauge in the back of the truck and he left the tailgate down. The gauge fell off the truck between the job site and his home. The licensee stated they searched the job site and the route taken by the technician." Texas event: I-9205 * * * UPDATE AT 1040 EDT ON 7/1/2014 FROM IRENE CASARES TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On Saturday June 28, 2014, the gauge was reported, via email from the licensee, as found and the gauge was sent off for any damage identification and leak check. It was reported that the gauge was not damaged and passed the leak check. Two violations were cited." Notified the R4DO (Hagar), FSME Events Resource (via e-mail) and Mexico (via e-mail).. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-06-30
50217 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-06-20 08:15 | 2014-06-20 08:12 | 2014-06-20 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR MAINTENANCE "Notification for planned, routine, preventative maintenance on Technical Support Center [TSC] HVAC. The expected start of preventative maintenance is 06/20/14 at 0815 EDT. Planned completion is 06/20/14 at 1500 [EDT]. Maintenance renders the TSC nonfunctional. The planned TSC alternative will be the Control Room. "This event is reported in accordance with 10 CFR 50.72 (b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE TO TIM JONES TO JOHN SHOEMAKER AT 1559 EDT ON 6/20/14 * * * Maintenance is complete and the TSC HVAC was restored to service at 1455 EDT on 6/20/14. The TSC is now functional. The licensee has notified the NRC Resident Inspector. Notified R2DO (Haag). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-20
50216 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-06-20 01:10 | 2014-06-20 07:31 | 2014-06-24 | RADIATION MONITORS DECLARED NON-FUNCTIONAL "At 0110 [EDT] on June 20, 2014, Nine Mile Point Unit 2 lost communication to the DRMS (Digital Radiation Monitor System Computer). The DRMS provides the Control Room alarm functions for Offgas Pretreatment Process Radiation Monitors 2OFG-CAB13A/13B and Cooling Tower Blowdown Effluent Radiation Monitor 2CWS-CAB157. Due to the loss of the Control Room alarm function, 2OFG-CAB13A, 2OFG-CAB13B, and 2CWS-CAB157 have been declared non-functional. Compensatory measures (i.e. collect and analyze grab samples) have been implemented per the requirements of the Offsite Dose Calculation Manual (ODCM). "The non-functional radiation monitors are necessary for accident assessment and are credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to the out of service radiation monitors is considered a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." The licensee has notified the State. * * * UPDATE PROVIDED BY CHRIS SKINNER TO JEFF ROTTON AT 1313 EDT ON 06/24/2014 * * * "At 1208 [EDT] on June 21, the DRMS was declared functional. With the alarm functions restored, radiation monitors 2OFG-CAB13A, 2OFG-CAB13B, and 2CWS-CAB157 were declared functional and compensatory actions per the ODCM have been discontinued." The licensee notified the NRC Resident Inspector and the State of New York. Notified R1DO (Bickett). .. . . | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-20
50215 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-06-19 20:35 | 2014-06-20 01:08 | 2014-06-20 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 1435 [CDT] on June 19, 2014 while performing Unit 1 A Train Safeguards Logic Test at power, it was discovered, while testing the Safety Injection Automatic Actuation Relay Logic, that the 1SI-15x, SI RELAY TRAIN A, was not making up the contact to energize 1SI-16x, SI AUX RELAY TRAIN A. As a result, the 8 hour exception for testing allowed under LCO 3.3.2 Condition C no longer applied, and the 6, 12, and 42 hour clocks associated with condition C were entered. "At 2035 [CDT] on June 19, when the 6 hour time limit to complete Condition C.1 action could not be completed operators began preparation to shutdown Unit 1 to Mode 3 by 0235 on 6/20/14. "At 2245 [CDT] on June 19, 2014 operators commenced reducing reactor power of Prairie Island Unit 1. As of 0003, June 20, Unit 1 was at 55 percent power and continuing to reduce load. "This event is reportable per 10CFR50.72(b)(2)(i) - 'The initiation of any nuclear plant shutdown required by the plant's Technical Specification'. "The protection of the health and safety of the public is not affected by this issue. "The NRC Resident Inspector has been notified." | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-06-20
50214 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-06-20 00:01 | 2014-06-20 00:29 | 2014-06-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "The National Weather Service predicts that the Missouri River level at Fort Calhoun Station will exceed 1004 feet above mean sea level on 6/20/14 at approximately 2300 CDT. Fort Calhoun Station will begin a ramp down in power to satisfy technical specification 2.16 which states, 'When the Missouri River level reaches elevation 1004 feet mean sea level, the reactor shall be in a HOT SHUTDOWN condition [Mode 3] and in Cold Shutdown [Mode 4] within 36 hours following entry into Hot Shutdown.' The river level is currently 998 feet 3 inches and rising approximately 0.5 inches per hour. At time 0001 CDT 6/20/14 Fort Calhoun station will initiate a plant shutdown to Hot Standby and will proceed to a Cold Shutdown condition within 36 hours following entry into Hot Shutdown, as required." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY SCOTT LINDQUIST TO JEFF ROTTON AT 2340 EDT ON 06/22/2014 * * * "EN 50214 is being retracted. At 2300 [CDT] on 6/21/14, actual Missouri River level at Fort Calhoun Station peaked at 1001' 2" mean sea level (msl) and did not reach TS 2.16 (1) shutdown criteria of 1004' msl. Based on current Army Corps of Engineers and National Weather Service published Missouri River levels, the river upstream of Fort Calhoun Station has peaked and is trending down following the recent storms. River level is predicted to continue trending downward to normal summer navigation season levels. Plans to shutdown have been terminated. Fort Calhoun Station will continue to monitor weather and river levels. Current reactor power is 66% and Fort Calhoun Station is raising power to 100%." The lowest reactor power achieved was 30 percent at 1200 CDT on 06/20/2014. The licensee notified the NRC Resident Inspector. Notified R4DO (Hay) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-06-20
50213 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-06-19 16:28 | 2014-06-19 17:06 | 2014-06-19 | UNANALYZED CONDITION DUE TO A POSTULATED HOT SHORT THAT COULD AFFECT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) circuits has determined the described condition to be applicable to the Perry Nuclear Power Plant (PNPP) resulting in an unanalyzed condition with respect to fire safe shutdown requirements. "In the postulated event, a fire induced hot short could adversely impact safe shutdown equipment. The potential exists for a secondary fire to occur due to unfused DC control circuits associated with the Turbine Emergency Bearing Oil Pump, Reactor Feed Pump Turbine 'A' Emergency Lube Oil Pump, Turbine Emergency Seal Oil Pump, and Reactor Feed Pump Turbine 'B' Emergency Lube Oil Pump. These circuits are routed from the respective equipment to other plant areas including the Unit 1 Control Room, Division 1 Cable Spreading, and Division 1 Cable Chase. "Without overcurrent protection for these circuits, the potential exists that an initial fire event affecting these circuits could cause short circuits without protection that would cause excessive current through the circuit beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where these circuits are routed challenging the ability to achieve and maintain safe shutdown. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-19
50212 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-22 08:30 | 2014-06-19 15:19 | 2014-06-19 | EMERGENCY DIESEL GENERATOR INVALID ACTUATION "This report describes an invalid actuation of the Unit 2, Train A (2-01) Emergency Diesel Generator (EDG) that occurred on April 22, 2014. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A). 10CFR50.73(a)(1) states, in part, 'In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the Reactor Protection System (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' "On April 22, 2014, Comanche Peak Nuclear Power Plant Unit 2 was in Mode 5 during the 14th refueling outage. At approximately 0830 CDT, while performing a lockout test on EDG 2-01, the Reactor Operator made a place keeping error that resulted in EDG 2-01 starting and rolling up to approximately 300 RPM. The start signal should have been blocked as part of the test. However, a step was skipped due to a place keeping error and this resulted in an inadvertent start of EDG 2-01 during the performance of a subsequent step. "The specific train and system that actuated was the Unit 2, Train A, Emergency Diesel Generator. During the inadvertent EDG start the system started and functioned correctly, and the EDG only reached 300 RPM before it was shut down. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-06-19
50211 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-19 08:03 | 2014-06-19 15:08 | 2014-06-19 | PROCESS RADIATION MONITOR MAINTENANCE "System affected: Normal and High Range SLCRS [Supplementary Leakage Collection and Release System] ventilation process radiation monitors. "Actuations and their initiation signals: None. "Causes: Removed from service for scheduled maintenance. "Effect of event on plant: None. "Actions taken or planned: Complete required calibration. "Additional information: Will be returned to service following maintenance." The licensee notified the NRC Resident Inspector and applicable State and local agencies. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-19
50210 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-06-18 15:45 | 2014-06-18 21:20 | 2014-08-13 | LOSS OF HPCI ROOM COOLING "At 1545 [EDT], while testing of the Emergency Service Water system (ST-8Q) was being performed at the James A. FitzPatrick Nuclear Power Plant (JAF), two of five unit coolers (66UC-22H and 66UC-22K) in the East Crescent were found with indicated flow of 0 gpm. The other three unit coolers in the East Crescent Area were found with sufficient flow. At least four unit coolers are required to support the functionality of the East Crescent Area Ventilation Subsystem (TRO 3.7.C). The East and West Crescent Area Ventilation Subsystems support the Operability of the Emergency Core Cooling Systems (ECCS) and Reactor Core Isolation Cooling (RCIC) system by removing heat from the areas, in the event that ECCS and RCIC were used to mitigate the consequences of an accident. "The West Crescent Area Ventilation Subsystem remained functional. The accident mitigating function of the division of ECCS and RCIC located in the West Crescent Area were unaffected by this condition. However, this condition could have prevented the function of one division of the ECCS, including the single train of High Pressure Coolant Injection (HPCI), located in the East Crescent. Therefore, this condition could have prevented fulfillment of the safety function of HPCI and it is being reported under 10 CFR 50.72(b)(3)(v)(D). "As part of the testing, the throttle valves to the unit coolers (66UC-22H and 66UC-22K) were cycled and normal flow was restored. This condition no longer exists." The licensee is investigating the loss of flow to the "H" and "K" unit coolers and the restoration of flow by cycling the unit cooler supply throttle valves. The licensee will be notifying the NRC Resident Inspector. * * * RETRACTION FROM DAVID CALLEN TO DANIEL MILLS AT 1506 EDT ON 8/13/2014 * * * "FitzPatrick is retracting EN # 50210 made on June 18, 2014 at 2120 EDT. The plant was at 86% power at the time. The ENS notification was an 8-Hr non-emergency notification to 10 CFR 50.72(b)(3)(v)(D) when it was discovered that two of five unit coolers in the East Crescent (66UC-22H and 66UC-22K) were found with indicated flow of 0 gpm while testing. The other three unit coolers in the East Crescent (66UC-22B, 66UC-22D, 66UC-22F) were found with sufficient flow. At least four unit coolers are required to support the functionality of the East Crescent Area Ventilation subsystem (TRO 3.7.C). The East and West Crescent Area Ventilation subsystems support the Operability of the Emergency Core Cooling Systems (ECCS) and Reactor Core Isolation Cooling (RCIC) system by removing heat from these areas in the event that ECCS and RCIC are used to mitigate the consequences of an accident. As part of testing, throttle valves to unit coolers 66UC-22H and 66UC-22K were cycled and normal flow was restored. "The West Crescent Area Ventilation subsystem remained functional. The accident mitigating function of the division of the ECCS and RCIC located in the West Crescent Area were unaffected by this condition. Initial review of this condition determined that it could have prevented the function of one division of the ECCS, including the single train of High Pressure Coolant Injection (HPCI), located in the East Crescent. Therefore, this condition was initially reported under 10 CFR 50.72 (b)(3)(v)(D) as a condition that could have prevented fulfillment of the Safety function of HPCI. "This EN# 50210 is being retracted based upon a subsequent engineering analysis that determined that there is reasonable assurance that the three unit coolers with sufficient flow (66UC-22B, 66UC-22D, and 66UC-22F) would have been capable of removing accident heat loads as a function of time to maintain East Crescent area temperatures at a value which ensures operability of supported equipment. The analysis considered unit cooler heat transfer capability at the modified design condition flow of 22 gpm for historically observed lake temperatures and for flow at tested conditions. Additional margin in flow at the tested condition provided increased heat removal capability and provided added assurance that accident heat load would have been removed. The East Crescent Area Ventilation subsystem was, therefore, functional with three unit coolers (functionality never was lost) and the supported ECCS remained Operable. The Operability determination for the condition has subsequently been revised based upon the engineering analysis, to state the condition was not immediately reportable per 10 CFR 50.72." The licensee has notified the NRC Resident Inspector Notified R1DO (Kennedy) | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-06-18
50209 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-18 08:32 | 2014-06-18 12:35 | 2014-06-18 | MAINTENANCE BEING PERFORMED ON MAIN STEAM LINE RADIATION MONITORS "At 0832 EDT on 6/18/2014, Millstone Station Unit 2 removed the Main Steam Line Radiation Monitors RM-4299B and RM-4299C from service for pre-planned maintenance. Portable handheld radiation detectors will be used to assess radiation releases. Both radiation monitors will be restored no later than 2200 EDT on 6/19/14." The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-18
50208 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-06-17 19:00 | 2014-06-18 09:58 | 2014-06-18 | ITEMS RELIED ON FOR SAFETY (IROFS) BYPASSED "At approximately 1900 hours (EDT) on June 17, 2014, an employee was observed improperly operating two (2) spring return valves identified as Items Relied On For Safety (IROFS) and Safety Related Equipment (SRE). The spring return valves were observed to be 'propped' open. These spring return valves were intended to be manually operated to prevent [a chemical solution] from overfilling a column, spilling to the floor, and causing an acute chemical exposure. No actual overflow occurred. Although the operator was observing and monitoring the filling of the column, the operation of the spring return valves was improper. Operations in the area have been placed in a safe condition and an investigation is underway. This condition was determined to be reportable at 0910 (Eastern Time) on June 18, 2014. "There were no actual or potential safety consequences to the public or the environment. There were no actual safety consequences to the workers. The potential safety consequences to the workers include exposure to [a hazardous chemical] solution. "The licensee notified the NRC Resident Inspector and NRC Region 2." NFS Event (PIRCS) No. - P44298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2014-06-26
50207 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-06-17 17:29 | 2014-06-17 21:45 | 2014-06-17 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO LOSS OF A AND B CONTROL BAY CHILLER TRAINS "At 1729 [CDT] on June 17, 2014 Browns Ferry Units 1, 2, and 3 initiated actions to commence a reactor shutdown to comply with TS LCO [Technical Specifications Limiting Condition of Operation] 3.0.3. TS LCO 3.0.3 was entered at 1632 and was required due to the concurrent loss of 'A' and 'B' Control Bay Chiller units which resulted in loss of cooling to the U1 and U2 4kV Shutdown Board Rooms. Required actions for the loss of cooling to the U1 and U2 4kV Shutdown Board Rooms is to declare the electrical equipment in the 4kV Shutdown Board Rooms inoperable. The declaration of inoperability of the equipment supported by the U1 and U2 4kV Shutdown Boards resulted in TS LCO 3.0.3 for Units 1, 2 and 3. TS LCO 3.0.3 requires actions to be initiated within one hour to place the units in MODE 2 within 10 hours; MODE 3 within 13 hours; and MODE 4 within 37 hours. "This event requires a 4 hour report IAW 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector has been notified. "Service Request 899734 was initiated in the Corrective Action Program." The 'B' Control Bay Chiller train was operating when the control room entered the Loss of Chilling procedure. The 'A' Control Bay Chiller train was started to supply Control Bay cooling, and the 'A' train unit tripped during start. The failure affected unit-3 because each unit has a 50% capacity common standby gas treatment system. The loss of the the U1 and U2 4kV shutdown boards failed two of the three systems. * * * UPDATE PROVIDED BY TODD BOHANAN TO JEFF ROTTON AT 2154 EDT ON 06/17/2014 * * * "'A' Control Bay Chiller declared operable at 2035 CDT. TS LCO 3.0.3 exited and plant shutdowns have been secured." The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Haag) | 98 | 94 | 98 | 100 | 96 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-06-17
50206 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-17 07:49 | 2014-06-17 13:50 | 2014-06-17 | STACK RADIATION MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE At 0749 EDT, Millstone Station Unit 2 removed the Stack Radiation Monitor RM-8169 from service for planned maintenance. Maintenance and testing were completed and the Stack Radiation Monitor was returned to service at 0945 EDT. The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-17
50205 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-06-16 | 2014-06-16 18:58 | 2014-06-16 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of Arizona via email: "On June 16, 2014, the Agency [State of Arizona] was notified of the theft of a Troxler Model 3450 Moisture-Density gauge Serial Number 533, from a locked box on a pickup truck parked in a secure area of the licensee facility. Other equipment was also stolen from the truck. The locks and one hasp and a gate lock were ground off. The theft occurred over the June 14 -15 weekend. "The investigation into this event is ongoing. "The AZ Governor's Office, FBI, US NRC, and the states of CA, NV, CO, and NM are being notified of this event." First Notice: 14-014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-06-24
50204 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2014-06-13 | 2014-06-16 16:40 | 2014-07-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the State of Wisconsin via email: "During an inventory on June 13, 2014, the licensee determined a total of 6 tritium exit signs were not accounted for at the facility. One 20 Ci SRB Technologies sign and five 11.5 Ci Safety Light Corporation signs were missing. Three of the signs are known to have been removed during a previous remodeling and are presumed to have been disposed of with the waste. The three other signs are missing from their normal locations. Maintenance staff have been alerted to the missing items and told to look for them in the storage areas. Additional training is being developed that will require any person who removes an exit sign, regardless of type, to return it to the Environmental, Health, and Safety Department for review prior to disposing. A plan is also in place to remove all tritium exit signs from the facility and replace with electrically wired signs. The Wisconsin Radiation Protection Section is continuing to monitor the situation." Event Report ID: WI 140007 * * * UPDATE FROM KYLE WALTON TO JOHN SHOEMAKER AT 1630 EDT ON 7/1/14 * * * The State of Wisconsin reported that one of the missing signs has been found and only two signs remain missing. The licensee will continue searching for the missing signs. Notified the R3DO (McCraw) and FSME Events Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2014-06-24
50203 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-06-16 10:27 | 2014-06-16 13:38 | 2014-06-16 | OFFSITE NOTIFICATION DUE TO HYDRAULIC OIL SPILL "At approximately 1027 CDT on June 16, 2014, Xcel Energy notified the Minnesota State Duty Officers that a hydraulic hose on a cement truck failed and spilled approximately 15 gallons hydraulic oil to grade at a building site for the new Site Administrative Building. The hydraulic oil spill did not enter the storm drain system or any water ways. The site is in the process of cleaning up the spill. "There is no impact to public health and safety or the environment due to this incident. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-16
50202 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-06-16 12:44 | 2014-06-16 13:34 | 2014-06-16 | POTENTIAL COMPROMISE OF SAFEGUARDS INFORMATION Discovered improperly controlled information that could have been used to defeat a security system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-06-16
50201 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-06-16 | 2014-06-16 11:43 | 2014-06-16 | AGREEMENT STATE REPORT - STUCK SHUTTERS The following was received from the State of Texas via email: "On June 16, 2014, the Agency [State of Texas] was notified by the licensee's Radiation Safety Officer (RSO) that while conducting routine maintenance checks, the shutter on two Ohmart-Vega Model SHD source holders containing 250 millicuries of cesium-137 failed to shut. A third SHD source holder shutter appeared to shut but there was no change in the radiation level as expected. The RSO has contacted a vendor to inspect and repair the gauges. The gauges are normally open. There were no exposures as a result of this event. More information will be provided as it is obtained in accordance with SA-300." Texas Incident: I-9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-06-24
50200 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-06-13 04:52 | 2014-06-13 11:54 | 2014-06-13 | LOSS OF BOTH TRAINS OF CONTROL STRUCTURE CHILLED WATER "On 6/13/2014 at 0417 [EDT], Limiting Conditions of Operation were entered on SSES Units 1 and 2 for an inoperable Train of Control Structure Chilled Water for planned maintenance. During clearance order application at 0452 on 6/13/2014, a switching move caused the in service [Division 1] Control Structure Chilled Water Train to trip and be declared inoperable. It was realized that a prior switching move had already rendered the standby train [Division 2] inoperable. There was no equipment failure or misoperation associated with this event. The trip of the running Control Structure Chiller was in accordance with its control logic scheme. This was not identified during the planning phase of this evolution. "During this time both divisions of Control Structure Chillers were inoperable and were not available to perform the required safety function. This condition also resulted in the inoperability of Control Room Emergency Outside Air Supply System due to the relationship between some of the equipment. This is a condition that, at the time of discovery, could have prevented fulfillment of Safety Functions and is reportable under 50.72(b)(3)(v)(D) as an 8 hour notification. "The loss of safety functions are based on 1) the SSC is inoperable in a required mode of operation, 2) the inoperability is due to procedural deficiency, and 3) there was no redundant equipment in the same system that was operable. "One Train of Control Structure Chilled Water and Control Room Emergency Outside Air Supply System were restored to operable status at 0503 on 6/13/2014." The licensee notified the NRC Resident Inspector. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-06-13
50199 | 0 | US ARMY |  |  |  |  | 2014-06-12 16:00 | 2014-06-13 08:27 | 2014-06-13 | LOST DEPLETED URANIUM PROJECTILE The licensee was conducting a test fire exercise at the Ford Farms section of the Aberdeen Test Center when a depleted uranium penetrator projectile went off it's intended flight path, exited the building, and landed in an area near the facility designated to receive test rounds. Ford Farms is an indoor hard target test facility. There were no injuries or projected dose to workers or the public. No additional effort will be made to recover the projectile because the projectile landed in a historic impact area of Aberdeen containing various other unexploded ordinance. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-06-23
50198 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-06-12 14:44 | 2014-06-12 18:29 | 2014-06-12 | SYSTEM RESTORATION ERROR CAUSES BOTH TRAINS OF CONTROL STRUCTURE CHILLED WATER SYSTEM TO BE INOPERABLE "On 6/12/2014, [multiple Limiting Condition of Operations] LCOs were entered on SSES Units 1 and 2 for an inoperable Division 2 train of Control Structure Chilled Water starting at 1344 EDT for the planned performance of a flow surveillance. During restoration steps at 1444 EDT on 6/12/2014, a Division 1 Control Structure Chilled Water control switch was mistakenly manipulated which caused the redundant operable train to be declared inoperable. During this time both divisions of Control Structure Chillers were inoperable and were not available to perform the required safety function. This is a condition that, at the time of discovery, could have prevented fulfillment of a Safety Function and is reportable under [10 CFR] 50.72(b)(3)(v)(D) as an 8 hour notification. "The loss of safety function is based on 1) the SSC is inoperable in a required mode of operation, 2) the inoperability is due to personnel error, and 3) there was no redundant equipment in the same system that was operable. "The Division 1 train of Control Structure Chilled Water was restored to operable status at 1446 EDT on 6/12/2014." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-06-12
50197 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-06-12 12:47 | 2014-06-12 18:09 | 2014-06-12 | INADEQUATE DC CABLE PROTECTION COULD ADVERSELY AFFECT SAFE SHUTDOWN "Postulated event could adversely affect safe shutdown equipment. "This is a non-emergency notification. "While operating at 100 percent power in mode 1, Harris plant personnel determined that inadequate cable protection exists in control cables for a DC powered main turbine lube oil pump. A short circuit could cause excessive current through affected cables, potentially resulting in overheating. The affected cables pass through the Control Room and other areas and could adversely affect safe shutdown. Compensatory measures (hourly fire watches) have been implemented for affected areas of the plant which ensures continued public safety. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-12
50196 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-06-12 11:30 | 2014-06-12 15:35 | 2014-07-01 | AGREEMENT STATE REPORT - RADIATION LEVELS ON TRANSPORTATION TRAILER EXCEEDED 200 MR/HR The following information was received via email from the State of Tennessee: "The Tennessee Division of Radiological Health was notified on June 12, 2014 by a representative of Energy Solutions that an 'exclusive use' truck shipment was received from Philotechnics of Oak Ridge, TN. The truck was identified to have radiation levels on the bottom surface of the truck of approximately 350 mR/hr. "The State of Tennessee dispatched an inspector to Energy Solutions." State of Tennessee notified NRC Region 1 (Janda). TN Report No.: TN-14-120 * * * UPDATE FROM RUBEN CROSSLIN TO JOHN SHOEMAKER AT 1229 EDT ON 7/1/14 * * * The following update was received from the State of Tennessee via email: "The suspect package of waste was identified as a one cubic yard 'film box' containing Ge-68 waste generated by Siemens Medical Solutions. The maximum contact radiation measurement was 900 mR/hr on the bottom of the box. The box was classified as LSA 1 [low specific activity], however no markings were on the box identifying it as LSA 1. The State Division of Radiological Health (DRH) issued a letter to Philotechnics (the shipper) detailing items of non-compliance with DRH regulations. This incident is not closed." Notified R1DO (Noggle) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-06-20
50195 | 0 | U.S. AIR FORCE |  |  |  |  | 2014-04-21 | 2014-06-12 14:19 | 2014-06-12 | LOST NICKEL-63 ION SCAN SOURCE "On 21 April 2014, BE [AMDS Bioenvironmental Engineering] received an email from AFRRAD [Air Force Radioactive Recycling and Disposal] with a certification of transfer & receipt indicating that the Ionscan [Model 400/ serial number 10172] received by AFRRAD did not contain radioactive material. BE made a site-visit to 305th APS Passenger Terminal [Building 1706 located in New Jersey on 87 AMDS/SGPB, Joint Base McGuire-Dix-Lakehurst] to assist in searching for the ion scanner source. When the source could not be found, BE emailed a picture of what the component should look like to the URSO [Unit RSO] and his alternate to further assist in searching for the source while also asking for documentation of the last time the source was sent to manufacturer to determine whether the source was removed at that time. Neither the source nor the documentation could be found. "From 21 April - 21 May 2014, BE maintained communication with the URSO and his alternate and informed them that if they did not find the source by 21 May, a telephonic notification would be made to the RIC [Radioisotope Committee]. During this period, BE communicated the health risks both to 305 APS & 87 AMDS commanders and affected personnel. "On 21 May, the URSO made it clear that they had exhausted all efforts to find the source. Later that day, BE made telephonic notification to the RIC (Maj. Ed Kelly) indicating that the source was missing and could not be found." Ionscan 400 contains a Ni-63 source with an activity of 15 milliCi. The Sealed Source and Device Registry number (SS&DR) associated with the Ionscan 400 is NR-0163-D-801-G. The device is used to screen passengers for hazardous material. The licensee will be notifying NRC Region IV (Cook) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-06-20
50194 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-11 21:40 | 2014-06-12 12:07 | 2014-06-12 | SUSPECTED TAMPERING OF FIRE PROTECTION SYSTEM At 0910 CDT on 6/12/2014, Comanche Peak identified apparent tampering with two portions of the fire protection system within the protected area. The licensee notified the NRC Resident Inspector, FERC and NERC. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-06-12
50193 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-06-10 | 2014-06-12 11:30 | 2014-06-12 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE The following information was received via email from the State of Illinois: "On June 11, the Radiation Safety Officer/Medical Physicist for Northwest Community Hospital in Arlington Heights, IL called to report a medical event. The previous morning a patient was to be administered approximately 38 milliCi of Y-90 labeled microspheres for treatment of liver cancer in the left lobe of the liver via the hepatic artery. Instead, approximately only 21 milliCi was delivered. Post treatment measurements of the delivery system showed substantially elevated readings at the catheter/vial interface suggesting either blockage or perhaps improper flow allowing the microspheres to coagulate. The physician is considering an increase in dosage for the patient's second treatment which is scheduled in two to three weeks in order that the ideal dose be delivered. However, if that cannot be accomplished, the interventional radiologist does not believe the patient's health to be adversely affected by the under dose. A written report of the event from the licensee is pending at this time." IL Report Number: IL-14010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-06-20
50192 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-05-14 | 2014-06-12 09:50 | 2014-06-12 | AGREEMENT STATE REPORT - POTENTIAL DOSE EXCEEDING EXTREMITIES LIMIT The following information was obtained from the Commonwealth of Massachusetts via email: "On 6/11/14, licensee reported to Agency [Commonwealth of Massachusetts] a potential dose exceeding the adult occupational shallow dose equivalent to the skin or extremities limit of 50 rem. Licensee reported situation occurred during March-April 2014 dosimeter wear period and involved employee working with Y-90 in hot cell. Licensee reported extremity ring badge pierced through the employee's glove resulting in contamination of ring badge. March-April 2014 extremity ring exposure reading of 52,480 mRem. Year-to-date extremity ring exposure at 53,400 mRem. The year-to-date whole body badge exposure is at 51 mRem. "Licensee reported corrective actions identified and implemented to reduce likelihood of recurrence. Consultant hired to review dose assessment and assist in completing 30-day written report. "No other details from the licensee at this time. "The Agency inspector will conduct a site visit. The Agency is awaiting a 30-day written report by the licensee. "The Agency considers this event to still be OPEN." Event Docket #: 18-1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-06-20
50191 | 0 | WATERFORD | 3 |  |  | [3] CE | 2014-04-18 04:29 | 2014-06-12 09:31 | 2014-06-12 | MASONEILAN ACTUATORS DISCOVERED TO FAIL-CLOSED INSTEAD OF THE REQUIRED FAIL-OPEN CONFIGURATION "This is a non-emergency notification from Waterford 3 required under 10 CFR PART 21 concerning the deviation of a basic component from manufacturing purchase specifications. "On 04/18/2014, during pneumatic actuator replacement for Emergency Feedwater [EFW] valve EFW-224A (EFW to Steam Generator #1 Primary Flow Control Valve), it was identified that the fail action of the actuator was incorrect in that it was in a fail-closed instead of fail-open configuration. The actuator model, as identified in Waterford 3 site receipt/acceptance document and the actuator's name plate data, was a Masoneilan model 47 Sigma-F, which is specified as a fail-open actuator. However, the actuator was discovered to have a fail closed action, which is indicative of a Masoneilan model 48 actuator. "The fail-action of these Masoneilan Sigma-F actuators can be changed in accordance with its technical manual TDM120.0565 with no additional parts; therefore, Waterford 3 corrected the fail action of EFW-224A's replacement actuator (to fail-open) and ensured the handwheel indicator was corrected prior to entering mode 4. "Two of these actuators were received and accepted as Masoneilan model 47 Sigma-F (fail-open) actuators in September of 2010, both of which were labeled as such, yet configured in the fail-closed action. One of these two actuators remains in the warehouse and has been placed on hold. The vendor, Dresser Masoneilan, has been notified in writing on May 12, 2014. "On 6/9/2014 at approximately 1600 CDT, Entergy concluded that for those potential applications of this valve operator model in the EFW system, had they been installed without correcting the deviation, it could have resulted in a substantial safety hazard in that it could have prevented fulfillment of EFW safety function, and therefore reportable under 10CFR PART 21. The Waterford 3 Site VP was informed on 06/11/2014." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2014-06-12
50190 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-11 21:40 | 2014-06-11 23:17 | 2014-06-11 | UNUSUAL EVENT DECLARED DUE TO HALON GAS RELEASE IN UNIT 2 CABLE SPREADING ROOM "Release of Halon into the Unit 2 Cable Spreading Room. No indication of fire in the area. "HU3.1 (Toxic, corrosive, asphyxiant or flammable gases in amounts that have or could adversely affect normal plant operations) was declared at 2154 CDT due to Halon release and Oxygen levels below safe habitability conditions (19% oxygen). Ability still exists to maintain safe operations and safely shut down the reactor. "No adverse plant response or control board alarms indicated. No smoke or fire in the room and access is provided with SCBA. "Escalation criteria would be if not able to maintain safe operations or safely shut down the reactor. "Exit criteria would be when normal oxygen levels are restored to Unit 2 Cable Spreading Room. "Local NRC resident notified at 2223 CDT." Unit 2 is stable at 100% power. Unit 1 was not affected and remains stable at 100% power. The licensee notified the State of Texas, the local counties, and the NRC Resident Inspector. Notified DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. * * * UPDATE FROM SCOTT HARVEY TO CHARLES TEAL AT 1642 EDT ON 6/12/14 * * * At 0330 CDT the Unusual Event was terminated. The licensee notified the NRC Resident Inspector. Notified R4DO (Werner), NRR (Uhle), IRD (Grant), DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-06-11
50189 | -1 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-06-11 14:34 | 2014-06-11 22:42 | 2014-06-13 | ONE CONTAINMENT SPRAY TRAIN CHEMICAL ADDITIVE FLOW OUT OF SPECIFICATIONS "At 1434 [CDT] on 06/11/14, the 1A Containment Spray chemical additive flow was found out of tolerance low during surveillance testing. This resulted in an unanalyzed condition in that insufficient chemical additive flow might have resulted in lower than assumed containment spray Ph values during past periods. The impact of the unanalyzed condition has not been fully evaluated. Based on the above, this is being reported in accordance with 10CFR50.72(b)(3)(ii)(B). Engineering analyses are in progress to evaluate the past condition. Actions are in progress to restore the 1A Containment Spray chemical additive flow to within tolerance. The 1B Containment Spray system is operable per Tech Spec 3.6.6 and is capable of providing required chemical additive flow." The required flow is 30 to 63 gpm. Measured flow was 27 gpm. The last measurement was six years ago. The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY JOHN LOGAN TO JEFF ROTTON AT 1803 EDT ON 06/13/2014 * * * "The purpose of this report is to retract EN report #50189 (June 11, 2014). This EN report was made for the 1A Containment Spray chemical additive flow which was found out of tolerance low during surveillance testing. At the time of reporting, it was concluded that this was an unanalyzed condition in that insufficient chemical additive flow may have resulted in lower than assumed containment spray pH values during past periods. This was reported in accordance with 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "At approximately 1700 CDT on Thursday, June 12, 2014, Braidwood Generating Station concluded that the prior EN notification could be retracted based on the completion of Engineering Change 398472, 'Evaluation of As-Found Results for 1A Containment Spray NaOH Additive Flow.' "The Engineering Change concluded that the approval of the alternate source term (AST) license amendment resulted in the elimination of a minimum containment spray (CS) spray pH value. The current containment release analysis does not credit the addition of sodium hydroxide (NaOH) to CS spray for fission product removal from the containment atmosphere. The long-term retention of captured fission products in the sump water assumes the sump water pH is greater than 7. This is established by the transfer of the containment spray additive tank (CSAT) contents to the sump during CS system operation. To transfer the maximum CSAT inventory to the sump within 8 hours, a minimum NaOH eductor flow of approximately 10 gpm is required. The minimum NaOH injection flow for the 1A CS eductor system (27.0 ' as-found' and 27.7 'as-left' gpm) exceeded 10 gpm so the eductor injection flows meet the criteria to transfer CSAT inventory to the containment recirculation sump within the expected minimum CS system operating time. The out of tolerance flow values recorded at the time of the initial notification are acceptable. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Daley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-06-11
50188 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-10 23:27 | 2014-06-11 01:23 | 2014-06-11 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT ACTIVATION OF AN EMERGENCY SIREN "On 6/10/14 at approximately 2327 EDT, the Operations Shift Manager was made aware that the Berrien County Sheriffs Department (BCSD) had been notified of an Emergency Siren that had actuated. BCSD was notified by local residents. BCSD reset the emergency siren and a local police officer verified the siren was no longer actuating. "The cause of the actuation is under investigation at this time. The siren remains in service pending further investigation. There are a total of 70 sirens and all remain functional. "This notification is being made under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-11
50187 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-06-10 20:32 | 2014-06-11 00:23 | 2014-06-11 | SECONDARY CONTAINMENT DECLARED INOPERABLE "Nine Mile Point Unit 2 Secondary Containment was declared inoperable on 6/10/14 from 2032 EDT until 2036 EDT during the restoration of Reactor Building Ventilation System to a normal lineup. "While performing actions to restore ventilation fans the Above Refuel Floor Exhaust Fan, 2HVR-FN5A, tripped when started resulting in building differential pressure becoming less negative than -0.25 inches. Tech Spec 3.6.4.1 Secondary Containment, Action A.1 to restore within 4 hours was entered at 2032 EDT on 6/10/14. "The standby Above Refuel Floor Exhaust Fan, 2HVR-FN5B, was started per procedure and building differential pressure was restored. Secondary Containment was declared operable at 2036 EDT on 6/10/14 and Tech Spec 3.6.4.1 action was exited. "Secondary containment being inoperable is a 8-hour report for 10 CFR 50.72(b)(3)(v)(c), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material." The licensee has notified the NRC Resident Inspector and will notify the State of New York. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-06-11
50186 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-06-10 21:05 | 2014-06-10 21:52 | 2014-06-10 | PROTECTIVE ACTIONS TAKEN DUE TO WEATHER CONDITIONS Site security measures taken due to tornado warning on site from 2105 to 2203 EDT. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-06-10
50185 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-06-10 16:00 | 2014-06-10 19:38 | 2014-06-10 | OFFSITE NOTIFICATION - NON-WORK RELATED ON-SITE FATALITY "At 1600 EDT on June 10, 2014, a non-work related on-site fatality as a result of natural causes occurred at the Peach Bottom Atomic Power Station. The fatality was not related to the health and safety of the public or on-site personnel. Specifically, a contract truck driver was found non-responsive in a truck in the parking lot. "The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. The location of the parking lot is outside of the Protected Area but within the owner controlled area. "An Event of Potential Public Interest has been completed. Peach Bottom Atomic Power Station will make notifications due to a fatality on-site. This ENS notification is in response to a notification to another government agency in accordance with 10CFR50.72(b)(2)(xi). "The licensee notified the NRC Resident Inspector." The licensee notified the Emergency Management Agencies in Pennsylvania and Maryland, the Pennsylvania State Police, as well as the surrounding counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-10
50184 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-06-05 | 2014-06-10 18:05 | 2014-06-10 | AGREEMENT STATE REPORT - PROCESS GAUGE SOURCE DISCONNECTED "On June 6, 2014, the Agency was notified by the licensee's Radiation Safety Officer (RSO) that on June 5, 2014, after retracting a 148 milliCurie cobalt-60 source into an Ohmart-Vega model SHLM-CR gauge, the source separated from the cable. The licensee reported the gauge shutter closed and they locked the shutter in the closed position. The licensee stated the manufacturer had been contacted and would be at the facility on the morning of June 6, 2014. The RSO stated he would provide additional information as soon as he could. There were no exposures as a result of this event." NMED Report: TX140032 Texas Incident #I-9200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-06-18
50183 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-06-10 07:12 | 2014-06-10 16:25 | 2014-06-10 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector and the Regional Safeguards Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2014-06-10
50182 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-06-09 07:15 | 2014-06-09 18:11 | 2014-06-14 | RADIATION MONITORING SAMPLE RACK DECLARED NON-FUNCTIONAL "At 0715 hours PDT on June 9, 2014, the Rad Waste Building process radiation monitoring sample rack was declared non-functional. The cause of the equipment malfunction is under investigation. Compensatory measures were implemented to obtain radiation readings from the associated effluent release pathway. Field team assessment function was unaffected and remains available. "This event is being reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee will notify the NRC Resident Inspector." * * * UPDATE PROVIDED BY QUOC VO TO JEFF ROTTON AT 2019 EDT ON 06/14/2014 * * * "At 1255 PDT on 06/13/2014, the Rad Waste Building process radiation monitoring sample rack was declared functional. "The NRC Resident Inspector has been notified." Notified R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-09
50181 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2014-06-07 17:00 | 2014-06-09 16:55 | 2014-06-09 | AGREEMENT STATE REPORT - STUCK PROCESS GAUGE SHUTTER The following information was received via e-mail: "On Sunday, June 8th, 2014, the Wisconsin Radiation Protection Section received notice from the mill [NewPage Wisconsin Systems] Radiation Safety Officer (RSO) for the Wisconsin Rapids facility that the licensee had a gauge with a stuck shutter. The stuck shutter was discovered on Saturday, June 7th at 5:00 pm [CDT]. The device is an Ohmart model A-2102 (serial number M-3212) fixed gauge originally containing 100 mCi of Cs-137. The facility is currently shut down for maintenance. VEGA Americas, Inc. has been called for immediate repairs. The mill RSO stated that the gauge was in the normal operating position and did not pose a radiation safety hazard. The gauge has been roped off from personnel. Personnel are not allowed inside the chip chute since it is in the path of the radiation beam between the broken source and its detector. "The Wisconsin Radiation Protection Section will continue to monitor the situation." Wisconsin Event: WI140006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2014-06-17
50180 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-06-08 16:15 | 2014-06-08 17:03 | 2014-06-09 | OFFSITE NOTIFICATION DUE TO TRITIUM DISCOVERED IN ONSITE WELL "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) because Dresden Nuclear Power Station is in the process of informing the Illinois Emergency Management Agency (lEMA) and Illinois Environmental Protection Agency (IEPA) of recent groundwater monitoring results at Dresden Station. Additionally, the station intends to issue a press release. "As part of the Station's extensive environmental monitoring and sampling program, sample results from an onsite sampling well near the 2/3 contaminated water storage tank (CST) indicate elevated levels of tritium. This is an on-site leak, requiring the notification of the State of Illinois. Based on sampling data obtained, the tritium is currently confined to Exelon property. "The IEPA/lEMA regulation requires notification when a release to soil, groundwater or surface water goes offsite at greater than 200 pCi/L or remains on-site greater than 0.002 Curies. Based upon the sampling results from the monitoring well near the 2/3 CST with a concentration of approximately 0.0000013 Curies/liter it is likely that the 0.002 Curie on-site threshold has been exceeded. "The Station continues to track this issue by monitoring the existing wells and initiation of mitigative actions to contain any release and ensure it remains on-site. At this time, the source of the tritium has not been identified. Investigation continues to determine if an off-site release occurred. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1951 EDT ON 6/9/2014 FROM THOMAS DITCHFIELD TO MARK ABRAMOVITZ * * * "At 1830 [CDT], the station notified IEPA/IEMA, pursuant to 35 ILL. ADM. Code 1010.202, that from the time period of April 2, 2014, to June 8, 2014, elevated levels of tritium existed at the discharge of the plant. As part of the site investigation that was done in response to the event reported in EN 50180, it has been determined that no greater than 0.1 Curies were discharged from the site. The majority of this discharge was to the Kankakee River via the sewage treatment plant effluent. A small amount, determined to be less than 2%, was discharged to the Morris Illinois sewage treatment facility. This release is associated with the elevated tritium levels discovered on June 7, 2014 and reported to the IEPA on June 8, 2014. "The system is currently isolated, and is not discharging to the Kankakee River. The licensee notified the NRC Resident Inspector. Notified the R3DO (Daley). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-08
50179 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2014-06-06 16:10 | 2014-06-06 18:30 | 2014-06-06 | AGREEMENT STATE REPORT - FIRE AT A NUCLEAR MEDICINE FACILITY The following is a summary of an email received from the State of Alabama: A fire was reported at a nuclear medicine facility in Cullman, AL at around 1610 CDT. The Nuclear Medicine Tech at Health Imaging Services stated that she had gathered the 2 e-vials (286.8 microCuries of Ba-133, and 195.4 microCuries of Cs-137), PET waste box, and a rod source and took these materials to the Coleman Regional Medical Center [CRMC] for storage. An individual at the Alabama Emergency Management Agency [AEMA] stated that fire personnel had access to radiation survey equipment, and that the incident appeared to be a structure fire and not a radiation event. The Nuclear Medicine Tech at Health Imaging Services stated that she was able to retrieve her survey meter, but it was not functioning properly. She stated that one rod source remained in the scanner (about 1 milliCurie Ge-68), and that the scanner appeared to not be compromised. The Nuclear Medicine Tech at Health Imaging Services stated that she and the RSO from CRMC would return to perform radiation surveys with a properly functioning survey meter later this evening. All sources appeared to be accounted for, except for the rod in the scanner, and appropriate surveys are to be performed later. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2014-06-16
50178 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2014-06-06 16:22 | 2014-06-06 16:40 | 2014-06-06 | NOTIFICATION OF UNUSUAL EVENT DUE TO A FIRE ALARM INSIDE CONTAINMENT At 1622 EDT, the licensee declared a notification of unusual event under EAL HU2.1 for a fire alarm on the third level inside the containment building. The alarm was received at 1607 EDT. Upon receipt, the licensee dispatched their fire brigade which determined that no fire existed. The fire brigade is conducting a containment walkdown to confirm that there are no issues inside of containment. The licensee did not request offsite assistance. The plant continues to operate at 100% power and is stable. The licensee has notified the NRC Resident Inspector, state and local authorities. Notified DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. * * * UPDATE FROM COREY PAGE TO DONG PARK AT 1700 EDT ON 6/6/14 * * * At 1648 EDT, the licensee terminated from their notification of unusual event. The basis for termination was visual confirmation that no fire existed inside containment. The licensee has notified the NRC Resident Inspector, the State of South Carolina, and the counties of Chesterfield, Darlington and Lee. Notified R2DO (Freeman), NRR EO (Skeen), IRD MOC (Grant), DHS, FEMA, and NICC. FEMA NWC and Nuclear SSA were notified via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-06-06
50177 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-06-06 11:27 | 2014-06-06 15:13 | 2014-06-06 | OFFSITE NOTIFICATION DUE TO WASTE WATER SPILL "At approximately 11:27 AM EDT on June 6, 2014, Duke Energy personnel notified the North Carolina Department of Environment and Natural Resources of a spill of treated domestic waste water. The waste water was released through a break in the discharge line from the waste water facility to the permitted discharge outfall. The treated waste water entered the plant's storm drain system. The release has been stopped and the line repaired. An investigation is in progress to determine the cause and any additional corrective actions. There is no impact to public health and safety or the environment due to this incident. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-06
50176 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-06 12:32 | 2014-06-06 12:50 | 2014-06-06 | VOLUNTARY NOTIFICATION FOR AN ITEM OF REGULATORY INTEREST "Salem Unit 2 has early vintage Model 93A Reactor Coolant Pumps (twenty, one-inch bolt configuration). The Reactor Coolant Pumps (RCPs) have been removed and are being inspected to resolve issues associated with the failure of bolts which secure the turning vane assembly to the thermal barrier. Inspections have identified turning vane assembly detachment and dropping of the reactor coolant pump turning vane diffuser on the 23 RCP. The inspections identified evidence of slight contact between the impeller and the diffuser. "Salem Unit 2 has had no indications to date of adverse operating conditions of any RCPs due to turning vane assembly detachment which would compromise plant safety. This condition has been evaluated against the reporting requirements of 10 CFR 50.72. It has been determined that the condition does not rise to the significance necessitating a report under any specific requirements of 10 CFR 50.72. PSEG is voluntarily reporting this condition IAW with NUREG 1022, Section 4.2.2 so that the NRC and the industry will be informed." The other three RCPs in Unit 2 are currently undergoing evaluation to determine if the same condition exists on them. Based on the findings of those evaluations, the licensee will determine whether reporting under 10 CFR 21 is warranted. Salem Unit 1 has the same model RCPs but they have a different bolt configuration (1.5 inch versus 1 inch) and they have not exhibited the bolt failures exhibited by the Unit 2 pumps. The licensee has notified the State of New Jersey Bureau of Nuclear Engineering and will be notifying the Lower Alloways Creek township and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2014-06-06
50175 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-06-05 16:01 | 2014-06-05 17:20 | 2014-06-05 | DISCHARGE CANAL RADIATION MONITORS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "Planned preventive maintenance will render the discharge canal radiation monitors inoperable for both A and B trains. As a result, this represents a loss of emergency assessment capability and is reportable under 10 CFR 50.72 (b)(3)(xiii). The planned maintenance is expected to last two hours. During this time, the site Chemistry Department will be perform sampling as a compensatory measure. The health and safety of the public remains protected as the plant is operating in a normal condition. "The NRC Resident Inspector was notified prior to removing the discharge canal radiation monitors from service." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-05
50174 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-06-05 12:30 | 2014-06-05 14:07 | 2014-06-05 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following was received via email: "On 6/5/2014 at approximately 1230 [EDT], Troxler gauge, (Model 3430, Serial # 30167) licensed to University Engineering Scientist, Inc. was stolen from a truck parked at a construction site for a new Walmart in Mirimar, FL. The police was notified. There is a possible video of the event." Florida Incident #: FL14-050 A typical Troxler gauge contains 8 mCi of Cs-137 and 40 mCi Am-241/Be. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-06-13
50173 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-06-04 07:53 | 2014-06-04 16:38 | 2014-06-04 | NON-LICENSED SUPERVISOR IN VIOLATION OF FITNESS FOR DUTY POLICY A non-licensed supervisor had a confirmed positive result for alcohol during a random fitness for duty test. The employee's access to the plant has been terminated. The licensee has notified the NRC Senior Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2014-06-04
50172 | 0 | AREVA INC |  |  |  |  | 2014-06-04 | 2014-06-04 15:22 | 2014-06-04 | PART 21 - DEFECT IDENTIFIED IN SINGLE LOOP OPERATION MINIMUM CRITICAL POWER RATIO The following is a synopsis of information received via facsimile from AREVA: AREVA identified a defect is in the calculation of the single loop operation (SLO) minimum critical power ratio (MCPR) operating limits for Browns Ferry Units 1, 2, and 3. Specifically, the defect is associated with the usage of non-conservative inputs in the SLO pump seizure analyses for the three plants, which results in non-conservative limits for SLO. Individual informing the Commission: Alan B. Meginnis, AREVA Inc., 2101 Horn Rapids Road, Richland, WA 99354. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-06-04
50171 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-06-03 06:00 | 2014-06-04 09:38 | 2014-06-24 | AGREEMENT STATE REPORT- DAMAGED GAUGE The following information was received by the State of Texas by email: "On June 3, 2014, the Agency [Texas Department of State Health Services] received notice that the licensee had a damaged Berthold LB300ML gauge (S/N 10004). The gauge had been hit with molten steel and damage had been done to attachment points ('ears') for a locking mechanism and carrying handle. No damage to the 2.5 milliCurie cobalt-60 source (S/N 1374-07-11) or the gauge shutter occurred. The gauge is scheduled for repair on June 5, 2014. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident: I-9198 * * * UPDATE FROM ART TUCKER TO HOWIE CROUCH VIA EMAIL ON 6/24/14 AT 0959 EDT * * * "On June 23, 2014, the Agency [Texas Department of State Health Services] received a written report from the licensee stating the gauge shutter was not damaged during this event. The licensee stated they were able to close the shutter at the time of the event. The gauge was placed in a locked storage box. The manufacturer has completed repairs to the gauge and the gauge has been returned to service. The licensee stated no additional exposure was received by their employees or members of the general public. "Additional information will be provided in accordance with SA-300." Notified R4DO (Allen) and FSME Events Resource email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-06-12
50170 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-06-03 19:02 | 2014-06-03 23:22 | 2014-06-03 | DIESEL GENERATORS DECLARED INOPERABLE DUE TO NOT MEETING HIGH ENERGY LINE BREAK REQUIREMENTS "D1 and D2 Emergency Diesel Generators (DG) were declared inoperable at 1902 CDT due to the station identifying that the Turbine Building HELB [High Energy Line Break] heatup analysis temperature of 270 F exceeded the maximum temperature limit of 200 F for both diesel generators supply and exhaust fan blade positioners. "LCO 3.8.1 Condition B was entered for both DGs and LCO 3.8.1 Condition E was entered for two DGs inoperable on the same unit. The DGs could start and run if required at the time of entry. "This condition is reportable per 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented the fulfillment of a safety function. "Unit 1 continued to operate in Mode 1 at 100% power while bypasses were being put in-service to fail the diesel generators supply and exhaust fan blade positioners in the full cooling mode to allow the LCO conditions to be exited. "At 2002 CDT the bypasses were installed on the D1 Diesel Generator Supply and Exhaust Fan Blade Positioners therefore LCO 3.8.1 Condition E was exited for both D1 and D2 Emergency Diesel Generators being inoperable. In addition LCO 3.8.1 Condition B was exited for D1 Diesel Generator due to it being declared Operable. "At 2056 CDT the bypasses were installed on the D2 Diesel Generator Supply and Exhaust Fan Blade Positioners therefore LCO 3.8.1 Condition B was exited for D2 Diesel Generator due to it being declared Operable. "At no time was the health and safety of the public threatened. "The Senior NRC Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-06-03
50169 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-06-03 16:50 | 2014-06-03 20:06 | 2014-06-03 | OFFSITE NOTIFICATION DUE TO SPILL OF TREATED DOMESTIC WATER "At approximately 4:50 PM EDT on June 3, 2014 Duke Energy personnel notified the North Carolina Department of Environment and Natural Resources of a spill of treated domestic waste water. The waste water was released through a valve onto the surrounding ground and may have entered the plant's storm drain system. The release has been stopped. An investigation is in progress to determine the cause and additional corrective actions. "There is no impact to public health and safety or the environment due to this incident. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The NRC Resident Inspector has been notified." The gray water was dripping from a valve onto the ground. The total quantity of the seepage is unknown. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-06-03
50168 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-03 12:59 | 2014-06-03 15:40 | 2014-06-03 | HIGH AND LOW RANGE VENTILATION PROCESS RADIATION MONITOR PRE-PLANNED MAINTENANCE At 1259 EDT, Millstone Station Unit 3 removed the High and Low Range Ventilation Process Radiation Monitors from service for planned maintenance. The radiation monitor is expected to be out of service for approximately less than 24 hours. Compensatory measures are in place. The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 0 | 60 | 0 | 0 | 60 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-03
50167 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-06-03 13:30 | 2014-06-03 15:17 | 2014-06-03 | AGREEMENT STATE REPORT - LOST AND FOUND TROXLER MOISTURE DENSITY GAUGE A Troxler Model 3430 (8 mCi Cs-137 and 40 mCi Am-241:Be) fell off the back of the truck when the licensee was leaving the construction site. The gauge was discovered just outside the site by a landscaper who contacted the personnel at the construction site. The licensee was contacted by construction personnel. The licensee returned to the site and took custody of the gauge. It was out of his control for approximately 30 to 45 minutes. Florida Incident #: 14-049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-06-11
50166 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-03 | 2014-06-03 14:15 | 2014-06-03 | WATTS BAR UNIT 2 POTENTIALLY DEFECTIVE FUSES INSTALLED "WBN [Watts Bar Nuclear] Unit 2 (under construction) determined that Littelfuse Part Number FLAS005.T fuses manufactured under three date codes are potentially susceptible to nuisance opening according to Littelfuse letter dated April 30, 2014. Littelfuse Part Number FLAS005.T fuses are commercial grade and dedicated by TVA for use as a basic component in safety related systems. No confirmed examples have been identified that would have created a substantial safety hazard at this time. The potentially defective fuses were purchased for WBN Unit 2 and have been installed on WBN Unit 2 only. No potentially defective fuses have been installed on WBN Unit 1, SQN [Sequoyah] Units 1 or 2, or BFN [Browns Ferry Nuclear] Units 1, 2, or 3. At this time, there is no safety significance because fuel has not been loaded on WBN Unit 2. Installed and potentially defective Part Number FLAS005.T fuses will be replaced prior to obtaining a WBN Unit 2 Operating License. This issue has been documented in TVA's corrective action program as Problem Evaluation Report 878252 and is being conservatively reported by WBN Unit 2 under 10 CFR 50.55(e)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 50.55(e) |  |  |  | 0 | 2014-06-03
50165 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-06-03 09:33 | 2014-06-03 13:41 | 2014-06-03 | HIGH RANGE STACK MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE At 0933 EDT, Millstone Station Unit 2 removed the Stack High Range Radiation Monitor RM-8168 from service for planned maintenance. Maintenance and testing were completed and the Stack Radiation Monitor returned to service at 1252 EDT. The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-03
50164 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2014-04-05 07:00 | 2014-06-03 06:42 | 2014-06-03 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This notification is being made in accordance with 10 CFR 50.73 (a)(2)(iv)(A) to provide information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment valves in more than one system. "On April 5, 2014, with the reactor at 100% power, an invalid PCIS Group 3 actuation occurred from a momentary spike of the 'A' Refuel Floor radiation monitor which reached the instrument's high radiation trip set point. A radiation protection technician was dispatched to the refuel floor and dose rates in the vicinity of the 'A' radiation monitor detector were verified to be normal and below the alarm set points. The radiation monitor was verified to be indicating normal expected radiation levels. The detector was replaced, a functional check and calibration of the radiation monitor was completed satisfactory and the instrument channel was returned to service. The issue has been entered into the station's corrective action program. "Both trains of Standby Gas Treatment System started as designed and Reactor Building ventilation isolated as a result of the invalid PCIS actuation. "The PCIS functioned successfully, providing a complete Group 3 isolation. PCIS Group 3 involves the following system isolation valves: "Drywell and Suppression Chamber Air and Vent: V16-19-6, 6A, 6B, 7, 7A, 7B, 8, 9, 10, 23 "Containment Makeup: V-16-20-20, 22A, 22B "Containment Air Sampling: VG-23, 26, V109-76A, 76B "Containment Air Compressor Suction: V72-38A, 38B "Containment Air Dilution: VG-9A, 9B, 22A, 22B, NG-11A, 11B, 12A, 12B, 13A, 13B "Since no actual high radiation condition existed which required the PCIS Group 3 isolation, and the actuation was not in response to actual plant conditions satisfying the requirements for isolation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public. "In accordance with 10 CFR 50.73(a)(1) a telephone notification is being made instead of submitting a written Licensee Event Report. The licensee has notified the NRC resident inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-06-03
50163 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-06-02 07:52 | 2014-06-02 16:47 | 2014-06-02 | NON-LICENSED CONTRACT EMPLOYEE SUPERVISOR IN VIOLATION OF FITNESS FOR DUTY POLICY A non-licensed contract employee supervisor had a confirmed positive result for a controlled substance. The employee's access to the plant has been terminated. The licensee has notified the NRC Senior Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2014-06-02
50162 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-06-01 13:14 | 2014-06-01 17:51 | 2014-06-01 | LOSS OF TECHNICAL SUPPORT CENTER COOLING CAPABILITY "At 1314 [CDT] on 6/01/2014, Technical Support Center ventilation alarm was received in the main control room. The Equipment Operator reported that the trouble alarm for the roof mounted condensing units was in alarm and the condensing units were tripped. Upon resetting the alarms the condensing units ran for three to five minutes and tripped again. This caused a loss of Technical Support Center cooling capability. Technical Support Center Air Handling system and filtration remain in operation. The room temperature is being monitored locally. Wet bulb temperature at 1500 [CDT] was reported to be 78.5 deg F. Corrective action process has been initiated. "This event is reportable under 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 3 since this condition affects an emergency response facility." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-06-01
50161 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-05-31 11:36 | 2014-05-31 14:28 | 2014-06-01 | EMERGENCY TONE ALERT RADIO TRANSMITTER NOT FUNCTIONAL "At time 1136 CDT, 5/31/14 Cooper Nuclear Station was informed by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability and is reportable under 10CFR50.72(b)(3)(xiii). "Nemaha, Richardson and Atchison county authorities within the 10 mile EPZ have been notified of the condition and the affect on the tone alert radios and will utilize Local Route Notification (backup notification method). "Estimated return to service time is unknown. The cause of the failure is a severed communication line." The licensee also found FTS 2001 lines to be non-functional. The communications line was severed during road construction. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1530 EDT ON 6/1/2014 FROM KYLE SAYLOR TO MARK ABRAMOVITZ * * * At 2232 CDT on 5/31/2014, the licensee was notified that the tone alert system had been returned to service. At 1230 CDT on 6/1/2014, the FTS 2001 phone system testing was completed verifying the normal status of these phones. The licensee will notify the NRC Resident Inspector. Notified the R4DO (Vasquez). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-31
50160 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-05-30 16:10 | 2014-05-30 20:16 | 2014-05-30 | GROUTING IN FIRE PENETRATIONS DOES NOT MEET REQUIREMENTS "Conditions were identified in which grouting in some fire penetrations through hollow block walls on Units 1 and 2 do not comply with design drawings. While some grouting is present in the penetration, the determination has been made that the qualification of the amount and configuration of the grouting present does not meet Appendix R requirements. Further evaluation by Engineering concluded that this condition could compromise both safe shutdown paths on each unit in the event of a postulated fire. Given this information, the determination was made that this condition meets the reporting criteria of 10CFR50.72(b)(3)(ii)(B). "Compensatory measures were established in accordance with the plant's Fire Hazard Analysis (FHA) to compensate for this condition to ensure that safe shutdown paths are preserved until the conditions can be corrected." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-05-30
50159 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2014-05-29 | 2014-05-30 12:51 | 2014-05-30 | AGREEMENT STATE REPORT - A FIXED GAUGE SHUTTER DISCONNECTED FROM ITS HANDLE The following event was submitted via e-mail: "While completing the annual inventory checks, it was discovered that the handle of a Berthold Cs-137 source, S/N: 281, Model No. LB7440, with an activity of 281 mCi, had separated from the shutter mechanism. The shutter was closed and was verified with a RadEye B20 S/N: 0520. This source has been moved and put in storage until the shutter can be fixed. A visit has been scheduled for the repair, with the manufacturer. Documentation will be provided upon completion of the repairs." Nevada Report #NV-140014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50158 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2014-05-30 09:30 | 2014-05-30 17:06 | 2014-05-30 | FITNESS FOR DUTY - LICENSED OPERATOR IN VIOLATION OF FITNESS FOR DUTY POLICY A licensed operator violated the station's fitness for duty policy due to alcohol during a random fitness-for-duty test. The employee's access to the plant has been withdrawn. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2014-05-30
50157 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-05-30 10:00 | 2014-05-30 13:49 | 2014-06-05 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT After attempting to retract the source during radiography operations, the radiographer noticed elevated radiation levels. The radiographer set up a boundary and notified the RSO. The RSO determined that the source was not fully retracted but was able to retract the source. The RSO was in a 40 mr/hr area for about 5 minutes. The licensee will send the camera to the manufacturer for repair. "Exposure Device: Make: QSA Global, Inc. Model: Delta 880 Serial #: D 8543 "Source: Make: QSA Global, Inc. Model: A424-9 Serial #: 14620C Radionuclide: Ir-192 Initial Activity: 104.9 Ci Initial Date: May 8, 2014 Current Activity: 85.3 Ci Current Date: May 30, 2014" Colorado Incident Number: I14-13 * * * UPDATE ON 6/5/14 AT 1200 FROM CHERI HALL TO DONG PARK * * * The following information was received via e-mail: "Below are the dosimeter results for everyone involved in the 5-30-14 incident. Month (5-1-14 to 5-31-14) "Radiographer: DDE [deep dose equivalent]: 55 mrem; LDE [lens dose equivalent]: 55 mrem; SDE [shallow dose equivalent]: 55 mrem "Assistant: DDE: 105 mrem; LDE: 107 mrem; SDE: 107 mrem "RSO (performed retrieval) DDE: 11 mrem; LDE: 11 mrem; SDE: 10 mrem" Notified R4DO (Taylor) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50156 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-05-30 | 2014-05-30 16:13 | 2014-05-30 | AGREEMENT STATE REPORT - UNDERDOSE FROM A Y-90 PROCEDURE The following report was received via email: "[The Florida Bureau of Radiation Control] received a call from [the licensee's RSO] regarding an underdose incident on a patient. During the procedure, the technician noticed bubbles in the administration line, and stopped the procedure. It was estimated that the patient only received 4 mCi out of the 16 mCi dose prescribed. [The licensee's RSO] will be sending a full report of the incident to this office. [The Florida Bureau of Radiation Control] will assign an inspector to investigate." Florida Incident Number: FL 141-046 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50155 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-05-30 08:30 | 2014-05-30 14:47 | 2014-05-30 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED AT A JOB SITE The following report was received via fax: "The Troxler gauge operator was in the process of calibrating the instrument for use at a temporary job site in Northborough, MA, and during this procedure the gauge was run over by a work vehicle. The operator of the gauge called and notified the RSO of McArdle Gannon Associates, our Agency [Massachusetts Radiation Control Program], and Troxler of the incident. "The gauge operator provided the location of the incident, the model number of the Troxler Gauge (Model 3440), and indicated that the sources were located in the shielded gauge housing when struck by the work-vehicle. The Troxler Model 3440 contains two isotopes; Am-241, and Cs-137 with activities of 44 and 9 mCi, respectively. The operator also indicated that a safety perimeter was being established around the incident site using stakes and caution tape. "An Agency [Massachusetts Radiation Control Program] inspector arrived at the site, and determined exposures were 63 mR/hr at contact, and approximately 0.4 mR/hr at a distance of 1 (one) meter. The device and vehicle which struck the device were surveyed for contamination, with all results indicating background levels. The inspector also identified that the Am-241 and Cs-137 sources were accounted for within the device. "The licensee has contacted the gauge manufacturer and arrangements are underway for a leak test and safe transport of the gauge to the licensee's authorized storage location in Pembroke, MA, and eventual disposal of the gauge. "The Agency [Massachusetts Radiation Control Program] investigation remains open." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50154 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-05-30 10:43 | 2014-05-30 14:43 | 2014-05-30 | HIGH PRESSURE COOLANT INJECTION PUMP RECEIVED AN INVALID ISOLATION SIGNAL "At 1043 CDT, during an instrument test, the High Pressure Coolant Injection (HPCI) system isolated due to an invalid signal. The isolation was on the 'A' (inboard) logic, which rendered the HPCI system INOPERABLE. The isolation was received while instrument technicians were installing a relay block during the performance of Surveillance Test Procedure 3.3.6.1-43 'HPCI Steam Line High DP Instrument Channel Functional Test.' "Operations Personnel have repressurized HPCI piping, installed the relay cover, and declared HPCI System OPERABLE at 1209 [CDT]. "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) due to the failure of a single train system preventing accident mitigation. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-05-30
50153 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-05-30 07:59 | 2014-05-30 14:43 | 2014-05-30 | SECONDARY CONTAINMENT AIRLOCK INOPERABLE FOR 10 SECONDS "At 0759, on May 30, 2014, both doors in one of the Secondary Containment Airlocks were open concurrently. The doors being open at the same time caused a failure to meet SR 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered INOPERABLE per TS LCO 3.6.1.4. Upon discovery, immediate action was taken to close the doors. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to OPERABLE status. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C). "The NRC Resident Inspector has been notified." The cause of this event was a misaligned door magnet. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-05-30
50152 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2014-02-12 | 2014-05-30 12:15 | 2015-03-05 | AGREEMENT STATE REPORT - LOST CALIBRATION SOURCE "On February 12, 2014, the nuclear cardiology and radiation safety staff concluded, a Cesium-137 Rod Source; 1059 microCi on November 11/11/2003; Manufactured by Bench Mark; Serial Number: BM0837- 002-23; Model Number: BM08, was lost. "Following discovery of the lost source, the nuclear cardiology staff and this consultant conducted an extensive search of the nuclear cardiology imaging room and hot lab in an effort to find the source. Unfortunately, we were unsuccessful in locating the calibration rod. The lost source was routinely stored in the locked hot lab cabinet in a leaded pig. The only time the source was removed from the leaded pig was to perform daily calibrations of the well counter. Through our internal investigation we were unable to ascertain the event that attributed to the missing source. "Subsequently, contacted [the Rhode Island Department of Health], to provide official notice that the source was lost. At the time of the incident, the activity of the source was calculated at 0.083 microCi. On February 21,2014 a replacement Cs-137 Button Source; 6.60 microCi on 12/18/2009; Manufactured by NEN was added to the Sealed Source Inventory. The new source is stored in the locked hot lab cabinet in a leaded vial. The new source is used for instrument calibrations on the well counter. The nuclear cardiology staff will conduct a daily inventory of the sealed sources to assure completeness." RI Event Reference 2014-002 * * * UPDATE FROM CHARMA WARING (VIA FAX) ON 3/5/15 AT 1535 EST The State of Rhode Island considers this report closed. NMED Item #120538. Notified R1DO (Burritt) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50151 | 0 | UNIVERSITY OF KANSAS CANCER CENTER |  |  |  |  | 2014-04-01 | 2014-05-30 14:15 | 2014-05-30 | ADMINISTRATIVE ERROR MEDICAL EVENT "A patient at the Lee's Summit location in Missouri was administered the radiopharmaceutical Xofigo. The normal therapy regimen is six doses. On two of those instances (April 29 and April 1, 2014), the prescription sheet/written directive form that was used shows the units in millicurie instead of microcurie. The dosing amount of Xofigo is in microcuries. This was discovered during a routine NRC inspection on May 19, 2014. The NRC contacted us on May 29, 2014 to inform us that this was being declared a medical event. The patient received the correct dose in both instances; the error was a transcription error on the paperwork. A new form just for Xofigo administrations has been created which defaults to showing the units in microcurie." The licensee notified R3 (Bramnik). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2014-06-09
50150 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2014-01-30 | 2014-05-30 12:03 | 2014-05-30 | AGREEMENT STATE REPORT - RADIATION SOURCE STORED IN UNAPPROVED LOCATION "On January 30, 2014, two physicists within the Department of Radiation Oncology were emailed regarding the imminent shipment of a new Iridium-192 High Dose Rate (HDR) brachytherapy source. This notification was forwarded to the RSO. The source in its original shipping package was delivered by [the transport company] directly to the department on February 3, 2014. Upon arrival of the source, a front desk staff member tried unsuccessfully to notify two physics staff members while the transporter waited. When neither of physics staff members responded to the overhead page, front desk staff signed for the package at 9:43 a.m. The front desk staff member moved the package from the front desk area to the mold room floor (Room # 039.12), which is an unsecured location. "On February 14th, it was discovered that the source was not in the Radiation Oncology Hot Lab - the appropriate secured location. Upon investigation and questioning of the staff who signed for the package, the location of the source was determined at 2:15p.m. on February 14th. The source was then taken to the HDR suite by the HDR service engineer (on-site to perform the source exchange) before Radiation Safety personnel were able to perform a wipe test and survey the original shipping package. Upon arrival, Radiation Safety personnel performed a wipe test and survey of the inner shielding cask housing the source. "ADDITIONAL INFORMATION ASSOCIATED WITH THE EVENT: -The source in its original shipping package was inappropriately stored in the mold room for approximately 11 days, 5 hours. -Only one female in the department has a declared pregnancy. At no point in time during this period (February 3rd- February 14th) did she enter the mold room. - The mold room is used only for the preparation of electron cutouts or blocks used in Linac-based treatments. This room is used infrequently (~5 visits per week - about 10 to 15 minutes per visit) by radiation oncology staff (physicists and dosimetrists) wearing radiation dosimeters. - Adjacent areas to the mold room are a clerical area on one side and hallways on the three other sides. - Exposure information obtained from the Radiation Safety personnel who surveyed the package on Friday, February 14th were 34 mR/hr at the surface and 0.5 mR/hr at 1 meter. - The timing of the wipe test and survey was not in accordance with the requirement that a package containing radioactive material be opened and inspected by the recipient as soon as possible (within 3 hours) after receipt. - There was no notification directly from [the transport company] that the package was delivered. "CAUSES OF FAILURE: -Procedure entitled 'Opening and Receiving of Radioactive Materials' was not followed. -Communication break-down between the front desk personnel and physics staff. "ACTION TAKEN TO PREVENT RECURRENCE: 1. Establish one primary physicist and one back-up physicist to serve as the coordinator for the receipt of the radioactive package. Additional physicists within the department will be permitted access into the Radiation Oncology Hot Lab. Additionally, two physicists will sign off in the HDR source inventory logbook upon receipt of the source. 2. All physicists will be trained in accordance with departmental procedures and applicable Department of Transportation (DOT) regulations on the process of receiving this type of package into the department and ensuring its proper storage. 3. The shipping company will be contacted to add all physicists and Radiation Safety personnel to be notified that the source has been shipped. The shipping company will also provide a tracking number for every HDR source package shipped to this facility. Another notification will be made from the transport company that the source has arrived (including delivery confirmation, signature, time & date). 4. Training of all department personnel will be performed and documented. This training will include who is authorized to sign for a radioactive package, how to identify a radioactive package, and the process that should be followed to ensure a safe transfer of the package to Rhode Island Hospital custody. 5. The policy governing the receipt of this type of material will be reviewed, revised, and disseminated upon approval. 6. If the package has not been received within 72 hours of the shipping company's notification, the primary physicist will follow up with the shipping company to determine the location of the package." Rhode Island Event #2014-001 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2014-06-09
50149 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-05-25 09:42 | 2014-05-29 14:10 | 2014-06-20 | CONTROL ROOM VENTILATION BOUNDARY DOOR INOPERABLE "At 0942 on May 25, 2014, the Cook Nuclear Plant (CNP) declared both Control Room Emergency Ventilation trains inoperable in accordance with LCO 3.7.10 due to an inoperable Control Room Envelope when a control room boundary door was identified as not latching correctly during a security door check. The latch would not have been able to maintain the door closed during an event resulting in Control Room Pressurization. At this time, Security established a continuous door post and would have been able to maintain the door closed. "At 1602 on May 25, 2014, repairs to the control room boundary door latch were completed restoring the Control Room Envelope to Operable. "The licensee has notified the NRC Senior Resident Inspector. "This notification should have been made within 8 hours of the event in accordance with 10 CFR 50.72 (b)(3)(v)(D) per guidance in section 3.2.7 of NUREG-1022 - Event or Condition that Could Have Prevented Fulfilment of a Safety Function, but was not recognized at that time." * * * RETRACTION FROM PERRY GRAHAM TO JOHN SHOEMAKER AT 1443 EDT ON 6/20/14 * * * "The purpose of this report is to retract EN #50149 (May 25, 2014). On June 19, 2014, Cook Nuclear Plant concluded that the EN could be retracted based on the completion of a Maintenance Rule Evaluation (MRE) performed by Systems Engineering. "By design, the Control Room Envelope (CRE) pressure boundary is required to be maintained at a positive pressure during all modes of operation and during any irradiated fuel movement. New information contained in the MRE concluded the CRE function was not lost as the control room boundary door remained closed without manual assistance during normal operations. The amount of make-up air during normal operation is similar to the design flow for accident mode (approx. 800 cfm). It was concluded that the sealing integrity was not lost, thus the CRE function was maintained. The CRE would have remained operable and LCO 3.7.10 would not have been entered for the identified condition. "The licensee has notified the NRC Senior Resident Inspector." Notified the R3DO (Valos). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-05-29
50148 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-05-27 | 2014-05-29 12:54 | 2014-05-29 | AGREEMENT STATE REPORT - MEDICAL OVERDOSE The following report was received via e-mail: "Georgia Radioactive Materials Program (GA RMP) received a report yesterday (5/28/2014) of a medical event involving Nordion Y-90 TheraSpheres. The event occurred on 5/27/2014 at Cancer Treatment Centers of America (license #: GA 1632-1) - 600 Parkway North, Newnan GA 30265. GA RMP is tracking this under complaint number: 73962. "GA RMP was notified on 5/28/2014 by the facility's RSO. The event was discovered after treatment while verifying dose delivered to dose prescribed. At that point it was noticed that the doctor had prescribed a 20% reduction for the patient than what is considered the treatment standard. The patient received 35.31 mCi of TheraSpheres as opposed to the physician prescribed amount of 26.73 mCi. The activity delivered deviated by ~32%. The dose consequence to the tumor was 65.32 Gy as opposed to the written directive's 49.45 Gy. The tumor was located in the patient's liver. Finally, the patient was notified of the overdose by the physician. "The facility determined that the problem occurred in the treatment planning review process. The nuclear medicine technician performed the treatment plan review but verified with the standard treatment dose as opposed to the doctor prescribed dose. The facility is proposing a two person calculation sheet review for a corrective action in the future to avoid these sort of oversights. GA RMP will work with the facility to ensure these actions are sufficient to prevent reoccurrence. "It is worth mentioning that other than delivering the wrong dose, there were no complications with the procedure. No shunting issues, unintended organs dosed, equipment malfunctions, or contaminations occurred. "No outside agency notifications have been made other than this notification. GA RMP is responding at this time via telephonic investigation unless any additional doubt is raised on this event. We will follow up with more details and information to NMED as they become available." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-06-06
50147 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-05-28 20:00 | 2014-05-28 23:57 | 2014-05-29 | OFFSITE NOTIFICATION REGARDING POTENTIAL MALFUNCTIONING EMERGENCY NOTIFICATION SIREN "One emergency siren was making noise [siren 27]. Huntersville Fire Department was contacted by someone in the area of the siren. No siren was activated. Initial investigation shows power loss to this one siren around the time of occurrence. Local news media contacted Duke Energy representative to question if sirens were set off. Continue to investigate to determine the issue with this one siren. Emergency Planning notified Mecklenburg County of failure of siren #27." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-29
50146 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-05-28 06:50 | 2014-05-28 16:39 | 2014-05-28 | AGREEMENT STATE REPORT- LOST AND FOUND LICENSED MATERIAL The following information was received from the State of Louisiana by facsimile: "Event Location: The radiography crew was at the MARATHON PETROLEUM COMPANY REFINERY, 4663 West Airline Highway, Garyville, LA, St. John the Baptist Parish. The crew was in the refinery to do radiography weld testing. The weather for the day was stormy and raining. The crew was in the vehicle waiting out the weather when a tornado ripped the darkroom off of the company vehicle and took the camera and source with the darkroom. "Event type: The lost/found gamma camera is an AMERSHAM, MODEL 880 DELTA, S/N4045 exposure device housing 39 Ci of Ir-192 AEA Technology sources, Model #A424-9, S/N # 1040C. "The camera was located within the refinery boundary and appeared to be undamaged and the source remained in the shielded area. The camera was surveyed and only background radiation levels were detected. The camera was then transported to QSA Global on Langley Dr. in Baton Rouge, LA for leak tests, radioactive source and DU [Depleted Uranium] mechanical evaluation. [QSA Global] stated the device would be disassembled for the evaluation. If the results of the evaluation are negative, the equipment will be removed from service. The leak test results for radiation and DU were negative for removable contamination. "Notifications: LDEQ [Louisiana Department of Environmental Quality] was notified of the lost/found radiography source in a QSA Global, Amersham Delta 880 gamma camera/source holder housing a 39 Ci Ir-192 source. The source exposure device was located within the refinery boundary. After a field evaluation, the exposure device was moved to QSA Global in Baton Rouge, LA for a professional mechanical evaluation. The results of the evaluation will determine if this equipment will be returned to service or remain out of service. "Event Description: On May 28, 2014, [a senior trainer and business ops manager] called LDEQ and reported that a radiography crew dispatched to the Marathon Refinery in Garyville, LA had been hit by a tornado on the jobsite. The incident was at the Marathon Refinery, 4663 West Airline Highway in Garyville, LA. The tornado ripped the darkroom off of the truck with the gamma camera in the darkroom. After the storm had passed, the crew and the Marathon RSO surveyed the area in an attempt to locate the radiography source. The source and exposure device were located, field test/inspected for damage and radioactive contamination. When the equipment was deemed safe, it was transferred to QSA Global for a professional mechanical evaluation. "ALL EQUIPMENT AND PERSONNEL APPEAR TO BE SAFE AND UNHARMED. "LDEQ CONSIDERS THIS EVENT CLOSED." THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-06-05
50145 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-05-28 10:37 | 2014-05-28 11:26 | 2014-05-28 | UNUSUAL EVENT DUE TO RELEASE OF CHLORINATED WATER "At 1037 EDT on May 28, 2014 an Unusual Event [EAL HU5] was declared due to a release of toxic gas that could have adversely affected plant operations. The leak was due to a leak in pipe containing water and chlorine. The pipe has been isolated and the leak has stopped." The chlorine smell was initially noticed at approximately 1008 EDT. The leak was coming from a buried underground pipe. There were no personnel injuries or medical response needed. The licensee notified the NRC Resident Inspector, State, and local authorities. The licensee plans on issuing a press release. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, and Nuclear SSA via email. * * * UPDATE FROM ROBERT SALES TO CHARLES TEAL AT 1202 EDT ON 5/28/14 * * * At 1140 EDT on 5/28/14 Oyster Creek has exited the Unusual Event. The leak has been isolated and is not affecting normal plant operations. The licensee notified the NRC Resident Inspector, State, and local authorities. The licensee plans on issuing a press release. Notified R1DO (Rogge), NRR EO (Chernoff), IRD MOC (Gott), DHS ASWO, FEMA Ops Center, NICC Watch Officer, and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-05-28
50144 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-25 | 2014-05-27 16:22 | 2014-06-04 | AGREEMENT STATE REPORT - STOLEN AND FOUND RADIOGRAPHY CAMERA The following information was received from the State of Texas by email: "On May 19, 2014, the Agency [Texas Department of State Health Services] received a complaint alleging multiple rule violations had been committed by an industrial radiographer working for the licensee. On May 27, 2014, during the complaint investigation, the licensee's site radiation safety officer (SRSO) stated that on April 25, 2014, the radiographer had taken one of the licensee's radiography trucks which contained a SPEC 150 exposure device with a 23 curie iridium-192 source following completion of a job in San Antonio, Texas. The radiographer had possession of the truck and exposure device with its source until April 30, 2014. The licensee's SRSO stated they attempted during that time to contact the radiographer and to locate the truck using its GPS locator system, but they were unsuccessful. The licensee located the truck at a recreational vehicle park in Portland, Texas. The licensee's SRSO stated the exposure device was found laying in the floor of the dark room, the dark room door was not locked, and the dark room's alarm was not activated. The SRSO stated to the Agency investigator during the May 27th telephone interview that it did appear to him that an exposure could have resulted to persons in an unrestricted area during the event. An investigation into this event is ongoing and more information will be provided as it is obtained in accordance with SA-300." Texas Incident: I-9196 * * * RETRACTION FROM KAREN BLANCHARD TO CHARLES TEAL ON 6/4/14 AT 1332 EDT * * * The following was received from the State of Texas via email.: "Investigation has determined that no theft occurred and this was not a reportable event. Investigation will continue in order to identify and address other potential regulatory violations." Notified R4DO (Taylor), Grant (IRD), Wray (ILTAB), and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-06-04
50143 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-05-26 02:52 | 2014-05-26 10:39 | 2014-05-26 | CONTROL ROOM OVERHEAD ANNUNCIATOR MALFUNCTION "At time 0252 EDT, the control room overhead annunciators malfunctioned resulting in the inability to receive more than one station alarm input and could not be acknowledged using the normal station alarm acknowledge pushbutton. "This condition existed from time 0252 EDT until time 0516 EDT on 5/26/2014 at which time the system was restored. During the entire period, backup assessment capability was functional, dependent upon redundant assets as described in existing station documentation and/or functionality of the control room alarm typer. Additionally, the station computer alarms and Safety Parameter Display System remained functional during the entire time period. "The licensee will continue to investigate the annunciator system. "The licensee notified the NRC Resident Inspector." The licensee will also notify State and local government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-26
50142 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-05-25 07:02 | 2014-05-25 07:30 | 2014-05-25 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0702 EDT on 5/25/14, Millstone Units 2 and 3 experienced a loss of offsite power and subsequent trip of both units. An Unusual Event was declared by Millstone Units 2 and 3 at 0715 EDT. Power is currently being supplied to all emergency busses by the emergency diesel generators. Offsite power is not available. At this time, it appears that the loss of offsite power is due to a localized issue in the Millstone switchyard. The surrounding areas were not affected. A decision was made to take the NRC to monitoring mode at 0749 EDT with Region 1 in the lead. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. * * * UPDATE FROM MICHAEL CICCONE TO CHARLES TEAL AT 1330 EDT ON 5/25/14 * * * All EDGs have been secured and offsite power has been restored. The licensee is reporting the loss of two stack radiation monitors - 8168 and 8169. This is reportable under 10CFR50.72(b)(3)(xiii). Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant). * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1548 EDT * * * At 1414 EDT the licensee terminated the Unusual Event. Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant), DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) | 0 | 2014-05-25
50141 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-05-25 07:02 | 2014-05-25 07:30 | 2014-05-25 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0702 EDT on 5/25/14, Millstone Units 2 and 3 experienced a loss of offsite power and subsequent trip of both units. An Unusual Event was declared by Millstone Units 2 and 3 at 0715 EDT. Power is currently being supplied to all emergency busses by the emergency diesel generators. Offsite power is not available. At this time, it appears that the loss of offsite power is due to a localized issue in the Millstone switchyard. The surrounding areas were not affected. A decision was made to take the NRC to monitoring mode at 0749 EDT with Region 1 in the lead. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1330 EDT * * * "The loss of offsite power was due to one main line coming into the plant shorting to ground. Emergency plan procedures have been implemented, natural circulation has been established, and the plant is stable. Offsite electrical power has been restored to both Unit 2 and Unit 3. Emergency diesel generators have been secured, and plant equipment has been restored to a normal line up. "Extended loss of instrument air following the loss of offsite power complicated the recovery actions. The normal reactor coolant system letdown flow path was not able to be established. This resulted in the rupture of the pressurizer relief tank rupture disk inside containment. The relief valve on the volume control tank lifted when restoring normal letdown. This caused the primary drains transfer tank to overflow into the auxiliary building. This overflow path has been isolated. Supplementary leakage collection system radiation monitor HVR-RE19B, and auxiliary building normal ventilation radiation monitor HVR-RE10B, are indicating normal levels." Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant). * * * UPDATE FROM MICHAEL CICCONE TO DANIEL MILLS AT 1548 EDT * * * At 1414 EDT the licensee terminated the Unusual Event. Notified R1DO (Gray), R1DRA (Lew), NRR EO (Kokajko), IRD MOC (Grant), DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode3: Power Operation; FMode3: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2014-05-25
50140 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-05-25 05:36 | 2014-05-25 07:37 | 2014-05-25 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF CONDENSER VACUUM "This is an non-emergency event notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification). "On 05/25/2014 at 0536 EDT, as part of a planned maintenance outage to repair a leaking check valve inside the containment building, Unit 4 power level had been lowered to 19% reactor power for the planned opening of the reactor trip breakers. Unit 4 experienced a loss of condenser vacuum. An automatic turbine trip signal was generated which initiated a reactor trip signal. The reactor tripped as required on the automatic trip signal. Unit 4 is currently in Mode 3 and stable. The loss of vacuum is under investigation at this time. All other plant systems are working as designed." The reactor trip was uncomplicated with no other safety system actuations. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. The grid is stable and Unit 4 is in its normal shutdown electrical lineup. Unit 3 was not affected and continues to operate at 100% power. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-05-25
50139 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-05-24 | 2014-05-24 18:28 | 2014-05-24 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following was received from the State of Florida: A Troxler moisture density gauge, Model 3430 (Serial #39376), was stolen from a locked trailer located at the 36th Street Bridge Project. Additional information will be provided when it is available. Florida Event Number: FL14-045 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-06-02
50138 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2014-05-24 10:09 | 2014-05-24 13:51 | 2014-05-24 | OFFSITE NOTIFICATION DUE TO INDIVIDUAL REQUIRING ASSISTANCE FROM OFFSITE EMERGENCY PERSONNEL "Offsite notification has been made to the Arkansas Department of Health due to Pope county EMS rescue personnel entering a radiological / contaminated area. "An individual was working in a radiological / contaminated area only accessible by ladder. The individual was unable to use a ladder to egress the area and requested assistance in exiting. Pope county EMS rescue with the on-site rescue team provided the necessary assistance which required the team to enter a radiological / contaminated area. "The team, including the individual in question, has exited the radiological / contaminated area. They were evaluated by Radiation Protection and were not contaminated. The individual was transported to a local medical facility for further evaluation." The individual was assisted in exiting the 'A' steam generator cavity. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-24
50137 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-04 | 2014-05-23 17:19 | 2014-05-23 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE The following was received from the State of Arizona via email: "On May 22, 2014, the Agency was notified of a medical event that occurred on April 4, 2014 involving Y-90 labeled SIR Spheres. "On April 4, 2014, an adult liver tumor patient was treated with an injection of SIR Spheres. The patient was prescribed 59.4 Gy to the liver, but instead, the actual dose to the liver was approximately 39 Gy. It was determined that the error occurred in the step of transferring the dose from the delivery vial to the dosing vial. The step of drawing up the sterile fluid was inadvertently omitted by the nuclear medicine technologist working alone which led to much less than the expected activity/sphere being transferred to the dosing vial. Only after the completion of the procedure was the large amount of residual activity detected and noted. The physicians noted that physiologic factors can affect the amount of spheres reaching the tumor so the discrepancy of the dose delivered apparently was not alarming or significant to them. The RSO discovered the medical event during a records review and recognized that the patient only received 63% of the prescribed dose." Arizona First Notice Number: 14-013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-06-02
50136 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-05-23 11:30 | 2014-05-23 16:57 | 2014-05-23 | LOSS OF ASSESSMENT CAPABILITY DUE TO FAILED AREA RADIATION MONITOR "At 1130 CDT, an Area Radiation Monitor (ARM) was determined to be non-functional as a result of a failed calibration test. This represents a loss of assessment capability reportable under 10CFR50.72(b)(3)(xiii). A portable radiation monitor has been placed in the affected area as a compensatory measure. "The health and safety of the public was protected as the plant was in a normal condition with no initiating event in progress or signs of elevated radiation levels on any other radiation monitors. "The NRC Resident Inspector has been notified." The failed ARM is located in the 'A' RHR core spray room. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-23
50135 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-05-22 | 2014-05-23 16:05 | 2014-06-16 | AGREEMENT STATE REPORT - PATIENT OVEREXPOSURE DUE TO MISCALCULATION The following was received from the State of Nebraska via fax: "At 1430 CDT, the RSO from Nebraska Methodist Hospital called to report a possible overexposure to a patient who had received a prostate treatment of implanted lodine-125 seeds. The RSO, who was also the Medical Physicist on the case, stated that he had mistakenly used the millicurie value for the air kerma value. The treatment dose was intended to be 145 Gray (14,500 rad) but the implant dose was calculated to be 178 Gray (17,800 rad) so the dose differentiated by 27 percent. It is unknown if the target organ (rectum) will exceed 50 rem." Nebraska Item Number: NE140004 * * * UPDATE FROM TRUDY HILL TO CHARLES TEAL AT 1659 EDT ON 6/16/14 * * * The following was received from the State of Nebraska via email: "In a letter dated June 3, 2014, the RSO/Medical Physicist from Nebraska Methodist Hospital updated the information for this incident. The implanted dose was 184 Gray. The dose to the organ at risk (rectum) is as follows: Only a small percentage of the entire organ (rectum) was imaged and contoured, in the plan that was 12cc. An estimate of the increased dose ranges from 16 Gray in the highest dose regions comprising 90% of the contoured volume and 27 Gray in the highest dose regions comprising 30% of the contoured volume. "The patient was informed within 24 hours of the discovery of the misadministration." Notified R4DO (Hay) and FSME Event Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2014-06-02
50134 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2014-05-23 12:10 | 2014-05-23 15:32 | 2014-05-23 | OFFSITE NOTIFICATION - RELEASE OF HYDROGEN GAS IN EXCESS OF REPORTABLE QUANTITY "At 1210 EDT on Friday, May 23, 2014, the Massachusetts Department of Environmental Protection and the Plymouth Massachusetts Fire Department were notified of a hydrogen release in accordance with plant procedures and 310CMR40.300, Massachusetts Contingency Plan Notification for Oil and Hazardous Material; Identification and Listing of Oil and Hazardous Material. This was due to a release of hydrogen gas to the environment exceeding the reportable quantity of ten pounds. The release was from the generator hydrogen cooling system. There was no plant damage. Hydrogen system pressure has been restored to the normal operating band and is stable. The cause of the event is under investigation. "This event posed no danger to the health and safety of plant personnel or members of the general public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-23
50133 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-16 01:48 | 2014-05-23 15:15 | 2014-05-23 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR INADVERTENT FAST START OF DIESEL GENERATOR DURING TESTING "In accordance with 10 CFR 50.73(a)(2)(iv)(A), this 60-day telephone notification addresses an unplanned, invalid actuation of the 2B-B Diesel Generator (DG). The event occurred on 04/16/2014 at approximately 0148 EDT while Watts Bar (WBN) Unit 1 was in Mode 6 for a refueling outage. At this time, an 18 month performance of 0-SI-82-6, '18 Month Loss of Offsite Power DG 2B-B,' was in process which required that 2-HS-82-113 (Maint-Auto Hand Switch Generator 2B-B) be placed in the Auto position. When this action was taken, the 2B-B DG experienced a fast start. At 0314 EDT on 04/16/2014, while in the process of stopping the DG, the DG experienced a second fast start. For both starts of the 2B-B DG, the DG successfully functioned and achieved its rated speed of 900 RPM. Following the second start of the 2B-B DG, an emergency stop was performed on the DG in accordance with SOI 82.04, 'Diesel Generator (DG) 2B-B.' The cause of the invalid starts was determined to be an intermittent open between a relay pin on the R3 relay (DG start relay) and the relay base due to oxidation. This event was documented in TVA's corrective action program as Problem Evaluation Report (PER) 872575. "The NRC Resident Inspector has been informed of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-05-23
50132 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-05-22 21:50 | 2014-05-23 01:01 | 2014-05-23 | BOTH HPCI SECONDARY CONTAINMENT AIRLOCK DOORS OPEN SIMULTANEOUSLY "On May 22, 2014, at 2150 hours, the Shift Manager was notified that both HPCI Secondary Containment interlock doors were open simultaneously. The doors were immediately closed and Secondary Containment pressure remained negative. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open. As a result, entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to Secondary Containment being inoperable. "This event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-05-23
50131 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-05-22 07:08 | 2014-05-22 09:34 | 2014-05-22 | PLANNED MAINTENANCE ON THE AUXILIARY BUILDING SERVICE WATER RETURN MONITOR "On May 22, 2014 at 0708 CDT, Kewaunee Power Station rendered the Auxiliary Building Service Water Return Monitor (R-20) nonfunctional for planned maintenance. R-20 is used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that would result in an Alert or Unusual Event and is being conservatively reported under 10CFR50.72(b)(3)(xiii) as a loss of emergency assessment capability. "R-20 is planned to be restored to functional by 1530 CDT today, 05/22/2014. "The NRC Regional Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-22
50130 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-05-22 02:10 | 2014-05-22 09:31 | 2014-05-22 | UNPLANNED ISOLATION OF REACTOR BUILDING VENTILATION RADIATION MONITOR "At 0210 [EDT] on May 22, 2014, Nine Mile Point Unit 2, the reactor building vent radiation monitor (Vent WRGMS) was removed from service due to a problem with the check source. "The unplanned isolation of Vent WRGMS is a 8-hour report for 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability. "Until the equipment is restored, Chemistry will perform sampling requirements per the ODCM. "The NRC Resident Inspector has been notified." The licensee notified the State of New York Public Service Commission. | 0 | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-22
50129 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-05-21 17:21 | 2014-05-22 02:02 | 2014-05-22 | STANDBY LIQUID CONTROL INOPERABLE DUE TO TANK INLEAKAGE "On 5/21/2014 at 1721 CDT, BFN [Browns Ferry Nuclear] U2 declared both trains of standby liquid control (SLC) inoperable due to suspected in-leakage to the U2 SLC tank. Control Room Operators received an alarm for high tank level and corresponding high level on the control room indicator. Personnel were dispatched to check the tank level locally and reported that tank level was high and rising. Based on this report, the SLC tank isolation valve common to both pumps was closed to prevent potentially overflowing the tank. It was subsequently determined that the sensing line had become clogged causing erroneous level indication and the local report of level was incorrect. Sensing lines for the tank level instrumentation were subsequently cleared, indicated tank level then returned to normal, and local check verified that tank level was normal. Operability was restored with tank level being verified normal and isolation valve returned to the open position. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D). This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). "The NRC Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-05-22
50128 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-05-21 11:00 | 2014-05-21 17:39 | 2014-05-21 | UNANALYZED CONDITION INVOLVING FIRE SAFE SHUTDOWN CAPABILITY "This notification is to report a condition involving degraded control power wiring that resulted in an adverse impact on the ability to perform Fire Safe Shutdown for a postulated fire in the Main Control Room / Cable Spreading Room (MCR/CSR) complex. Therefore, this notification is being made pursuant to 10CFR 50.72(b)(3)(ii)(B). "At approximately 1100 hours [EDT], based on inspections being performed as part of an extent-of-condition review, Engineering personnel concluded that a degradation existed involving transfer / isolation switches that potentially impacted the ability to mitigate an Appendix R fire postulated to occur in the MCR/CSR complex. During scheduled maintenance outage windows on March 6, 2014 and May 5, 2014, broken wires were identified and repaired while the associated systems were out of service. Based on completion of the extent of condition walkdowns today, an additional location was identified, raising the potential that this condition existed for a longer period of time. The wiring degradation is limited to the capability of using Shutdown Method 'D' as described in the Peach Bottom Atomic Power Station Fire Protection Program. Shutdown Methods 'A', 'B' and 'C' used for other postulated fire areas were not affected by this condition. The postulated fire would have had to cause the normal control power fuses to fail for the issue to impact the safe shutdown function. "Compensatory measures have been established until the condition is corrected. "The NRC Resident Inspector has been informed of this notification." In the event of fire resulting in a loss of control power, compensatory measures will allow restoration of control power by replacing blown fuses. The compensatory measures are detailed in a temporary change to the MCR/CSR complex fire response procedure. The condition will be repaired during future equipment outages at the earliest opportunity. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-05-21
50127 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2014-04-08 | 2014-05-20 19:03 | 2014-05-20 | AGREEMENT STATE REPORT - OHMART FIXED GAUGE WITH A BROKEN SHUTTER HANDLE The following information was received from the State of Washington via email: "This incident is a report of a broken fixed gauge shutter handle which originally was reported to [Washington Division of Radiation Protection] as a GL [General Licensed] device. This incident is a failure of the on/off (shutter) mechanism with the shutter stuck in the closed (safe) position when the handle broke off. [Washington Division of Radiation Protection] learned later that this was not a GL device as reported . . . but a specific license gauge. [Washington Division of Radiation Protection] acted upon the reporting criteria as this meets 10 CFR 31.5 (c)(5) criteria that applies to general license radioactive material and a report within 30 days with a description and remedial action of actual or indicated failure to the on-off mechanism. This report falls into that 30 day time frame but the device is a specifically licensed device. "Licensee informed Washington Department of Health (WA DOH) on 14 May 2014 that a shutter handle broke off a fixed gauge during shutdown for routine operations on 8 April 2014. Surveys by radiation safety officer and by health physics service provider consultant confirmed dose rates were within acceptable ranges and consistent with gauge SS&D sealed source and device data. The gauge manufacturer is scheduled to be onsite 23 May 2014 to assess and repair. An investigation continues and corrective actions are pending. "WA DOH incident number WA-14-019. "One Ohmart fixed gauge, model SH-F1, serial 2860GK. 100 millicuries original activity [Cs-137] in November 1996; now 67 millicuries today 20 May 2014. Source model pending, source serial believed same as device serial. Source and shutter and device conditions unknown, but believed to be undamaged and intact (dose rates similar to SS&D data). Problem with source and device to be determined by gauge manufacturer scheduled to be onsite 23 May 2014 to assess and repair." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2014-05-28
50126 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-05-19 | 2014-05-20 15:00 | 2014-05-20 | AGREEMENT STATE REPORT - PATIENT RECEIVED UNINTENDED SHALLOW SKIN DOSE The following information was received from the State of Florida via email: "[On] Monday May 19, 2014, on follow-up visit, the patient presented with burns on the thighs and the labia. [The] Radiation Oncologist ordered an immediate investigation: High Dose Remote After Loader (HDR) Prescription event. No further action will be taken on this incident." The patient received 21Gy in three (3) fractions. Following completion of treatment, a review of the Treatment Planning on Oncentra TPS revealed a reference length of 1223 mm instead of 1323 (expected value +/- 1 mm). The reference length used in the TPS was measured prior to CT with the SPS (Source Position Simulator) by two physicists. Therefore, the radiation was 10 cm short from reaching the target which explains the occurrence of burns on the patient's thighs. "The three prescribed fractions were delivered on: 3/31/14, 04/07/14 and 04/14/14." Florida Incident Number: FL14-043 The device used is an HDR containing Ir-192 with a Capri Applicator. A corrective action plan has been developed by the licensee to prevent recurrence. The licensee informed both the prescribing physician and the patient. No long-term adverse health effects are expected. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-05-28
50125 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-05-20 08:53 | 2014-05-20 14:30 | 2014-05-20 | LOSS OF ASSESSMENT CAPABILITY DUE TO PRE-PLANNED MAINTENANCE ON STACK RADIATION MONITOR At 0853 EDT, Millstone Station Unit 2 removed the Stack Radiation Monitor RM-8169 from service for planned maintenance. Maintenance and testing were completed and the Stack Radiation Monitor returned to service at 1100 EDT. The licensee informed both State and local agencies and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-20
50124 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-05-20 08:35 | 2014-05-20 10:52 | 2014-05-20 | MANUAL REACTOR TRIP DURING REACTOR STARTUP "On May 20, 2014, at 0835 hours during plant startup, Beaver Valley Power Station Unit 2 Operations personnel manually tripped the reactor due to meeting the pre-briefed trip criteria of 85% narrow range level on the 'A' Steam Generator. This manual trip criterion was reached after the steam generator water level began to oscillate following the start of the 'A' Condensate pump. A manual main steam line isolation was performed in order to limit reactor coolant system cool down. Plant trip response was as expected without complications, and all control rods fully inserted in the core. The plant is currently stable in Mode 3. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "Beaver Valley Power Station Unit 1 was not affected by this event. "The NRC Resident Inspector has been notified." No relief or safety valves lifted during this event. The unit is maintaining primary temperature using the atmospheric steam dumps and main feedwater pumps. There is no primary to secondary leakage. The plant is in its normal shutdown electrical lineup. | 0 | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-05-20
50123 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-05-19 12:36 | 2014-05-19 18:16 | 2014-05-19 | CONTAINMENT DECLARED INOPERABLE DUE TO CONTAINMENT FAN COIL LEAK "At approximately 1236 CDT on May 19, 2014, a cooling water leak was identified on 23 Containment Fan Coil Unit flange. Unit 2 Containment was declared inoperable, which required entry into Technical Specifications (TS) LCO 3.6.1 Condition A, Containment inoperable, in MODES 1, 2, 3, and 4. Immediate actions were taken to isolate the Fan Coil Unit and was isolated within 1 hour from the initial identification of the leak and TS 3.6.1 Condition A was exited. This restored Containment to an Operable status. A Work Request (WR) was initiated to repair the leak, and to restore the 23 Containment Fan Coil Unit to an operable condition. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(C), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. "The plant remains safe, and this condition does not pose any additional risk to the public. Additionally, our defense in depth strategies are relied upon to take actions to protect the health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-05-19
50122 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-05-15 | 2014-05-19 17:55 | 2014-05-20 | AGREEMENT STATE REPORT - RECOVERY OF TWO MOISTURE DENSITY GAUGES BY AN ARIZONA LICENSEE The following information was provided by the State of Arizona via email: "Date: May 19, 2014 "Time: 2:30 PM (MST) "First Notice: 14-012 "Arizona Licensee: N/A "License No.: N/A "On May 15, 2014, the [Arizona Radiation Regulatory] Agency was contacted by a licensee who stated that he was called about the disposal of a nuclear density gauge. The caller stated that they were not licensed and did not want to go to the regulatory agency but needed to get rid of the gauge. The caller also stated that if [the licensee] did not take the gauge, he would take it to a dumpster or leave it out in the desert. [The licensee] contacted the Agency on the afternoon of the 15th to discuss the situation. [The licensee] was contacted on the 16th and subsequently met the unknown caller and picked up the gauge. The gauge was brought to the Agency, where it was leak tested and secured. "The depth moisture gauge came in two different wood boxes. The first box contained a Troxler depth moisture probe, model number 1255, with a 100 millicurie Americium-241:Be source and an origin date of 05/03/1975. The second box contained a Troxler depth density gauge, model number 1351, with a 7.7 millicurie Cesium-137 source and an origin date of 07/13/1982 "The Agency continues to investigate the event." The State of Arizona will notify the Governor's Office and the FBI. * * * UPDATE AT 1553 EDT ON 05/20/14 FROM BRIAN GORETZKI TO S. SANDIN VIA EMAIL * * * The State of Arizona identified the Arizona licensee who picked up and dropped off the sources at the Agency. "The Am-241:Be probe/gauge has 3 labels on it with all different model and serial numbers. They are as follows: Model: 104a Serial #: J-3475 Model: 1255 Serial #: 810 Serial #: Am-239 Date: 5/30/75 "The Cs-137 gauge has the same thing. They are as follows: Model: 504 Serial #: 212 Model: 1351 Serial #: 212 Model: 40-6475 Date: 7/13/82 "[The Agency] crossed referenced the model/serial numbers in the NMED database and did not get any hits." Notified R4DO (Gepford) and FSME (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-05-27
50121 | -1 | BECKLEY APPALACHIAN REGIONAL HEALTH |  |  |  |  | 2014-05-18 10:30 | 2014-05-19 16:25 | 2014-05-21 | WRONG FORM OF RADIOACTIVE ISOTOPE ADMINISTERED FOR CARDIAC STRESS TEST A patient received a dose of MDP (25 mCi Tc-99m) which is used for bone scans vice cardiolite (31 mCi Tc-99m) for a cardiac stress test. The wrong dose was administered due to technician error. Both the prescribing physician and patient have been informed. No adverse health effects are anticipated. The licensee has corrective actions under review. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM JENNIFER BAILEY TO DONG PARK AT 1012 EDT ON 5/21/2014 * * * "Retraction of Event # 50121 [is requested] for Beckley Appalachian Regional Healthcare, License # 47-17725-02. The event reported did not exceed 5 rem as specified in section 35.3045 (a) (1)." Notified the R1DO (Gray) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2014-05-27
50120 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-05-16 10:40 | 2014-05-19 14:53 | 2014-05-19 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE STOLEN FROM TRANSPORT VEHICLE The following information was provided by the State of California via email: "RHB [Radiological Health Branch] Richmond received Hazardous Material Spill Report - Cal EMA [Emergency Management Agency] Control #:14-2601, from Warning Center on May 17, 2014. The report stated that the Silicon Valley Soil Engineering's moisture density gauge manufactured by CPN, model MC-1 DR-P, Serial MD 70803844, was stolen from the transport vehicle on May 16, 2014, at 10:40 a.m. [PDT]. The gauge contained 50 mCi of Am-241 and 10 mCi of Cs-137. "RHB will be inspecting this licensee to develop more information. "5010 Number (Date Notified): 051914" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-05-27
50119 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2014-05-17 06:30 | 2014-05-17 19:30 | 2014-05-17 | A CONTRACT SUPERVISOR VIOLATED THE LICENSEE FITNESS-FOR-DUTY PROGRAM "A contract supervisor violated the site Fitness-tor-Duty (FFD) policy as a result of off site activities. The individuals plant access has been suspended. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-05-17
50118 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2014-04-30 08:00 | 2014-05-16 16:15 | 2014-05-16 | AGREEMENT STATE REPORT - MISDELIVERY OF A RADIOACTIVE SOURCE The following information was received from the State of Nevada by email: [A Common Carrier] misdelivered an Ir-192 source for 645 North Arlington Avenue, Suite 120, Reno, NV 89503. The address was correct, but the source was inadvertently delivered to the Main Hospital receiving at 235 West Sixth Street, Reno, NV 89503. The source bucket was then delivered to the Radiation Safety Officer (RSO) - at the correct address. Once received by the RSO, the delivering employee was contacted and questioned about length of contact and it was estimated that 2 mrem of dose was received for 10 minutes of contact. The employee as well as the Director for the receiving department were contacted and told to refuse shipment of anything with a radioactive label and to call the RSO immediately. The shipper (Varian) was contacted and they filed a formal complaint with [the Common Carrier]. Nevada Event: NV140011 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2014-05-26
50117 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-05-15 16:20 | 2014-05-15 23:49 | 2014-05-16 | DEGRADED FIRE BARRIER "A degraded fire barrier was identified during a walkdown on May 15th, 2014 at 1620 [CDT]. The barrier separates Appendix R safe shutdown divisional equipment. "A fire watch has been established as a compensatory measure. The health and safety of the public was not jeopardized as a result of this condition as there have been no fires or initiating events. "The discovery of this degraded fire barrier is being reported as an unanalyzed condition as defined by 50.72(b)(3)(ii)(B). "The licensee has notified the NRC Senior Resident Inspector." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-05-16
50116 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-05-15 19:20 | 2014-05-15 23:10 | 2014-05-15 | UNIT 1 AND UNIT 2 EMERGENCY DIESEL GENERATORS START AND LOAD DUE TO LOSS OF ONE 34.5KV LINE "On 5-15-2014 at 1920 hours [EDT], with Unit 1 & 2 operating at 100% power, the North Anna 34.5 kV Bus 5, offsite power feed to the 'C' Reserve Station Service Transformer, was lost which resulted in the loss of power to the Unit 1 'H' Emergency Bus and the Unit 2 'J' Emergency Bus. As a result of the power loss, the 1H Emergency Diesel Generator and the 2J Emergency Diesel Generator automatically started as designed and restored power to the associated emergency bus. During this event, the Unit 2 'A' Charging Pump, 2-CH-P-1A, automatically started as designed due to the loss of power event. "The valid actuation of these ESF [Engineered Safety Feature] components due to the loss of electrical power is reportable per 10 CFR 50.72 (b)(3)(iv)(A). "The Unit 1 'H' Emergency Bus off-site power source was restored to service and the 1H Emergency Diesel Generator was secured and returned to automatic. The Unit 1 Action Statement of Technical Specification 3.8.1 was cleared at 2115 hours on 5-15-2014. The Unit 2 'J' Emergency Bus power feed continues to be from the 2J Emergency Diesel Generator and this line-up will remain until the off-site power source can be restored to operable status. The Unit 2 'A' Charging Pump has been secured and returned to automatic. "Both Units are in a stable condition. An investigation is underway to determine the cause of the 34.5 kV Bus 5 loss of power." Power was returned to the Unit 1 'H' Emergency Bus via the Unit 1 'B' Reserve Station Service Transformer. The licensee will be notifying local Louisa County officials and has notified the NRC Resident Inspector. | 100 | 96 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-05-15
50115 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2014-05-14 14:54 | 2014-05-14 18:07 | 2014-05-14 | PRESS RELEASE CONCERNING WILDFIRE NEAR THE FACILITY "SONGS [is] making a 4-Hour notification per 10CFR72.75 (b) to the NRC Operations Center regarding the following: "There has been a fire in the vicinity of the station. The fire is not on plant property and has not challenged station operations. Entry into SONGS' Emergency Plan and activation of the Emergency Response Organization is not required at this time. Because of the fire near the plant, Southern California Edison will be making a press release today to update the public as to the situation at the plant." The licensee notified an onsite NRC Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-14
50114 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-05-13 17:05 | 2014-05-14 17:58 | 2014-05-14 | FIVE GALLONS OF DIESEL FUEL SPILLED ONSITE REQUIRING STATE NOTIFICATION "At 1705 [EDT] on May13th, 2014, approximately 5 gallons of diesel fuel oil was spilled onto the ground on the south side of the Service Water Intake structure at the Salem Generating Station. The spill of diesel fuel was caused by a leak from the fuel supply line to the service water hot air furnace. The leak was isolated at the time of discovery and the spill terminated. The diesel fuel oil cleanup is in progress by Clean Harbors personnel and will continue until the spill has been remediated. "Nuclear Environmental Affairs Department determined a 4 hr report to the NRC under RAL 11.8.2.a. was warranted due to the 15 minute notification to the New Jersey Department of Environmental Protection at 1651 [EDT] on May 14, 2014." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-14
50113 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-05-12 | 2014-05-14 15:57 | 2014-06-18 | AGREEMENT STATE REPORT - STUCK SHUTTER ON A PROCESS GAUGE "On May 14, 2014, the licensee notified the Agency [Texas Department of Health] that when it was locking out sources on May 12, 2014, for a shutdown it was unable to close the shutter on one of its Ohmart-Vega model SHLG-2 fixed nuclear gauges which contained a 3 curie cesium-137 source. The licensee contacted the manufacturer. A service company came to the licensee's facility on May 14, 2014, and closed the shutter, removed the gauge, and placed it in storage. "The licensee will send the gauge to the manufacturer for repair. The gauge normally operates with the shutter in the open position. No one received any exposure as a result of this event. Additional information will be provided as it is obtained in accordance with SA-300." TX # I-9193 * * * UPDATE PROVIDED BY ART TUCKER TO JEFF ROTTON VIA EMAIL AT 1249 EDT ON 06/18/2014 * * * "A review of the licensee's written report found that a second gauge had failed during this event. The second gauge was an Ohmart-Vega model OHM-S-A2 gauge containing a 3000 milliCurie cesium - 137 source. The licensee stated that while trying to close the shutter on this gauge, the pin for the actuator handle broke and the handle came loose from the gauge. The handle was placed on the gauge and held in place with wire. The shutter was left in the open position. On May 14, 2014, the manufacturer was able to free the shutter and place it in the closed position. The gauge was removed from its mounting and package for shipment by the manufacturer. No significant exposure was received by any individual as a result of this event. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Hay) and FSME Resources (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-05-22
50112 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2014-03-18 19:30 | 2014-05-13 14:40 | 2014-05-13 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of containment isolation valves which occurred during the most recent refueling outage at Fermi 2. On 3/18/2014, at approximately 1930 EST, shortly after transferring Division 2 Reactor Protection System (RPS B) from the alternate to the normal power supply, Operations personnel noted that an unexpected half-scram occurred. Initial investigation found a fuse in an RPS Power Distribution Panel had blown. Further investigation found that a power contactor had failed causing the fuse to blow. The contactor failure resulted in an invalid half scram and actuations (closure) of Torus Water Management System (TWMS) Outboard containment isolation valves, Division 2 Drywell Pneumatics Inboard and Outboard containment isolation valves and the Drywell Floor and Equipment Drain Sumps Inboard containment isolation valves. All valves operated as expected. Since containment isolation valves in more than one system were actuated by this failure, this event constitutes an event or condition that resulted in manual or automatic actuation of the system listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B)(2) and is reportable under 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been informed of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-05-13
50111 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2011-09-21 | 2014-05-12 17:10 | 2014-05-12 | AGREEMENT STATE REPORT - LOST AND FOUND INDUSTRIAL GAUGE SOURCE CONTAINING AMERICIUM-241 "The Tennessee Division of Radiological Health (DRH) performed an inspection of Blues City Brewery (BCB) on 9/21/2011. The facility was previously owned by Coors Brewing Company through 9/1/2006. "During the inspection, it was discovered that a 3.7 GBq (100 mCi) Am-241 source (Industrial Dynamics Company - IDC model 06110-1, serial #5533) was missing. The source had originally been contained inside a level gauge (IDC model FT -100, serial #90205). According to IDC records, IDC had removed the source from the gauge on 9/29/1999, wipe tested the source, packaged it for shipment, and left the package in the possession of the Coors Brewing Company's RSO. The IDC RSO stated that they had no further record regarding the source. BCB conducted a thorough search of their facility for the source without success. DRH contacted the former Coors Brewing Company's RSO, but he did not have any additional information regarding this source. "On 10/25/2012, DRH received a quarterly report (7/1/2012 to 9/30/2012) from IDC that stated they recovered the source." Tennessee Event TN-12-126. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2014-05-20
50110 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-05-12 08:45 | 2014-05-12 17:37 | 2014-05-12 | PLANNED MAINTENANCE ON SAFETY PARAMETER DISPLAY SYSTEM "At 0845 [CDT] during planned maintenance, the annunciators which would indicate flooding in the Emergency Core Cooling System (ECCS) Pump Rooms to the max safe water level in the rooms were disabled. These max safe water level alarms are used to assess the emergency action level (EAL) entry condition (HA4) for flooding (ALERT classification). "Compensatory measures are in place to perform periodic walk downs of RHR A, RHR B, RHR C, HPCS, LPCS, RCIC rooms and the fuel building basement once per shift to verify no leakage. Additionally, the annunciator for max normal water level is operational and pump run times are still available in the Main Control Room to indicate increased leakage into the ECCS rooms. This max normal water level alarm is used to assess the EAL entry condition (HU4) for flooding (Unusual Event classification) and EOP-8 entry. "Since the operator compensatory actions that were established are not proceduralized, then this is reportable as a loss of emergency assessment capability under 10 CFR 50.72(b)(3)(xiii). "The expected return to service time of all alarms is 2300 CDT." The licensee will notify the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-12
50109 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-05-12 15:00 | 2014-05-12 16:57 | 2014-05-12 | TRITIUM CONFIRMED IN WATER SAMPLES ON-SITE UNDERGROUND "On May 12, 2014, at 1458 CDT, River Bend Station management determined that tritium confirmed to be present in water samples taken from in-leakage into the below-ground elevation of the turbine building basement, through an underground pipe penetration, was reportable in accordance with NEI 07-07, Ground Water Protection Initiative. The leakage was tested for gamma and tritium activity. No gamma contamination was detected. Tritium was measured at 28,270 picocuries per liter. The source and volume of the radioactive in-leakage is unknown. "The leakage into the plant is currently being contained, and actions are in progress to identify the source. The Louisiana Department of Environmental Quality was notified at 1500 CDT today [5/12/14]. This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as an event requiring notification of the state government. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-12
50108 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2014-05-12 10:20 | 2014-05-12 14:48 | 2014-05-12 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "During a review from industry operating experience it was identified that there are three additional unprotected DC control circuits for non safety related DC motors which are routed from the turbine building to other separate fire areas (this is in addition to the one circuit that was previously identified and submitted under event #50059). Fuses used to protect the motor power conductors appear to be inadequate to protect the control conductors. The concern is that under fire safe shutdown conditions, it is postulated that a fire in one area can cause short circuits potentially resulting in secondary fires or cable fires in other areas where the cables are routed. The secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. "This condition is reportable as an 8 hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-05-12
50107 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-05-06 | 2014-05-12 12:53 | 2014-05-12 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was received from the State of Ohio via email: "Licensee contacted BROP [Bureau of Radiation Protection] at approximately 2:30 PM on 5/6/14 to report that a radiography crew experienced a source disconnect during radiography operations earlier in the day. After completing the 3rd shot of the day a radiographer attempted to crank the source back into the camera. The drive cable appeared to crank back in but reading on the survey meter indicated that the source was still outside the camera, apparently in the area of the collimator. Licensee personnel attempted to crank the cable in and out several times in an attempt to retract the source, but were unsuccessful. The area was secured and monitored by licensee personnel pending further retrieval efforts. "The corporate RSO was contacted, who dispatch two trained source retrieval personnel to the location. During evaluation it was determined that the drive cable had broken near the male connector. Licensee personnel were able to unlock the camera, feed the broken drive cable through the camera, and retrieve the source into the shielded position. Retrieval was accomplished at approximately 6:30 PM that evening. A new drive cable was connected to the camera and the radiographers were able to continue operating the camera with the new drive cable without incident. "The two licensee retrieval personnel recorded doses of 20 mRem and 40 mRem on their pocket dosimeters. The licensee is having the broken drive cable returned to their corporate office for examination to determine the cause of the break. Licensee is preparing a written report on this incident." The Radiography Camera involved is a QSA Model 880D, Serial number D8378 containing 46.1 Curie Ir-192 source. The sealed source is model number A424-9, serial number 12727C. The incident occurred at the Kensington, OH site. State of Ohio Reference No.: 2014-010 Corrective actions included obtaining a new cable. Repairs were made without an engineering change to the system. State of Ohio submitted the NMED Item Number: OH140006 on 05/07/14. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-05-20
50106 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-05-12 07:31 | 2014-05-12 11:13 | 2014-05-12 | UNIT 2 STACK HIGH RANGE RADIATION MONITOR REMOVED FROM SERVICE FOR PRE-PLANNED MAINTENANCE The Unit 2 Stack High Radiation Monitor, RM-8168, was removed from service for pre-planned maintenance. There are no actuations associated with this Radiation Monitor. Testing was completed and the radiation monitor was restored to operable at 1013 EDT, on 5/12/14. The licensee has informed the NRC Resident Inspector and applicable State and Local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-12
50105 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-05-11 08:02 | 2014-05-11 16:00 | 2014-05-12 | LOSS OF THE METEOROLOGICAL TOWER COMPUTER SYSTEM "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0802 (CDT), on 05/11/2014, the meteorological tower computer system failed which resulted in a loss of meteorological data to the plant. Information Technology personnel have reported to the plant for investigation. Proceduralized compensatory measures for dose assessment include use of National Weather Service followed by historically determined default values. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-11
50104 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-05-09 15:26 | 2014-05-09 16:46 | 2014-05-09 | NON-LICENSED EMPLOYEE SUPERVISOR IN VIOLATION OF FITNESS FOR DUTY POLICY "A non-licensed employee supervisor had a confirmed positive drug test during a random fitness-for-duty test. The employee's access to the plant has been revoked." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-05-09
50103 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-05-08 | 2014-05-09 15:57 | 2014-05-09 | AGREEMENT STATE REPORT INVOLVING OVER DOSE TO PATIENT The following information was received from the State of Texas via email: "The University of Texas Medical Branch reported that a patient received .975 MBq (26.35 æCi) instead of the prescribed .37 MBq (10 æCi) of I-131 for a diagnostic test for Grave's Disease on May 7, 2014. The rinse bottle used to add water to the I-131 to ensure all Iodine was ingested was contaminated from a previous therapeutic treatment on May 2, 2014. The rinse bottle tip which was used to squirt water into a 20 mCi I-131 solution for the therapeutic dose siphoned some of the iodine back into the bottle. The expected thyroid dose for the diagnostic procedure was 26 cGy (rad). The calculated thyroid dose with the additional contamination from the bottle was 68.51 cGy (rad). The Agency directed that the hospital immediately inform the patient. An investigation into this event by the Texas Department of State Health Services in ongoing. Additional information will be provided IAW with SA300 reporting requirements. "Texas Incident #: I-9192" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-05-19
50102 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-05-08 18:15 | 2014-05-09 12:37 | 2014-05-09 | NON-LICENSED CONTRACT SUPERVISOR IN VIOLATION OF FITNESS FOR DUTY POLICY "A non-licensed contract supervisor has been found in violation of the Fitness for Duty Policy. The individual's access to the plant has been terminated. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2014-05-09
50101 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-05-09 | 2014-05-09 12:42 | 2014-05-09 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of Texas via email: "The licensee called to report the theft of a moisture density gauge. The vehicle was dispatched to a work location in Houston. On the way, the driver stopped at a McDonald's not far from the office. When the driver arrived at the job site, he discovered the tailgate down and the security chain had been cut. The licensee had not filed a police report when the RSO notified the radiation control program in Texas. The RSO was instructed to contact police as soon as possible. The gauge is a Humboldt model 5001 EZ. The serial number is 3664. The device contains an 11 millicurie Cs-137 source, serial number 0283cx, and a 44 millicurie Americium 241/Be source, serial number nj03996. The licensee was encouraged to offer a reward for the return of the gauge. "Texas Incident #: I-9191" * * * UPDATE AT 1623 EDT ON 05/09/14 FROM ROBERT FREE TO S. SANDIN VIA EMAIL * * * "The licensee emailed that the device was recovered by a passerby who found it by the side of the road. The licensee reported the device was still locked in its transportation container. The licensee recovered the container, leak tested the device and found no radioactive contamination. There was no radiation exposure to a member of the public. Notified R4DO (Whitten), FSME_Events Resource and ILTAB via email, and Mexico via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-05-19
50100 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-05-08 18:24 | 2014-05-08 21:57 | 2014-05-08 | OFFSITE NOTIFICATION MADE DUE TO OIL LEAK "At 1824 hours [EDT] on May 8, 2014, an oil leak was discovered on EX-07 Safeguards Transformer 1-1 that sprayed outside the transformer containment berm. The oil released to the ground was approximately 70 gallons, which is greater than the reporting requirements. The oil was not released to any surface water and has no drain path to reach any surface water. The State of Michigan, via the Pollution Emergency Alert System (PEAS) and Van Buren County was notified as required by the Site Spill Plan by the Control Room at 2003 hours." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-08
50099 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2014-05-08 10:24 | 2014-05-08 21:15 | 2014-05-16 | HIGH PRESSURE FIRE WATER SPRINKLER SYSTEM B-6 DECLARED INOPERABLE "At 1024 CDT, on 05-08-2014, the Plant Shift Superintendent was notified that the C-333 High Pressure Fire Water (HPFW) Sprinkler System B-6 had been inspected by Fire Services and 5 sprinkler heads had visible corrosion or paint on them, including 2 heads adjacent to each other. The system configuration was evaluated using EN-C-822-99-047 [Engineering Notice], 'Effects of Impaired Sprinkler Heads on System Operability' and determined that with these heads potentially impaired, a portion of the building would not have sufficient sprinkler coverage. The HPFW system is required to be operable according to TSR LCO [Technical Safety Requirement Limiting Condition for Operation] 2.4.4.5. HPFW Sprinkler System B-6 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. "Based on past testing results, there is a possibility that the heads would have been able to perform their specified safety function. Once the heads are removed from the system, testing will be performed to determine the actual effect on operability. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Region II (Marvin Sykes) has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-14-0444; PGDP Event Report No. PAD-2014-05; NRC Worksheet No. 50099; Responsible Division: Operations." * * * RETRACTION FROM DEREK WARFORD TO VINCE KLCO AT 1932 EDT ON 5/16/2014 * * * "Subsequent to the event, the corroded sprinkler heads were replaced with new heads and the removed heads were tested in the laboratory. Based on the test results, one of the adjacent heads that was potentially impaired was determined to be fully functional and in accordance with EN-C-822-99-047, HPFW Sprinkler System B-6 was capable of performing its intended safety function. Since this event does not meet the criteria for a reportable event under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed, the event notification is being retracted. "The NRC Region II (Marvin Sykes) has been notified of this retraction." Notified the R2DO (Desai) and NMSS EO (Csontos). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2014-05-08
50098 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2014-05-08 16:45 | 2014-05-08 20:57 | 2014-05-08 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the potential for secondary fires being caused by DC Motor control circuit wiring has determined the described condition to be applicable to Nine Mile Point Unit 1 resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and configuration for the containment isolation valve IV-33-04 does not include separate over current protection for the power and control wiring. The only protection for the control circuit wiring is provided by the power circuit fuses. "In the postulated event, a fire in the reactor building at the DC MOV could cause one of the control circuit wires to short and potentially over heat creating a secondary fire in the raceway system in a different fire zone. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. This event entered into the Nine Mile Point corrective action program as Condition Report (CR) 2014-004630. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire zone inspections) have been implemented for affected areas of the plant." The licensee has notified the State and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-05-08
50097 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-05-04 08:32 | 2014-05-08 17:46 | 2014-05-08 | MANUAL INITIATION OF THE REACTOR PROTECTION SYSTEM WHILE SHUTDOWN "On 5/4/14 while the plant was in Mode 3 and the reactor not critical, unexpected position indications were observed on a Control Rod while withdrawing an Axial Power Shaping Rod (APSR). Due to the uncertainty of rod positions, the APSR was inserted into the core. The reactor trip breakers were then opened from the Control Room using the manual trip pushbuttons. All Control and Safety Rods were unlatched and fully inserted into the reactor core before the reactor trip breakers were opened. "This manual initiation of the Reactor Protection System with the reactor not critical is being reported per 10 CFR 50.72(b)(3)(iv)(A). The reportability of this event was determined based on an extent of condition review for Event Number 50086 that occurred 5/5/14. The failure to meet the 8-hour reporting requirement has been entered into the Corrective Action Program." The licensee notified the NRC Resident Inspector, the State of Ohio, and Ottawa and Lucas Counties. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-05-08
50096 | 0 | SCIENTECH |  |  |  |  | 2014-05-07 | 2014-05-08 14:57 | 2014-05-08 | PART 21 - POTENTIAL DEFECT IN NUS-710DU TRIP UNIT TO PRODUCE A VALID TRIP OUTPUT SIGNAL The following summary was provided by Curtiss-Wright Flow Control Corporation: "In certain operating configurations, NUS-710DU Trip Units could fail to produce a valid trip output signal. "Transistor Q8 on the referenced units uses a TO-66 package and is flush mounted on the component side of the PCB. The TO-66 package, based on JDEC drawing TO-213 does not specify the size of the glass-sealed holes in the case (collector) around the base and emitter leads. Random samples measure approximately 0.11" in diameter. The PCB includes standard 0.100" solder pads on both non-component and component sides. During manufacture, Q8 is secured using screws and nuts with leads centered in the through-holes, so no direct solder pad to case contact is possible. However, the presence of the pad on the component side could facilitate, under certain conditions, excessive solder flow, creating a close proximity, or in the extreme case bridging, between solder on the emitter or base solder pad and the Q8 case. Permanent bridging would be detected during acceptance testing. However, in at least one case, with the trip unit mounted in the trip unit chassis via an extender card, the proximity was close enough to create contact when the board was slightly flexed. "The trip units have two modes of operation, NORM and REV, selectable by switch S2, and four operating configurations: (1) NORM mode, rising trip, energize on trip, (2) REV mode, falling trip, energize on trip, (3) NORM mode, falling trip, de-energize on trip and (4) REV mode, rising trip, de-energize on trip. "In configuration (1 ), the set point is applied to the negative terminal of a comparator and the input is applied to the positive terminal. When the input rises above the set point, the output of the comparator goes to the positive rail, turning on Q7. When Q7 turns on, it pulls the base of Q8 low, causing Q8 to turn on. When Q8 turns on, the trip output goes to approximately +24V. "In configuration (2), the set point is applied to the positive terminal of the comparator and the input is applied to the negative terminal. When the input drops below the set point, the output of the comparator goes to the positive rail and turns on Q8, resulting in a trip output of approximately +24V. "In configurations (1) and (2), bridging at Q8 would cause an output trip signal. "In configuration (3), when the input drops below the reset point, the output of the comparator goes to the negative rail, which causes Q8 to turn off. When Q8 turns off, the trip output goes to approximately zero volts. "In configuration (4), when the input rises above the reset point, the output of the comparator goes to the negative rail and turns off Q8, de-energizing the unit output. "In configurations (3) and (4), bridging at Q8 would prevent a valid trip signal from being generated by keeping the output at logic high. "Plant: Limerick/Part Number: NUS-710DU0TS/Quantity: 2/Serial Numbers:1303582, 1303583 "Plant: Limerick/Part Number: NUS-710DU0TT27000/Quantity: 6/Serial Numbers: 1304197, 1304198, 1304199, 1304200, 1304201, 1304202 "Plant: Columbia/Part Number: NUS-710DU0TT45059/Quantity: 5/Serial Numbers: 1303632, 1303633, 1303634, 1303635, 1303636 "Plant: Grand Gulf/Part Number: NUS-710DU0TT27000/Quantity: 3/Serial Numbers: 1303672, 1303673, 1303674 "Plant: Perry/Part Number: NUS-710DU0TT27000/Quantity: 33/Serial Numbers: 1304219, 1304220, 1304221, 1304222, 1304223, 1304224, 1304225, 1304226, 1304227, 1304228, 1304229, 1304230, 1304231, 1304232, 1304233, 1304234, 1304235, 1304236, 1304237, 1304238, 1304239, 1304240, 1304241, 1304242, 1304243, 1304244, 1304245, 1304246, 1304247, 1304248, 1304249, 1304250, 1304251. "Should you have any questions regarding this matter, please contact Robert Queenan, Division Manager, Scientech/Instrumentation and Controls, at (208) 524-9311." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | ID | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-05-08
50095 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-05-08 04:29 | 2014-05-08 12:17 | 2014-05-08 | LOSS OF 34 EMERGENCY SIRENS "At approximately 0429 hours (EDT) on May 8, 2014, McGuire was informed that 34 emergency sirens were incapable of activation from the primary location. The loss of these 34 sirens for more than one hour is reportable pursuant to 10 CFR 50.72(b)(3)(xiii). Until repairs are complete, backup route alerting is in place. "Troubleshooting is in progress. During troubleshooting, an inadvertent actuation of emergency sirens occurred at 1030 hours (EDT) on May 8, 2014. Mecklenburg County Emergency Management was notified of this inadvertent actuation which is being reported pursuant to 10 CFR 50.72(b)(2)(xi). Although these sirens were activated there was no incident at McGuire. This event does not impact public health and safety. "The NRC Resident Inspector and local agencies were notified." * * * UPDATE FROM NICHOLAS BARTSCHER TO DANIEL MILLS ON 5/08/2014 AT 1603 EDT * * * The emergency sirens have been repaired and are functional. The NRC Resident Inspector has been notified. Notified R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-05-08
50094 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-05-06 22:00 | 2014-05-08 10:44 | 2014-05-08 | RADIOGRAPHY SOURCE TUBE CRIMPED PREVENTING SOURCE RETRACTION "On May 7, 2014, the Agency [Texas Department of State Health Services] received notice that a source retraction failure had occurred on May 6, 2014 around 10 o'clock PM. The camera was a QSA Global 880D (sn D11607) with a 46 curie iridium-192 source (sn 12764C). The guide tube had fallen off of the guide tube stand and crimped. The source was retrieved by the licensee by uncrimping the guide tube. No overexposures resulted from this event. The guide tube was removed from service. All other parts are removed from service pending inspection by the licensee." Texas Incident Report: I-9190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-05-16
50093 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2014-05-07 14:50 | 2014-05-07 15:19 | 2014-05-07 | VOLUNTARY NOTIFICATION TO OFFSITE GOVERNMENT AGENCIES DUE TO LEAK OF WATER CONTAINING LOW LEVEL TRITIUM CONCENTRATION IN ACCORDANCE WITH NEI INITIATIVE 07-07 "A leak containing a low level tritium concentration assumed to be greater than 100 gallons of water, with the potential to reach groundwater, occurred at Oconee Nuclear Station. A water sample indicated that the tritium level was 3150 picocuries per liter; which is less than a quarter of the US Environmental Protection Agency drinking water standard of 20,000 picocuries per liter for tritium. "While conducting a transfer from one chemical treatment pond to another, water was observed seeping from the ground at a location near the transfer piping between the ponds. The transfer was terminated and the ground seepage subsided. Actions have been taken to prevent further use of the chemical treatment pond discharge path at this time. Based upon the on-site location and low tritium levels, there is no health or safety impact to the public or employees. "Voluntary notification of state and local agencies is being made via the industry groundwater protection initiative; measured tritium levels were below any required notification threshold." Agencies notified: South Carolina Department of Health and Environmental Control, South Carolina Emergency Management, City of Seneca, City of Anderson, Greenville Water System, Oconee County Administration, Pickens County Administration, Anderson County Administration, Oconee County Emergency Management, Pickens County Emergency Management, Greenville County Emergency Management, and Clemson University Utility Services. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-05-07
50092 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-05-07 04:56 | 2014-05-07 07:45 | 2014-05-07 | AUTOMATIC TRIP DUE TO GENERATOR PROTECTION RELAY "This 4 and 8 hour notification is being made to report that Salem Unit 1 experienced an unplanned automatic reactor trip and subsequent Auxiliary Feedwater System actuation. The automatic trip was initiated from a generator protection relay. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. 11, 12 and 13 Aux Feedwater Pumps automatically started as expected on low Steam Generator water level following the reactor trip. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "Salem Unit 1 is currently in Mode 3. Reactor Coolant system pressure is at 2235 PSIG and temperature is 547 F with decay heat removal via the Main Steam Dumps and Auxiliary Feedwater Systems. Condenser vacuum was available for the duration of the event. "The 12 Chiller was tagged for maintenance prior to this event and had no adverse impact on the post trip plant response or stabilization. No personnel were injured during this event." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-05-07
50091 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-04-30 | 2014-05-06 15:15 | 2014-05-06 | AGREEMENT STATE REPORT - INCORRECT DOSAGE ADMINISTERED TO PATIENT "I am reporting a Medical Event and Abnormal Occurrence. The event resulted from incorrect dosage administered to the patient for the second phase of the yttrium-90 SirSperes for treatment of the liver. The patient was administered 43 millicuries of Y-90 for the second phase instead of 12 to 12.5 mCi as intended. The event occurred at Cedars Sinai Medical Center (California Radioactive Materials License number 0404-19) in Los Angeles, CA, on April 30, 2014. Los Angeles County Public Health, Radiation Management was notified on May 1, 2014. During the original report date, the licensee did not have any information regarding the radiation dose to the patient and was working with their Medical Physicists. On May 6, 2014, Cedars Sinai Medical Center reported that the patient received 363 Gray instead of the intended dose within the range of 53-102 Gray. Per the licensee, both the patient and referring physicians have been notified. The patient has not reported any side effects that were unanticipated and the patient will continue to be medically monitored." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-05-14
50090 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-05-06 08:30 | 2014-05-06 13:27 | 2014-05-09 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL DURING INSTRUMENT TESTING "At 0830 [CDT] on 05/06/2014, the Unit 3 reactor automatically scrammed due to low reactor water level as a result of a trip of both recirculation pumps. Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure. Reactor feedwater pumps are in service to control reactor water level. "Primary Containment Isolation System Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. The Reactor Feedwater System controlled and maintained water level above the level 2 initiation setpoint. "Prior to the Scram, the reactor was operating at 100% power. A Core and Containment Cooling Systems Analog Trip Unit Functional Test was in progress. The cause of the recirculation pump trip is under investigation. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." U1 and U2 remained at 100% power and were unaffected. * * * UPDATE AT 1302 EDT ON 05/09/14 FROM TODD BOHANAN TO DONG PARK * * * "Investigation revealed that a failed power supply caused an Anticipated Transient Without Scram/Alternate Rod Insertion (ATWS/ARI) signal to be generated when a level 2 Reactor Water Level was simulated on one instrument. All systems responded to the ATWS/ARI signal as designed. This signal opened the Recirc Pump Trip breakers for both Recirculation Pumps and opened the ARI valves to bleed air from the Reactor Protection System (RPS) scram air header. The resulting transient caused reactor water level to dip below the RPS trip setpoint (level 3 Reactor Water Level), a normal plant response, and the automatic scram signal occurred. At the time of the RPS scram signal, all rods were inserting and reactor power was approximately 2-3% and lowering. "The NRC Resident Inspector has been notified." Notified R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-05-06
50089 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-03-09 16:13 | 2014-05-06 12:50 | 2014-05-06 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID ACTUATION OF AN EMERGENCY SERVICE WATER SYSTEM "This 60-day report, as allowed by 10CFR 50.73(a)(1), is being made pursuant to 10CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of an emergency service water system. "On 3/9/14, at approximately 1536 EST, the E2 Emergency Diesel Generator (EDG) was started for a post maintenance operability test. The 'A' safety-related Emergency Service Water (ESW) pump was being used to provide cooling to the EDG. At approximately 1613 EST and 1622 EST, unexpected automatic starts of the 'B' ESW pump and the non-safety related single train Emergency Cooling Water (ECW) pump occurred. The EDG run was terminated at 1622 EST to investigate the cause of the unexpected starts. "It was determined that a failed angle drive adaptor resulted in invalid input to the speed switch, which resulted in the unplanned starts of the 'B' ESW pump and the ECW pump. Except for the failure of the angle drive adaptor, all systems and equipment operated as expected. "The NRC resident has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-05-06
50088 | 0 | MANSON CONSTRUCTION |  |  |  |  | 2014-05-03 12:00 | 2014-05-06 11:47 | 2014-05-06 | PROCESS GAUGE SHUTTER FAILED TO FUNCTION PROPERLY The licensee Radiation Safety Officer (RSO) determined that the shutter to a Berthold Model LB7440-D-CR process gauge with a 500 mCi Cs-137 source (source s/n: 031-08) did not open despite repeated attempts to cycle and lubricate the shutter opening mechanism. The RSO made this determination using instrumentation after rotating the shutter opening handle 180 degrees to the normally open position. The shutter had apparently become disconnected from the opening mechanism. The instrument is installed on a hopper dredge and is pointed down in an area not normally accessible by personnel. A licensed Berthold technician has been contacted and will come to the site to repair the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 40.60(b)(2) |  |  |  | 0 | 2014-05-14
50087 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-05-05 | 2014-05-06 09:26 | 2014-05-06 | AGREEMENT STATE REPORT - FIXED GAUGE STUCK SHUTTER The following information was received from the Commonwealth of Virginia: "The licensee discovered a shutter stuck in the open position during a routine test of a fixed gauge on May 5, 2014. The gauge is a Ronan Engineering Model SA1, serial number M-7299. It is used as a low-level indicator in a pre-dryer vessel and contains a 26.9 milliCurie (decay corrected) cesium-137 source. The licensee indicated that using unusual force to try to close the shutter would likely damage the actuator rod mechanism. The shutter is kept in the open position during operations and does not pose an additional radiation exposure to personnel. The licensee performs radiation surveys at one foot from the gauge surface during routine tests. The maximum reported result for this gauge was 300 microR per hour. The licensee has contacted the manufacturer to repair the gauge. The Agency [Virginia Radioactive Materials Program] will continue to monitor the situation until the shutter is repaired." Virginia Event: VA-2014-004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-05-14
50086 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-05-05 14:56 | 2014-05-05 21:17 | 2014-05-05 | MANUAL REACTOR SCRAM WITH ROD MOTION WHILE SHUTDOWN "During planned testing of the Control Rod Drive (CRD) system, the reactor trip breakers were opened via the manual reactor trip push buttons to de-energize a CRD motor in response to a high temperature. The partially withdrawn control rods fully inserted and all other rods remained in their initial positions. "This manual Reactor Protection System (RPS) actuation while the reactor was not critical is reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector, the State of Ohio, and Ottawa and Lucas Counties. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-05-05
50085 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-05-03 12:09 | 2014-05-03 15:15 | 2014-05-03 | AUTOMATIC REACTOR SCRAM DUE TO GENERATOR/TURBINE LOAD MISMATCH "At 1209 CDT on 3 May 2014, Dresden Unit 2 automatically scrammed on a Generator-Turbine Load Mismatch signal following a main generator trip. All rods inserted to their full in positions. "All systems operated as expected. Reactor vessel inventory and pressure are being maintained in automatic. "The cause of the scram was due to a main generator trip that occurred during a voltage regulator channel transfer. Troubleshooting is in progress to determine the exact cause of the generator trip. "This condition is being reported pursuant to 10CFR50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." The plant is in a normal shutdown electrical lineup. Main feedwater is being used to maintain reactor vessel level and decay heat is being removed by the main condenser via the turbine bypass valves. There was no impact on Unit 3 which remains stable at 100 percent power. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-05-03
50084 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-05-02 19:20 | 2014-05-03 03:42 | 2014-05-08 | REACTOR BUILDING STACK RADIATION MONITOR FAILURE "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 1920 (PDT), on 05/02/2014, PRM-RE-18, Reactor Building Stack Monitor - Intermediate Range Detector, failed downscale. PRM-RE-1A and PRM-RE-1C, the Reactor Building Stack Monitor - Low and High Range Detectors, both remain operable and fully functional. Compensatory measures are being implemented per plant procedures at this time. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1754 EDT ON 05/08/14 FROM JASON LOVEGREN TO DONG PARK * * * "Following completion of maintenance activities PRM-RE-1B, Reactor Building Stack Monitor - Intermediate Range Detector was returned to operable status at 0810 PDT on 05/08/2014, restoring its required emergency assessment capability. "The NRC Resident Inspector has been notified." Notified R4DO (Whitten). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-03
50083 | 0 | FLOWSERVE US INC. |  |  |  |  | 2014-05-02 | 2014-05-02 16:48 | 2014-05-02 | PART 21 REPORT - CHECK VALVES WITH MISSING JAM NUTS The following is a synopsis of information received via facsimile from Flowserve: Jam nuts were found to be missing on size 4, pressure class 600, normally open, in-line check valves per Flowserve drawing no. 07-45546-01. The valves are used in saturated steam service and must close with a reverse flow of less than 7000 lbs/hr steam at 95 and 1085 psig. The valve operating parts are identified as safety related. These valves were supplied to both Diablo Canyon and Sequoyah nuclear power plants. Flowserve recommends that all in-service valves be inspected for proper torque and that dual thread staking be provided per revised Flowserve drawings. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-05-02
50082 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2014-05-02 05:30 | 2014-05-02 16:30 | 2014-05-02 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was provided by the State of Alabama via facsimile: "On the morning of May 2, 2014 at approximately 0530 CDT, a CPN model MC-3 moisture density gauge, serial number M30129990, containing 10 millicuries of Cs-137 and 50 millicuries of Am-241:Be was damaged while in use at a temporary job site in Birmingham, Alabama when it was run over by a motorist. The licensee, Dunn Construction, notified the Alabama Office of Radiation Control at 0803 CDT. Dunn Construction is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 812. The licensee representative stated that the source rod became unattached, but was returned to the shielded position. Radiation levels around the gauge were found to be within the normal range. The gauge was placed back in the transport container and returned to the licensee's facility. The licensee was advised to perform a leak test of the gauge." Alabama Incident 14-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2014-05-12
50081 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-05-02 11:25 | 2014-05-02 13:43 | 2014-05-02 | ON-SITE MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee with a foreign body in his left eye reported to the on-site dispensary this morning. The plant nurse administered first aid and then released the employee to an off-site medical facility for further evaluation. A whole body survey of the employee in his plant clothing was performed. The maximum amount of contamination present was on the employee's boots, 370,667 dpm/100cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was whole body frisked out of the plant. The employee was free of contamination upon release." Licensee notified NRC Region II Division of Fuel Facility Inspection personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-05-02
50080 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-05-01 20:45 | 2014-05-01 22:33 | 2014-05-02 | LOSS OF HPCI OPERABILITY DUE TO WATER ACCUMULATION IN THE HPCI TURBINE "While investigating a Unit 1 high pressure coolant injection (HPCI) room instrument sump level high alarm, condensation was observed dripping out around the HPCI turbine shaft gland seals. A steady stream of water was also observed coming out of the governor end gland seal along with a slight leak coming from the coupling end. Observation revealed that leakage through the 'closed' steam admission valve (1E41-F001) was apparently resulting in water accumulation in the HPCI turbine. A blown fuse that prevented the associated HPCI exhaust drain pot from draining in conjunction with the leakage by the steam admission valve was determined to be sufficient to impact HPCI operability. Required actions were taken in accordance with the Technical Specifications. "Efforts are underway to determine the actions needed to restore the HPCI system to operable status." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JOHN SELLERS TO CHARLES TEAL AT 0154 EDT ON 5/2/14 * * * "HPCI has been restored to an Operable but degraded nonconforming condition. Fuses replaced and automatic functions restored. Leakage confirmed to not be excessive for this condition. Compensatory actions established. Restoration time 2345 EDT 5/1/14." The licensee will notify the NRC Resident Inspector. Notified R2DO (Ayers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-05-01
50079 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-05-01 16:10 | 2014-05-01 18:12 | 2014-05-01 | DEGRADED CONDITION DISCOVERED ON REACTOR VESSEL HEAD CONTROL ROD DRIVE PENETRATION "On 5/01/2014 during the Beaver Valley Power Station Unit No. 2 (BVPS-2) refueling outage, it was determined that the results of planned ultrasonic (UT) examinations performed on one of the 66 penetrations of the reactor vessel head would not meet the applicable acceptance criteria. This penetration will require repair prior to returning the vessel head to service. The indication was not through wall and there was no evidence of leakage based on inspections performed on the top of the reactor vessel head. The examinations were being performed to meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to find potential flaws/indications well before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. Currently 52 of 66 penetrations have been examined, with 51 satisfactory. All of the penetrations will be examined during the current refueling outage. "The plant is currently shutdown and in a mode undefined [Defueled] and the reactor vessel head is not currently installed. Repairs are currently being planned and will be completed prior to startup. "This is reportable pursuant to 10CFR50.72(b)(3)(ii)(A) since the as found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-05-01
50078 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2014-05-01 10:16 | 2014-05-01 11:50 | 2014-05-01 | AUTOMATIC REACTOR TRIP "At 1016 [EDT] CCNPP [Calvert Cliffs Nuclear Power Plant] Unit 1 automatically tripped due to an RPS actuation. Cause is under investigation. All safety functions are met with normal heat removal. Electric plant is in a normal lineup. No ESFAS [Engineered Safety Feature Actuation System] actuations have occurred." Steam Generator atmospheric dump valves momentarily opened and then closed. There is no known steam generator tube leakage. All control rods fully inserted on the trip. There was no impact on Unit 2 from this event. The licensee notified the NRC Resident Inspector and provided a courtesy notification to the Calvert County Control Center. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-05-01
50077 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-05-01 08:40 | 2014-05-01 09:54 | 2014-05-01 | SERVICE WATER RADIATION MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "The Service Water Radiation Monitor will be removed from service to facilitate planned preventative maintenance. As a result, this represents a loss of emergency assessment capability under NUREG 1022 revision 3 specific to RU 1.2 and RA 1.2. The planned maintenance is expected to last 7 hours. During this time, the site Chemistry Department will perform sampling every thirty minutes per procedure. As a result of the sampling, reasonable assurance exists to monitor and detect rising radiation levels in order to protect the health and safety of the public. "The NRC Resident Inspector has been informed." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-05-01
50076 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-04-30 10:37 | 2014-04-30 17:36 | 2014-04-30 | MOMENTARY LOSS OF SECONDARY CONTAINMENT DUE TO AIRLOCK INTERLOCK MALFUNCTION "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), Event or Condition that could have prevented fulfillment of a Safety Function needed to Control the Release of Radioactive Material and 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. Unit 1 was in mode 1 and in a condition of moving irradiated fuel in the secondary containment. Unit 2 was in mode 5 and in the condition of moving irradiated fuel in the secondary containment, core alterations, and operations with the potential to drain the reactor vessel. An employee entered a secondary containment interlock [Unit 2] and identified that both doors of the interlock opened simultaneously when the door on the auxiliary building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately 5 seconds. With both doors open, TS SR 3.6.4.1.2 [Technical Specification Surveillance Requirement] was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, has remained less that -0.25 inches of water column at all times. Initial investigation determined that the interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the interlock." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-04-30
50075 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-04-30 11:40 | 2014-04-30 16:59 | 2014-04-30 | POSTULATED HOT SHORT FIRE EVENT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "Based on a review of industry operating experience, it was identified that each unit has two un-fused DC control circuits for non safety-related DC motors which are routed from the turbine building through other separate fire areas including the Control Room. The DC breakers used to protect the motor power conductors are insufficient to protect the control conductors for these circuits. It is postulated that a fire induced short in one fire area could adversely impact safe shutdown equipment by overheating the cable and causing a secondary fire in other fire areas where the cable is routed. At Unit 1, cables for the affected circuits are routed in the Turbine Building, Cable Spreading Area and Control Room. At Unit 2, cables for the affected circuits are routed in the Turbine Building, Normal Switchgear, Service Building Cable Tray Area, Cable Vault, Instrument Relay Room, Control Building West Communication Room, Control Building Cable Spreading Area and Control Room. "The postulated secondary fires or cable failures are outside the assumptions of each unit's fire protection analysis. A preliminary investigation of the issue indicates that existing fire protection safe shutdown procedures could be used to safely shut down the plant if needed. This condition is reportable as an 8-hour report in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures will be implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-04-30
50074 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-04-24 | 2014-04-30 15:26 | 2014-05-09 | AGREEMENT STATE REPORT - SECOND SCHEDULED MEDICAL DOSE NOT DELIVERED DUE TO EQUIPMENT FAILURE The following information was provided by the State of Virginia via facsimile: "On April 24, 2014, the licensee performed a two part therapy procedure using yttrium-90 microspheres (Sirtex SirSpheres). The procedure was to treat the same lobe of the liver via two different arterial pathways. There were no problems with the first injection, but the second injection failed and none of the yttrium-90 was delivered to the patient. The licensee determined that the failure occurred because of a faulty Surefire Medical catheter. The authorized user decided not to repeat the administration of the second dose but will treat the region with an alternate method. The licensee indicated that the prescribed dosage for the first injection was 11.7 millicuries and that 12.7 millicuries (27,500 rem to the target region of the loft lobe) was delivered. The prescribed dosage for the second injection was 8.3 millicuries (to give a dose of 26,200 rem to the targeted region) but no activity was delivered. This resulted in a medical event for the second injection (or fraction) as well as for the entire procedure." VA Event Report ID No.: VA-2014-003 * * * UPDATE ON 5/9/14 AT 1420 EDT FROM CHARLES COLEMAN TO DONG PARK * * * The following information was provided by the Commonwealth of Virginia via facsimile: "The licensee submitted a written report on May 9, 2014, which contained additional information from its review of the event. The licensee's review concluded that the failure of the catheter (Surefire Medical, Model SHF-38120-mT) during the second procedure was attributable a kink or fold in a basket on the catheter which resulted in a catheter occlusion. The licensee concluded that the short arterial segment used for the arterial pathway and the acute angle at the arterial origin, along with possible manipulation or patient movement, resulted in a kink or fold as the basket entered the acute angle of the artery. The catheter will be returned after decay of the radioactivity to the manufacturer for examination. The licensee submitted corrective actions for the procedure which include retraining of personnel to use extra care in ensuring the catheter is firmly set and to flush the catheter prior to administration of the microspheres to ensure there is no occlusion. The agency will review implementation of the corrective actions during a future inspection." Notified R1DO (Lilliendahl) and FSME Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-05-08
50073 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-04-30 09:10 | 2014-04-30 14:35 | 2014-04-30 | ON-SITE MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee with low blood sugar reported to the on-site dispensary this morning. The plant nurse administered first aid and then sent the employee to an off-site medical facility for further evaluation. A whole body survey of the employee in her plant clothing was performed. The maximum amount of contamination present was on the employee's right boot (7,887 dpm/100cm2). Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into her personal clothing, and was whole body frisked out of the plant. The employee was free of contamination upon release." The licensee notified the NRC Fuel Facility Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-04-30
50072 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-04-30 08:00 | 2014-04-30 08:09 | 2014-04-30 | TSC OUT OF SERVICE DUE TO MAINTENANCE "On April 30, 2014, at 0800 EDT, the Technical Support Center (TSC) will be unavailable due to pre-planned maintenance on a motor control center associated with the TSC. The TSC is expected to be restored to a functional status in approximately 13 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures, and the TSC staff will relocate to an alternate TSC location in accordance with the Hatch emergency plan and applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the planned loss of an emergency response facility (ERF). An update will be provided once the TSC has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY JOHN SELLERS TO JEFF ROTTON AT 2011 EDT ON 04/30/2014 * * * "The planned maintenance activities have been completed. The power was restored to the TSC at 1802 EDT on 4/30/14. Ventilation has been confirmed to be functional. The TSC was fully functional at 1802 EDT on 04/30/14." The licensee has notified the NRC Resident Inspector. Notified R2DO (Ayres). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-30
50071 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-29 15:30 | 2014-04-29 16:56 | 2014-04-29 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE SHUTTER FAILED TO CLOSE The following information was received via email: "On March 26, 2014, during an inspection, the inspector noted that a moisture density gauge being returned to storage was overdue for a leak test. Further investigation indicated that the shutter would not close when moved to the closed position. The gauge is a Troxler Model 3430B, Serial Number 35809 containing 9 millicuries of Cesium-137 and 45 millicuries of Am-241. The licensee promptly had the shutter cleaned and a leak test performed. The sources were not leaking and the shutter worked as designed. "The investigation into this event is ongoing pending the licensee response to inspection findings." Arizona First Notice: 14-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-05-07
50070 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-04-25 11:15 | 2014-04-29 15:48 | 2014-04-29 | AGREEMENT STATE REPORT - RECOVERED SOURCE "A DOT special permit was issued by our Agency to allow the transport of unidentified radioactive material [RAM] from one waste transfer station to the originating transfer station. Subsequently, a contractor (Atlantic Nuclear) was hired by the waste services operator to isolate the RAM, identify it, label it accordingly, and store it in a secure onsite location. The contractor was not able to definitively identify the RAM. The contractor employed portable multi-channel analyzer's in the effort (both an ICS-4000, and LMJ-702), but no positive identification of the isotope(s) could be made. The material in question is encapsulated in what appears to be a metal enclosure, and the contractor postulated that the material might be Ra-226 due to the number of gamma energy lines measured. It was also postulated that metal encapsulation may be providing interferences, and further testing is required to establish the identity of the isotope. The dose rate measurements conducted by the contractor revealed: At contact 35-40 mR/hr; at 12 inches approx. 3 mR/hr. "The contractor, Atlantic Nuclear (MA Lic. No. 56-0477), is planning to pick up the materials for storage pending disposal in accordance with their specific license. The Agency [Massachusetts Radiation Control Program] investigation remains open." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-05-07
50069 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-04-29 08:25 | 2014-04-29 12:12 | 2014-04-29 | AGREEMENT STATE REPORT - RECOVERY OPERATIONS FOR WELL LOGGING SOURCE The following information was received via E-mail: "At approximately 0825 MDT on 04/29/14, the Colorado Radiation Program received notification from Weatherford International, LLC (Colorado license 1116-01), a well logging licensee, regarding a source recovery operation taking place on a well located in Weld County, Colorado (well - 'Razor #261,' operated by Whiting Oil Company). During well logging operations (which involved a 5 Ci Am241:Be source, and a 1.5 Ci Cs-137 source) on 04/28/14, an 'unintentional pull off' occurred sometime around 2200 MDT at a depth of approximately 3500 feet below the surface. A source recovery ('fishing') company was called in to perform source recovery operations and the sources became unstuck around 0230 MDT on 04/29/14. Recovery operations are underway at this time. Fluids are being monitored to verify the sources remain intact during the recovery operations. At this time, the sources are estimated at being 1000 feet below surface, and are continuing to move toward the surface. "The Radiation Program remains in contact with the licensee and continues to monitor the situation." * * * UPDATE FROM JAMES JARVIS TO DONALD NORWOOD AT 1312 EDT ON 4/29/2014 * * * "At 1030 MDT on 4/29/14, the licensee reported that the sources have been recovered, are intact, and have been returned to their storage containers at the temporary jobsite. Surveys of the fluids, sources, work area, and drilling platform areas do not indicate the presence of contamination. The licensee reported that visual inspection of the tools in which the sources were used indicated no significant damage. The sources used on the job will be returned to the Weatherford location in Casper Wyoming where they will be formally leak tested. In addition to the Colorado license, Weatherford also holds an NRC license (NRC 42-26891-01). According to the Colorado RSO, the well logging operation was being conducted under the Colorado license, and involved crew members from both the Colorado and Wyoming locations. The sources were brought from the Casper, Wyoming office." Notified R4DO (Haire) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-05-07
50068 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-28 22:21 | 2014-04-28 22:58 | 2014-04-28 | PROTECTIVE ACTIONS TAKEN DUE TO WEATHER CONDITIONS Certain site security measures taken due to severe weather conditions. Compensatory measures were taken. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-04-28
50067 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-04-28 | 2014-04-28 15:28 | 2014-04-28 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "On April 28, 2014, at approximately 0845 AM [PDT], [the licensee pending ARSO], an authorized user of radioactive gauges of Twining Laboratories of Southern California, Inc., RML [California Radioactive Materials License] #7780-37 located in San Bernardino, CA, contacted RHB Brea [Radiation Health Branch located in Brea, CA] concerning the moisture/density gauge, CPN model, MC-1, serial number MD10606201 (Cs-137, 0.370 GBq, Am-241, 1.85 GBq) that had been stolen from a temporary storage/construction site in San Bernardino County on the I-15 North freeway at the top of the Cajon Pass at the Oak Hills Road exit. "[The licensee pending ARSO] arrived at the temporary storage area to begin work on Monday morning and noticed that the construction facility had been broken into and that other tools and equipment had been taken as well as the radioactive gauge, which was charging while locked in a gang box which was removed in it's entirety once the construction fence and locked cargo container were breached. [The licensee pending ARSO] has contacted the San Bernardino Sheriff's Department which has filled out a theft report which will be copied and sent to RHB Brea as part of this report. "The RSO of Twining Laboratories of Southern California, Inc., is currently on vacation and [the licensee pending ARSO] is receiving assistance and recommendations from another RSO of Twining Laboratories of Southern California, Inc., RML #6872-19 located in Long Beach, CA. [The licensee pending ARSO] is contacting pawn shops and landfills in the area to determine if he can locate the stolen radioactive gauge in advance of utilizing local papers to attempt to retrieve the stolen gauge. The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame." CA 5010 Number: 042814 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-05-06
50066 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-28 | 2014-04-28 18:52 | 2014-05-02 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "On April 28, the Agency [Arizona Radiation Regulatory Agency] was contacted by the licensee. The licensee indicated that an employee had a moisture density gauge stolen at a Motel in Goodyear, AZ. The gauge is a Humboldt Model 5001, Serial Number 1140 containing 10 millicuries of Cesium-137 and 40 millicuries of Am-241. The device was stolen from a pickup truck at the Towne Place Suites, 13971 West Celebrate Life Way, Goodyear, AZ, 85338. The device was in a steel box bolted to the truck bed. The lock or bolts were cut. A secondary lock was also cut and the device was removed. "The investigation into this event is ongoing. The AZ Governor's Office, US NRC, FBI, and the states of CA, CO, NV, and NM are being notified of this event. Mexico is also being notified." AZ First Notice: 14-009 * * * UPDATE PROVIDED BY AUBREY GODWIN TO JEFF ROTTON AT 1736 EDT ON 05/02/2014 * * * The following information was provided via email from the State of Arizona: "On May 1, 2014 the AZ Department of Public Safety [AZDPS] received a report that someone had found some HAZMAT including radioactive material. The semi-homeless individual released the gauge he claimed to have found in a garbage dumpster to AZDPS. AZDPS released the gauge to the Agency on May 2, 2014. After leak testing and testing for contamination the licensee was contacted to arrange return of the gauge. "The State of Arizona investigation into this event is closed." Notified R4DO (Haire), FSME Events Resource, Country of Mexico, and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-05-06
50065 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-04-04 14:30 | 2014-04-28 16:15 | 2014-04-28 | AGREEMENT STATE REPORT - SCRAP FACILITY GATE ALARM "On 04/04/14 at approximately 1430 MDT, the Colorado Radiation Program received phone notification of a scrap load that had been rejected at a recycling facility in Englewood, CO due to a gate radiation alarm. Scrap facility personnel performed surveys around the container using hand held survey instruments. Surveys indicated readings up to a maximum of 120 microrem/hour (Ludlum Model 3). Recycling facility staff indicated that the load would not be returned to the shipper until the following week and that the load/roll-off container was segregated onsite. The Colorado Radiation Program issued a DOT special permit and the scrap metal was returned to the originator, Baker-Hughes (Colorado License No. 678-01; 285 County Road 27, Brighton, CO 80603) on or about 04/11/14. "Preliminary communications with Baker-Hughes personnel indicated that it performed well fracking work in mid-March 2014 and worked with another Colorado licensee - well logging tracer company, Protechnics (Colorado License No. 545-01; 703 Greenway Drive, Fruita, CO 81521). Baker-Hughes is not authorized for tracer material use. Baker-Hughes requested that Protechnics perform surveys on the rejected scrap load to determine whether the contamination was naturally occurring radioactive material, or tracer material. Protechnics performed radiological surveys on or about 04/15/14 at the Baker-Hughes facility and determined that a small amount of tracer material remained in one component (a manifold removed from the pumping truck) of the scrap load. Protechnics identified the tracer material as Iridium-192. The tracer material combined with approximately 10 lbs. of fracking sand was removed/decontaminated from the scrap component and was packaged by Protechnics and returned to their facility in Fruita, CO for decay in storage. Protechnics estimated the activity of Ir-192 tracer material in the component to be approximately 0.015 mCi. After receiving a preliminary written report from Protechnics on 04/16/14, Colorado Radiation Program staff performed phone interviews of Baker-Hughes personnel and Protechnics personnel. "Colorado Radiation Program staff performed on-site verification surveys of the scrap load (post-decontamination) on 04/21/14. Surveys indicated that no radiation levels above instrument background were detected on the remaining decontaminated scrap. "The Colorado Radiation Program is continuing to investigate the incident to determine further actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-05-06
50064 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-04-24 | 2014-04-28 10:20 | 2014-09-09 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT The following information was received via E-mail: "On the evening of April 24, 2014 Elekta, (Georgia license - GA 1153-2) working under a Nebraska reciprocity general license, was installing the initial source (9.98 curies of lr-192) into the new Flexitron unit at Saint Francis Medical Center (Nebraska Radioactive Material License # 08-09-01) in Grand Island, Nebraska. During the upload procedure, the source did not completely retract into the safe and became hung-up on the in-drive. The device gave an error stating the source was detached from the cable. Following the manufacturer's recommended emergency procedures, the engineer entered the room to investigate the issue and determined the source cable needed to be cut to remove it from the stuck source drive. The Field Service Engineer (FSE) then quickly cut the exposed source cable and, using pliers, manually inserted the source into the transport container. However, due to the fact that the source cable was short, he could not get it completely into the center of the shielded transport container. The exposure rate at one meter from the transport container was 200 mR/hour. The facility physicist and FSE insured the door to the treatment room was sealed and marked so no one could enter overnight. "The following morning, April 25, 2014, work began to construct temporary shielding made of lead bricks on a trolley in order to transport the container to the facility hot lab. Additionally, arrangements were made with Elekta's source manufacturer to acquire a type A container of the proper size to house and ship the source transport container to their facility, thus removing it from St. Francis premises. "Elekta's Radiation Safety Officer failed to notify the State of Nebraska Radioactive Material's Program in a timely manner. The incident occurred after business hours and Friday April 25, 2014 was a State holiday (Arbor Day). No call was made to the emergency call number for the State and the information was only obtained by the Nebraska Program Manager by a series of e-mails and a voicemail after 0800 CDT on Monday, April 28, 2014." Item Number: NE14003 * * * UPDATE FROM TRUDY HILL TO CHARLES TEAL AT 1659 EDT ON 6/16/14 * * * The following information was received via email: "On April 29, 2014, a special Type A container from Alpha Omega Services (AOS) arrived on site and the source was packaged in it for shipment. On May 1, 2014, source was shipped to AOS. On May 7, 2014, the source was received at AOS facility for safe decay storage before shipping back to Mallinckrodt. "On May 21 & 22, 2014, the HDR unit involved in the incident was shipped back to Nucleotron B. V. in the Netherlands for investigations. No results as of June 16, 2014." Notified R4DO (Hay), R1DO (Welling) and FSME Event Resource via email. * * * UPDATE FROM TRUDY HILL (VIA EMAIL) TO HOWIE CROUCH AT 1123 EDT ON 09/09/14 * * * The following information was obtained via email: "As of July 25, 2014 there is still no determination as to the cause of the source hang-up. The HDR unit is still being analyzed at the factory in the Netherlands. "As of August 27, 2014, Elekta's R & D Department has not uncovered the root cause of the incident. Extensive analysis of the drive and the log files have not been able to reproduce the specific error. R & D are in the final stages of the root cause investigation and should be completed soon. "On September 8, 2014, Elekta submitted their close out report on the incident. After exhaustive & extensive analysis of the drive and the log files, the R & D Department has not been able to reproduce the specific error and could not uncover the root cause of the incident." Nebraska considers this report as closed. Notified R1DO (Jackson), R4DO (Azua) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-05-06
50063 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2014-04-27 20:12 | 2014-04-27 23:57 | 2014-04-28 | AUTOMATIC REACTOR TRIP DUE TO AN AUXILIARY TRIP ON CORE PROTECTION CALCULATOR "At approximately 1932 [CDT] on 4/27/2014, the System Operations Center (SOC - Dispatcher) informed Unit 2 of a system wide grid emergency and ordered both Unit 1 and Unit 2 to come off line as soon as possible. "At approximately 2012 [CDT], Unit 2 automatically tripped from 51% power due to an Auxiliary Trip on CPCs (Core Protection Calculator) due to Axial Shape Index (ASI) trip. All Control Element Assemblies inserted into the core. Both vital and non-vital 4160V and 6900V buses remain powered from Startup #3 Transformer. All Systems responded as designed. "At 1932 [CDT], Unit 1 commenced a Rapid Plant Shutdown at a rate 5-7% per min with the intention to take the turbine offline and leave the reactor critical at 10-12% power on the Turbine Bypass Valves. When the Unit 2 reactor tripped, Unit 1 stopped the power reduction and stabilized the plant at approximately 19% Reactor Power and 125 Generated Megawatts. With SOC concurrence, Unit 1 stabilized power and was told to limit site output to <200 MWe. At 1932 CDT, Unit 1 began a down power from 100% power and Unit 2 began a down power from 95% power. On Unit 2, decay heat is being removed by the main condenser using the turbine bypass valves. Unit 2 is stable in Mode 3 with stable offsite power. The system wide grid emergency is believed to be caused by tornados in the region. The licensee has notified the NRC Resident Inspector and the State. | 0 | 0 | 0 | 0 | 51 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-04-28
50062 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-27 16:00 | 2014-04-27 17:44 | 2014-04-28 | TECHNICAL SUPPORT CENTER OUT-OF-SERVICE "The Technical Support Center (TSC) cooling system is not operating properly. The temperature of the TSC is currently 80 degrees F. The TSC is still capable of being pressurized." If needed, facilities in the Admin building are available for use as the back-up TSC. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1133 EDT ON 04/28/14 FROM SHAUGHN RICE TO S. SANDIN * * * "TSC Ventilation (VH) System is out-of-service. TSC is not capable of being pressurized, filtered or cooled. This is planned maintenance for work to repair leak reported on 04/27/14." The licensee informed the NRC Resident Inspector. Notified R2DO (King). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-27
50061 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-04-26 23:22 | 2014-04-27 01:45 | 2014-05-14 | MINIMUM PATHWAY LIMIT OF MSIV COMBINED LEAKAGE EXCEEDED DURING SURVEILLANCE TESTING "On 4/26/14 at 2322 EDT it was determined that the combined leakage for Main Steam Isolation Valves (including MSIV's, Main Steam Line Drains, HPCI Steam Supply and RCIC Steam Supply) per SR [Surveillance Requirement] 3.6.1.3.12 exceeded the minimum pathway limit of 300 scfh [standard cubic feet per hour]. The MSIV Combined leakrate of 309 scfh exceeded the limit of 300 scfh with the Local Leak Rate Test failure of the HPCI Steam Supply Outboard Isolation Valve. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii), as it was discovered that the required leakage limits were exceeded." The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1415 EDT ON 05/14/14 FROM JAY BARNES TO S. SANDIN * * * The licensee is retracting this event based on the following: "Subsequent engineering review identified an administrative error with procedures used to calculate MSIV leakage. Recalculation using revised procedures resulted in a MSIV Combined leakrate of 129 scfh, which is below the associated minimum pathway limit of 300 scfh specified in SR 3.6.1.3.12. "Therefore, this condition is not reportable and EN 50061 is being retracted." The licensee informed the NRC Resident Inspector. Notified R1DO (Jackson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-04-27
50060 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-04-25 22:28 | 2014-04-26 01:24 | 2014-04-26 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "System Affected: Millstone Station Stack Radiation Monitor, RM-8169 "Actuations and Their Signals: None "Causes: Preplanned Maintenance "Effect of Event on Plant: None "Actions Taken or Planned: Completed testing and restored operability" (on 4/26/14 at 0037 EDT) "Additional Information: None" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-26
50059 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2014-04-25 11:13 | 2014-04-25 16:29 | 2014-04-25 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry Operating Experience identified that there were unprotected DC control circuits for non safety-related DC motors which are routed from the turbine building to other separate fire areas. Fuses used to protect the motor power conductors appear to be inadequate to protect the control conductors. The concern is that under fire safe shutdown conditions, it is postulated that a fire in one area can cause short circuits potentially resulting in secondary fires or cable failures in other fire areas where the cables are routed. The secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-04-25
50058 | 0 | WATERFORD | 3 |  |  | [3] CE | 2014-04-24 10:22 | 2014-04-24 20:32 | 2014-04-24 | NON-LICENSED CONTRACT SUPERVISOR CONFIRMED POSITIVE ON FOLLOW-UP FITNESS FOR DUTY TEST A non-licensed contract supervisor was confirmed positive for alcohol on a follow-up fitness for duty test. The supervisor's access to the facility has been terminated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2014-04-24
50057 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-02-05 | 2014-04-24 16:38 | 2014-04-24 | AGREEMENT STATE REPORT - LEAKING GENERALLY LICENSED SOURCES The following was received from the state of Colorado via email: "On or after February 05, 2014, while working on a license renewal action, the Colorado Radiation Program was informed by the licensee that it had three (3) generally licensed electron capture detectors (ECDs), containing ~15-18 mCi of Ni-63 (each), that [leak tests] indicated contamination in excess of regulatory limits. The devices were determined to be manufactured by Hewlett-Packard and Agilent Technologies (model number verification is pending). "The licensee reported that upon discovery, the devices were contained to minimize potential contamination spread. The area where gauges were used/handled was surveyed and determined to be free of contamination. The licensee indicated that the manufacturer was notified and the devices have been returned to the manufacturer for disposal. "Further investigation by the Colorado Radiation Program is pending." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-05-02
50056 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-04-23 15:30 | 2014-04-24 14:08 | 2014-04-24 | FITNESS FOR DUTY REPORT - FALSE NEGATIVE ERROR OCCURRED ON QUALITY ASSURANCE TEST "Contrary to the requirements in 10 CFR 26.137(b), a Department of Health and Human Services (DHHS) certified laboratory returned results for a blind specimen that was inconsistent with what was expected. "On 04/22/2014, blind specimens from the same lot number were sent to the two contracted DHHS laboratories. On 04/23/2014, one of the labs reported unexpected results while the other laboratory reported the expected results. At approximately 1530 [CDT] on 04/23/2014, the lab report was reviewed by Fitness For Duty Management at Callaway Plant and the inaccurate result was identified. On 04/24/2014, the Medical Review Officer (MRO) contacted Clinical Reference Laboratory (CRL) to discuss the testing discrepancy and directed the lab to retest the specimen. The MRO requested that CRL initiate an investigation to determine the reason for the inaccurate result and provide a report of the results of that investigation within 20 days. "10 CFR 26.719(c)(3), 'Reporting Requirements,' requires that 'if a false negative error occurs on a quality assurance check of validity screening tests, as required in  26.137(b), the licensee or other entity shall notify the NRC within 24 hours after discovery of the error.'" The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2014-04-24
50055 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-04-24 02:30 | 2014-04-24 07:50 | 2014-04-24 | LOSS OF SECONDARY CONTAINMENT DURING ROUTINE SWAP OF A POWER SUPPLIES "On April 24, 2014 at 0230 [EDT], Secondary Containment Zone 3 (Unit 1&2 Reactor Building) differential pressure lowered to 0.10 [negative inches] WG [Water Gauge] when restoring Unit 1 Zone 3 HVAC during a routine swap of RPS power supplies, due to a trip of the Unit 1 Zone 3 Supply fan. Zone 3 differential pressure was restored to > 0.25 [negative inches] WG at 0243 hours. Zone I (Unit 1 Reactor Building) ventilation is isolated with secondary containment relaxed for refuel outage on Unit 1. Zone II (Unit 2 Reactor Building) ventilation remained in service and stable. "Zone 3 differential pressure recovered to SR 3.6.4.1.1 requirements of 0.25 WG [negative inches] at 0243 hours and was verified to be stable. LCO 3.6.4.1 was entered at 0230 hours and exited at 0313 hours. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 [negative inches] WG for all three Reactor Building Ventilation Zones when secondary containment is required. "This event is being reported under 10CFR50.72(b)(3)(v)(C) and per the guidance of NUREG-1022,Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-24
50054 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2014-04-23 13:02 | 2014-04-23 17:18 | 2014-04-23 | SPECIFIED SYSTEM ACTUATION DURING ROD TESTING "This is a non-emergency eight hour notification in accordance with 10 CFR 50.72(b)(3)(iv)(A), for a valid manual actuation of the Reactor Protection System. "While performing rod control system testing with the reactor subcritical in MODE 3, a rod control demand position indicator failed when one bank of rods were withdrawn. The group step counter demand exceeded the Technical Specification allowable value. On 4/23/2014 at approximately 1302 [EDT], the Unit 3 reactor trip breakers were manually opened to comply with Technical Specification 3.1.3.3 action. The rods being tested were fully inserted when the reactor trip breakers were opened. All other rods remained fully inserted. Unit 3 remains in MODE 3." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-04-23
50053 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-22 14:00 | 2014-04-23 16:46 | 2014-04-23 | AGREEMENT STATE REPORT - LOST AND FOUND MOISTURE DENSITY GAUGE The following was received from the State of Arizona via email: "The Agency [State of Arizona] was informed by the Licensee at approximately 2:45 PM [MDT], April 22, 2014 that at approximately 2:00 PM a worker had lost a Campbell-Pacific Model MC-1, SN MD41007631 moisture density gauge off a pickup truck. The worker forgot to close the tailgate. The gauge contained 10 millicuries of Cesium 137 and 50 millicuries of Americium 241. At approximately 3:15 PM, the Mesa Fire Department reported they had possession of a gauge found on a freeway near the work site. "A review of the situation confirmed that this was the lost source by the Licensee. The Agency [State of Arizona] has released the gauge to the Licensee for leak testing. "The NRC, FBI and Governor's Offices are being notified of this event. "The Agency continues to investigate this event." First Notice: 14-008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-05-01
50052 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-04-23 10:00 | 2014-04-23 12:51 | 2014-04-23 | OFFSITE NOTIFICATION DUE TO DECEASED MIGRATORY BIRD FOUND ON PLANT PROPERTY "Monticello Nuclear Generating Plant personnel discovered the remains of a deceased migratory bird on plant property. The cause of death was not immediately apparent and no work was ongoing in the vicinity at the time the bird was found. Notifications to the United States Fish and Wildlife Service will be made for this discovery. This event is being reported per 10CFR50.72(b)(2)(xi)." The licensee has informed the NRC Resident Inspector. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-23
50051 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-04-23 10:00 | 2014-04-23 11:47 | 2014-04-23 | 2R-22 SHIELD BUILDING VENT GAS RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "At 1000 CDT on April 23, 2014, 2R-22, Shield Building Vent Gas Radiation Monitor was removed from service for planned maintenance. This monitor has no compensatory measures that will allow timely classification of two Emergency Action Levels (EALs); NUE (Notification of Unusual Event) and Alert classifications when out of service. It is also used for offsite dose projection calculations. This results in a loss of emergency assessment capability while 2R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The Unit 2 Shield Building Ventilation Stack is also monitored by the high range monitor, 2R-50, which is used for the same purpose in Site Area Emergency classifications. 2R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidence by normal reading on 2R-22 prior to its removal from service. Maintenance is expected to last approximately 4 hours and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of the radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-23
50050 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2014-04-22 | 2014-04-23 09:46 | 2014-04-23 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE HANG-UP The following was received from the State of Kansas via fax: "Today [on] 4/22/14, [the] x-ray radiography crew had a source hang-up, at the NCRA plant in McPherson, Kansas, at approximately 0930 CDT. [The] radiography crew performed their operational and emergency procedures very well. A 35 curie Ir-192 source hung up in the source guide tube. [The crew] made the necessary adjustments to their boundaries, kept watch over them, allowed no one to enter, notified [the crew supervisor] and the Kansas RSO. They re-adjusted the crankouts and pulled them to straighten out the cranks and guide tube, and were able to retract the source into the device with one attempt, and were successful. There was no disconnect or anyone exposed to radiation levels above regulatory limits. "Notification of the incident was given to the plant safety coordinators at the time of the incident, and they remained at distance to avoid exposure, the full time of the incident lasted approximately 10-15 minutes from the initial determination of a stuck source to retraction of the source into the device." Three monitored IRISNDT staff were onsite and they watched over the boundaries while the retraction was completed. After the incident, all IRISNDT staff read their Instadose film badges and got readings from their personal dosimeters ranging from 1.2 to 3.8 mRem. Kansas incident # KS140007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2014-05-01
50049 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-04-22 14:00 | 2014-04-22 15:22 | 2014-04-22 | OFFSITE NOTIFICATION DUE TO DECEASED MIGRATORY BIRD FOUND ON PLANT PROPERTY "Monticello Nuclear Generating Plant personnel discovered the remains of a deceased migratory bird on plant property. The cause of death was not immediately apparent, no work was ongoing in the vicinity at the time the bird was found. Notifications to the Minnesota Department of Natural Resources and the Division of Fish and Wildlife will be made for this discovery. This event is being reported per 10CFR50.72(b)(2)(xi)." The NRC Resident Inspector will be informed. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-22
50048 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2013-05-13 | 2014-04-22 10:25 | 2014-04-22 | AGREEMENT STATE REPORT INVOLVING A TRITIUM EXIT SIGN DESTROYED IN A FIRE The following information was received from the State of Utah via fax. "The Utah Division of Radiation Control [DRC] was notified at 1:38 p.m. MST on Wednesday, August 13, 2013 of an incident where a church chapel was destroyed by fire. The fire had occurred three months earlier on May 13, 2013. No one noticed the radiation symbol mixed with the trash until a representative of the church, watching the residue being shoveled from the chapel. He noted the radiation symbol stuck to the remains of the melted sign. "The DRC contacted the church representative and was informed of the details of the fire. "The DRC Radioactive Materials Section Manager was notified of the incident. "Notification to the NRC was completed on January 24, 2014. "The tritium sign was melted by the high heat of the fire. There were no remaining identifiable components. The debris from the sign was mixed with other burnt materials and the trash had been shoveled into waste containers. The church representative said there was nothing recoverable in the fire's residue. "The EXIT sign (Model B-100) was manufactured by SRB Technologies in 2005. The sign was designed to operate for 20 years using 18.9 curies of tritium. The estimated activity of tritium remaining inside the sign when it was destroyed was approximately 12 Curies." Utah Event Report ID No.: UT140001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2014-04-30
50047 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-04-20 14:42 | 2014-04-20 19:58 | 2014-04-20 | EMERGENCY CORE COOLING SYSTEM PIPING LEAK WHILE SHUTDOWN "A leak was discovered in the area of EPV0109, COMBINED SI/RHR [Safety Injection/Residual Heat Removal] TO ACCUMULATOR D OUTLET LINE VENT. The leak rate was estimated at 2.5 gallons per hour. The plant is in Mode 5, RCS [Reactor Coolant System] depressurized. "This leak is considered a material problem that causes abnormal degradation of or stress upon the reactor coolant system pressure boundary, reportable in accordance with 10CFR 50.72(b)(3)(ii)(A). "Efforts are underway to characterize the leak and plan for repairs. The leak has been secured after realigning RHR cooling from the B to the A train. "The Resident Inspector has been notified." The cause of the leak is being investigated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-04-20
50046 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2014-04-20 02:15 | 2014-04-20 08:08 | 2014-04-20 | LOSS OF SECONDARY CONTAINMENT DUE TO OPENING IN REACTOR BUILDING ROOF DRAIN PIPING "Due to openings found in degraded roof drain piping, Brunswick Nuclear Power Plant Unit 2 secondary containment was declared inoperable at 0215 [EDT] on 04/20/2014. During operator rounds the Reactor Building Aux Operator noted rainwater coming out of a roof drain line into the Reactor building. Upon further investigation a rusted area 2 foot by 2 inches was found on the pipe. Several through wall holes were found in this rusted area and the remainder of the rusted area was allowing water to weep through. The openings resulting from the through wall holes and rusted area exceeded the allowable openings in secondary containment, and this would have challenged secondary containment from performing its safety function. This event did not result in any adverse impact to the health and safety of the public. This is a non-emergency notification. "INITIAL SAFETY SIGNIFICANCE EVALUATION: At the time that is was discovered that Unit 2 Secondary Containment was inoperable. Unit 2 was at 100% steady state conditions. Reactor building ventilation was in service in a normal alignment. The Unit 2 reactor building differential pressure was normal during the entire time secondary containment was inoperable. At no time was there a release of radioactive material from Unit 2 secondary containment. "CORRECTIVE ACTIONS: The Unit 2 reactor building roof drain line has had a temporary repair applied. This repair has been evaluated by the Engineering department with site procedures and meets the requirements to maintain Secondary Containment operable. Unit 2 Secondary Containment operability was restored at 04/20/2014 0600 [EDT]." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-20
50045 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-04-19 11:00 | 2014-04-19 11:53 | 2014-04-19 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE ON MAIN STEAM LINE RADIATION MONITORS Main steam line radiation monitors RM-4299A, RM4299B, RM4299C will be removed from service for a period of approximately 4 days during planned maintenance on the power supplies. This constitutes a loss of assessment capability. The radiation monitors will be returned to service following maintenance. The licensee has notified the NRC Resident Inspector, the State of Connecticut, and the local government. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-19
50044 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-04-18 20:39 | 2014-04-18 22:55 | 2014-04-26 | DEGRADED CONDITION DUE TO REACTOR HEAD VESSEL PENETRATION INDICATIONS "On April 18, 2014, V.C. Summer Nuclear Station (VCSNS) Unit 1 identified 3 reactor vessel head penetrations (9, 43 and 51) that did not meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1. The station is in a refueling outage (RF21) and the plant is currently shutdown and defueled. The reactor vessel head contains a total of 66 penetrations and the volumetric inspection efforts are complete. "The indications are not through wall as indicated by volumetric and bare metal visual inspections. The penetrations will be repaired to meet the requirements of 10 CFR 50.55a prior to returning the vessel head to service. The inspection results are reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified. The licensee will notify the State of South Carolina and local counties." * * * UPDATE FROM BETH DALICK TO JOHN SHOEMAKER AT 1302 EDT ON 4/26/14 * * * "On April 26, 2014, V. C. Summer Station (VCSNS) Unit 1 finalized the inspections of the reactor vessel head penetrations. Confirmatory dye penetrant inspections determined that penetrations 15 and 22 also did not meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1. The station is in a refueling outage (RF21) and the plant is currently shutdown and defueled. "The indications are not through wall as indicated by volumetric and bare metal visual inspections. The penetrations will be repaired to meet the requirements of 10CFR50.55a prior to returning the vessel head to service. "The inspection results are reportable pursuant to 10CFR50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified. "The licensee will notify the State of South Carolina and local counties." Notified R2DO (McCoy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-04-18
50043 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-18 12:52 | 2014-04-18 14:35 | 2014-04-18 | CABLE ROUTING UNANALYZED FOR FIRE SAFE SHUTDOWN BARRIER "While implementing a multiple spurious operations (MSO's) modification during a refueling outage, it was identified that a fire safe shutdown cable routing location may have been in question. On 04/18/2014 at 1252 CDT, it was determined that this cable was routed through a cable tray that was not designed to have a fire safe shutdown barrier. This created an unanalyzed condition that significantly degrades plant safety, consistent with NUREG 1022, Rev. 3 guidance. "This cable is associated with a Motor Operated Valve (MOV) used to isolate the containment sump from the Residual Heat Removal (RHR) pump suction during normal system operations. "Compensatory measures in this area were already in effect for the resolution of MSO's scenarios. The compensatory measures assure the Systems, Structures, and Components (SSC's) associated with this cable remain operable." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-04-18
50042 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-04-16 | 2014-04-17 13:53 | 2014-04-17 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA FAILURE OF SOURCE TO RETRACT TO SAFE POSITION The following was received from the State of Illinois via email: "On Wednesday at midday, the Regional Radiation Safety Officer (RSO) for the licensee's South Roxana, IL area was called by their two man crew working at the WRB Refinery in Roxana, IL. The crew reported that following a sixth 'shot' on an elevated tank from an overhead platform, the source to the radiography camera would not retract into the safe position. The source had previously been 'run out' to a distance of just over 7 feet into a collimator, and although the crank and assembly rotated freely without notable restriction through two ninety degree turns, the source would not enter the camera. The crew reported that the guide tube had not been affected during the previous shots and noted that the equipment had regularly passed the routine maintenance inspection prior to that day. "The Regional RSO assembled his emergency response equipment kit and arrived at the site approximately 30 minutes later. The crew had maintained a perimeter and advised responsible site safety personnel of the matter with instructions to ensure the affected area was to remain off limits until the situation was resolved. The Regional RSO inspected the guide tube and set up and like the crew was unable to retract the source. Calls were then placed to the company's regional management and to the Illinois Emergency Management Agency to advise of the situation. The set up was disassembled and the collimated end point placed into a shielded configuration using bags of lead shot so that the full length of the guide tube could be more closely inspected. Minor dents and obstructions of the guide tube were noted and although when corrected by the Regional RSO, would still not allow the source to be safely returned. With the help of the radiography crew, the camera and guide tube assembly was subsequently moved to a more accessible lower platform by the Regional RSO to allow for additional inspection and to create a more direct path. The source however would still not retract into the camera. Dose rates with the source in the collimator were measured as 390 millirem at 8 feet and 695 millirem at 6 feet which was the closest distance the Regional RSO remained in. Additional support from the regional office was requested to thoroughly patrol the boundaries of the area as it appeared additional time was going to be required and the camera would need to be lowered further to gain better access for potential repairs. "While additional equipment was being collected from the regional office, the manufacturer was advised of the situation and consulted. The manufacturer suggested the issue may lie with the drive cables from the reserve crank end and they would likely have to be disconnected from the source cable. When the additional equipment arrived, the crank housing was disconnected from the camera following the manufacturer's suggestion and from a distance, the cable was manually retracted. The source subsequently was returned to the shielded and locked position with no further difficulties. The total time for recovery was approximately two and a half hours. "Later, close inspection of the drive crank assembly showed that the reserve section of the crank had been subjected to heat or burned such that the exterior plastic covering had melted along approximately 3 inches of its length. Upon testing, this damaged section prohibited movement of the cable past this point. It's surmised that the crank assembly may have come to rest against an uninsulated section of the piping while taking shots that morning at the refinery that led to the burning/melting of the protective covering over the braided cable which led to the inability to retract the source. "A check of the Regional RSO direct reading dosimeter showed less than 80 millirem as a result of the recovery operation. Members of the radiography crew received a total dose for the day of less than 100 millirem. The camera was last inspected by the manufacturer on March 14, 2014 and the manufacturer's associated equipment on February 4, 2014 by the Regional RSO. The associated equipment is being returned to the manufacturer for evaluation and repair/replacement." Illinois event # IL14007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2014-04-25
50041 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-15 | 2014-04-17 08:53 | 2014-04-17 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECT The following information was received from the State of Texas via email: "On April 16, 2014, the Agency [Texas Department of State Health Services] received notice that on April 15, 2014, a radiography source disconnect had occurred at a temporary field site in or near Martinsville, Texas at approximately 4:45 PM. The camera was a QSA 880D with a 22 curie iridium-192 source. The source was retrieved. No exposure to the public resulted from this event. The cause of failure is unknown at this time, but a crank malfunction is suspected. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident #: I-9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-25
50040 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-04-17 03:35 | 2014-04-17 06:00 | 2014-04-17 | LOSS OF SECONDARY CONTAINMENT DURING PREPARATION FOR LOCA/LOOP TESTING "On April 17, 2014 at 0335 EDT, Secondary Containment Zone 3 (Unit 1&2 Reactor Building) differential pressure went to 0.15 inches WG [negative] following securing Unit 1 Zone 3 HVAC in preparation for a LOCA/LOOP test. Zone 3 HVAC was restored at 0420 EDT. Zone I (Unit 1 Reactor Building) ventilation is isolated with secondary containment relaxed for refuel outage on Unit 1. Zone II (Unit 2 Reactor Building) ventilation remained in service and stable. "Zone 3 differential pressure recovered to SR 3.6.4.1.1 requirements of 0.25 inches WG [negative] at 0420 EDT and was verified to be stable. LCO 3.6.4.1 was entered at 0335 EDT and exited at 0420 EDT. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge [WG] for all three Reactor Building Ventilation Zones. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-17
50039 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-16 09:08 | 2014-04-16 10:48 | 2014-04-16 | OFFSITE NOTIFICATION DUE TO MINOR HYDRAULIC OIL SPILL IN THE DELAWARE RIVER "At 0908 EDT on April 16th, 2014, approximately one pint of hydraulic fluid was spilled into the Delaware River in front of the Unit One Circulating Water System (CWS) Intake trash racks at the Salem Generating Station. The spill of hydraulic fluid was caused by a leak from the crane used to rake debris from the Unit One trash racks. The crane was stopped and the leak terminated at the time of discovery. The oil was cleaned up by onsite personnel at 0930 EDT. "Nuclear Environmental Affairs Department determined a 4 hr report to the NRC under RAL 11.8.2.a. was warranted due to the 15 minute notification to the New Jersey Department of Environmental Protection at 0922 EDT. Additionally, a report of the spill was made to the National Response Center at 1034 EDT." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-16
50038 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-04-15 15:15 | 2014-04-15 19:16 | 2014-04-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILURE OF CONTROL ROOM AIR CONDITIONING "At 1505 CDT the 'A' control room air conditioner (VA-46A) trouble alarm annunciated in the control room. The unit was confirmed to be not functioning properly and was declared inoperable at time 1515 [CDT]. The 'B' control room air conditioner (VA-46B) was previously declared inoperable due to maintenance. With both control room air conditioners inoperable the plant entered technical specification 2.0.1, a 6 hour shutdown action statement. Repairs to the 'B' had been previously planned and are in progress to allow the unit to be returned to service as soon as possible. Troubleshooting and subsequent repairs to the 'A' unit are in progress. At 1812 [CDT], the station commenced a shutdown to comply with the required action statement." The NRC Resident Inspector has been informed. * * * UPDATE FROM ORTIZ TO KLCO ON 4/15/14 AT 2237 EDT * * * "At time 2050 [CDT], VA-46A was declared operable based on installation of an emergency temporary modification. TS 2.0.1 has been exited. Shutdown has been secured and FCS is stable at a nominal 33% power." The licensee notified the NRC Resident Inspector. Notified the R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-04-15
50037 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-04-12 | 2014-04-15 10:07 | 2014-04-15 | NEW JERSEY AGREEMENT STATE REPORT - RADIOACTIVE GAUGE SHUTTERS STUCK The following information was obtained from the State of New Jersey via email: "Event date and time: April 12, 2014 (time was not included in initial report) "Event location: aboard dredge vessel M/V Glenn Edwards working in NJ waters near Long Branch, NJ "Event type: Fixed gauges with stuck shutter "Notifications: RSO notified NJDEP [New Jersey Department of Environmental Protection] staff in person on 4/14/2014 at approximately 0900 [EDT] during an inspection. "Event Description: The M/V Glenn Edwards has three fixed gauges used to measure slurry density of dredged materials; one on the starboard arm, one on the port arm, and one on the bow of the dredge. The licensee reported that a survey and inspection of the gauges on 4/12/2014 revealed that two of the three gauges have shutter handles which are not functioning to move the internal shutter cylinder. The bow device (Berthold LB 7444-D-CR containing 100 mCi Co-60 at installation) appears to be stuck in the closed position. The starboard device (Berthold LB 7444-CR containing 500 mCi Co-60 at installation) appears to be stuck in the open position. The beam is oriented out to sea, away from any occupied space. The licensee reports that there is no exposure hazard to licensee personnel, crew or other members of the public. The licensee is contacting the device manufacturer to arrange for repair/disposal and has committed that a service provider would be contracted to perform the work. "The event is reportable to NJDEP under N.J.A.C. [New Jersey Administrative Code] 7:28-51.1 (adoption of 10 CFR 30.50(b)(2)). "NJDEP will continue to monitor the situation and provide updates as necessary. A notification was also made to the Florida Bureau of Radiation Control." The operator of the dredge vessel is a licensee of Florida (Florida License #4019-1) working under reciprocity in the State of New Jersey. New Jersey Incident Number: 512693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-04-23
50036 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-14 06:00 | 2014-04-14 18:21 | 2014-05-05 | AGREEMENT STATE REPORT - STOLEN PORTABLE GAUGE The following information was received by email: "On April 14, 2014 at approximately 0600 MST, the licensee discovered that a portable gauge was stolen out of the bed of a pick-up truck at a technician's home. The gauge was being housed in a transport box, which was chained to the bed of the truck. The lock was cut and the entire box was stolen. The gauge is a CPN MC Series, serial #MC380404231, and contained 50 millicuries of Cs-137 and 10 millicuries of Am-241. "The Agency [Arizona Radiation Regulatory Agency] continues to investigate the event. "The USNRC, California, Nevada, Utah, Colorado, New Mexico, FBI, and Governor's Office are being notified of this event [by the Agency]." Arizona Event: 14-007 * * * UPDATE AT 1722 EDT ON 5/5/14 FROM GORETZKI TO SNYDER * * * The following information was received by email: "On May 3, 2014, at approximately 0300 [MST], the Agency received a telephone call from the Phoenix Fire Department that they had responded to an incident at an apartment complex where a radioactive gauge was found. The gauge was found next to a dumpster by the apartment security guard while he was doing his rounds. The Agency responded and took possession of the gauge. The lock on the handle was still intact and the shutter was closed. It was noticed that the electronics looked like they had been tampered with but the gauge seemed to be in good condition otherwise. A survey of the gauge was performed, with nothing out of the ordinary noted. "The investigation into this event is closed." Arizona Supplemental Notice: 14-007 Notified R4DO (Whitten), FSME Events Resource (email) and Mexico (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-04-22
50035 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-11 | 2014-04-14 15:58 | 2014-04-15 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received from the State of Texas by email: "On March 14, 2014, the Agency [Texas Department of State Health Services] received a call from the radiation safety officer (RSO) of a licensee. The RSO stated that during an instrument check on Friday, April 11, 2014, technicians found two line level indicators with stuck shutters. The open position is the normal operating position for these types of instruments. The technicians stated there was no apparent damage to the rod or the shutter mechanisms. The level indicators are located on the sides of a very tall product receiver bin containing polyethylene resin. There were no exposures and employees are not routinely around these sources. The instruments contained Cesium-137 at 5000 milliCuries each. The level indicators are tagged as inoperable and a service company has been contacted to inspect and repair the instruments. Further information will be entered in accordance with SA300." * * * UPDATE FROM IRENE CASARES TO VINCE KLCO VIA EMAIL ON 4/15/2014 AT 1235 EDT * * * "The first line of the initial report contained the wrong report date. The first line should have read: On April 14, 2014, the Agency received a call from the radiation safety officer (RSO) of a licensee. Additional information: The gauges are Ohmart model SHLM-BR-4 gauges. The sources are in the out position, but the licensee's RSO stated there has not been any additional exposure to radiation to any individual due to this event. Additional information will be provided as it is received in accordance with SA300." Notified the R4DO (Gaddy) and FSME Resources via email. * * * UPDATE FROM IRENE CASARES TO VINCE KLCO VIA EMAIL ON 4/15/2014 AT 1604 EDT * * * "On April 15, 2014, the Agency was contacted by the licensee and informed they were able to retract the source and fully close the shutter placing the source in the fully shielded position. Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (Gaddy) and FSME Resources via email. Texas Incident: I-9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-22
50034 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-04-14 06:00 | 2014-04-14 14:48 | 2014-04-15 | POST-ACCIDENT HYDROGEN SAMPLE ANALYZERS OUT-OF-SERVICE "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0600 CDT on 4/14/14, it was determined that the ability to obtain a post-accident hydrogen sample from Unit 1 containment was lost. With both trains of Post-Accident Hydrogen Analyzers (PAHA) out of service, it was discovered that there was reduced sample flow indicated on the backup methodology through a containment sample port (R67). Repair efforts are underway. A follow-up notification will be sent when assessment capability is restored." The NRC Resident Inspector has been notified. * * * UPDATE FROM DARRIN GARD TO CHARLES TEAL AT 1425 EDT ON 4/15/14 * * * Assessment capability has been restored as of 1933 EDT on April 14, 2014 utilizing the containment particulate rad monitor sample port R-67. The licensee has notified the NRC Resident Inspector. Notified R2DO (Widmann). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-14
50033 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-04-09 | 2014-04-14 12:35 | 2014-04-14 | AGREEMENT STATE REPORT - IODINE-125 SEED FOUND IN WELL CHAMBER The following was received from the State of Nebraska via fax: "On April 9, 2014, the State of Wisconsin Radiation Protection Section called to inform the State of Nebraska Radioactive Materials Program that a State of Wisconsin licensee (University of Wisconsin) had found an Iodine-125 seed (measured at 0.255 millicuries) in a well chamber that had been sent to the University of Wisconsin from Regional West Medical Center (Nebraska Radioactive Material License # 21-01-03) for calibration. The I-125 seed has been secured by the University of Wisconsin and is awaiting disposition." "The State of Nebraska Radioactive Materials Program called Regional West to confirm that there was no misadministration to the patient since one seed was left in the counting chamber. Regional West confirmed that the proper dose was administered to the patient." Nebraska Report #: NE140002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2014-04-22
50032 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-13 21:13 | 2014-04-13 23:49 | 2014-04-14 | REACTOR TRIP DUE TO ACTUATION OF MAIN GENERATOR PROTECTION RELAY "This 4 and 8 hour notification is being made to report that Salem Unit 1 experienced an unplanned automatic reactor trip and subsequent Auxiliary Feedwater system actuation. The automatic trip was initiated from a generator protection relay. A walkdown of the main generator and all protection circuitry has been completed with no visible problems identified. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. 11, 12, and 13 Aux Feedwater Pumps automatically started as expected on low Steam Generator water level following the reactor trip. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "Salem Unit 1 is currently in Mode 3. Reactor Coolant System pressure is at 2235 psig and temperature is 547 degrees F with decay heat removal via the main steam dumps and Auxiliary Feedwater Systems. "There was no major primary or secondary equipment tagged for maintenance prior to this event. Condenser vacuum and Steam Generator Feed Pumps were available for the duration of the event. No personnel were injured during this event." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Township. Unit 1 is in a normal shutdown electrical lineup. Unit 2 is in a refueling outage and was unaffected by the Unit 1 trip. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-04-14
50031 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-12 20:08 | 2014-04-12 23:20 | 2014-04-12 | MANUAL REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE FAILING SHUT "At 2008 EDT, Vogtle Unit One was manually tripped in response to loop 1 outboard Main Steam Isolation Valve failing shut. All systems operated correctly in response to the reactor trip. All control rods fully inserted. System response allowed for an uncomplicated reactor trip response. Unit 1 is stable in Mode 3 and cause investigation is in progress." "The NRC Senior Resident Inspector was notified." There was a normal post trip feedwater isolation due to low Tave. Offsite power remains available. Decay heat is being removed by the main condenser. The plant is stable in Mode 3. There was no impact on Unit 2. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-04-12
50030 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-04-12 10:12 | 2014-04-12 13:24 | 2014-04-12 | AUTOMATIC REACTOR SCRAM DUE TO TRANSFORMER SUDDEN PRESSURE RELAY ACTUATION "At 1012 CDT on April 12, 2014, Dresden Unit 2 automatically scrammed on TR-2 sudden pressure relay actuation. All rods inserted to their full-in positions. "Following the reactor scram, the 'A' reactor recirculation pump did not run back to minimum speed automatically. Operators took action to run the recirculation pump to minimum speed manually. All other systems operated as expected. Reactor vessel inventory and pressure are being maintained in automatic. "The cause of the scram was due to a trip of the sudden pressure relay for Main Power Transformer 2. Troubleshooting is in progress to determine the cause [of the trip of the sudden pressure relay]. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." Normal offsite power remains available. There was no impact on Unit 3. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-04-12
50029 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-04-11 | 2014-04-11 21:29 | 2014-04-11 | AGREEMENT STATE REPORT - MISSING/LOST PORTABLE GAUGE The following was received from the State of Colorado via email: "The State of Colorado needs to report a missing/lost portable gauge. The licensee is AG Wassenaar, Inc. (Colorado license number CO 212-01). The gauge is a Troxler model 3430, serial number 36856 with 333 MBq (9 mCi) of Cs-137 and 1.63 GBq (44 mCi) Am-241:Be. "The technician who was using the gauge was working at one job site and then drove to a 2nd job site. The technician cannot remember if he placed the portable gauge in the transportation box or not, and whether or not the gauge was secured for transport appropriately. When the technician arrived at the 2nd job site at approximately 1430 MDT on 4/11/14, he noticed that the gauge was missing. The technician and radiation safety officer have traveled the area between the two job sites and were not able to locate the missing gauge. The licensee reported the missing gauge at approximately 1750 MDT on 4/11/14. "The investigation by the licensee and the Department [State of Colorado] is ongoing." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-04-21
50028 | 0 | QAL-TEK ASSOCIATES |  |  |  |  | 2014-04-11 | 2014-04-11 15:50 | 2014-04-17 | MOISTURE DENSITY GAUGE LOST DURING SHIPMENT The licensee shipped a moisture density gauge to a customer in Billings, Montana. However, the customer notified the licensee that the package had not arrived. The licensee contacted the common carrier. The common carrier was able to confirm that they had weighed the package at their facility in Salt Lake City, Utah on 4/5/14 and it was scanned at that same facility on 4/9/14. The common carrier said that the normal routing for the package is through the Denver, Colorado office. A search of that facility did not find the package. The moisture density gauge is a Troxler Model 3440 containing 8 mCi of Cs-137 and 40 mCi of Am/Be as of 2004. * * * UPDATE FROM MONTE POPE TO DANIEL MILLS ON 4/17/2014 AT 1318 EDT * * * The licensee notified NRC that the moisture density gauge was found by the common carrier at the Denver, Colorado office. The gauge was found undamaged, and indications are that the gauge never left the Denver office. The common carrier delivered the gauge to the correct address on 4/17/14. Notified R4DO (Gaddy), FSME (Email), and Canada (Fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-04-21
50027 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-04-10 | 2014-04-11 09:00 | 2014-04-11 | PROCESS GAUGE WITH SOURCE EXPOSED The following information was received from the State of Ohio via email: "The assistant RSO of BP Husky refinery called the Ohio Department of Health Bureau of Radiation Protection [Department] at 0933 EDT on April 10, 2014 to report an incident that happened overnight. "Thermo Fisher had been contracted to remove an old Ohmart gauge for disposal. During the removal of the gauge, the gauge and the gauge rigging fell. The gauge was still attached to the source well and was being removed as a single unit. The damaged gauge fell and became stuck inside the vessel tower skirt. During the fall, the gauge was damaged and the source became exposed. The dose rate from the device is 640 mRem/hr at 1 ft. The area, which is located inside a secured refinery, is roped and barricaded. No personnel were injured during the incident. "The gauge is an Ohmart SHRM-BW. It contained 1000 mCi of Cs-137 when installed in 1966. "The Department sent an inspector to the site to observe the source and gauge recovery efforts on April 10, 2014. VEGA (the successor company of Ohmart) sent a field service representative to provide technical assistance. As of 1830 CDT on April 10, 2014, efforts to return the source to the shielded position were unsuccessful. "The Department continues to monitor efforts to secure the source in a shielded position." * * * UPDATE FROM KARL VON AHN TO CHARLES TEAL ON 4/11/14 AT 1556 EDT * * * "At 1530 EDT on April 11, 2014, the BP Husky Refinery RSO called the Department to report that the VEGA and Thermo Fisher service personnel were able to retract the sealed source back into the shielded position. A preliminary check of the sealed source leak tests did not indicate any leakage of the sealed source." Notified R3DO (Pelke) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-04-21
50026 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-04-10 21:00 | 2014-04-10 22:40 | 2014-04-10 | OFFSITE NOTIFICATION DUE TO A DEAD DUCK FOUND ON SITE "Monticello Nuclear Generating Plant personnel discovered the remains of what appeared to be a deceased duck on plant property. The cause of death was not immediately apparent, no work was ongoing within the vicinity at the time. Notifications to the Minnesota Department of Natural Resources and the Division of Fish and Wildlife will be made for this discovery. This event is reported per 10CFR50.72(b)(2)(xi). "The licensee has notified the NRC Senior Resident Inspector." Plant personnel could not determine if the duck was an endangered species. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-10
50025 | 0 | CAMERON MEASUREMENT SYSTEMS |  |  |  |  | 2014-04-10 | 2014-04-10 20:21 | 2014-06-09 | PART 21 - BARTON MODEL 288A AND 289A DIFFERENTIAL PRESSURE SWITCH DEFECT Cameron Measurement Systems is reporting a defect affecting versions of the Barton Model 288A and 289A differential pressure indicating switches and spare switch assemblies for these products. The defect being reported is an out of specification concentricity issue with the roller that actuates the switches. This represents a switch setpoint repeatability concern. Any additional safety significant issues that might be identified in our ongoing investigation will be addressed in subsequent advisories that will be published. If you have any questions please contact Chuck Rogers, Director of Quality and Safety, at (281) 582-9507 or Jim Greer, Engineering Manager, at (800) 291-3550. * * * UPDATE AT 1626 EDT ON 6/9/2014 FROM CHUCK ROGERS TO MARK ABRAMOVITZ * * * The following information was excerpted from an e-mail: "Cameron has performed switch setpoint repeatability testing which has verified that rollers, even those with out of tolerance run-out, can meet the published 0.25% repeatability specification as long as the roller moves freely along the switch operating cam. However, if the roller were to 'skid' or 'skip' on the cam, or rotate when the roller is off the cam due to vibrations such that the roller does not return to the exact same radial position when it's on the cam at the switch setpoint there may be a setpoint shift unless the roller has no run-out. A change in the switch setpoint could be as much as ñ0.32% even for the current run-out specification of 0.0003 inches. As such, given that Cameron could ship product with switch repeatability verified to be 0.25% during production testing and that an additional 0.32% could be possible due to the allowable roller run-out, a field performance of 0.57% is possible. Given wear and other uncertainties Cameron would recommend that a user consider a conservative field repeatability value for switch setpoint calculations. "An important piece of information that was gleaned from the current testing effort is that switch repeatability testing is very dependent on the sensitivity of the calibration equipment utilized. Most calibration pressure sources and measurement displays have lags in the indication of the actual pressures applied that can cause errors and, even more critical, is the lag that occurs between the operator's response to the indication of the switch trip and the reading of the pressure source display. Cameron discovered that the observation of the indicator pointer (properly calibrated) is more accurate in verification of switch repeatability than any pressure source and electrical switch contact monitoring device we utilized. Once the switch setpoint is established, a pencil mark at this trip point on the indicator scale can be utilized to verify subsequent trip points. "In conversations with customers that called to discuss the original Advisory concerns, Cameron became aware that some users may believe that the Model 288A and 289A switch performance is not impacted by changes in the environment where they are located. The Barton qualification for these products was a radiation augmented mild environment test program. A sample of products was exposed to 3 Mrads of radiation and then subjected to a 12G maximum seismic simulation. The products performed within specification for this limited testing at standard factory environmental conditions. In our opinion, field calibrations and switch setpoint testing should be performed at the same temperature conditions as expected when the instruments are required to perform their safety functions. Performance testing at one temperature may not necessarily ensure appropriate performance at another temperature. "If you have any questions, want to place an order for a replacement instrument, switch actuation arm (with roller) or a switch and plate assembly, or want to begin the RMA process for an instrument factory repair please contact Mabel Loo, Customer Service Manager, Cameron Measurement Systems, City of Industry, CA at (800) 291-3550." Notified the R1DO (Dental), R2DO (Freeman), R3DO (Daley), R4DO (Werner), and Part-21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-04-10
50024 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-04-10 15:20 | 2014-04-10 16:23 | 2014-04-10 | SAFEGUARDS REPORT - UNAUTHORIZED PERSON ENTRY INTO A PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-04-10
50023 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2013-09-10 15:05 | 2014-04-10 15:40 | 2014-04-10 | UF6 PRESENT IN THE SMALL COMPONENT DECONTAMINATION TRAIN "(1) Radiological or chemical hazards involved, including isotopes, quantities, and chemical and physical form of any material released Uranium-hexafluoride (UF6): "3.1 grams of solid UF6 was present in the Small Component Decontamination Train (SCT) and was assumed to be enriched to 5 weight percent U235. Thus 0.16 grams of U235 were present. Neither criticality nor chemical release occurred. "(2) Actual or potential health and safety consequences to the workers, the public, and the environment, including relevant chemical and radiation data for actual personnel exposures to radiation or radioactive materials or hazardous chemicals produced from licensed materials (e.g. level of radiation exposure, concentration of chemicals, and duration of exposure): "None; the administrative limit to ensure criticality is prevented is 730 grams of U235. The mass present was about two ten-thousandths of the administrative mass limit. This administrative mass limit is less than one half of the analyzed 0.95 keff safe mass. "(3) The sequence of occurrences leading to the event, including degradation or failure of structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences: "The IROFS prevent the accumulation of U235 above the administrative mass limit of 730 grams U235 in the SCT. The IROFS determine a net weight of residual material in a container by comparing the initial, prior to first use, tare weight to the empty weight, after outgassing. "It was discovered that upon cleaning, the technicians were determining a net weight using the most recent empty weight, not the prior to first use tare weight. This resulted in the potential to nullify the weight of remaining trace quantities of residual material. "This represents a failure of management measures such that no IROFS, as documented in the ISA summary, remain available and reliable, in an accident sequence evaluated in the ISA, to perform their function. Therefore, this one hour event report being completed in accordance with 10 CFR 70 Appendix A (a)(4). "(4) Whether the remaining structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function: "All structures, systems, equipment, components, or activities of personnel remain available and reliable to perform their safety functions. "(5) External conditions affecting the event; "There were no external conditions that affected this event. "(6) Additional actions taken by the licensee in response to the event: "The area was isolated, operations in the SCDT were halted and a criticality anomalous condition was declared per Operating Requirement Manual. An immediate reconciliation of the IROFS54a and 54b mass record logs was completed and it was determined that the mass present in the SCDT, 0.155 grams U235, was well below the administrative mass limit of 730 grams. "(7) Status of the event (e.g., whether the event is on-going or was terminated); "No event occurred; there was insufficient material present for criticality to be possible. No release of licensed material occurred. This event was the discovery of a failed management measures related to an IROFS. "(8) Current and planned site status, including any declared emergency class; "Plant is running at full capacity. This event did not warrant any change in plant status. No declared emergency occurred nor are any planned. "(9) Notifications, related to the event, that were made or are planned to any local, State, or other Federal agencies; "No notifications other than this report have been made nor are any planned. "(10) Status of any press releases, related to the event that were made or are planned. "No press releases have occurred nor are any planned." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2014-04-10
50022 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-10 05:55 | 2014-04-10 14:33 | 2014-04-25 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee violated the site Fitness-for-Duty (FFD) policy. The affected individual will be evaluated under for-cause FFD testing. The employee's plant access has been suspended. The NRC Resident Inspector has been informed. * * * UPDATE AT 0100 EDT ON 04/25/14 FROM BUD HINCKLEY TO S. SANDIN * * * The licensee provided additional clarifying information. The NRC Resident Inspector will be informed. Notified R3DO (Cameron). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2014-04-10
50021 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2013-11-06 13:07 | 2014-04-10 13:52 | 2014-04-10 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - UNUSUAL EVENT DUE TO EXPLOSION "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This notification describes a previously undeclared event that is now reported pursuant to the requirements of 10 CFR 50.72(a)(3). No emergency situation exists at this time. "On November 6, 2013, while operating at 100% reactor power under steady state conditions, a U-1 control room alarm was received indicating low fluid pressure in the Train 'A' hydraulic accumulator of Main Steam system isolation valve MSIV-170. A plant operator was dispatched according to the alarm response procedure to perform a pre-charge check of the accumulator. A pre-charge check returns hydraulic fluid from the accumulator to a vented tank that serves as a fluid reservoir. During this operation the fluid reservoir tank and supporting piping were damaged by the rapid expansion of nitrogen gas that had entered the hydraulic system by way of a leak across an accumulator piston O-ring. As a result of the damage and loss of hydraulic fluid, MSIV-170 and its associated hydraulic accumulators were declared inoperable at 1307 Mountain Standard Time. It was determined at that time that the failure of the fluid reservoir due to rapid expansion did not constitute an explosion and a declaration of an Unusual Event was not made according to Emergency Action Level (EAL) HU2, 'Fire within the Protected Area not extinguished within 15 minutes of detection or explosion within the Protected Area.' "Subsequent review has determined that the reservoir failure should have been characterized as an explosion within the Protected Area and that a declaration of an Unusual Event should have been made per EAL HU2. "The NRC Resident Inspector has been notified." The licensee has notified the State of Arizona and Maricopa County. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | AZ | POW | [5 empty] | 0 | 2014-04-10
50020 | 0 | ROSEMOUNT NUCLEAR INSTUMENTS, INC |  |  |  |  | 2014-04-10 | 2014-04-10 11:50 | 2014-04-10 | PART 21 - MODEL 1154HP TRANSMITTERS WITH INTEGRAL 1159 REMOTE DIAPHRAGM SEALS MAY EXHIBIT DEGRADED FUNCTIONAL RELIABILITY "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that certain Model 1154HP transmitters with integral 1159 Remote Diaphragm Seals may exhibit degraded functional reliability. "The standard maximum working pressure for Model 1154 transmitters with integral 1159 Remote Diaphragm Seals is 2000 psi. "Per the unique requirements of Point Beach Nuclear Generating Station, Model 1154HP5RAGN0080 pressure transmitters with integral 1159A50AS0111 Remote Diaphragm Seals were manufactured to operate at a non-standard maximum working pressure of 2750 psi. "Once installed in the field, two transmitters exhibited unexpected drift in the output signal when operated at line pressures of approximately 2235 psi. "To date there are no known additional reported functional reliability issues with other Model 115x Series transmitters with integral 1159 Remote Diaphragm Seals in a similar configuration. "RNII does not have complete information relating to specific plant applications and therefore cannot determine the potential effects of the condition on plant operation. "This notification affects seven Model 1154HP transmitters with integral 1159 Remote Diaphragm Seals shipped to Point Beach Nuclear Generating Station since March 2013." Name and address of the individual providing the information: Mr. Marc D. Bumgarner Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-04-10
50019 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2014-04-08 | 2014-04-09 19:02 | 2014-04-09 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The following information was received from the State of Arizona via email: "On April 8, 2014, the Agency was contacted by the Licensee who indicated that an employee and a Troxler Gauge was missing. The licensee was informed around 6:00 AM that the employee did not show up on a job on the Indian Reservation. The licensee has notified both the Arizona Department of Public Safety and the New Mexico Department of Public Safety. The gauge is a Troxler Model 3430, Serial Number 7052 containing 9 millicuries of Cesium-137 and 45 millicuries of Am-241. The individual was discovered to have had a diabetic coma and the gauge was still with the individual and the licensee is sending another operator to retrieve the gauge. The individual is in Gallup, NM. "The investigation into this event is ongoing. "The U.S. NRC, New Mexico, and Arizona Governor's Office have been notified of this event." Arizona First Notice: 14-006 * * * UPDATE AT 1930 EDT ON 4/9/14 FROM AUBREY GODWIN TO S. SANDIN * * * The Troxler Gauge has been recovered and is in the licensee's possession at their Flagstaff, AZ office. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2014-04-17
50018 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-09 | 2014-04-09 16:46 | 2014-04-09 | AGREEMENT STATE REPORT - CABLE DISCONNECT ON RADIOGRAPHY CAMERA The following report was received from the State of Texas via email: "The licensee called [Texas Department of Health] to report that a disconnect occurred due to a broken drive cable. The SPEC-150 radiography device contained a 28 curie iridium-192 source. The cable broke near the ball stop on the crank out connector. The source remained in the source guide tube. The radiography crew called the incident in and waited for an authorized person to retrieve the source. The source was retrieved with minimal exposure. Incident doses were based on pocket dosimeter readings. The radiographer received 15 mrem and the trainee received 2 mrem. The radiographer retrieving the source received 25 mrem and his assistant received 9 mrem. "It is believed that the cable failed due to metal fatigue. The individual providing the report did not know when the cable was last tested." Texas Incident #: I-9180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-17
50017 | 0 | BALDOR ELECTRIC CO. |  |  |  |  | 2014-03-19 | 2014-04-09 15:19 | 2014-04-09 | PART 21 - POTENTIAL DEFECT IN MOTORS SHIPPED TO DTE ELECTRIC COMPANY The following is excerpted from a report received by fax: "NUCLEAR NONCONFORMANCE REPORT "1. CUSTOMER: DTE Electric Company, P.O. BOX 44440, DETROIT Ml 48244 "2. PURCHASE ORDER: 4700670925 - QTY 2 "3. PART/COMPONENT NAME: AC MOTORS "4. PART/COMPONENT#: B1038686-010 T1/DTE P/N 100309425 and B1038686-010 T2/DTE P/N 100309425 "5. QUANTITY ON HAND - 1 SHIPPED- 2 "6. LOCATION OF ALL UNITS: Motor in service at DTE, Enrico Fermi Power Plant 2 (Qty 1) and at Baldor Gainesville Motor Plant (Qty 1) "7. DATE NONCONFORMANCE ASCERTAINED: March 13, 2014 "8. DESCRIPTION OF DEFECT/NONCONFORMANCE: This is a reportable 10CFR21 notification because we believe it is possible that the B1038686-010 T1, 1E motor shipped by Baldor Electric, contains a design where the shaft journal is not long enough to allow the proper fit between the motor shaft and the o-ring of the inpro seal rotating element. "The motor (Bl038686-010 T2) returned for evaluation under RA310488951 was in response to the inpro seal separating. Upon inspection Baldor has determined the shaft journal is not long enough to allow the proper fit between the motor shaft and the o-ring of the in pro seal rotating clement. "9. CORRECTIVE ACTION TAKEN: Baldor has notified DTE Electric Company's Quality Assurance of our findings. Through them we have initiated replacement of the motor identified as located at DTE, Enrico Fermi Power Plant 2. "A review was completed by design engineering to determine this design issue has only occurred for the Specification ID B1038686, of which Baldor has only shipped the 2 motors identified above. The design of the shaft/inpro seal fit has been completed to correct the issue. "10. ANY ADVICE RELATED TO DEFECT/NONCONFORMANCE: Separation of the rotating element from the in pro seal obviously reduces the full effectiveness of the in pro seal. However, if this were to occur, the motor is still functional. Baldor has confirmed the motor with a failed inpro seal as received is still equivalent to IP55. Grease from the DE bearing will still be retained as intended, and water ingress into the motor would only occur if sprayed directly. Baldor recommends continued use of B1038686-010T1 until the next outage unless direct spray is expected. B1038686-010T2, which is currently in Baldor's possession, will be repaired by changing the rotating assembly. Baldor has notified DTE that we will be manufacturing a complete motor per the revised bill of material to replace B1038686-010T1 which is currently in service. "11. INDIVIDUAL COMPLETING THIS REPORT: James Thigpen, QA Manager, Baldor Electric, Gainesville, GA 30506, April 09, 2014" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-04-09
50016 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-04-13 | 2014-04-09 16:20 | 2014-04-09 | AGREEMENT STATE REPORT - SOURCE DETECTED IN A LOAD OF SCRAP METAL The following report was received from the Louisiana Department of Environmental Quality via fax: "Event date and time: The source was detected in a load of scrap metal on April 13, 2013. "Event location: Source was detected in a load of scrap metal, being loaded for transport to a smelting mill, at the Southern Scrap facility, [in Scott, LA.]. "Event type: The radioactive source was a rod source, later determined to be 3.29 mCi of Cs-137. The source was retrieved and stored [in a] shielded [location] until Southern Scrap's licensed consultant, ARS [American Radiation Services], was able to package and transport the unknown source to their facility in Port Allen, LA. "Notifications: LDEQ [Louisiana Department of Environmental Quality] was notified by phone on April 18, 2013 at 1620 [CDT] of the discovery. "Event description: On April 13, 2013, an unknown source of radiation was discovered in a load of scrap being sent to NUCOR Steel in TX. The source was detected before the load of scrap left the Southern Scrap yard. American Radiation Services (ARS), a licensed radiation safety contractor, was called to prepare [the source] for safe shipping, determine the isotope and activity, and do an appropriate disposal of the unknown source. "ARS made the determinations and found the rod source to be 3.29 mCi of Cs-137. [ARS then] packaged [the source] for transportation and disposal. ARS contacted ADCO Services, in Illinois, for the disposal. (During an earlier attempt for a licensee to utilize ADCO Services, [LDEQ] learned that ADCO did not have a current Illinois license to provide services.) ARS was notified the ADCO Services was not licensed to provide services and that ARS would have to contact and contract with another licensee for these services. "ARS contacted QSA Global in Baton Rouge, LA, and arranged for their receipt and disposal of the orphaned source. The origin and owner of the source could not be determined and Southern Scrap absorbed the cost of the safety services and disposal. QSA Global took possession of the source June 7, 2013. The initial notification was made to the NRC in April 2013; however, documentation of this call to the [NRC] OP Center could not be located. The supporting documents are attached to the fax. Transport vehicle description: ARS Company Vehicles. "Media attention: N/A" Louisiana Event: #LA-140005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-04-17
50015 | 0 | QUALTECH NP |  |  |  |  | 2014-04-09 | 2014-04-09 15:21 | 2014-05-09 | PART 21 - POTENTIAL DEFECT IN GENERAL ELECTRIC TYPE CR120AD CONTROL RELAYS The following information was received via fax: "This letter is being issued by QualTech NP, Huntsville, AL, to provide an initial notification to the Nuclear Regulatory Commission and Nebraska Public Power District [NPPD] Cooper Nuclear Station concerning a potential defect in General Electric Type CR120AD control relays. A failure analysis revealed that the most likely initiator of the failure was a flaw or defect in the start wrap of the magnet wire. The flaw created an arc that involved windings directly beneath the start wrap which resulted in an open circuit on the coil windings. This failure is classified as infant mortality, which is similar to the failure mode identified in the 10 CFR part 21 30 day report (accession number 9706190261) dated June 12, 1997 submitted by GPU Nuclear. "Investigation of documents dating back to 1997 revealed that the manufacturer issued an informal recommendation to detect infant mortality in these relays by performing burn-in testing and mechanical cycle aging of the relay. QualTech NP, in conjunction with NPPD, determined that the risk of infant mortality can be mitigated by subjecting these relays to a 100 hour burn-in and performance of 100 mechanical cycles prior to installation. "It has been confirmed that only two orders, with two units each, for this particular relay are affected. Both orders have been shipped to Nebraska Public Power District as requested by purchase orders 4500149953 and 4500142705. All subject relays shall be subjected to a 100 hour bum-in and exposed to 100 mechanical cycles or returned to QualTech NP for replacement. "Additional details will be provided in the formal written report. Please contact Matthew Thelen at 256-924-7441 (office) or mthelen@curtisswright.com for additional information. "Matthew Thelen Project Manager QualTech NP Huntsville Operations a business unit of Curtiss-Wright Flow Control Company http://qualtechnp.cwfc.com" * * * UPDATE AT 1707 EDT ON 05/09/14 FROM MATTHEW THELEN TO S. SANDIN VIA FAX * * * "(File No.: QTHuntsville 10CFR21-2014-01) "To whom it may concern: "This letter is being issued by QuaiTech NP, Huntsville Operations to provide a final notification to the Nuclear Regulatory Commission and Nebraska Public Power District (NPPD) Cooper Nuclear Station concerning a potential defect in General Electric Type CR120AD control relays. "Replacement relays have been provided to NPPD. All required dedication procedures at QualTech NP have been revised to include a 100 hour burn-in and 100 mechanical cycles in an effort to detect infant mortality. No further actions are required at this time. "This 10CFR part 21 file is closed." Notified R2DO (Bonser), R4DO (Whitten) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-04-09
50014 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-04-09 11:30 | 2014-04-09 14:28 | 2014-04-11 | AGREEMENT STATE REPORT - RADIOGRAPHER OVEREXPOSURE The following information was received from the Ohio Bureau of Radiation Protection via email: "The corporate RSO for Acuren Inspection made an immediate telephone notification under OAC [Ohio Administrative Code] 3701:1-38-21(B)(1) [same as 10 CFR 20.2202(a)(1)] to the Ohio Department of Health Bureau of Radiation Protection at 1320 [EDT on] April 9, 2014, to report a radiographer overexposure at a temporary job site in Marietta, OH. The event happened about 1100-1130 [EDT] this morning. The initial estimates regarding the male radiographer is that he may have received a 15 Rem whole body exposure and an estimated 3000-5000 Rem to the hand. The radiographer's whole body dosimeter is being sent off for immediate processing. "The radiographer has been sent for medical attention. REAC/TS [Radiation Emergency Assistance Center/Training Site] was contacted by the licensee who gave REAC/TS the contact information for the attending physician of the radiographer. "The radiographer was working with an 88 Ci Ir-192 source at the time. The radiographer supposedly had all his dosimetry and a survey meter at the time of the incident. "The corporate RSO and a local [RSO] are both enroute to the temporary job site. "Sequence of events: The radiographer had sat down and was chatting while waiting for an exposure to complete. At the end of the shot time, he had assumed that the other radiographer had retracted the source and proceeded to set up for the next shot. When he noticed that the other radiographer was not present he went back and checked to find that the source had not been cranked back. "The [State of Ohio] Department will have an inspector on scene in the morning to investigate the incident and also to observe and review the incident reenactments. "Ohio event report number 2014-007." * * * UPDATE FROM KARL VON AHN TO CHARLES TEAL ON 4/10/14 AT 1530 EDT * * * "On April 10, 2014, the [State of Ohio] Department performed an onsite inspection and observed the licensee perform a reenactment of the incident scenario. "It was determined that the radiographer did not handle the end of the source tube with the source in it and did not receive the initially assumed hand dose. The whole body deep dose is still expected to be about 15 Rem. The hand dose is expected to be on the order of the whole body dose, about 15 Rem. "During the reactive inspection, the [State of Ohio] Department found that the radiographer's alarming rate meter had a dead battery, and the survey meter was not functional and had not been checked that day. "The Assistant Radiographer was trailing the radiographer approximately one and a half minutes in entering the shielded bunker, and it was the assistant radiographer's alarming rate meter and survey instrument that identified the presence of the exposed source. The source collimator was not being used in the bunker, and so the 89 Ci Ir-192 source was not shielded." Notified R3DO (Pelke), FSME Duty Officer (McIntosh), and FSME Event Resource. * * * UPDATE FROM KARL VON AHN TO CHARLES TEAL ON 4/11/14 AT 1234 EDT * * * "The Acuren Inspection Services RSO has provided the Department [State of Ohio] with the following updates: "(1) The radiographer's whole body dosimeter reading was 836 mRem. "(2) Based on the dose estimates from the scene reenactments, Acuren will assign the radiographer a whole body dose of 13 Rem, and an extremity dose of 6.5 Rem. [The radiographer's chest was much closer to the source than his dosimeter was.] "(3) The radiographer will be under continued medical surveillance and REAC/TS will remain involved." Notified R3DO (Pelke), FSME Duty Officer (McIntosh), and FSME Event Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-04-17
50013 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2014-03-25 | 2014-04-09 13:37 | 2014-04-09 | PART 21 - POTENTIAL DEFECT IN GENERAL ELECTRIC SB1 SWITCHES AND HEA RELAYS The following is an excerpt from a fax received from United Controls International (UCI): "The purpose of this letter is to provide the NRC with a report in general conformity of the requirements of 10CFR Part 21.21. On March 19, 2013, United Controls Issued an Interim letter regarding a discovered manufacturing change in the contact assembly of General Electric SBM series switches. Since 2009, the manufacturing process of the contact assembly of the SBM switch contacts has changed to have the whole assembly (contact holder and contact tip) tin plated. This was discovered while investigating an SBM switch that failed at a customer site due to high contact resistance across closed contacts. The finding that there was a manufacturing process change in the SBM switches lead to further discussions and evaluations regarding equipment of similar design. General Electric SB1 series switches and HEA series relays use the same contact arrangement design as the SBM series switches. The contact assemblies of the SB1 switches and HEA relays are subject to the same tin plating process of the contact assembly as previously reported on the SBM series switches. "At this time, UCI is unable to evaluate if this manufacturing change may have an adverse effect on the capability of the General Electric SB1 switches and GE HEA relays to perform in their intended safety related application. "UCI will notify the affected Utilities to our findings." The affected Part Number, Utility, Order Number and Quantity is listed below: Part Number 12HEA61B23SX2; Utility CFE; Order 700372018; Quantity 3 Part Number 12HEA61C236X2; Utility FPL Turkey Point; Order 02260642-34; Quantity 2 Part Number 12HEA61C237; Utility OPPD; Order 180520; Quantity 4 Part Number 12HEA61C238X2; Utility OPPD; Order 180520; Quantity 3 Part Number 12HEA61C237; Utility OPPD; Order 185929; Quantity 2 Part Number 12HEA61C237X2; Utility OPPD; Order 188314; Quantity 2 Part Number 12HEA63C239X2; Utility FPL St. Lucie; Order 02260642-41; Quantity 8 Part Number HEA61C234X2; Utility Antung; Order PP100204; Quantity 2 Part Number HEA61C244X2; Utility OPPD; Order 179664; Quantity 5 Part Number HEA61C241X2; Utility OPPD; Order 179664; Quantity 2 Part Number HEA63C239X2; Utility FPL St. Lucie; Order 02260642-103; Quantity 3 Part Number 12HEA61C238X2; Utility OPPD; Order 194686; Quantity 4 Part Number 16SB1BB339STS2P; Utility Duke Oconee; Order 156606; Quantity 11 Part Number 165BlFB2C85SWM2Y; Utility Nextera Seabrook; Order 2259825-3; Quantity 1 Part Number 16SB1LB2C01LSM2P; Utility CFE; Order 700327408; Quantity 3 Utility CFE is the Comisi¢n Federal de Electricidad (Mexico) and Utility Antung is located in Taiwan. "If you have any questions or wish to discuss this matter or this report, please contact: Jim Garrison Engineering Manager, Seismic and Equipment Qualification JGarrison@unitedcontrols.com 770-496-1406 X 103." The 10CFR Part 21.21 received on March 19, 2014 is EN #49940. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-04-09
50012 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-04-08 21:14 | 2014-04-08 23:13 | 2014-04-08 | UNIT 1 MANUALLY TRIPPED FOLLOWING THE LOSS OF AN OPERATING STEAM GENERATOR FEED PUMP (SGFP) "This 4 and 8 hour notification is being made to report that Salem Unit 1 has performed an unplanned manual reactor trip and subsequent Auxiliary Feedwater system actuation. The trip was initiated due to loss of Steam Generator water level [SGWL] following the loss of one of the running SGFPs (#11 Steam Generator Feed Pump). The reactor was manually tripped prior to reaching the automatic SGWL low setpoints. #11/12/13 Aux Feedwater Pumps automatically started following the reactor trip on low Steam Generator water level. "Salem Unit 1 is currently in Mode 3. Reactor Coolant system pressure is at 2235 PSIG and temperature is 547 degrees Fahrenheit with decay heat removal via the Main Steam Dumps and Auxiliary Feedwater Systems. Unit 1 has no active shutdown technical specification action statements in effect. All control rods inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Engineered Safety Feature] systems functioned as expected. "There was no major primary or secondary equipment tagged for maintenance prior to this event. No personnel were injured during this event." The licensee will inform the Lower Alloways Creek Township and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-04-08
50011 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-04-08 08:12 | 2014-04-08 17:13 | 2014-04-08 | AGREEMENT STATE REPORT INVOLVING PALLIATIVE DOSE ADMINISTERED TO THE WRONG TREATMENT SITE The following report was received from the State of Florida via email: "This treatment was set up by the treatment planner taking into account the previous two treatments performed on the right side back in 2008 and 2007. The treatment planner did not realize that the pain had resolved on the right side and that the treatment was to be performed on the left side. The treatment was reviewed and signed according to protocol and was started by [the Authorized User] at 8:12 am. The 19.14 minute treatment was stopped at 1.72 minutes when it was realized that the patient was to be treated on the left side. At 8:42 am [the Authorized User] had [the Neurosurgeon] inform the patient that we interrupted the treatment because we had started treating the right side instead of the left side. The treatment planner created a treatment plan for the left side, the patient was treated and the stereotactic frame was removed at 10:00 am. This Medical Event will have no detrimental effects on the patient. No further action will be taken on." Florida Incident Number: FL14-035 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-04-16
50010 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-04-08 09:51 | 2014-04-08 14:14 | 2014-04-08 | LOSS OF STACK GAS EFFLUENT RADIATION MONITOR At 0951 EDT Operators discovered that RM-8168 (Stack Gas Effluent Radiation Monitor) was inoperable due to a temporary loss of power to the motor. This resulted in a loss of assessment capability. The licensee followed the required steps in the Alarm Response Procedure and restored the Radiation Monitor to service at 1310 EDT. The licensee informed State/local agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-08
50009 | 0 | U. S. GEOLOGICAL SURVEY |  |  |  | 1000 KW TRIGA MARK I | 2014-04-08 10:27 | 2014-04-08 13:56 | 2014-04-08 | REPORT OF TECHNICAL SPECIFICATION VIOLATION "Event details: "While performing a routine reactor pulse for surveillance purposes, the signal input cable to one of the power monitoring safety channels was disconnected, making the associated high power scram not functional. The pulsing procedure requires disconnecting this cable for preoperational testing, but states that the instrument input be returned to its normal operating status prior to actually performing the operation. Contrary to the procedure, this was not done and the reactor was operated at 2 watts for 7 minutes without that required safety channel operating. A second safety channel was fully operational during that time. The high power scrams are not required during pulse mode operations. The disconnected cable was subsequently discovered and reconnected." The licensee informed the NRR Program Manager (Morlang). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | CO | NPR | [5 empty] | 0 | 2014-04-08
50008 | 0 | LOUISIANA DEPT OF ENVIRONMENTAL QUA |  |  |  |  | 2014-02-06 | 2014-04-08 11:27 | 2014-04-08 | AGREEMENT STATE REPORT - CONTROL OF RADIOACTIVE MATERIAL The following was received from the State of Louisiana via fax: "A general licensed device gauge, containing [decay] corrected 30.47 mCi of Cs-137, serial number B-0187 was improperly disposed of. A recycling company had with a torch burned into the gauge and had come within one (1) mm of the source capsule. The Department of Energy had exercised eminent domain and taken over the oil well next to a strategic reserve for their use during November 2011 from Boardwalk LA Midstream, LLC. The gauge was not leaking and the source capsule was still intact. QSA Global has accepted the gauge for disposal. The Department [Louisiana Department of Environmental Quality] considers this matter closed." Louisiana report # LA-140004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-04-16
50007 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-04-08 06:18 | 2014-04-08 09:45 | 2014-04-08 | SHUTDOWN ACTION INITIATED BECAUSE HPCI AND RCIC WERE SIMULTANEOUSLY INOPERABLE "U1 entered Technical Specification 3.0.3, and initiated actions to reduce power via control rod insertion in preparations to enter startup within the following 6 hours. Entry into Tech Spec 3.0.3 was a result of both HPCI and RCIC injection systems being inoperable at the same time. "During startup from the U1 refueling outage, RCIC and HPCI full flow testing was unable to be completed at rated reactor pressure prior to the expiration of the 12 hour allowance per Tech Spec Surveillances 4.7.3.b* and 4.5.1.b.3** respectively. This occurred due to testing issues encountered while attempting to perform the rated pressure pump valve and flow tests. "U1 HPCI testing was completed satisfactorily at 0830, and HPCI was restored to operable. Plant shutdown was terminated at 0830 [EDT] as conditions for 3.0.3 no longer existed." The licensee will notify the NRC Resident Inspector. | 17 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-04-08
50006 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-08 04:28 | 2014-04-08 05:21 | 2014-04-08 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "VEGP Unit 2 was at 100% power, normal activities, when digital feedwater trouble alarms were received on all 4 steam generators (SG) with level stable in all generators. Operating crew entered abnormal operating procedure for feedwater malfunction when SG #3 level began rapidly lowering. Operators attempted to take manual control of SG #3 main feedwater regulating valve and were unable to raise SG #3 level. SG #3 level lowered to the Lo-Lo Level setpoint causing an automatic reactor trip. All control rods fully inserted and SG #3 level remained off scale low on narrow range indications. Auxiliary feedwater and feedwater isolation actuated as expected. [Unit 2] is currently stable in Mode 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the low SG water level and determine restart criteria and time of restart." All control rods fully inserted on the trip. Decay heat is being removed via auxiliary feedwater to steam generators steaming to the condenser steam dumps. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2014-04-08
50005 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-04-07 15:00 | 2014-04-07 16:12 | 2014-04-07 | REMOVAL OF RADIATION MONITORS FROM SERVICE FOR PLANNED MAINTENANCE "Both Discharge Canal Radiation Monitor Sample Pumps will be removed from service to facilitate planned maintenance activities. This represents a loss of emergency assessment capability under NUREG-1022 Revision 3 since the Discharge Canal Radiation Monitors are used to assess NUE [Notification of Unusual Event] and Alert thresholds. The Sample Pumps are expected to be unavailable for approximately two hours. During this time, Chemistry will be obtaining samples every 2 hours. As a result of the sampling, reasonable assurance exists that rising radiation levels will be able to be detected and monitored in order to protect the health and safety of the public. "The NRC Resident [Inspector] has been notified prior to removing the Radiation Monitors from service." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-07
50004 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-04-07 06:00 | 2014-04-07 13:17 | 2014-05-10 | CONTROL ROOM SPECIAL VENT BOUNDARY INOPERABLE "At approximately 0600 CDT on April 7, 2014, Units 1 and 2 Control Room Special Vent System (CRSVS) Boundary was declared inoperable when a Control Room door handle fell off. Air could be felt flowing through the hole, causing an opening in the Control Room Envelope (CRE) Boundary. An opening reduces the protection of the Control Room Envelope provided to the operators in the event of a Design Basis Accident. The CRSVS Boundary was declared Inoperable, which required entry into Technical Specifications (TS) LCO 3.7.10. Condition B, one or more CRSVS trains inoperable, in MODES 1, 2, 3, or 4. Actions were immediately initiated to implement mitigating actions. A Work Request (WR) was initiated to repair the door, and work is in progress to restore the Control Room Boundary to an operable condition. "This condition is reportable under 10CFR50.72(b)(3)(v)(C), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. "The plant remains safe, and this condition does not pose any additional risk to the public. Additionally, our defense in depth strategies are relied upon to take actions to protect the health and safety of the public. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION ON 5/10/14 AT 2032 EDT FROM STEVE INGALLS TO DONG PARK * * * "Engineering evaluation has determined that the door would still fulfill its safety function of maintaining the integrity of the Control Room Envelope while the door handle was broken. The Control Room Special Vent System Boundary remained operable with the door handle off, therefore, there was no loss of safety function. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Riemer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-07
50003 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-04-05 | 2014-04-07 11:30 | 2014-04-14 | AGREEMENT STATE REPORT - TWO SR-90 SEALED SOURCES FAILED PRE-SHIPMENT LEAK TEST The following information was received from the Commonwealth of Massachusetts via email: "On Saturday, 4/5/14, licensee left voice mail notification for this Agency (Massachusetts Radiation Control Program) of the same day determination of two potential leaking or contaminated sealed sources that had been taken out of long-term storage and intended to be shipped for eventual disposal. Notification received by Agency on Monday, 4/7/14. Follow-up contact with licensee by Agency on 4/7/14. The source was returned to storage pending licensee contact with manufacturer. Licensee reported leak lest results are preliminary in nature and were determined by licensee to be above background. There was no evidence of contamination beyond the source itself. Five-day written report from licensee to follow. "Additional Reference: NMED Item Number TRA "Manufacturer: Eckert & Ziegler / IPL "Model #: SIF.D1 "Manufacture date: 3/2004 (0.100 Ci) "Serial #: MI318 / MC915 "Isotope: Sr-90 "Isotope activity (Ci): 0.078 (4/2014) "Leak test result (microCi): 0.002 (preliminary) / 0.0007 (preliminary)" * * * RETRACTION FROM CARPENITO TO KLCO VIA FAX ON 4/14/2014 AT 1515 EDT * * * "The Licensee's written report was received by the Agency on 4/10/14. The Licensee confirmed that leak test results were unchanged from the earlier report. With this new information, the Agency determined that this is not a reportable event because results were below the reportable level of 0.005 microcuries. The Agency considers this matter to be closed." Notified the R1DO (Burritt) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-04-15
50002 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-04-05 10:25 | 2014-04-05 18:16 | 2014-04-05 | LOSS OF ENCLOSURE BUILDING In preparation for a scheduled outage, maintenance personnel removed the upper and lower boots of the main steam safety valves. Upon discovery, Operations personnel declared the Enclosure Building inoperable. Maintenance re-installed the boots and the integrity of the Enclosure Building was restored and the building returned to service. The licensee notified the NRC Resident Inspector, the State of Connecticut, and the town of Waterford. | 0 | 46 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-04-05
50001 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-04-04 14:53 | 2014-04-04 22:12 | 2014-04-04 | SEISMIC MONITOR DECLARED NON-FUNCTIONAL DUE TO SPURIOUS ALARM "At 1453 CDT on April 04, 2014, the station's Seismic Monitor generated a seismic event alarm that was determined to be invalid based upon no recorded readings above alarm setpoint, no seismic activity being felt on site, and no activity detected by National Earthquake Information Center or Monticello Nuclear Generating Plant. The monitor was declared non-functional since it would not generate a control board seismic event alarm during an actual event until the invalid event was reset. This monitor has no credited compensatory measure that will allow timely classification of two Emergency Action Levels (EALs), NUE (Notification of Unusual Event) and Alert classifications when out of service. This results in a Loss of Emergency Assessment Capability while the Seismic Monitor is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Maintenance has reset the alarm and has evaluated the monitor's performance. The alarm has been determined to be spurious. The monitor is working properly and will generate a control board alarm during an actual event, as determined by observed normal operation and the lack of any self-diagnostic error messages. At 1900 CDT on April 04, 2014 the monitor was declared functional and returned to service. "There was no seismic activity during the out of service period indicated by the local seismic monitor display and no reports of seismic activity were reported to the site by National Earthquake Information Center or Monticello Nuclear Generating Plant. This event did not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-04
50000 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-03 | 2014-04-04 18:18 | 2014-04-04 | TEXAS AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following information was obtained from the State of Texas via email: "The licensee called to report that a radiography crew had damaged the source guide tube of their QSA 880D industrial radiography camera. The incident occurred at a temporary job site near Beeville, Texas. The crew was working in some elevated pipe racks and had used a rope to suspend the camera. The knot on the rope came loose, dropping the camera to the ground. The camera landed on the source guide tube crimping it and preventing the retraction of the radiography source which was extended into the collimator. A second radiography crew on the site secured their camera and placed it on the collimator to shield the source. The radiographers then called an RSO in Deer Park, Texas and another in Corpus Christi, Texas to get advice and instruction to secure the source. The crew then dragged the camera to a shielded location behind a concrete pillar. Two radiographer trainees were assigned to maintain a perimeter around the camera to prevent access by unmonitored individuals. The radiographers were able to use pliers to un-crimp the source guide tube and return the source to its shielded position." No radiography personnel received overexposures due to this event. Texas Incident # I-9177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-14
49999 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-04 | 2014-04-04 16:37 | 2014-04-04 | AGREEMENT STATE REPORT - CAMERA SOURCE DISCONNECT The following information was received by facsimile from the State of Texas: "On April 14, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee's Corporate Radiation Safety Officer (CRSO) that one of their radiography crews had experienced source disconnect while using an INC IR 100 exposure device. The device contains a 70 curie iridium - 192 source. The CRSO stated the radiographers had completed a shot and noted the dose rates on the camera had not returned to normal after retracting the source. The radiographers increased the barriers around the exposure device and contacted their supervisor for assistance. The CRSO stated the source had been recovered by an individual listed on their license to retrieve sources. The CRSO stated he did not believe any individual received an exposure which exceeded any limits. The CRSO stated no member of the general public received any exposure. The CRSO stated he had just learned of the event and was beginning his investigation and would provide the Agency with additional information as it was obtained. This Agency will provide additional information as it is received in accordance with SA-300." Texas Incident: I-9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-14
49998 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-04-04 13:15 | 2014-04-04 16:34 | 2014-04-04 | CRITICALITY ACCIDENT EVACUATION ALARM NOT AUDIBLE IN CERTAIN AREAS OUTSIDE THE MATERIAL HANDLING AREA "At approximately 1315 hours (Eastern Daylight Time) on April 4, 2014, while testing the audibility of the criticality accident evacuation alarm in the Building locker room, a report was made that the alarm could not be heard in an office trailer restroom. Subsequent testing confirmed the evacuation alarm could not be heard in the office trailer restroom when the fan was running. Safety management personnel were notified of the problem and other restrooms were tested. Testing revealed that the alarm was not able to be heard in three (3) additional office trailer restrooms. All affected restrooms were posted with signs indicating the areas are not to be occupied pending resolution of the audibility issue. It should be noted that the restrooms are located outside of the material processing areas. "The licensee notified the NRC Resident Inspector." See similar event EN #49848. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2014-04-08
49997 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-04-04 09:45 | 2014-04-04 12:13 | 2014-04-04 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PRE-PLANNED MAINTENANCE The Millstone Station Stack Radiation Monitor, RM-8169 was removed from service for pre-planned maintenance. This is reportable as a loss of assessment capability in accordance with 10 CFR 50.72 (b)(3)(xiii). RM-8169 was restored following pre-planned maintenance at 1150 EDT on 4/4/2014. The licensee notified the NRC Resident Inspector and applicable State and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-04
49996 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-04-04 08:00 | 2014-04-04 08:58 | 2014-04-04 | WIDE RANGE GASEOUS MONITORING SYSTEM REMOVED FROM SERVICE FOR GREATER THAN 72 HOURS "Nine Mile Point Unit 2 Ventilation Wide Range Gaseous Monitoring System was removed from service on 4/1/2014 at 1140 EDT to support isolation of the Unit 2 Reactor Building Ventilation during a Division 2 electrical bus outage. The monitoring system will be out of service for greater than 72 hours due to the planned maintenance window. "NMP2 is in Mode 5, refueling. Compensatory actions remain in effect in accordance with the Off-Site Dose Calculation Manual. Expected return to service is 4/5/14. "This event is being reported in accordance with 10 CFR 50.72 (b)(3)(xiii) due to a loss of assessment capability." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-04
49995 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2014-04-03 13:01 | 2014-04-03 17:08 | 2014-04-03 | AUTOMATIC REACTOR TRIP "At approximately 1301 [CDT] on 4/3/2014, Unit 2 tripped from 100% power for unknown reason(s). All Control Element Assemblies [CEA] inserted into the core. (Note that CEA 03 Plant Monitoring System indication still indicates fully withdrawn. However, CEA 03 in-limit light and control panel indication validate that CEA 03 is fully inserted.) 4160v bus 2A1 and 6900v bus 2H1 transferred to Startup Transformer #2. 4160v bus 2A2 appeared to de-energize and re-energize on Startup Transformer #3. 6900v bus 2H2 is de-energized. 2K4B emergency diesel generator started but did not tie onto the 2A4 4160v bus. Emergency Feedwater actuated on low steam generator level." Offsite power remains available and decay heat is being removed to the main condensers using the turbine bypass valves. Unit 1 was not affected. The licensee has notified the NRC Resident Inspector and will notify the State. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-04-03
49994 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-04-03 09:06 | 2014-04-03 13:54 | 2014-04-03 | EMERGENCY SIRENS DECLARED NONFUNCTIONAL "At approximately 0906 EDT, the Harris Nuclear Plant (HNP) offsite emergency sirens were identified to be nonfunctional. Troubleshooting was initiated and the offsite emergency sirens were restored and verified to be functional at 1127 EDT. This event requires an 8-hour non-emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. In the event that the sirens would have been needed, the State of North Carolina and all four counties within the 10-mile emergency planning zone would have implemented mobile route alerting, as detailed in the Emergency Plan. "The NRC Senior Resident Inspector was informed. There was no impact to public health and safety." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-04-03
49993 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-04-03 10:06 | 2014-04-03 11:43 | 2014-04-03 | OFFSITE NOTIFICATION DUE TO OIL SPILL ON SITE "At 0730 EDT on April 3, 2014, it was determined that approximately 40 gallons of turbine lube oil (MOBIL DTE 732) had been released to the ground from the Unit 1 Turbine Building. The release occurred during the process of depressurizing the Unit 1 main generator. The source of the leak was identified and secured. The area of the oil spill has been contained, [and] no oil reached storm sewers or surrounding waters. "Notification of the lube oil spill was made to the Underground Storage Tank Section of the North Carolina Division of Waste Management at 1006 hours EDT on April 3, 2014. This report is made in accordance with 10 CFR 50.72(b)(2)(xi) as an event related to protection of the environment for which notification to another government agency has been made. "This event did not result in any adverse impact to the health and safety of the public. "The safety significance of this event is minimal. There was no adverse impact to public health and safety. The area of the oil spill has been contained, no oil reached storm sewers or surrounding waters. Efforts are in progress to excavate the soil containing the lube oil. "The source of the lube oil leak was identified and secured. Efforts are in progress to excavate the soil containing the lube oil." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-03
49992 | -1 | UNIV OF TEXAS |  |  |  | 1100 KW TRIGA MARK II | 2014-04-02 11:25 | 2014-04-03 09:37 | 2014-04-29 | CONSOLE KEY LEFT UNATTENDED After performing routine maintenance and surveillance procedures, the reactor operator left the reactor control room for a rest break. During this break the reactor operator left the console key inserted and unattended in the console. Another operator came by and noticed that the key was in the console without the other reactor operator in the control room. The second reactor operator notified the reactor manager. The reactor manager immediately removed the key from the console. The reactor manager then suspended the first reactor operator's operating rights until corrective actions have been determined and implemented. During the time the key was unattended, all control elements were fully inserted. Based upon video review, the length of time the key was unattended was 14 minutes. The relevant Technical Specification to this situation is 6.1.3 (Staffing): the minimum staffing when the reactor is operating shall be one licensed reactor operator in the control room. The licensee notified NRC NPR (Adams and Bassett). * * * RETRACTION FROM MICHAEL KRAUSE TO DONALD NORWOOD AT 1934 EDT ON 4/29/2014 * * * "SUMMARY: After further review the facility has determined that the 'Unattended Key Left in Console' event originally reported as a reportable occurrence was indeed not a reportable occurrence and retracts the official notice, changing the notification to a for your information only as was discussed with the facility NRC Project Manager Alexander Adams in a call following the notification. "DETAILS: On April 2, 2014, after the reactor had been shutdown for an extended period due to maintenance repairs, an operator was performing surveillance / maintenance activities which required the console key to be inserted into the reactor control system. The maintenance was done with the reactor in the shutdown mode with the reactor subcritical by more than $1.00. After a portion of the maintenance was completed, the operator left the control room for a short break and did not remove the reactor key from the console before leaving the room. All control rods were fully down at the time the operator left the room and remained in that condition for 14 minutes until the key was removed from the console by the reactor manager. A review of video surveillance confirmed the reactor remained shutdown while the key was unattended. The facility does not normally leave the key unattended in the control console so the initial response was to report this event as a reportable occurrence based on the Standard English Dictionary definition of shutdown. A follow-up review of the requirements in the Technical Specification Section 6.1.3 required a licensed operator in the control room when the reactor was not 'Shutdown', with 'Shutdown' defined in Technical Specification Section 1.19 as the reactor subcritical by at least $1.00. Since the reactor was clearly shutdown based on the Technical Specification definition, the report of a reportable occurrence is hereby retracted and the notification can be interpreted as a for your information notice only. Nonetheless, the operator who left the key in the console was given retraining and review by the reactor manager prior to being allowed to resume licensed activities since his actions had come very close to a Technical Specification violation." Notified R4DO (Haire), and NRC NPR (Adams and Schoenebeck). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | TX | NPR | [5 empty] | 0 | 2014-04-03
49991 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-03 01:00 | 2014-04-03 02:44 | 2014-04-03 | REACTOR COOLANT SYSTEM SAFETY INJECTION LINE ULTRASONIC TEST INDICATION "On Tuesday, April 1, 2014, while performing planned inspections of Reactor Coolant System piping welds, two flaw indications were identified on a 1.5 inch Safety Injection Line connection to the Reactor Coolant System piping. On Wednesday, April 2, 2014, after confirmatory inspections and evaluation, one of the two flaw indications was determined to not meet the acceptance criteria specified in ASME Code Section XI. As such, this indication is reportable under 10 CFR 50.72(b)(3)(ii) as a degraded condition. A repair plan is being developed. There is no impact on current Unit 2 refueling operations. This condition and repair have no impact to the health and safety of the public or employees. "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-04-03
49990 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-04-02 16:00 | 2014-04-02 21:08 | 2014-04-02 | FIRE RELATED UNANALYZED CONDITION THAT COULD IMPACT CREDITED SAFE SHUTDOWN ANALYSIS "This is a non-emergency notification. As part of converting to NFPA (National Fire Protection Association) 805, Catawba determined that there are conditions that may not ensure required equipment remains available under certain postulated fire scenarios. The determination concluded that the effects of a postulated fire in specific fire areas could prevent critical systems or components from performing their intended functions, potentially resulting in the inability to achieve and maintain safe shutdown. "Affected fire areas are as follows (elevation numbers are in parentheses): 1. Residual Heat Removal/Containment Spray Pump Room (522) 2. Unit 2 Auxiliary Feedwater Pump Room (543) 3. Unit 1 Auxiliary Feedwater Pump Room (543) 4. Auxiliary Building Common Area (543) 5. Unit 2 Electrical Penetration Room (560) 6. Unit 1 Electrical Penetration Room (560) 7. 2ETB Switchgear Room (560) 8. 1ETB Switchgear Room (560) 9. Unit 2 Battery Room (554) 10. Unit 1 Battery Room (554) 11. Auxiliary Building Common Area (560) 14. Unit 2 ETA Switchgear Room (577) 15. Unit 1 ETA Switchgear Room (577) 17. Unit 1 Cable Room (574) 18. Auxiliary Building Common Area (577) 20. Unit 1 Electrical Penetration Room (594) 45. Unit 1 Cable Room Corridor (574) 46. Unit 2 Cable Room Corridor (574) 48. Unit 2 Inside Doghouse 49. Unit 1 Inside Doghouse RB1. Unit 1 Reactor Building RB2. Unit 2 Reactor Building "This is reportable as an unanalyzed condition that significantly degrades plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). Fire watches have been implemented as appropriate in response to this determination. This condition has been entered into the Catawba Corrective Action Program. "The NRC Resident Inspector will be notified." The licensee will notify the State of North Carolina and South Carolina and well as the local counties. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-04-02
49989 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-04-02 | 2014-04-02 17:21 | 2014-04-02 | AGREEMENT STATE REPORT - STUCK SHUTTER ON TWO NUCLEAR GAUGES The following information was received from the State of Texas via email: "On April 2, 2014, the licensee notified the Agency [Texas Department of Health] that earlier that morning, while it was doing lockouts on fixed nuclear gauges in preparation for the annual shutdown of its facility, the handles on two shutters broke. The handles sheared their roll pins. The two gauges are mounted on digesters and are used for level control. The licensee was able to close one of the shutters, but the other shutter remains stuck in the open position. There is no exposure risk to any person. The licensee contacted a service company and arrangements have been made for the company to come on-site and make repairs next week. "Device #1 Information: Kay Ray, Model 7063, 1.5 curies cesium-137 (original activity in 1972) "Device #2 Information: Kay Ray, Model 7063P, 1.0 curie cesium-137 (original activity in 1972) "Further information will be provided per SA-300 as it is obtained." Texas Incident #: I-9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-10
49988 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2014-04-02 13:40 | 2014-04-02 15:32 | 2014-04-02 | ALERT DECLARED DUE TO FIRE IN UNIT 2 TURBINE BUILDING "Quad Cities Unit 2 Alert Classification (HA3) Due to Fire. "On April 2, 2014, at 1340 CDT, an ALERT was declared due to a fire in the Unit 2 turbine building. Prior to declaring the ALERT, Unit 2 was manually scrammed at 1302 CDT. All control rods inserted and all automatic isolations actuated as designed. The Main Steam Isolation Valves were manually closed. The fire has been extinguished. Unit 2 is currently in Hot Shutdown. "The cause of the event is under investigation. "Unit 1 remains at 100% power. "The Senior Resident Inspector has been notified of the event." Unit 2 is still being supplied from off-site power and is in a normal shutdown electrical lineup with the exception of Bus 29-1 (480 VAC safety bus) that was deenergized. One Unit 2 emergency diesel generator is inoperable due to the loss of power to its cooling water pump. The licensee has notified the State and local agencies. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email. * * * UPDATE FROM MIKE HAYES TO DONG PARK AT 2252 EDT ON 04/02/2014 * * * At 2132 CDT on April 2, 2014, the licensee terminated the Unit 2 Alert declaration. Unit 2 is stable in Mode 3 (Hot Shutdown). Unit 2 is proceeding to Mode 4 (Cold Shutdown) on shutdown cooling. The licensee notified the NRC Resident Inspector and the State emergency agencies. Notified the IRD (Gott), R3DO (Passehl), and NRR EO (McGinty). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2014-04-02
49987 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-04-02 14:01 | 2014-04-02 14:42 | 2014-04-05 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS RELEASE "Release of toxic or flammable gas affecting the Protected Area boundary deemed detrimental to the safe operation of the plant." Emergency Action Level entered: MU-1. The leak is Trichloroethylene (TCE) gas used in the Off-Gas building. The Off-Gas building ground and basement levels were evacuated due to the leak. There is no safe-shutdown equipment located in the Off-Gas building. The licensee is working to isolate the leak. The licensee informed the NRC Resident Inspector. The licensee notified the State of Ohio and the local counties. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, DOE Ops Center, USDA Ops Center, HHS Ops Center, and Nuclear SSA via email. * * * UPDATE AT 1630 EDT ON 4/2/14 FROM DON ROGERS TO S. SANDIN * * * The licensee notified the following outside agencies: U.S. EPA National Response Center, Ohio EPA, Perry Township Fire Department, Lake County Emergency Planning Committee, and the U.S. Coast Guard. Notified R3DO (Passehl). * * * UPDATE FROM MICHAEL ADLER TO DANIEL MILLS AT 0115 EDT ON 04/05/2014 * * * "Unusual Event has been terminated on 4/5/2014 at 0059 EDT. The trichloroethylene leak has been stopped. Access has been restored to all normally accessible areas." Unit 1 remains in Mode 1 at 100% power. The licensee notified the NRC Resident Inspector and the Local and State emergency agencies. Notified the IRD MOC (Gott), R3DO (Passehl), and NRR EO (McGinty). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA OPS Center, EPA EOC, FDA EOC, and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2014-04-02
49986 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2014-04-01 09:00 | 2014-04-02 14:25 | 2014-04-02 | AGREEMENT STATE REPORT - BROKEN I-125 SEED DURING IMPLANTATION The following information was received from the State of Maryland via email: "This is a synopsis of an I-125 seed breaking during an implant procedure at GBMC [Greater Baltimore Medical Center]. We [GMBC] will be meeting as a team to discuss corrective action and how to avoid something like this happening again. "An I-125 implant was performed at GBMC Hospital on Tuesday, April 1, 2014. 78 Bard I-125 seeds, activity 0.319 mCi/seed, were ordered for the procedure, 71 seeds were used, and 70 seeds were confirmed after the procedure on CT evaluation in Radiation Oncology. The unused seeds (7.5 seeds) were returned to Radiation Oncology and recorded as per policy and procedure. "The chief physicist and dosimetrist were called to Cysto at approximately 0900 EDT when the case was completed to [the attending physician's] satisfaction. Upon entry of the Cysto room [the attending physician] informed the physics staff that a seed had jammed in the Mick applicator and he had to use force to continue and complete the case. "On arrival, the physics staff surveyed the patient 1 meter above the umbilicus and found 1.7 mR/hr reading using Model 14C Geiger counter (Serial number 167038, Calibration date 1/30/14). The patient was removed from the OR and sent to recovery room. "Upon additional survey of the room, it was discovered that a seed was fractured, when a portion of the seed was found on the sterile table. At that time, a thorough and complete area survey was performed. The reading was found to be 1.2 mR/hour on the table, trash, and blood drain. [A staff member] was called to bring an additional survey meter (Model 3 Geiger counter Serial number 39484, Calibration date 4/29/13). All contaminated items were collected for proper storage in the hot lab in Radiation Oncology. All staff and personnel involved in the case were thoroughly monitored and cleared using 14C Geiger counter (Serial number 167038, Calibration date 1/30/14). After the removal of the contaminated items the Cysto room was thoroughly monitored and clear of radiation contamination. "The patient was then brought down to the Radiation Oncology department where a CT scan was performed to ensure seed count. VeriSeed program was used to confirm that the patient was implanted with 70 seeds. "[The Chief Medical Physicist] contacted Bard to discuss the shattered seed. It was suggested that radiation oncology staff be monitored for thyroid uptake. Bioassay studies were thereby performed and the results were found to match background readings. "On Wednesday, April 2, 2014, the patient's recovery area was scanned using Model 3 Geiger counter Serial number 39484, Calibration date 4/29/13. A reading of 300 CPM was recorded. The background was also recorded to be 300 CPM. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2014-04-10
49985 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-04-02 01:23 | 2014-04-02 08:42 | 2014-04-02 | SECONDARY CONTAINMENT INOPERABLE DUE TO TWO AIR LOCK DOORS OPEN SIMULTANEOUSLY "At 0123 EDT on April 2, 2014, Nine Mile Point Unit 2 was in Mode 5, Refueling, and in the other specified condition of Operations with Potential for Draining the Reactor Vessel. During this condition both redundant personnel airlock doors were open at the same time in an airlock penetration of the reactor building. This condition represents a loss of Secondary Containment safety function. Technical Specification 3.6.4.1, Action A.1 was entered for the loss of Secondary Containment and was promptly exited when the doors were closed. "Secondary containment being inoperable is an 8-hour report per 10 CFR 50.72(b)(3)(v)(C), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-02
49984 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-04-01 13:57 | 2014-04-01 18:39 | 2014-04-01 | UNIT 2 SECONDARY CONTAINMENT INTERLOCKED DOORS OPENED SIMULTANEOUSLY "On April 1, 2014, at 1357 hours, the Control Room was notified that two Secondary Containment interlock doors (between the Unit 2 Reactor Building and Unit 2 Turbine Building) were open simultaneously. The doors were immediately closed and Secondary Containment pressure remained negative. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open simultaneously. As a result entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to Secondary Containment being inoperable. "This event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-04-01
49983 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-11-12 09:30 | 2014-04-01 15:47 | 2014-04-01 | AGREEMENT STATE REPORT - CAMERA FAILED TO RETRACT SOURCE PROPERLY The following information was received from the State of Texas via email: "On March 26, 2014, the Agency [State of Texas - Department of State Health Services] received information that a source disconnect had occurred in November of the previous year. A subsequent report from the licensee received April 1, 2014 indicates that the disconnect occurred on November 12, 2013 at a temporary field site just west of Wink, Texas. The drive cable had become worn, allowing the source to be pushed out without being fully engaged with the pigtail. The source was pushed out of the guide tube but did not retract when the drive cable was cranked in. The camera was a QSA Model 880D S/N D6125, source QSA Global model A424-9 Ir-192 at 66.7 Ci, S/N 99589B. The source was recovered without further incident by attaching another drive cable. No exposure to the public resulted form this event. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident Number: I-9174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-09
49982 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-04-01 06:45 | 2014-04-01 14:02 | 2014-04-02 | VENTILATION FAN FAILURE AFFECTING RHRSW/ESW PUMP OPERABILITY AND EDG OPERABILITY "At 0645 EDT on the morning of April 1, 2014, with James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, the Control Room received an alarm associated with the ventilation system for the 'B' division of the Residual Heat Removal Service Water (RHRSW) and Emergency Service Water (ESW) pump room. Investigation identified that the ventilation exhaust fan (73FN-3B) associated with this pump room had tripped due to thermal overload. The overload relay was reset at 0704 EDT and the fan automatically started; the fan is currently operable. During this period, the fan would not have automatically started. "The ventilation systems for the RHRSW and ESW pump rooms are not included in the JAF Technical Specifications (TS), nor are they in the JAF Technical Requirements Manual (TRM). The ambient temperature limit in the RHRSW and ESW pump room was never challenged. However, with 73FN-3B non-functional, it is procedurally required to declare 10P-1B (RHRSW Pump B), 10P-1D (RHRSW Pump D) and 46P-2B (ESW Pump B) inoperable. The 'B' ESW pump cools the 'B' EDG subsystem, which would therefore also be inoperable. During this period, the 'A' EDG subsystem was inoperable for an emergent issue. Because the 'A' and 'B' EDG subsystems were concurrently inoperable for a period of approximately 45 minutes, this condition resulted in a loss of safety function for the Emergency Diesel Generators, which is reportable pursuant to 10 CFR 50.72(b)(3)(v)(A)." Both affected emergency diesel generators were in the same division with another redundant division operable. The licensee notified the NRC Resident Inspector and will be notifying the State of New York. * * * UPDATE AT 1200 EDT ON 4/2/14 FROM CHRIS ADNER TO S. SANDIN * * * The statement "Both affected emergency diesel generators were in the same division with another redundant division operable" is incorrect. Both divisions of emergency diesel generators were inoperable, since one of two available emergency diesel generators per division were inoperable at the time of this event. The Licensee notified the NRC Resident Inspector. Notified R1DO (Cahill). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2014-04-01
49981 | 0 | PATRIOT ENGINEERING AND ENVIRONMENT |  |  |  |  | 2014-04-01 07:30 | 2014-04-01 11:50 | 2014-04-01 | THEFT OF SEAMAN MODEL C-200 NUCLEAR DENSITY GAUGE A technician for Patriot Engineering and Environmental, Inc. took possession of a Seaman Model C-200 (Serial # L-102) nuclear density gauge on the evening of 3/31/2014 for use at a jobsite the next day. He secured the gauge in the back of his pickup truck with a chain and 3 padlocks. Two of the padlocks secured the gauge to the bed of the pickup truck and the third padlock secured the wrapped chain to the device. Between 0100 EDT and 0730 EDT on the morning of 4/1/2014, the gauge was stolen from the back of the pickup truck. Indianapolis Metro Police Department was contacted and they are investigating. The gauge contains 4.5 mCi of Radium 226 (Source Serial # B8633) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-04-09
49980 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-04-01 06:16 | 2014-04-01 10:06 | 2014-04-01 | OFFSITE NOTIFICATION DUE TO FATALITY ON SITE "At approximately 0616 CDT on April 1, 2014, a supplemental employee at Wolf Creek developed a personal medical condition. Wolf Creek Emergency Medical Technicians on site responded and an ambulance transported the individual to an offsite hospital. The individual was located in one of the office areas inside the protected area. The offsite hospital declared the individual deceased upon arrival on April 1, 2014. "The individual was outside the Radiological Controlled Area. No radioactive material or contamination was involved. This notification is being performed in accordance with 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The licensee will notify the State and Coffey County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-04-01
49979 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2014-04-01 00:26 | 2014-04-01 02:44 | 2014-04-01 | AUTOMATIC REACTOR TRIP DUE TO ELECTRICAL ISSUE "At 0026 on 04/01/2014, following the turbine shutdown and removal of the main generator from service in preparation for refueling outage 16, Seabrook had a reactor trip and all control rods were fully inserted. The trip was caused by an electrical issue that caused 345 KV bus 6 to deenergize and power was lost to the Unit Auxiliary Transformers (UATs). The in-house busses transferred to the Reserve Auxiliary Transformer (RAT) supplies and the momentary loss of power to in-house Bus 1 caused 2 reactor coolant pumps to trip, generating a 2 loop loss of flow reactor trip signal. The exact cause of the initiating electrical issue is being investigated. "The NRC Resident Inspector has been notified. "Emergency feedwater actuated at 0035 due to a low low water level in steam generator 'C'. Plant equipment response is being evaluated and the plant is stabilized in Mode 3 with decay heat removal through the steam dump system to the condensers. There was no release and the emergency feedwater system is being restored to standby. "The event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73." | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-04-01
49978 | 0 | WATERFORD | 3 |  |  | [3] CE | 2014-03-31 15:58 | 2014-03-31 20:30 | 2014-03-31 | LOSS OF SIX EMERGENCY SIRENS "At approximately 15:58 hours (CDT) on March 31, 2014, Waterford 3 was informed that five emergency sirens were inoperable during the performance of a monthly siren inspection. Subsequent review during preparation of this notification has identified an additional one inoperable siren, which brings the total number of inoperable sirens to six. There are a total of seventy-three sirens distributed among two parishes (counties). The loss of these six sirens for more than one hour is considered a major loss of offsite response capability and is reported pursuant to 10 CFR 50.72(b)(3)(xiii). "The affected parish Emergency Operations Center was notified of the condition and it was confirmed that they will use the preplanned alternative method of Route Alerting for the affected areas until notified that repairs to the sirens have been completed. "Waterford 3 has initiated preparations to repair the sirens, with actual repairs expected to commence tomorrow. The performance of the monthly siren inspection will continue during daylight hours today and resume tomorrow. There is no effect on the plant. This issue has been entered into the Waterford 3 Corrective Action Program and appropriate corrective actions will be developed. "The NRC Resident Inspector and local agencies were notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-31
49977 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2014-03-31 13:02 | 2014-03-31 18:57 | 2014-03-31 | UNIT 2 REACTOR PRESSURE BOUNDARY LEAKAGE AND UNIT SHUTDOWN "On March 31, 2014, at 1302 [CDT], with Unit 2 operating in Mode 1 (coastdown), leakage was identified from the body of a one inch isolation valve associated with a Control Rod Drive Hydraulic Control Unit (CRD HCU 18-27 insert valve 101). The leakage is several drops per minute; attempts to isolate the leak have been unsuccessful. The associated piping communicates with the reactor coolant system (through the CRD mechanism). "Technical Specification 3.4.4 (RCS Operational Leakage), Condition C, was entered at 1302 hours. Condition C requires the unit to be placed in Mode 3 (Hot Shutdown) in 12 hours. At 1616 hours, a Technical Specification required shutdown was initiated on Unit 2. "The cause and resolution of the leakage are being pursued. "This condition is being reported under 50.72(b)(3)(ii)(A) given the defect is associated with the primary coolant system pressure boundary. This notification is also being made in accordance with 10 CPR 50.72(b)(2)(i) given the initiation of a plant shutdown required by the plant Technical Specifications." The licensee has notified the NRC Resident Inspector. | 0 | 54 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2014-03-31
49976 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-18 | 2014-03-31 16:40 | 2014-04-03 | AGREEMENT STATE - DISCOVERED I-125 SOURCE MISSING FOLLOWING SURGERY The following information was received from the State of Texas via email: "UT Southwestern, RSO called to report that an I-125 seed implant [135 mCi] had been lost during a breast implant procedure on 03/18/14. The treatment staff did not notify Radiation Safety until 03/26/14. The room had been cleaned before Radiation Safety had a chance to search. [The] RSO will provide more details in his written report." Texas Incident #: I-9173 * * * UPDATE ON 4/3/14 AT 1529 EDT FROM ARTHUR TUCKER TO DONG PARK * * * The following information was received from the State of Texas via email: "On April 3, 2014, the Agency [Texas Department of Health] contacted the licensee to confirm the activity of the missing I-125 seed. The licensee's Radiation Safety Officer stated the activity was 135 microcuries. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Gepford), FSME Events Resource, and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-08
49975 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2014-03-28 21:10 | 2014-03-31 14:44 | 2014-03-31 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION -- UNUSUAL EVENT DUE TO SEISMIC EVENT "On March 28, 2014 at 2110 PDT, station staff felt a minor seismic event, which was verified on the NEIC [National Earthquake Information Center]. On-shift staff reviewed basis documentation and EAL [Emergency Action Levels] classification, and concluded the event was below the threshold to classify the event. "During post event reviews [conducted on 3/31/2014], it has been determined that those events met the classification criteria for declaration of a Notification of Unusual Event for a seismic event as specified by the Emergency Plan. No emergency situation exists at this time." Site personnel did perform the steps of the Earthquake abnormal operating procedure even though the entry requirements were not met. There were no plant or equipment issues identified during the site walk downs. The licensee has notified the NRC Resident Inspector, the State of California and other Local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-03-31
49974 | 0 | GE-HITACHI NUCLEAR ENERGY |  |  |  |  | 2014-03-31 | 2014-03-31 09:07 | 2014-08-29 | INTERIM PART 21 REPORT - CONTAINMENT LOADS POTENTIALLY EXCEED LIMITS WITH HIGH SUPPRESSION POOL WATER LEVEL IN THE ABWR DESIGN The following summary was excerpted from GE Hitachi Interim Part 21 Report received via email: "A potential analysis error has been identified that is associated with the ABWR (Advanced Boiling Water Reactor) hydrodynamic loads determined by using the Technical Specification Suppression Pool High Water Level (HWL) as an analysis input condition. Vessel coolant inventory is transferred into the containment Suppression Pool during a postulated LOCA blowdown, thereby increasing the Suppression Pool water level. The correction in the analysis may lead to a Suppression Pool water level greater than what is currently assumed in structural analyses which apply the containment hydrodynamic loads generated during a postulated LOCA event." Facility Identification: South Texas Project Units 3 and 4, Clinton ESP Site, Grand Gulf ESP Site, North Anna ESP Site, and includes the ESP application for the PSEG Site and Victoria County Station ESP application. If you have any questions, then contact: Dale E. Porter, GE-Hitachi Nuclear Energy Americas LLC, Ph. #(910) 819-4491. * * * UPDATE AT 1343 EDT ON 06/26/14 FROM JIM HARRISON TO S. SANDIN VIA EMAIL * * * "June 26, 2014 "MFN 14-013 R1 "This letter provides supplemental information concerning an evaluation being performed by GE Hitachi Nuclear Energy (GEH) regarding the potential increase in hydrodynamic loads that may be experienced by containment structures during a postulated Loss of Coolant Accident (LOCA) associated with Reference 1, and requests additional time to complete the evaluation for the determination of reportability of this condition. "A potential analysis error has been identified that is associated with the ABWR hydrodynamic loads determined by using the Technical Specification Suppression Pool High Water Level (HWL) as an analysis input condition. Vessel coolant inventory is transferred into the containment Suppression Pool during a postulated LOCA blowdown, thereby increasing the Suppression Pool water level. The correction in the analysis may lead to a Suppression Pool water level greater than what is currently assumed in structural analyses which apply the containment hydrodynamic loads generated during a postulated LOCA event. For example, a postulated Feedwater Line Break (FWLB) may transfer a large quantity of FW liquid into the Suppression Pool with a notable increase in pool water level, even assuming a portion of the discharged fluid spills over into the lower drywell region of the ABWR containment. A higher Suppression Pool water level may result in increased hydrodynamic loads acting on the submerged walls and structures in the containment. The higher Suppression Pool water level can extend the wetted regions of the Suppression Pool walls and the ABWR access tunnel, as well as result in wetted submerged structure segments that were not previously considered wetted. This potential analysis error affects the LOCA containment hydrodynamic loads including condensation oscillation (CO) and chugging, as well as Safety Relief Valve (SRV) actuation loads. "Assessing the overall impact of increased hydrodynamic loads calculated with higher Suppression Pool water level requires an evaluation of the containment structural components' design bases. GEH is in the process of examining revised containment loads, and determining available margin in the ABWR containment component design specifications to accommodate potentially increased load source forcing functions. ABWR plants may then compare affected plant-specific containment structural design bases to these specifications for relative margin. An extended time period is needed in order to complete the revised containment load determination and evaluate the impact on containment structures. "GEH is requesting additional time to complete the analysis previously noted in Reference 1. The information required for this GEH 60-Day Interim Report Notification per 21.21(a)(2) is provided in Attachment 1. The commitment for follow-on actions is provided in Attachment 1, item (vii). "If you have any questions, please call me at (910) 819-4491. "Sincerely, "Dale E. Porter Safety Evaluation Program Manager GE-Hitachi Nuclear Energy Americas LLC" Notified R2DO (Rich) and Part 21 Reactor Group via email. * * * UPDATE FROM LISA SCHICHLEIN TO JOHN SHOEMAKER AT 0745 ON 8/29/14 VIA EMAIL * * * "August 29, 2014, MFN 14-013 R2, Specification 000N7289-R2 "When considered with the realistic assumptions and the lowered scale factors, the condition reported in Reference 1 [of the final report] is determined as non-reportable, and there is no Substantial Safety Hazard nor will it lead to exceeding a Technical Specification Safety Limit for the affected plants and plant designs. The GEH evaluation within 10 CFR Part 21 is now closed." If you have any questions, please call; Dale E. Porter Safety Evaluation Program Manager GE-Hitachi Nuclear Energy Americas LLC Ph. (910) 819-4491. Notified R2DO (Rose) and Part 21 Reactor Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-03-31
49973 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2014-03-29 16:20 | 2014-03-29 23:49 | 2014-03-30 | DIVISION 3 CORE STANDBY COOLING SYSTEM VENTILATION FAILED "This report is being made pursuant to SAF 1.8, 10 CFR 50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During steady state operations on Unit 1 at 1620 [CDT] hrs. on 3/29/14, the Division 3 Core Standby Cooling System (CSCS) Pump Room, SWGR Room, and Battery Room Ventilation failed in such a manner that heat could not be removed from the rooms. These Division 3 systems supply power and cooling water to the High Pressure Core Spray system (HPCS), which is a single-train system. The HPCS system and its associated power supplies were declared inoperable based on long-term temperature considerations. The system remains available due to manual damper adjustments that than can be made per an approved procedure." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-03-30
49972 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2014-03-29 10:08 | 2014-03-29 14:09 | 2014-03-29 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "Actuation of RPS with reactor critical. Reactor Scram occurred at 1008 [CDT] on 03/29/2014 from 87% CTP [core thermal power]. The cause of the Scram appears to be a Turbine Generator Trip. "05-S-01-EP-2 RPV Control, 05-1-02-I-1 Reactor Scram ONEP and 05-1-02-l-2 Turbine Generator Trip ONEP were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS [emergency core cooling systems] initiation signals were reached and no ESF or Diesel Generator initiations occurred. "All control rods are fully inserted. MSIVs [main steam isolation valve] remained open and no SRVs [safety relief valves] lifted. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band and reactor pressure is being controlled via Main Turbine Bypass Valves to the main condenser. There are no challenges to Primary or Secondary Containment at this time." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-03-29
49971 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-26 | 2014-03-28 18:28 | 2014-07-22 | AGREEMENT STATE REPORT INVOLVING A STOLEN THERMO NITON DEVICE USED IN METAL ALLOY IDENTIFICATION The following information was provided by the State of Texas via email: "On March 28, 2014, the Agency [Texas Department of State Health Services] received a letter from the licensee Radiation Safety Officer (RSO) stating they had determined a Thermo Niton device model number XLP-8182 containing 30 millicuries of Americium- 241 had been stolen by one of their employees. The employee had been sent to the country of Mexico with the device to analyze materials for purchase by their company. The RSO stated when they had gone several weeks without contact with the employee they began trying to locate him. The RSO stated they had not located either the employee or the device. The RSO stated he did not believe the individual had come to any harm in Mexico, but stated they had heard the employee had bought a new home in the State of Arizona and was probably there. The licensee has contacted local law enforcement. The RSO stated they did not believe any individual would receive any exposure due to this event. The Agency will contact the State of Arizona's program on March 31, 2014. Additional information will be provided as it is received in accordance with SA-300." The device is used to identify metal alloys. Texas Incident #: I-9172 * * * UPDATE AT 1147 EDT ON 07/22/14 FROM ART TUCKER TO S. SANDIN * * * The following information was provided by the State of Texas via email: "This update is provided to correct the licensee's name, the model number of the device and provide additional information. The Company's name is CNA Metals Inc. and not CAN Metals as initially reported. The model number for the device is XLP 818Q and not XLP 8182 as initially reported. During the Agency's investigation, the licensee stated they had not authorized the individual to take the device into the country of Mexico. The licensee has no information that confirms the device entered the country of Mexico. Additional information will be provided as it is received in accordance with SA 300." Notified R4DO (Miller), ILTAB (email), FSME Events Resource (email) and Mexico (fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-04-07
49970 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-03-28 13:58 | 2014-03-28 17:21 | 2014-03-28 | FAILURE OF SECONDARY CONTAINMENT DOOR INTERLOCK "At 1358 [CDT] on March 28, 2014, the Control Room was notified that two Secondary Containment doors (DOOR-62 and DOOR-63) were open at the same lime. This occurred while two employees were entering and exiting the Reactor Building at the exact same time. The time that both doors were open was approximately one (1) second. Secondary Containment differential pressure was maintained throughout the event. "With both doors open, technical specification surveillance requirement SR 3.6.4.1.3 was not met and Secondary Containment was declared inoperable. Secondary Containment was declared operable after independently verifying at least one Secondary Containment access door was closed. "The health and safety of the public was maintained as the plant was in a normal condition with no initiating event in progress or signs or elevated radiation levels within Secondary Containment. The NRC Resident Inspector has been notified." | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-03-28
49969 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2014-03-28 13:30 | 2014-03-28 16:45 | 2014-03-31 | ITEMS RELIED ON FOR SAFETY NOT OPERABLE "It was determined at 1:30PM today (3/28/14) that one of the Items Relied on for Safety (IROFS) associated with the Dry Conversion Process recycle operation was inoperable. Although the second IROFS preventing moderation intrusion to the recycle container continued to operate within its allowable parameters, it alone was not sufficient to meet performance requirements. "The affected equipment has been shut down and at no time was an unsafe condition present. While this did not result in an unsafe condition, the event is being reported pursuant with the reporting requirements of 10CFR70 Appendix A (b)(2) within 24 hours of discovery. "Additional corrective actions, extent of condition, and the cause of the failure are being determined." The licensee will notify NRC Region 2, State of North Carolina Radiation Protection, and New Hanover County Emergency Management. * * *UPDATE PROVIDED BY SCOTT MURRAY TO JEFF ROTTON AT 1219 EDT ON 03/31/2014 * * * "After further review, it was determined, at approximately 1125 EDT on 3/31/2014, that the second IROFS [mentioned in the initial report] was not reliable to meet performance requirements. As a result, the report is amended as follows: "The second IROFS preventing significant moderator intrusion to the recycle container was available, but its reliability could not be confirmed. The control continued to limit significant moderator intrusion and an unsafe condition did not exist. The remaining IROFS was not sufficient to meet performance requirements. "As a result, the event report is being conservatively amended pursuant with the reporting requirements of 10CFR70 Appendix A (a)(4) within 1 hour of discovery." The IROFS that was inoperable in the initial report was a process flow moisture probe. The second IROFS that was believed to be available in the initial report but later determined to not be reliable was a set of process control valves used to prevent moderation intrusion to the recycle container. The licensee will notify NRC Region 2, State of North Carolina Radiation Protection, and New Hanover County Emergency Management. Notified R2DO (Sykes) and NMSS EO (Rahimi) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | ALL SAFETY ITEMS UNAVAILABLE | [8 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) | PART 70 APP A (a)(4) |  |  | 0 | 2014-03-28
49968 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2014-03-28 13:00 | 2014-03-28 16:21 | 2014-03-28 | KEOWEE EMERGENCY POWER SYSTEM 13.8kV CABLE MAY NOT COMPLY WITH LICENSING BASIS "Event: In an NRC Component Design Basis Inspection (CDBI) debrief held at 1300 EDT on March 28, 2014, it was stated that a potential non-compliance and unanalyzed condition exists with respect to the design and installation of the Keowee emergency power system 13.8kV power cables associated with the underground power path. The NRC stated that Duke does not have sufficient documentation to support the station's position that the cables comply with the station's licensing basis. In particular, there are questions related to the station's compliance with IEEE-279-1971. This issue has been documented in Duke's corrective action program. "Duke has reviewed the design associated with the subject 13.8kV cables and considers the design to be robust. Pending further analysis and/or testing, Duke has made a decision to report this event in accordance with 10 CFR 50.72(b)(3)(ii) as an 'Unanalyzed Condition.' The Oconee NRC Senior Resident Inspector has been notified of the event. "Initial Safety Significance: An Immediate Determination of Operability has been performed and concluded the existing system design is adequately robust to address circuit faults. The health and safety of the public and station personnel is not impacted by this event. "Corrective Action(s): Corrective actions are being implemented in accordance with Duke's Corrective Action Program." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-28
49967 | 0 | C&D TECHNOLOGIES INC |  |  |  |  | 2012-02-14 | 2014-03-28 13:02 | 2014-10-28 | INTERIM PART 21 REPORT - MISALIGNED SEPARATORS IN LCR-25 STANDBY BATTERIES The following is the summary portion of the report submitted by fax: "Subject Interim Report - Inability to Complete 10CFR Part 21 Evaluation Regarding Misaligned Separators in LCR-25 Standby Batteries "The purpose of this letter is to provide the NRC a report in general conformity to the requirements of 10CFR Part 21.21 (a)(2). On February 14, 2012 C&D Technologies, Inc. ('C&D') was informed by Entergy Operations that an LCR-25 battery installed at the Palisades Nuclear Power Plant had shown signs of misaligned separators (also known as shifted separators) of between 1/8 to1/4 [inch]. This was identified by the Palisades plant on or about November 4, 2011. On January 16, 2012, three additional cells were identified as experiencing separator misalignment. "C&D requested that Palisades return the affected batteries for evaluation of this anomaly and issued a Return Material Authorization for that purpose. But since voltage readings were acceptable for all units involved, Palisades determined that an operability issue did not exist and opted to keep the batteries in service until their refuel outage scheduled for Fall, 2013. C&D inadvertently closed the internal corrective action without providing an Interim Report as required by 10CFR, Part 21. "C&D has not performed a root cause technical evaluation to determine if there is any defect in the component or manufacturing process or whether the reported condition may have been due to user abuse of product, improper maintenance or other negligence or error. "Thus, C&D is submitting this interim report to the NRC and notifying C&D's customers that use C&D LCR-25 batteries of this interim report, and is initiating an action plan to evaluate the reported potential defect and determine whether it could pose a substantial safety hazard for any U.S. licensee using such batteries. "If you have any questions or wish to discuss this matter or this report, please contact: Robert Malley VP Quality and Process Engineering bmalley@cdtechno.com (215) 619-7830" The sites affected are: Palisades - 65 x LCR-25 NUC Batteries and, Crystal River - 4 x LCR-25 NUC Batteries * * * UPDATE FROM LARRY CARSON TO JOHN SHOEMAKER AT 1122 EDT ON 09/16/14 * * * The following was excerpted from the final report received from C&D Technologies, Inc. via facsimile: "Conclusion: The conclusion drawn from the return and analysis is that the misaligned separator was present from the time of assembly in the C&D facility through installation and initial operation. "Recommendations: C&D recommends that operators of nuclear batteries perform an inspection of their batteries to detect misaligned separators. Inspection may be performed visually, and with the aid of mirrors as necessary. "Corrective Actions: C&D has enhanced both in process and final battery inspection processes to detect and eliminate misaligned separators from shipment. C&D is also preparing an enhanced incoming inspection work form for nuclear battery operators that will better enable the operators to detect and segregate batteries with misaligned separators from use. "Further Reporting: No further reporting is anticipated. "C&D Contacts: Further information on this issue can be obtained from: "Larry Carson- Nuclear Product Manager Office Phone 215-775-1314 Email: lcarson@cdtechno.com "Robert Malley-VP Quality and Process Engineering Office Phone 215-619-7830 Email bmalley@cdtechno.com" Notified R1DO (Lilliendahl), R2DO (Sykes), R3DO (Dickenson), and NRR Part 21 Group via email. * * * UPDATE PROVIDED FROM ROBERT MALLEY TO JEFF ROTTON AT 1505 EDT ON 10/28/2014 * * * The following information was excerpted from the revised final report submitted by email: This update (dated 9/22/2014 and provided to NRC on 10/28/2014) is Revision 1 to Final Report from C&D Technologies originally submitted on 9/16/2014. "An interim report was submitted 3/27/14 while the product was being returned for analysis. "C&D has performed an analysis of the returned product, and is submitting this report to the NRC and notifying affected C&D customers to the possibility of separator misalignment in LCR, KCR, and LCY products [versus original report affecting LCR products only]. "U.S. Licensees using batteries possibly containing the potential defect are being notified of the filing of this final report with recommendations that they examine their batteries for any signs of similar problems. "If you have any questions or wish to discuss this matter or this report, please contact: "Robert Malley, VP Quality and Process Engineering, bmalley@cdtechno.com, (215) 619-7830." List of affected plants: NRC Region 1: Nine Mile Point, Millstone, Indian Point, Vermont Yankee, Limerick, Three Mile Island, Beaver Valley, Susquehanna, Salem, Hope Creek, Crystal River NRC Region 2: Oconee, St. Lucie, Harris, Robinson, Summer, Farley, Hatch, Vogtle, Browns Ferry, Sequoyah, Watts Bar NRC Region 3: Kewaunee, Fermi, Palisades, Braidwood, Byron, Clinton, LaSalle, Perry, Cook, Duane Arnold, Point Beach, Monticello, Prairie Island NRC Region 4: Arkansas Nuclear One, Grand Gulf, Waterford, Cooper, Fort Calhoun, Diablo Canyon Foreign: Bruce, Laguna Verde, Point Lepreau, Krsko, Darlington, Pickering, Chin Shan, Kuosheng, Maanshan, Lungmen Other: Knoll Atomic Power Laboratory Notified R1DO (Bickett), R2DO (Blamey), R3DO (Lipa), R4DO (Whitten) and NRR Part 21 Group via email. * * * UPDATE PROVIDED BY ROBERT MALLEY TO JEFF ROTTON AT 1143 EDT ON 10/28/2014 * * * The following was excerpted from the final report update received by fax: "The purpose of this letter is to update a report provided to the NRC on 09/22/14 regarding misaligned separators in Class 1 E battery products. We are revising Section II for the models of the product affected, and Section VIII for the advice provided for customers. These revisions are provided below: "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. "The products affected include LCUN and LCU model lines in addition to the previously reported LCR, KCR, and LCY products. [This did not add to the list of facilities affected] "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "Based on experience gained through site visits and review of products that completed product life C&D is changing the criteria for inclusion in the scope of this Part 21 report. The change increases the allowable separator misalignment. "If you have any questions or wish to discuss this matter or this report, please contact: "Robert Malley, VP Quality and Process Engineering, bmalley@cdtechno.com, (215) 619-7830." Notified R1DO (Bickett), R2DO (Blamey), R3DO (Lipa), R4DO (Whitten) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2014-03-28
49966 | 0 | MILLSTONE | 1 | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-27 12:00 | 2014-03-28 08:43 | 2014-03-28 | FITNESS FOR DUTY VIOLATION "A contractor supervisor violated the Dominion Nuclear Connecticut FFD policy. The program member's access has been suspended pending assessment and management review. "The NRC Senior Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.719 |  |  |  | 0 | 2014-03-28
49965 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-27 14:20 | 2014-03-27 17:37 | 2014-05-27 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED GAUGE The following information was received from the State of Arkansas via email: "The licensee notified the Arkansas Department of Health via postal mail on Thursday, 03/27/2014 at 1420 hours, of the stuck shutter event. The State's event number is ARK-2014-003. "The Ohmart source holder model number is HM-8 and the source contains 0.523 Curies of Cs-137. The problem was discovered during shutter checks and inventory. The licensee states that the gauge operations remain to be 24/7. The licensee stated that the area has been roped off and has proper posting. The licensee stated that they have notified applicable facility personnel of the radiological hazard and that there have been no known radiation exposures to personnel and/or members of the public. "The shutter will be fixed by Ohmart (date unknown at this time), whom will also diagnose the root cause of this event. The State of Arkansas is awaiting a 30 day written report post repairs." * * * UPDATE PROVIDED BY ANGIE HILL TO JEFF ROTTON AT 1412 EDT ON 03/31/2014 * * * The State of Arkansas reported that the original discovery date of the stuck shutter was September 16, 2013. The manufacturer, Ohmart, will be on site from May 5-9, 2014 to repair the shutter and perform a root cause evaluation. Notified R4DO (Gepford) and FSME Resources via email * * * UPDATE FROM ANGIE HILL TO VINCE KLCO ON 5/27/14 AT 1530 EDT * * * The following information was received from the State of Arkansas by email: "The approved Vendor Service Engineer arrived at Georgia-Pacific on Friday, April 11, 2014, to inspect the Ohmart Model HM-8 gauge shutter. The licensee stated that the gauge shutter offered increased resistance, but was not stuck. "The Vendor Service Engineer was able to move the handle by hand, verified that the shutter was not stuck, performed surveys and sealed source leak tests. The Vendor Service Engineer confirmed that there are no exposures of concern from the gauge, confirmed negative leaks and that the gauge is operating properly at this time. "The licensee confirmed that there are no known personnel radiation exposures or dose to the member of the public from this event. "The Department [Arkansas Department of Health] considers this event closed." Notified the R4DO (Vasquez) and FSME Resources via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2014-04-04
49964 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-03-26 | 2014-03-27 10:16 | 2014-03-27 | AGREEMENT STATE REPORT - Y-90 SIR-SPHERES TREATMENT DOSE LESS THAN PRESCRIBED The following was received from the State of Florida via email: "Y-90 Sir-Sphere injection delivered 62% of prescribed dose. Licensee or Owner is currently unknown. Radiation Services, Inc. (RSI) is a Medical Physics Consulting firm. This event was reported to RSI by a client as a request for consult. RSI did not perform the procedure. No other information is know at this time." Florida Incident Number: FL14-026 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-04-04
49963 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-03-27 01:51 | 2014-03-27 09:42 | 2014-03-27 | FAILURE OF SECONDARY CONTAINMENT DOOR INTERLOCK "At 0151 [CDT] on March 27, 2014, indication was received in the Control Room that two Secondary Containment doors, in the 2/3 Diesel Generator Interlock, were opened simultaneously. An equipment operator, in the field at the time of the event, reported that while opening the reactor building side interlock doors, individuals were able to open the diesel side interlock doors. The interlock mechanism preventing both doors from operating simultaneously did not operate as expected. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2, since two doors in a singular access opening were allowed to open. As a result, entry into Technical Specification 3.6.4.1 Condition A was made due to Secondary Containment being inoperable. The doors were open for approximately 5 seconds and were immediately secured. Secondary Containment differential pressure was maintained throughout the event. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-27
49962 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-03-26 10:15 | 2014-03-26 14:32 | 2014-03-26 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISORY LICENSED EMPLOYEE A supervisory licensed employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 88 | 0 | 100 | 88 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2014-03-26
49961 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-03-14 | 2014-03-26 11:06 | 2014-03-26 | LOUISIANA AGREEMENT STATE REPORT - TWO ABANDONED WELL LOGGING SOURCES The following information was obtained from the State of Louisiana via facsimile: "Event Location: The source became stuck down hole at Deer Island CL&F 005, Terrebonne Parish, LA "Event type: Two sources were in a device used to log down hole wells. The two sources became lodged down hole and Baker Hughes, after 'fishing', decided to cap the location and go around the sources. Cement and a whip-stock were used as deflection devices. "Notifications: LDEQ [Louisiana Department of Environmental Quality] was notified of the lodged sources on March 17, 2014 @ 15:00 hrs. [CDT]. At that time, Baker Hughes requested to plug the lodged location and place a deflection device to continue their work. The request was granted. "Event description: On March 17, 2014, Baker Hughes contacted LDEQ reporting that two well-logging sources became stuck down hole; a QSA Global 2.5 Ci Cs-137 source, SR# 90652B and a QSA Global 5 Ci Am/Be neutron source, SR# 77860B. A request to continue work was granted after a cement plug and a whip stock deflection device was placed at the location of the lodged sources. This incident was reported and will be abandoned and maintained by the requirements of LAC 33:XV.2051 and 2099 Appendix B. "The Department [LDEQ] considers this event closed." Louisiana Event Report ID No.: LA-140003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-04-03
49960 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-02-08 00:19 | 2014-03-26 10:55 | 2014-03-26 | INVALID ACTUATION OF A CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) to provide information pertaining to the invalid actuation of a containment isolation signal. "On February 8, 2014, at 0019 [EST], with the plant in Mode 6 and fuel moves in-progress, an invalid containment isolation actuation signal was generated that affected containment isolation valves in more than one system and caused both trains of the control room heating, ventilation and cooling systems to swap from normal to emergency mode of operation. For both occurrences, all necessary follow-up actions were taken in accordance with the abnormal operating procedure for a spurious containment isolation event. All equipment responded in accordance with the plant design. "The invalid actuation signal was caused by spurious upscale spikes in fuel handling area radiation monitor, RIA-2316. Actual radiation levels in the vicinity of RIA-2316 were verified to be normal and below the alarm set point. The indication on RIA-2316 spiked momentarily above the high alarm set point and then returned to normal levels. No alarms were received from the redundant fuel handling area radiation monitor, RIA-2317. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-03-26
49959 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-02-06 11:43 | 2014-03-26 10:55 | 2014-03-26 | INVALID ACTUATION OF A CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) to provide information pertaining to the invalid actuation of a containment isolation signal. "On February 6, 2014, at 1143 [EST], with the plant in Mode 6 and fuel moves in-progress, an invalid containment isolation actuation signal was generated that affected containment isolation valves in more than one system and caused both trains of the control room heating, ventilation and cooling systems to swap from normal to emergency mode of operation. For both occurrences, all necessary follow-up actions were taken in accordance with the abnormal operating procedure for a spurious containment isolation event. All equipment responded in accordance with the plant design. "The invalid actuation signal was caused by spurious upscale spikes in fuel handling area radiation monitor, RIA-2316. Actual radiation levels in the vicinity of RIA-2316 were verified to be normal and below the alarm set point. The indication on RIA-2316 spiked momentarily above the high alarm set point and then returned to normal levels. No alarms were received from the redundant fuel handling area radiation monitor, RIA-2317. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-03-26
49958 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-03-25 19:42 | 2014-03-25 22:44 | 2014-03-25 | MANUAL REACTOR SCRAM DUE TO LOSS OF CONDENSER VACUUM "The plant was stable at 85 percent power when off-gas flow started lowering. The operating crew entered the loss of vacuum off-normal procedure and commenced an emergency power reduction to attempt to slow/halt the loss of vacuum while attempting various prescribed actions in the off-normal procedure. When vacuum reached 24 in. Hg, a rapid plant shutdown was performed as prescribed in the off-normal procedure. Power was at 46 percent when a rapid plant shutdown was commenced with the mode switch placed in shutdown at 1942 CDT. All control rods fully inserted on the scram, no emergency core cooling system injected or was required, no safety/relief valve(s) lifted and all systems responded as expected on the scram. The plant will remain in mode 3 with normal makeup from the feedwater system and pressure control on the turbine bypass valves with the main condenser available as a heat sink. All vital and non-vital electrical busses are powered from reserve off-site sources and no emergency diesel generators started on the scram. The cause of the loss of vacuum is under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 46 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-03-25
49957 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2014-03-07 | 2014-03-25 15:50 | 2014-03-25 | AGREEMENT STATE REPORT - LOST HANDHELD TRACE DETECTOR CONTAINING NI-63 SOURCE The following information was received via facsimile: On the evening of March 11, 2014, the LA Department of Environmental Quality (DEQ) received a notification from Louisiana State University (LSU) that they had sent a Smiths Detection model Sabre 5000 handheld trace detector, containing 15 mCi of Ni-63, to the manufacturer for repairs. The device was sent by common carrier. The device was repaired and sent back to the common carrier's distribution center. The common carrier's records show that on December 20, 2013 at 1832 CST, the device was delivered and left at the front door of 3south LLC, the local distributor of Smiths Detection products. The records at 3south do not show receipt of the device. A claim was filed and the resolution took several weeks. The device was never located by the common carrier or the local distributor. The device was replaced by Smiths Detection. DEQ considers this event closed. Louisiana Event Report ID No.: LA-140002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2014-04-02
49956 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-03-24 23:00 | 2014-03-24 21:30 | 2014-03-25 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. Planned maintenance activities are being performed on 03/24/14 starting at approximately 2300 [EDT] to the Technical Support Center (TSC) ventilation system. "The work includes performance of planned carbon bed filter sample. The planned work activity duration is approximately 5 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "The NRC Resident Inspector has been notified. "This event poses no threat to the public or station employees." * * * UPDATE FROM THOMAS GARRISON TO HOWIE CROUCH AT 0325 EDT ON 3/25/14 * * * The TSC was returned to service at 0325 EDT on 3/25/14. The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Shaeffer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-24
49955 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-03-03 | 2014-03-24 18:15 | 2014-03-24 | AGREEMENT STATE REPORT - LEAKING NICKEL 63 SOURCE The following information was received via email: "Operations Manager of National Technical Systems, NTS- Silicon Valley, contacted RHB [California - Radiation Health Branch] Sacramento and reported that their analytical equipment, manufactured by Particle Measuring Systems, used for analyzing gases by ionizing them with a 10 milliCi Nickel-63 source was leaking. The Nickle-63 source leakage was discovered in their recent leak test that was performed in anticipation of shipping the unit to the calibration lab. This resulted in a reading well above the 11,000 DPM limits (it was 4.8 million DPM inside the outflow fitting of the equipment). National Technical Systems shipped the detector cell and equipment to Particle Measuring Systems for disposal. National Technical Systems conducted surveys in the area where the unit was stored and used, and no Nickel-63 contamination was found. According to the radiation safety officer of Particle Measuring Systems, the contamination was contained inside the outflow part of the equipment. "Equipment Manufacturer: Particle Measuring Systems; Equipment Name and Model: Air Sentry II, Chlorides Monitor "Based upon disposal and appropriate surveys, this item is closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-04-01
49954 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-03-24 14:12 | 2014-03-24 18:47 | 2014-03-24 | UNANALYZED CONDITION DUE TO POSTULATED FIRE-INDUCED SHORT "On March 24, 2014, during an extent of condition review for a separate problem evaluation report (PER) for the Browns Ferry Nuclear Plant (BFN), it was discovered that a postulated fire-induced wire-to-wire short of 250V DC control cables associated with 480V AC Shutdown Boards 2B, 3A, and 3B could cause the 480V AC Shutdown Board control power to spuriously transfer and could result in loss of control power to the 480V AC Shutdown Board. In the event of a 10 CFR 50 Appendix R fire, these conditions could result in loss of power to credited safe shutdown equipment that would challenge the ability to provide adequate core cooling during performance of BFN Safe Shutdown Instructions. "Roving fire watches have been established as compensatory measures in accordance with the BFN Fire Protection Report. "These conditions are being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). These conditions are also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(ii)(B). These conditions have been entered into the Corrective Action Program. "The NRC Resident Inspector has been notified of this event." | 0 | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-24
49953 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2014-03-23 20:50 | 2014-03-24 17:00 | 2014-03-28 | SAFETY EQUIPMENT POTENTIAL FAILURE - HIGH PRESSURE FIRE WATER SPRINKLER SYSTEM "At 2050 CDT, on 03-23-2014, the Plant Shift Superintendent was notified that the C-333 High Pressure Fire Water (HPFW) Sprinkler System A-16 had been inspected by Fire Services and 11 sprinkler heads had visible corrosion on them, including 4 heads adjacent to each other. The system configuration was evaluated using EN-C-822-99-047, 'Effects of Impaired Sprinkler Heads on System Operability' and determined that with these heads potentially impaired, a portion of the building would not have sufficient sprinkler coverage. The HPFW system is required to be operable according to [Technical Safety Review] TSR LCO 2.4.4.5. HPFW system A-16 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. "Based on past testing results, there is a possibility that the heads would have been able to perform their specified safety function. Once the heads are removed from the system, testing will be performed to determine the actual affect on operability. This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Region II (Marvin Sykes) has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-14-0324; PGDP Event Report No. PAD-2014-03; NRC Worksheet No. 49953 "Responsible Division: Operations" TSR LCO 2.4.4.5 Action B requires an hourly fire patrol in the affected area. * * *RETRACTION ON 3/28/14 AT 1959 EDT FROM JOE BARLETTO TO DONG PARK * * * "Subsequent to the event, the corroded sprinkler heads were replaced with new heads and the removed heads were tested In the laboratory. Based on the test results and the operability criteria defined in EN-C-822-99-047, A-16 was capable of performing its intended safety function. The clustered heads were on a single branch line in a ceiling beam pocket. The middle head failed testing, however overlapping coverage was provided by the adjacent heads on both sides." Notified R2DO (Sykes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2014-03-24
49952 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-24 13:27 | 2014-03-24 16:34 | 2014-03-24 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PRE-PLANNED MAINTENANCE "The Millstone Station Stack Radiation Monitor, RM-8169 was removed from service for pre-planned maintenance. This is reportable as a loss of assessment capability in accordance with 10 CFR 50.72 (b)(3)(xiii). "RM-8169 was restored at 1539 EDT." The licensee notified the NRC Resident Inspector and applicable State and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-24
49951 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-24 10:43 | 2014-03-24 15:11 | 2014-03-24 | RADIATION MONITOR OUT OF SERVICE FOR PRE-PLANNED MAINTENANCE "System affected: SLCRS [Supplementary Leakage Collection and Release System] radiation monitor. "Actuations and their initiation signals: N/A. "Causes: Pre-planned maintenance. "Effect of event on plant: Ventilation process radiation for SLCRS. "Actions taken or planned: Return to service within 24 hrs. "Additional information: None." The licensee notified the NRC Resident Inspector and applicable State and local agencies. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-24
49950 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-03-24 12:55 | 2014-03-24 13:45 | 2014-03-24 | OFFSITE NOTIFICATION DUE TO DEATH OF EMPLOYEE "On March 24, 2014, at approximately 0200 EDT, with Watts Bar Nuclear Unit 1 at 0% power while commencing a planned refueling outage and Unit 2 under construction, a radiation protection technician was found unresponsive in the protected area. "An emergency medical team responded and the individual was transported off site to a medical facility where he was pronounced dead at 0530 EDT. The individual was not contaminated and there were no radiological or industrial safety issues associated with Watts Bar Nuclear Plant. Due to notification of OSHA at 1255 EDT, this report is submitted pursuant to 10 CFR 50.72(b)(2)(xi), as a notification to a government agency. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-03-24
49949 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2014-03-24 09:05 | 2014-03-24 13:38 | 2014-03-24 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISORY EMPLOYEE A non-licensed supervisory employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector and the New York Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-03-24
49948 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-03-24 00:31 | 2014-03-24 05:14 | 2014-03-24 | SECONDARY CONTAINMENT INOPERABLE AND UNPLANNED ISOLATION OF THE REACTOR BUILDING VENT RADIATION MONITOR "At 0031 [EDT] on March 24, 2014, Nine Mile Point Unit 2 was lowering power for the planned refueling outage. The loss of reactor building heating resulted in the isolation of the reactor building to maintain building temperature. Isolation of the reactor building resulted in the isolation of the reactor building vent radiation monitor (Vent WRGMS) which is a loss of emergency assessment capability. The isolation of the reactor building also resulted in declaring secondary containment inoperable due to secondary containment differential pressure being positive. Secondary containment was declared operable at 0034 [EDT] when differential pressure was restored to greater than negative 0.25 inches water gauge. "Secondary containment being inoperable is a 8-hour report for 10 CFR 50.72(b)(3)(v)(c), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The unplanned isolation of Vent WRGMS is a 8-hour report for 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." The licensee will notify the New York Public Service Commission. | 0 | 18 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | LOSS COMM/ASMT/RESPONSE |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-03-24
49947 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-21 17:32 | 2014-03-21 21:22 | 2014-03-21 | FITNESS-FOR-DUTY INVOLVING A LICENSED SUPERVISOR A licensed supervisor violated the company's fitness-for-duty policy. The employee's plant access has been suspended. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2014-03-21
49946 | -1 | BOZEMAN DEACONESS HOSPITAL |  |  |  |  | 2008-09-09 | 2014-03-21 17:53 | 2014-04-09 | THREE MEDICAL MISADMINISTRATION INCIDENTS During a recent review of historical records, it was determined that three medical misadministration incidents had occurred. Two of these incidents occurred on September 9, 2008 and the third incident occurred on September 30, 2008. The patients were being treated for prostate cancer and were receiving I-125 brachytherapy. Two patients were each prescribed a source activity of 0.269 mCi but received 0.341 mCi. The third patient was prescribed 0.340 mCi but received 0.439 mCi. The patients have been followed elsewhere for the last few years. The licensee will assess the patients as soon as they are available. The licensee is in the process of notifying the patients of the misadministrations. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 0835 ON 4/9/14 FROM KARI CANN TO PETE SNYDER * * * The RSO for the hospital has reevaluated this report and has determined, in consultation with NRC Region IV, that due to a lack of complete information this report is retracted. If later, when more complete information is available it is determined that a report needs to be made it will be made at that time. Notified R4DO (Drake) and FSME EVENT RESOURCE (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2014-03-31
49945 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-03-21 04:30 | 2014-03-21 17:32 | 2014-03-21 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA WITH STUCK SOURCE The following Ohio Bureau of Radiation Protection report was received via facsimile: "The [Ohio] Bureau of Radiation Protection [BRP] was notified by the licensee's corporate RSO [Radiation Safety Officer] at 1505 [EDT] on 3/21/2014, about an incident involving a stuck radiography source. The incident took place at 0430 on 3/21/2014. Crew members were performing radiography in a boiler penthouse in Aberdeen, Ohio, when a magnetic stand fell over and crimped the source guide tube while the source was still out. Crew members called the RSO at their Woodlawn, Ohio [location], who instructed them to survey and post the area and control access until he arrived. The Woodlawn RSO arrived at the site around 0900, shielded the source and was able to bend the guide tube so the source could be retracted back into the camera. The source was safely [positioned] back into the camera around 0945 on 3/21/14. Because licensee personnel wear Instadose dosimetry badges by Mirion Technologies, the Woodlawn RSO was able to determine that the exposure he received from this source retrieval activity was 159 mRem. The licensee understands they are responsible to provide a written report to the BRP within 30 days." The radiography device is a QSA 880 Delta camera with a 27 Ci Ir192 source. Ohio State BRP Incident Report: #2014-006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-03-31
49944 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-03-20 | 2014-03-21 13:59 | 2014-03-21 | AGREEMENT STATE REPORT - INABILITY TO RETRACT RADIOGRAPHY SOURCE TO ITS FULLY SHIELDED POSITION The following information was received via facsimile: "The Department's [PA Department of Environmental Protection Bureau of Radiation Protection] Central Office was informed of this event on March 20, 2014. This event is reportable within 24 hours per 10 CFR 30.50(b)(2) and within 30 days per 10 CFR 34.101(a)(2). "Upon completion of a shot, the source was found to be stuck within the collimator and unable to be retracted. The area was roped off and controlled, the Radiation Safety Officer was notified, and a service provider (QSA Global) was called to perform retrieval operations. The source was returned to its fully shielded position at 0002 EDT on March 21, 2014. The radiographer, assistant radiographer, and recovery team received minimal exposure from this source retrieval operation. No one from the general public was exposed to radiation from this operation. Additional information will be provided upon receipt. "Camera Model: QSA Global 880 Delta; Isotope: Ir-192; Activity: 68 Ci. "The cause of the event is unknown at this time. The camera and cables are being returned to the manufacturer to be inspected. The Department plans a reactive inspection." PA Event Report ID No: PA140010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-31
49943 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-03-21 13:00 | 2014-03-21 14:20 | 2014-03-21 | SHIELD BUILDING VENT GAS RAD MONITORS OUT OF SERVICE FOR PLANNED MAINTENANCE "At 1330 CDT on March 21, 2014, 1R-22 and 2R-22, Shield Building Vent Gas Radiation Monitors will be removed from service for planned preventative maintenance and therefore [will be] nonfunctional. These monitors have no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs); NUE (Notification of Unusual Event) and Alert classifications when out of service. They are also used for offsite dose projection calculations. This will result in a Loss of Emergency Assessment Capability while 1R-22 and 2R-22 are out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 and Unit 2 Shield Building Ventilation Stacks are also monitored by high range monitors, 1R-50 and 2R-50, which are used for the same purpose in Site Area or General Emergency classifications. 1R-50 and 2R-50 are being monitored and are indicating normal values. There are no radioactive leaks that will impact the Shield Buildings as evidenced by normal readings on 1(2)R-22 prior to their removal from service. Preventative maintenance (belt inspections) is expected to last approximately 1 hour. Maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-21
49942 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-01-21 07:46 | 2014-03-21 14:10 | 2014-03-21 | 60 DAY OPTIONAL TELEPHONE NOTIFICATION OF AN INVALID PRIMARY CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On January 21, 2014, at 0746 hours Central Standard Time (CST), during performance of the 3C Emergency Diesel Generator (EDG) post modification test instructions, the EDG was supplying a shutdown board in isochronous mode when the 3B Residual Heat Removal (RHR) pump was started causing the voltage to drop to 2100 volts. At this time, Browns Ferry Nuclear Plant (BFN) Unit 3, received a half scram and Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolation signals as a result of losing the 3B Reactor Protection System (RPS) Motor Generator (MG) set due to a time delay relay failure on under voltage. The PCIS groups 2, 3, 6, and 8 isolations caused the initiation of all three trains of the Standby Gas Treatment (SBGT) system, Control Room Emergency Ventilation (CREV) subsystem 'A', and the Refuel fans tripped and isolated. Operations personnel responded to the PCIS initiation, ensured all equipment operated as designed, and placed affected systems back in service. "Plant conditions which initiate PCIS group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The apparent cause for this condition was a failure of a 3B RPS MG set time delay relay due to lack of a preventive maintenance strategy. The vendor manual for the time delay relay did not specify a qualified life. The replacement relay specified a replacement schedule of 10 years. The relay that failed was installed for approximately 13 years. To address this condition, preventive maintenance is being developed for MG set time delay relays. In addition, the only remaining relay, similar to the failed relay, is scheduled be replaced on August 25, 2014, for the 2A RPS MG set." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-03-21
49941 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-03-20 15:22 | 2014-03-21 12:53 | 2014-03-21 | FITNESS FOR DUTY - SIGNIFICANT PROGRAM VULNERABILITY "A significant Fitness for Duty (FFD) programmatic vulnerability was discovered during an NRC inspection. A potential exists that some members of the FFD site's random drug test pool could control and predict the date and time that the random list is run; thus mitigating the effectiveness of the 'random aspect' for the staff. Per 10 CFR 26.31(d)(2)(i), 'Random testing. Random testing must - Be administered in a manner that provides reasonable assurance that individuals are unable to predict the time periods during which specimens will be collected.' Since, these individuals may be able to predict the timeliness of random drug test events this condition is reportable per 10 CFR 26.719(b)(4) as a discovered programmatic vulnerability of the FFD program that may permit undetected drug or alcohol use by individuals who are assigned to perform duties that require them to be subject to the FFD program." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2014-03-21
49940 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2014-03-21 | 2014-03-21 08:46 | 2014-03-21 | PART 21 - SBM SELECTOR SWITCHES CONTACT ASSEMBLY UNPLANNED MANUFACTURING CHANGE The following is an excerpt from a fax received from Unified Controls International (UCI): "...there was a significant manufacturing process change to the General Electric SBM series switches in 2009. The high resistance across switch contacts in the GE SBM switches could lead to a failure of the switch to change state when required. Concerns have been raised regarding tin plated movable contacts used for make or break service and in use without protective lubrication. UCI is not capable to complete an evaluation of the affect that this change may have on in storage SBM switches or already installed SBM switches that were provided to the customers on the purchase orders listed in section [below]. UCI does not know the storage conditions, in service environmental conditions or in service cycling rates of the switches or how the each of these items may affect the change in contact resistance. Each affected customer needs to evaluate their in storage and in service switches and determine if the change in contact material could possibly create a safety hazard and effect the ability of the switches to perform in their safety related application." The applicable purchase orders are: Duke Energy, Purchase Orders: 131116,133980, 147875,129193,130989 (Non-Safety Related), 133920, 148974 (Non-Safety Related), 152090 (Non Safety Related), 133972, 169525 Antung Trading Company, Purchase Order: PP120210 CFE, Purchase Order: 700327408 Fluor, Purchase Order: A3PB-6-0016-00Q1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-03-21
49939 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-03-11 | 2014-03-20 17:31 | 2014-03-20 | AGREEMENT STATE REPORT - ERROR IN DOSE CALCULATION AND UNDERDOSE ADMINISTRATION The following was received from the Commonwealth of Virginia via fax: "Event description: On March 18, 2014, the licensee identified an error in a dose calculation for high dose rate (HDR) treatments administered to a patient on March 11-12. The initial report from the licensee indicates the patient was administered two out of a total of six prescribed fractionated doses. An error was made in planning the correct dwell position for the two fractions. The administered dose differed from the prescribed dose (was less than) by more than 20 percent. The licensee plans to correct for the underdose during the remaining fractions. The licensee is investigating if the dose to tissues other than the treatment site may have met the definition of a medical event." Virginia Event Report ID No.: VA-14-0002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-03-28
49938 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-03-20 10:20 | 2014-03-20 17:17 | 2014-03-20 | APPENDIX R FIRE DOOR FAILED TO CLOSE AND LATCH "At 1020 CDT, door 410B did not automatically close and latch as required. Door 410 B is an Appendix R fire door that is required for divisional separation of safe shutdown equipment. Due to the doors inability to close and latch as required, divisional separation could not be assured in the event of a fire. A continuous fire watch was established once the deficiency was discovered. The door was repaired and verified to be working properly. The door was non-functional for approximately one hour and fifteen minutes from the time of discovery. "Health and safety of the public was maintained as the plant was in a normal condition and there has been no actual condition needing the door to close and latch. "The NRC Resident Inspector has been notified." | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-20
49937 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2014-03-20 14:05 | 2014-03-20 14:15 | 2014-03-20 | FERMI DECLARES ALERT DUE TO A FIRE IN AN EMERGENCY DIESEL GENERATOR TURBO CHARGER LAGGING At 1405 EDT on 3/20/14, Fermi Nuclear Station declared an Alert due to a fire in the lagging of an Emergency Diesel Generator Turbo Charger. The Alert notification was based on EAL HA02, fire or explosion affecting the operability of plant safety systems required to establish or maintain safe shutdown. The fire in the EDG-11 turbocharger lagging occurred during testing. The fire was extinguished using handheld CO2 fire extinguishers and a reflash watch was set. EDG-11 has been removed from service and damage is minimal. The plant is shutdown in Mode 4 for Refueling Outage 16. All parameters associated with the reactor are stable. RHR Pump D remains in service in Shutdown Cooling and is unaffected by the EDG-11 fire. There has been no other impact on the plant electrical systems or shutdown cooling and Fermi Nuclear Station remains in an Alert pending further evaluation. The NRC remained in Normal Mode. The licensee has informed the NRC Resident Inspector. Notified DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, and FDA. Notified NuclearSSA via email only. * * * UPDATE FROM SAM HASSOUN TO JOHN SHOEMAKER AT 1535 EDT ON 3/20/13 * * * "At 1359 [EDT on 3/20/14], with the plant in Mode 4, a fire was confirmed on Emergency Diesel Generator (EDG)-11 turbocharger. At 1402, the fire was extinguished with a CO2 extinguisher. An ALERT was declared at 1405 and Assembly and Accountability was ordered by the Emergency Director. The Assembly and Accountability was completed satisfactorily by 1441. The fire was from oil soaked lagging on the engine turbocharger. The insulation was removed and the engine exhaust header was inspected. The damage was limited to only the lagging. The room has been ventilated using the Engine room fans and has been cleared of all of the smoke. The Emergency Director terminated the event at 1532 [EDT on 3/20/14]. The Resident Inspector has been notified." Notified R3RA (Pederson), NRR (Dorman), R3DO (Lara), IRD (Grant), IRD (Morris), DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA, and Canadian Nuclear Safety Commission (Tennant). Notified NuclearSSA via email only. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-03-20
49936 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-02-13 | 2014-03-20 12:35 | 2014-03-20 | AGREEMENT STATE REPORT - COLLIMATOR BLOCK BROKEN OFF OF THE SHUTTER ASSEMBLY The following was received from the State of Pennsylvania via email: Notifications: The [Pennsylvania Bureau of Radiation Protection] Department's Central Office was informed of this event on March 19, 2014. This event is reportable within 24-hours per 10 CFR 30.50(b)(2). "Event Description: During a routine monthly inspection of the gauge, [the licensee] discovered that the collimator block had broken off of the shutter assembly. The collimator block was found lying in the quarter inch steel box that the gauge is housed in to protect it from the operating conditions on the battery. The cause of this event is still being investigated. Radiation surveys performed indicated no employees were exposed as a result of this event. "Manufacturer: Thermo Measure Tech Model: 5204 Serial Number: B392 Isotope: Cs-137 Activity: 4 Ci "CAUSE OF THE EVENT: Unknown at this time. "ACTIONS: The broken shutter mechanism was removed and replaced by a licensed service provider. The shutter mechanism was tested and confirmed as operating properly. The [State of PA] Department plans a reactive inspection. "Media attention: None at this time." PA Event Report ID No: PA140009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-28
49935 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-20 09:11 | 2014-03-20 11:34 | 2014-03-20 | FIRE-RELATED UNANALYZED CONDITION THAT COULD IMPACT CREDITED SAFE SHUTDOWN ANALYSIS "This is a non-emergency notification. In preparation for converting from 10 CFR 50, Appendix R, to NFPA (National Fire Protection Association) Standard 805, an update to the Brunswick Steam Electric Plant (BSEP) Safe Shutdown Analysis has been performed which identified circuit configurations where fire damage, under certain postulated fire scenarios, could impact the ability to safely shut down following a fire, in accordance with 10 CFR 50, Appendix R. "Affected fire areas are CB-23E, RB1-N, RB1-S, RB2-N, RB2-S, TB1, DG-07, and DG-16E. A fire in one of these areas could potentially affect the post fire capability of the following safe shutdown systems: 1) Containment Overpressure Protection, 2) Emergency Bus Load Shed, 3) Control Room HVAC, or 4) Emergency Diesel Generator Building HVAC. "This is reportable as an unanalyzed condition that significantly degrades plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). "Fire protection compensatory measures (i.e. roving fire watches) currently exist in the affected fire areas. "This event did not result in any adverse impact to the health and safety of the public. The safety significance is minimal. Fire watches were already ongoing in these areas prior to the time of discovery. The conditions identified here are based on hypothetical fire scenarios that have not actually occurred. "This condition has been entered into the Corrective Action Program (i.e. CR 676576). Previous similar events were reported in NRC Event Reports 47341 and 49222, and in Brunswick LERs 1-2011-002 and 1-2013-002. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-20
49934 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2014-03-19 10:10 | 2014-03-20 08:50 | 2014-03-20 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.719 |  |  |  | 0 | 2014-03-20
49933 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2014-03-19 22:02 | 2014-03-20 00:29 | 2014-03-20 | POTENTIAL LEAK DISCOVERED AROUND PRESSURIZER HEATER BANK "This report is in accordance with 10 CFR 50.72(b)(3)(ii)(A). "During an inspection, a small amount of boric acid residue was noted in the vicinity of the Pressurizer heater components. Subsequent examination revealed a small flaw in Pressurizer Backup heater Bank B element 11. This component is part of the primary system boundary. Repair options are being evaluated. Currently, Unit 3 is in Mode 5 in preparation for refueling. The repair will be performed prior to restart." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-03-20
49932 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2014-03-18 | 2014-03-19 15:36 | 2014-04-17 | PART 21 - THOMAS AND BETTS PRINTED CIRCUIT BOARDS The following was received via fax: "This report documents the supply of faulty Logic Power supply assembly printed circuit boards for a Cyberex 20KVA Model AC Power Supply. These power supplies have the incorrect strap installed on the transformers of Cyberex P/N [Part Number] 30-80-56620 which potentially can lead to the transformer being loose and can cause failure of the power supply. Per the manufacturer, the band should have been made of stainless steel but the bands on the installed transformers were made of carbon steel and a corrosion resistant coating. The details of the potential failure of the power supply and the root cause are being evaluated and will be documented in the final report. "UCI [United Controls International] reviewed all the orders that were supplied to the customers and determined that two UCI orders are affected and the customer was notified on the day the issue was identified." Part Number 90-41-974313 (UCI serial numbers 03996-01 -0001, -0002, -0003) and P/N 41-01-596701 (UCI serial numbers 03967-03 -0001, -0002, -0003) supplied to Public Service Electric and Gas (PSEG) are affected. * * * UPDATE ON 4/17/2014 AT 1442 EDT FROM KORINA LOOFT TO DONG PARK * * * The following was received via fax: "This engineering evaluation is being written to document the supply faulty Power supplies for the 20KVA Cyberex Model AC Power supply with the Cyberex part numbers 41-01-596701 and 90-41-974313. "SUMMARY: UCI issued a certificate of conformance to PSEG for S/N: 003967-03-0001 thru 0003 on December 22nd 2012, to be used in safety related applications where seismic is the only design basis event. During the pre-installation testing in February 2014, PSEG identified loose transformers and a loud noise frequency whine and the power supply boards were returned to UCI. Below table lists the details of the power supplies that were returned to UCI. "On February 2nd 2014, UCI has initiated part 21 evaluation to determine the root cause for the failure and evaluate if a defect existed. During the evaluation, it was determined that the transformer strap band installed on Cyberex P/N 30-801-56620 transformer at the location T501 should have been made of stainless steel but the strap band on these power supplies was made up of zinc plated carbon steel. Due to this material difference, the transformer warped and it was evident it became loose. "The installation of the incorrect strap bands on the transformer apply to only one batch of manufactured PCB assemblies. The manufacturer addressed this issue since this was discovered and this was verified by UCI. UCI determined that the order along with the boards that failed pre-installation testing, were the only boards affected by this issue. The customer PSEG was notified on March 13th 2014 and the initial notification letter to NRC was sent on March 19th 2014. "The above mentioned power supplies were recalled from PSEG and two power supply boards of S/N: 003996-01-0002 and 003996-01-0003 are currently at UCI for evaluation and rework. However the S/N: 003996-01-0001 board has not yet been returned to UCI by PSEG. UCI performed an XRF analysis on one of the affected power supplies per part number lot and on UCI control samples to confirm and compare the material of the transformer strap bands. "EFFECT OF THE DEFECT: The installation of the incorrect transformer strap band resulted in the loosening of the transformer from the band. When installed in the system, the transformer might become loose and cause a loud whining noise. The installation of the incorrect material band on the transformer might lead to loosening of the transformer and causes whining noise when installed but no functional test failure will be observed. However, the loose transformer affects the safety function of the item during or after seismic event due to loss of structural integrity. "CORRECTIVE ACTIONS PERFORMED: A UCI corrective action # CAR 14-14 was opened to document the issue found and the corrective and preventive actions taken. As a result, UCI will create two new Commercial Grade dedication procedures for P/N: 41-01-596701 and 90-41-974313 to include the material verification of the transformer bands installed on these power supplies. These new procedures will be used for the existing and future orders of these part numbers. "All the affected power supply boards except S/N: 003996-01-0001 are currently at UCI undergoing rework to replace the transformer of the incorrect material strap band with a transformer of the correct (stainless steel) strap band. After rework, dedication will be performed per new dedication procedures as specified above." Notified R1DO (Burritt) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-03-19
49931 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-03-04 | 2014-03-19 16:03 | 2014-03-19 | AGREEMENT STATE REPORT - MISADMINISTRATION OF IODINE-125 SOLUTION DURING BRACHYTHERAPY The following information was received via facsimile: "A patient was prescribed 50 Gray to be delivered to a brain tumor bed via a GliaSite balloon inflated with 200 mCi of I-125 saline solution implanted for 66 hours. Upon removal of the balloon on March 7, 2014, it was discovered that the balloon had not inflated and no dose to the tumor bed had been delivered. "A three position stopcock was incorrectly positioned at the time of inflation and the I-125 saline solution was diverted to another syringe rather than to the balloon. All material is accounted for and is being held for DIS. The three position stopcock is not part of the vendor's kit. "Corrective Actions: In-service by the vendor scheduled, revision of policies and procedures to include verification of balloon via medical imaging post-infusion, and in-service to staff on new policies and procedures." NYS Incident: #1054 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-03-27
49930 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-03-18 | 2014-03-19 15:08 | 2014-03-19 | AGREEMENT STATE NOTIFICATION - FOUND DEPLETED URANIUM SHIELD The following was received from the State of New York via fax: "On 3/18/2014 NYC sanitation workers clearing a vacant lot in Queens discovered one depleted uranium (DU) shield and the remains of 3 to 4 plastic outer-packs from Mallinckrodt manufactured Mo/Tc radiopharmaceutical generators. Information on the packaging indicates the generators were supplied to NYS Licensee C5413 Triad Isotopes in 2013. Discussions with Triad Isotopes on 3/19/2014 indicate that Mallinckrodt contacted them in October 2013 regarding a shipment of 5 spent generators being returned from Triad to Mallinckrodt via their contractor MDS [that] did not make it to Mallinckrodt in Missouri. The DU shield is being secured by NYC while waiting to be picked up by Triad. NRC Region 3 has been contacted. NYS Incident #1055" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-03-27
49929 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-03-19 07:45 | 2014-03-19 09:36 | 2014-03-19 | RADIATION MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "On March 19th, 2014, at 0745 hours CST Kewaunee Power Station rendered the Auxiliary Building Service Water Return Monitor (R-20) non-functional for planned maintenance. R-20 is used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that would result in an Alert or Unusual Event and is being conservatively reported under 10CFR50.72(b)(3)(xiii) as a loss of emergency assessment capability. "R-20 is planned to be restored to functional by 1230 CST today 03-19-2014. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-19
49928 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-03-18 22:52 | 2014-03-19 03:07 | 2014-03-19 | REACTOR SCRAM DUE TO FAILURE TO CONTROL MAIN TURBINE MOISTURE SEPARATOR LEVEL "At 2252 on 03/18/2014, the Unit 3 reactor automatically scrammed due to a turbine trip from a high Main Turbine moisture separator level. Initial indications show the level controller for 3B2 Moisture Separator failed to adequately maintain level. Additionally local manual control attempts failed to restore moisture separator level. Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure. Reactor feedwater pumps are in service to control reactor water level. "Primary Containment Isolation System Groups 2, 3, 6 and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. Neither High Pressure Coolant Injection nor Reactor Core Isolation Cooling initiation signals were received. "The reactor had been operating near 35% power during scheduled power ascension. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-03-19
49927 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-03-17 10:18 | 2014-03-17 17:09 | 2014-03-18 | TECHNICAL SUPPORT CENTER HABITABILTY IMPACTED DUE TO LOSS OF AIR CONDITIONING "At approximately 1018 EDT on March 17, 2014, during a check of facility equipment, the Technical Support Center (TSC) was found to be degraded due to the loss of the air conditioning (AC) system. Due to the loss of AC, TSC habitability is impacted. "The emergency assessment function can be performed in the control room as addressed in emergency response procedures. This event is reported in accordance with 10 CFR 50.72(b)(3)(xiii). "This condition is common to both units. "Unrelated to this condition, Unit 3 is currently in the process of shutting down in preparation for a refueling outage. "Unit 4 will remain Mode 1, 100% Power. "The TSC AC system repairs are in progress." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0359 EDT ON 3/18/14 FROM PELL TO SNYDER * * * The TSC AC system has been repaired and restored to service. The licensee will notify the NRC Resident Inspector. Notified R2DO (O'Donohue). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-17
49926 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-03-17 12:02 | 2014-03-17 15:55 | 2014-03-17 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP INITIATED BY LOSS OF STATOR COOLING WATER "Ft. Calhoun station automatically tripped due to a loss of turbine load. The turbine tripped due to loss of stator cooling water. Maintenance was in progress on the stator cooling system when inventory was lost and low pump discharge pressure caused an automatic turbine trip and reactor trip. All systems operated as expected. Ft. Calhoun station is shutdown and stable in mode 3 at this time." All control rods fully inserted into the core and decay heat is being removed using the normal condenser steam dump system. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-03-17
49925 | 0 | WATERFORD | 3 |  |  | [3] CE | 2014-03-17 07:37 | 2014-03-17 15:53 | 2014-03-17 | LOSS OF EMERGENCY SIRENS "At approximately 0737 (CDT) on March 17, 2014, Waterford 3 was informed that four emergency sirens were inoperable. One other siren had previously been determined to be inoperable on March 12, 2014. Subsequent review during preparation of this notification has identified an additional eight inoperable sirens, which brings the total number of inoperable sirens to thirteen. There are a total of seventy-three sirens distributed among two parishes (counties). The loss of these thirteen sirens for more than one hour is considered a major loss of offsite response capability and is reported pursuant to 10 CFR 50.72(b)(3)(xiii). "The two affected parish Emergency Operations Centers were notified of the condition and it was confirmed that they will use the preplanned alternative method of Route Alerting for the affected areas until notified that repairs to the sirens have been completed. "Waterford 3 is working to repair the sirens. There is no effect on the plant. This issue has been entered into the Waterford 3 Corrective Action Program and appropriate corrective actions will be developed. "The NRC Resident Inspectors, local agencies, and the State of Louisiana were notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-17
49924 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-03-17 14:18 | 2014-03-17 15:12 | 2014-03-17 | DISPLAYED METEOROLOGICAL DATA POTENTIALLY INACCURATE "At 1418 EDT on 03/17/2014, it was determined the atmospheric stability classification data display on the plant process computer (PPC) could have been potentially inaccurate. "In September 2012, implementation of a hardware and software modification to separate the meteorological tower computer from the PPC introduced a calculation error to the PPC software design that resulted in the PPC potentially displaying inaccurate stability class data. The ability to accurately perform dose assessment calculations could potentially be affected when using the stability class indication obtained from the PPC. "The availability and accuracy of backup stability class data via the meteorological tower computer or from Weather Services International were not affected. "Within 24 hours of discovery, the procedurally described alternatives for obtaining stability class data were implemented. "Subsequently, the PPC stability class software calculation was corrected and the PPC stability class display restored for use. "There was no impact to any emergency declaration because there were no actual emergencies from the time the modification was implemented until the error was corrected. "The licensee has notified the NRC Resident Inspector." | 64 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-17
49923 | 0 | DRESSER-RAND COMPANY |  |  |  |  | 2014-02-17 | 2014-03-17 13:53 | 2014-04-17 | PART 21 - BEARING DEFECT The following was received via email: "On Dresser-Rand Drawing 75439A part number 07 is identified as a Heim LSS-8 bearing that has an Aluminum Bronze insert to accommodate a non-lubricated application. Dresser-Rand shipped 10 bearings part number 75439A07 to Dominion Nuclear in 2006 that were Seal Master Com 8 bearings that do not have an Aluminum Bronze insert. "This bearing is used on turbines that have a PG type mechanical governor with the cam plate linkage. Extended operation without lubrication will result in the Seal Master Com 8 bearing seizing. The customer should visually inspect this bearing for the bronze insert. If no insert is visible then the bearing should be replaced at the first opportunity." Licensees potentially affected (turbine serial numbers): Calvert Cliffs (T36674A, T36674B, T36674C, T36674D), DC Cook (T36700A, T36700B), Salem (T36988A, T36988B), Crystal River (T37009A), Davis Besse (T37686A, T37686B), Millstone (F37273A, T38587A), Summer (T38765A). International sites potentially affected: Bugey (T38498A, T38498B, T38880A, T38880B). * * * UPDATE AT 1102 EDT ON 04/17/14 FROM ED GRANDUSKY TO S. SANDIN VIA FAX * * * Dresser-Rand submitted their final report of the defect. This report is Dresser-Rand number 47. Notified R1DO (Burritt), R2DO (Blamey), R3DO (Hills) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-03-17
49922 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-17 10:25 | 2014-03-17 11:40 | 2014-03-17 | MILLSTONE STATION MAIN STEAM RADIATION MONITORS OUT OF SERVICE FOR MAINTENANCE At 1025 EDT on 3/17/14, the Millstone Station main steam radiation monitors were removed from service for pre-planned maintenance. This resulted in a degradation in the ability to detect steam generator tube leakage. The main steam radiation monitors will be returned to service within 79 hours. The licensee informed State/local agencies and the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-17
49921 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-03-17 07:50 | 2014-03-17 11:26 | 2014-03-17 | SECONDARY CONTAINMENT AIRLOCK DOOR INTERLOCK MALFUNCTION "At 0750 EDT on March 17, 2014, Operations determined that both the inner and outer secondary containment airlock doors, on the 20 foot elevation of the Unit 1 reactor building, had been simultaneously opened for approximately 10 seconds. This event occurred while an employee was exiting secondary containment immediately after another employee had previously entered. Upon recognition of the condition, the employees took action to secure both doors. The cause of this event was malfunction of the secondary containment airlock door interlock. "This condition is being reported in accordance with 10CFR50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. With both doors open, Surveillance Requirement 3.6.4.1.3 of Technical Specification 3.6.4.1, Secondary Containment, was not met, rendering secondary containment inoperable. At the time at the time of the condition, Unit 1 was engaged in Operations with the Potential to Drain the Reactor Vessel (OPDRV) and was crediting Secondary Containment as Operable. "This event did not result in any adverse impact to the health and safety of the public. "The safety significance of this is minimal. Secondary containment was only inoperable for approximately 10 seconds. This event did not result in any adverse impact to the health and safety of the public. "The door interlock investigation [is] in progress. Doorwatches with communications have been stationed on either side of the Unit 1 and Unit 2 20 foot reactor building air lock doors. All other secondary containment access doors on both Reactor Building have been controlled as emergency exit only. Installation of temporary video surveillance system [is] being pursued until long term corrective action can be established per the corrective action program. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-17
49920 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2014-03-17 05:14 | 2014-03-17 09:25 | 2014-03-17 | MANUAL REACTOR SCRAM DUE TO STEAM LEAK IN LOW PRESSURE TURBINE LINE "On 3/17/2014 at 0514 [CDT] the reactor was manually scrammed from approximately 41% core thermal power due to a steam leak in the turbine building. All control rods fully inserted and all systems actuated and operated as designed. All Main Steam Isolation Valves were manually shut. The Reactor Core Isolation Cooling System was manually initiated to assist in level control and pressure control. No safety relief valves actuated automatically. Manual cycling of safety relief valves and Reactor Core Isolation Cooling are being used to maintain reactor water level and pressure within normal bands. Group 2 and 3 RHR isolation signals were received; however no valve movement occurred since the affected valves are normally closed. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(3)(iv)(A) for the manual start of the reactor core isolation cooling system." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 41 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-03-17
49919 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-03-15 11:02 | 2014-03-15 14:56 | 2014-03-15 | MOMENTARY LOSS OF SHUTDOWN COOLING DUE TO A LOSS OF OFFSITE POWER "[Unit] 1 experienced a loss of offsite power (LOOP). [Unit] 1 station aux transformers (SATs) tripped. 1A and 1B emergency diesel generators (EDGs) started and properly restored power to ESF [engineered safety feature] bus 141 and 142. Safe shutdown loads (1A/B SX [essential service water] pumps and 1A/B CC [component cooling] pumps) properly started when signaled by the EDG sequencers. The 1A residual heat removal pump was manually restarted at 1105 [CDT] to restore shutdown cooling. There was no impact to RCS temperature. Additionally, a containment isolation signal was actuated when containment radiation monitors which are powered from the ESF buses briefly lost power until restored by the EDGs. All related equipment realigned as expected except for the 0A VC [control room] chiller that didn't start when required on the EDG sequencer. The cause of the LOOP and the 0A VC chiller issue is under investigation. Fuel moves were in progress and stopped safely. All fuel bundles are in a safe location." Unit 2 was not affected and remains in mode 1. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-03-15
49918 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2014-03-14 13:30 | 2014-03-15 11:32 | 2014-03-15 | HIGH PRESSURE FIRE WATER SYSTEMS DECLARED INOPERABLE "On 3/14/2014 at 1330 hours, the Plant Shift Superintendent was notified by Fire Services that adequate pressure could not be verified during post maintenance testing of an inoperable High Pressure Fire Water System for the C-335 building. During investigation into the issue, it was discovered that eleven operable High Pressure Fire Water Systems were also impacted. The facility is in TSR mode three as all cells have been sampled UF6 negative and the cell motors are not energized. In this mode, the High Pressure Fire Water Systems are still required to be operable per TSR 2.4.4.6; however, due to inadequate pressure, the eleven systems may not have been able to perform the intended safety function. The eleven operable High Pressure Fire Water Systems were declared inoperable and hourly fire patrols were initiated according to TSR LCO 2.4.4.5.9.1 at 1520 hours on 3/14/2014. "On 2/26/2014 at 1212 hours, three High Pressure Fire Water System Sectional Valves were isolated and declared inoperable in order to isolate a section of header which contained a small leak. Isolating these valves resulted in a single supply to twelve High Pressure Fire Water Systems in C-335. Upon investigation of the lack of pressure, it was determined that the sectional supply valve in the remaining supply loop was not operating as designed and is suspected to be the cause of the restricted water flow. "Sectional supply valves that had been used for isolation of the small leak have been opened to provide unrestricted flow to the affected sprinkler systems. Following the confirmation of adequate flow, the sprinkler systems were declared operable and the hourly fire patrols were discontinued at 1739 hours on 3/14/2014. The small leak will be monitored until repairs can be initiated or the leak becomes unmanageable. At that point TSR LCO actions will be entered as necessary. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Region II (Marvin Sykes) has been notified of this event via voice mail." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2014-03-15
49917 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-02-27 | 2014-03-14 16:48 | 2014-03-14 | AGREEMENT STATE REPORT - YTTRIUM 90 MEDICAL EVENT The following information was received from the State of Georgia via email: "Event Narrative: A patient was treated with Y-90 microspheres for cholangiocarcinoma. This was a bilateral disease that would require the treatment of both lobes of the liver. Significant tumor burden was in the central (segment IV) and medial sections. The medical team decided to treat the left lobe first as a result. "For the first treatment, 54.05 mCi was to be delivered to the left lobe. It had an expected dose of 69.0 Gy to the liver. Due to issues with hepatic arterial anatomy not previously anticipated, the medical team could not properly position the catheter. Because it was a bilateral disease that would eventually require the treatment of both lobes, they decided to move forward with the procedure. "Of the calibrated activity of 52.6 mCi, a post-therapy survey of the vial showed 88% of the dose or 46.3 mCi was delivered. A post-delivery Bremsstrahlung scan showed excellent coverage of Segment IV, with some minor coverage in the right lobe due to the arterial anatomy. 21.8 mCi was localized to Segment IV, and the approximate remainder, 24.5 mCi, ended up in the right lobe. There was no significant extrahepatic activity seen. "The medical team considered the treatment to be successful due to the patient's bilateral disease. The authorized user intended to treat the right lobe next, and the team reports that the treatment plan will be adjusted to take into account the diseased areas which were treated. There should be no adverse reaction from this initial treatment. "Cause and Corrective Actions: Occurred due to an arterial aberration causing a the interventional radiologist to be unable to canulate the artery. The hepatic arterial anatomy was different the day of treatment than the initial shunt study suggested on 5 February 2014. The patient's medical team decided to proceed with the catheter orifice just at the origin of the segment IV hepatic artery. The shunt fractions then resulted differently from the intended treatment for that day. "The medical team and RSO are continuing to discuss if any preventative actions can be achieved. Treatment with Y-90 microspheres is reported to be complicated by the degree that the disease and prior treatments have affected liver vasculature. This makes it hard to plan for these scenarios pre-treatment. "Generic Implications: Post treatment scans for Y-90 were reported by the licensee not to be a common practice, but they seem vital for determining if a treatment meets reportable limits. "Procedure Administered: Bilateral radioembolization of liver with Y-90 microspheres. "Intended Dose: 54.05 mCi (69.0 Gy) to left lobe of liver. "Actual Dose: 21.8 mCi to Segment IV of left lobe and 24.5 mCi to the right lobe. "Patient and Referring Physician Notified: Informed following the procedure's post-delivery Bremsstrahlung scan." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-03-24
49916 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-03-14 12:45 | 2014-03-14 16:15 | 2014-03-14 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee with a wooden splinter in his right hand reported to the on-site dispensary this afternoon. The plant nurse administered first aid. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination present was on the employee's right boot, 2760 dpm/100cm2. The plant nurse allowed the employee to return to work. The employee remained inside the Restricted Area over the course of the event." The licensee will inform R2 (Hartland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-03-14
49915 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-14 11:55 | 2014-03-14 15:38 | 2014-03-14 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "While evaluating IER 13-54, regarding the impact of unfused direct current (DC) circuits, a determination was made that the described condition is applicable to Edwin I. Hatch Units 1 and 2 for reactor protection system (RPS) battery/battery charger ammeter circuits. This results in an unanalyzed condition with respect to 10CFR50 Appendix R analysis requirements. "In the postulated event, a fire induced hot short could adversely impact safe shutdown equipment. The Unit 1 and 2 RPS battery/battery charger ammeter indication circuits are routed from the affected components to the main control room. It is postulated that a fire in one fire area can damage the affected cables and cause short circuits without protection that would overheat the cable and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. "Interim compensatory measures (i.e., fire watches) have been implemented for the affected areas of the plant. This condition is being reported pursuant to 10CFR50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-14
49914 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2014-03-13 16:30 | 2014-03-13 18:55 | 2014-03-13 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry Operating Experience identified that there were unprotected DC control circuits for non safety-related DC motors which are routed from the turbine building to other separate fire areas. Fuses used to protect the motor power conductors appear to be inadequate to protect the control conductors. The concern is that under fire safe shutdown conditions, it is postulated that a fire in one area can cause short circuits potentially resulting in secondary fires or cable failures in other fire areas where the cables are routed. The secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." . | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-13
49913 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-03-13 13:00 | 2014-03-13 15:46 | 2014-03-13 | CONTAMINATED PLANT EMPLOYEE RECEIVED MEDICAL TREATMENT INSIDE THE RESTRICTED AREA "An employee with a wooden splinter in his right hand reported to the on-site dispensary this afternoon. The plant nurse administered first aid. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination present was on the employee's right pant leg, 12,550 dpm/100cm2. The plant nurse allowed the employee to return to work. The employee remained inside the Restricted Area over the course of the event." The licensee will inform R2 (Hartland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-03-17
49912 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-12 | 2014-03-13 15:32 | 2014-05-20 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO A RADIOGRAPHER'S HAND The following information was received from the State of Texas via email: "On March 13, 2014, the Agency [Texas Department of Health] was notified by the licensee's Site Radiation Safety Officer (SRSO) that one of its radiographer trainees may have received an overexposure while performing radiography at a field site on March 12, 2014. The radiographers were using a QSA880D camera containing a 69 curie iridium - 192 source. At 2100 hours [CDT], the radiographers had completed a shot and the trainee went to the camera to disconnect the guide tube from the camera. The trainee stated while attempting to disconnect the guide tube he observed the reading on the dose rate meter had gone back up. The trainee backed away from the camera and the source was returned to the fully shielded position. It is unknown at this time where the source was located in the guide tube. The SRSO stated the trainee may have been in contact with the guide tube for as long as 15 seconds. The SRSO stated the radiographer trainer was near the trainee during the event. The SRSO stated the trainee's self-reading dosimeter was off scale. The SRSO did not know if the trainee's alarming rate meter was alarming at the time of the event. The SRSO stated he was not at the licensee's facility when he contacted this Agency, but he was returning to the facility. The SRSO stated he would provide additional information as soon as they had a chance to interview the individuals involved. The Agency contacted the licensee's Corporate Radiation Safety Officer who stated they were on their way to the company's facility to do reenactments and preliminary dose assessments. The SRSO stated the trainee's dosimetry had been collected and will be sent for processing. No other individual received an exposure due to this event. The Agency contacted the Radiation Emergency Assistance Center/Training Site (REAC/TS) and informed them of the event. REAC/TS agreed to provide the licensee with assistance when requested. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-9167 * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 3/14/14 AT 0957 EDT VIA FAX * * * "The Agency was contacted by the licensee's Corporate Radiation Safety Officer (CRSO) at 1700 [CDT] on March 13, 2014 and provided with additional information on the event. The CRSO stated they had interviewed the radiographers involved in the event and discovered a second radiography trainee was involved. The CRSO stated the three individuals were shooting welds on a tank. The two radiography trainees were inside the tank in a man lift basket operating the camera. The camera would hang on the side of the tank. The radiography trainees would place the collimator to perform the shoot and then back off from the camera the distance of the control cables, approximately 35 feet, and operate the camera. The trainer was in a man lift outside the tank placing film. The CRSO stated the camera had been retrieved from the wall of the tank and placed in the basket with them while they waited to set up for the next shoot. The radiography trainees stated they were in the basket for as long as 15 minutes, with the source not fully shielded. The radiography trainee who tried to remove the guide tube stated he had difficulty removing the guide tube, so the 10 to 15 second estimate for the time he spent trying to remove the guide tube was accurate. The radiography trainee stated when they retracted the source to the fully locked position, it took about one quarter turn of the crank handle to fully retract the source. "During the interviews with the radiographers, it was discovered that the radiography trainee who attempted to remove the guide tube was not wearing any personnel monitoring devices. He had left them in the truck. The other radiography trainee was wearing their dosimetry, but failed to turn the alarming rate meter on. The CRSO stated the dosimetry will be sent to their dosimetry [lab] for processing. "The CRSO stated they had contacted REAC/TS for assistance. They have taken the radiography trainee who attempted to remove the guide tube to the hospital for blood samples to be provided to REAC/TS. The radiography trainee will be taken to a medical facility again on March 14, 2014. "The Agency contacted the CRSO at 0700 [CDT] on March 14, 2014, and asked the condition of the radiography trainee's hand. The CRSO stated they were not aware of any issues with the individual's hand. The Agency discussed the previous event in Texas with similar circumstances. The consultant for the licensee working with the CRSO was also the consultant in the previous event and is providing the licensee with information gained in that event. "The licensee currently plans to have the Site RSO to manage the health aspects of this event. The CRSO will manage the investigation of the event. The CRSO stated the former Division of Nuclear Materials Safety Director for NRC Region IV will meet them in La Porte on March 14, 2014, to help with the reenactment." Notified the R4DO (Farnholtz), FSME EO (McIntosh) and FSME Resources via email. * * * UPDATE FROM ART TUCKER TO DONG PARK ON 3/15/14 AT 2120 EDT VIA EMAIL * * * "On March 15, 2014, the Agency [Texas Department of Health] was notified by the licensee that based on the reenactment of the event, they have calculated the exposure to the hand of the radiography trainee to be 3,680 rem. The calculation is based on the trainee's hand being 0.5 centimeter from the source for 10 seconds. The licensee reported the whole body deep dose equivalent was 6.0 rem for the trainee. The licensee stated they examined the trainee's hand today and did not see any visual effects of the exposure. The licensee stated the trainee has not experienced any pain in his hand. The licensee stated they will continue to monitor the trainee's hand. The licensee stated they are still corresponding with REAC/TS. "The badge for the second trainee in the basket was read by the dosimeter processor and reported to be 3.327 rem. The licensee stated based on the reenactment they believed the reading to accurately reflect the individual's exposure." Notified the R4DO (Farnholtz), FSME EO (Dudes), FSME Resources via email. * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 4/23/14 AT 0925 EDT VIA EMAIL * * * "On April 20, 2014, the Agency was notified by the licensee they had completed their investigation into the exposure to the radiographer who had come into contact with the guide tube while the source was not shielded. The investigation determined that the source was located at a distance of six inches from the hand of the radiographer when he contacted the guide tube. Interviews with the radiographer who retracted the source determined that the crank out handle had been rotated almost one full turn to retract the source, not one-quarter turn as initially reported. The error in the initial report was due to the radiographer who returned the source to the fully shielded position not having a clear understanding of the term he used as English is not his primary language. Based on that information, the calculated dose to the radiographer's hand is 4.0 rem for the event. The calculated whole body dose to the radiographer was calculated to be 12.0 rem TEDE [Total Effective Dose Equivalent]. The hand and TEDE dose calculated by this Agency are consistent with the numbers assigned by the licensee. Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (Azua), FSME EO (McIntosh) and FSME Resources via email. * * * UPDATE AT 1756 EDT ON 05/20/14 FROM ART TUCKER TO S. SANDIN VIA EMAIL * * * "On May 20, 2014, the Agency received a copy of the NRC Form 5 for the radiography trainee. The Form 5 listed the TEDE dose for 2014 as 12.369 rem and the SDE Max Extremity dose as 15.680 rem. Also, the reporting criteria was changed to match the exposure reported by the licensee. "Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Gepford) and FSME (McIntosh) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-21
49911 | 0 | WATERFORD STEAM ELECTRIC STATION |  |  |  |  | 2014-03-12 16:00 | 2014-03-13 14:46 | 2014-03-13 | PART 21 - ALLEN BRADLEY TYPE 700RTC RELAY SPURIOUSLY DE-ENERGIZING "This is a non-emergency notification from Waterford 3 required under 10 CFR PART 21 concerning an apparent deviation from dedicated manufacturing specifications. "On 10/17/2013, it was determined that there have been multiple inadvertent actuations of Engineered Safety Features Actuation Signal (ESFAS) equipment over the previous seven months. These equipment inadvertent actuations are occurring due to Allen Bradley type 700RTC relays spuriously de-energizing. The failure mode causes the relays to intermittently de-energize causing the associated equipment to perform its ESFAS function, not adversely impacting steady state plant operations. "The failed relays have been sent to the qualifying vendor and two other failure analysis laboratories for testing. The results were reviewed by Waterford 3 engineers and although the failure mode could not be repeated in the laboratory, the laboratories identified less than adequate solder joints on the relay control circuit and a failed capacitor. The cause of the failed capacitor was identified as less than adequate installation practices during manufacturing. Engineering has determined that effects of these deviations, combined with installation in an application near the qualifying vendor's maximum specified environmental conditions, relevant to elevated voltage and ambient temperatures, has resulted in accelerated aging effects on the sub-components of the relays. The failures have been observed on relays that have been in-service greater than three years. "Entergy concluded that for the applications for which the failure mode has been observed, and for other applications where these relays have been installed for more than 3 years, the failures did not result in a substantial safety hazard. However, on 3/12/2014, Entergy completed an evaluation concluding that, had this relay type been installed in other safety related normally energized applications for greater than 3 years, it could have resulted in a substantial safety hazard. Compensatory measures to preclude the malfunction of these relays, until long-term corrective actions are completed, have been implemented. As an interim measure the installed time for these relays is limited to 3 years or less, The Waterford 3 Site VP was informed the same day, 3/12/2014. "Waterford 3 has determined that the only other Entergy nuclear facility utilizing these Allen Bradley relay types, possibly in a safety related application, is at James A. Fitzpatrick, to which this condition has been communicated." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-03-13
49910 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-03-13 09:37 | 2014-03-13 14:12 | 2014-03-13 | APPARENT SECONDARY CONTAINMENT AIRLOCK DOOR INTERLOCK MALFUNCTION "At 0937 EDT on March 13, 2014, Operations determined that both the inner and outer secondary containment airlock doors, on the 50 foot elevation of the reactor building, had been simultaneously opened for approximately one minute. This event occurred while an employee was exiting secondary containment at the same time when an employee was attempting to enter secondary containment. Upon recognition of the condition, the employees took action to secure both doors. The apparent cause of this event was malfunction of the secondary containment airlock door interlock. However, upon investigation no failures of the interlock could be identified. The interlock was satisfactorily tested multiple times following the event. "This condition is being reported in accordance with 10CFR50.72(b)(3)(v)(c), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. With both doors open, Surveillance Requirement 3.6.4.1.3 of Technical Specification 3.6.4.1, Secondary Containment, was not met, rendering secondary containment inoperable. At the time at the time of the condition, Unit 1 was engaged in Operations with the Potential to Drain the Reactor Vessel (OPDRV) and was crediting Secondary Containment as Operable. "This event did not result in any adverse impact to the health and safety of the public. "The safety significance of this is minimal. Secondary containment was only inoperable for approximately one minute. This event did not result in any adverse impact to the health and safety of the public. "The door interlock was investigated and tested multiple times with no abnormalities noted. "The NRC Senior Resident has been notified." The licensee is establishing a door watch as a compensatory measure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-13
49909 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2014-03-13 06:31 | 2014-03-13 13:43 | 2014-04-14 | STANDBY LIQUID CONTROL SYSTEM SAMPLE CONCENTRATION OUTSIDE TECHNICAL SPECIFICATION LIMITS "On March 13, 2014 at 0631 EDT, sample analysis of the Standby Liquid Control (SLC) System tank yielded a sodium pentaborate concentration outside the technical specification [TS] limits, rendering both subsystems inoperable. The sodium pentaborate concentration was found to be 4 parts per million low, at 13.598% by weight, below the required concentration of 13.6% by weight. The Standby Liquid Control System tank concentration was diluted during restoration activities following planned maintenance of the B Standby Liquid Control System pump. This condition could have prevented the fulfillment of the safety function required to mitigate the consequences of an accident. Chemical addition to the Standby Liquid Control System tank is in progress to restore the sodium pentaborate concentration to within Technical Specification limits." The licensee has notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township. * * * RETRACTION FROM KEN BRESLIN TO VINCE KLCO ON 4/14/2014 AT 1329 EDT * * * "A subsequent review of the analytical data has determined that the SLC tank sample met the Technical Specification requirement for operability (13.6 weight percent) and therefore, there was no reportable condition. "The licensee has notified the NRC Resident Inspector." Notified the R1DO (Burritt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-03-13
49908 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2014-01-16 | 2014-03-13 13:05 | 2014-07-23 | PART 21 - UNSEATING OF VALVE SPRING ON SCRAM SOLENOID PILOT VALVE "This concerns an evaluation being performed by GE Hitachi Nuclear Energy (GEH) regarding a malfunction of a Scram Solenoid Pilot Valve (SSPV), which has been observed to impair control rod scram performance. As stated herein, GEH has not concluded that this is a reportable condition in accordance with the requirements of 10CFR 21.21(d). The SSPV manufacturer (ASCO Valve, Inc.) has not yet concluded its own investigation under 10CFR 21, and the results of that investigation are needed as input for the GEH evaluation. The manufacturer has issued an Interim Report, which provides confidence that this condition is limited to a very small portion of the suspect population. "A malfunction of a Scram Solenoid Pilot Valve was attributed to the disengagement of the valve spring from the valve plunger. The effect of the malfunction is to degrade scram performance of an affected control rod. The safety significance of this condition cannot be determined at this time, but several mitigating and compensatory functions have been identified." This evaluation affects Fermi 2, Columbia, Dresden 2-3, Oyster Creek, Peach Bottom 2-3, Quad Cities 1-2, and Browns Ferry 1-3. * * * UPDATE AT 1502 EDT ON 07/23/14 FROM LISA SCHICHLEIN TO S. SANDIN VIA FAX * * * "Subject: Completed Evaluation of Part 21 Potentially Reportable Condition Notification: Unseating of Valve Spring on SSPV "This letter provides information concerning an evaluation now completed by GE Hitachi Nuclear Energy (GEH) regarding the malfunction of Scram Solenoid Pilot Valves (SSPVs), which have been observed to impair control rod scram performance. As stated herein, GEH has concluded this condition is Not Reportable for two of the affected plants (Enrico Fermi 2 and Columbia Generating Station plants), but GEH does not have sufficient information to fully evaluate the safety significance of the condition for the remainder of the potentially affected plants. Given that, GEH closes this 10 CFR Part 21 evaluation with a Transfer of Information to potentially affected licensees, in accordance with the requirements of 10 CFR 21.21(b) and will communicate the determination of Not Reportable to the identified plants where sufficient information was available to make that determination. "Although the Enrico Fermi 2 and Columbia Generating Station plants are included in the attached list of U.S. plants potentially affected, inspections of all suspect SSPVs remaining at those plants indicate that no other SSPVs at those plants exhibit the condition (as informally reported to GEH), and therefore those plants were determined to not have a reportable condition. "This letter closes the supplemental 60-Day Interim Report Notification (MFN 14-010 R0), provided on March 13, 2014, per 10 CFR 21.21(a)(2). "If you have any questions, please call me at (910) 819-4491. "Sincerely, "Dale E. Porter "Safety Evaluation Program Manager "GE-Hitachi Nuclear Energy Americas LLC" Notified R1DO (Gray), R2DO (Musser), R3DO (Orth), R4DO (Miller) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-03-13
49907 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-03-13 10:39 | 2014-03-13 11:48 | 2014-04-02 | SAFEGUARDS REPORT - UNAUTHORIZED PERSON ENTRY INTO A PROTECTED AREA An actual entry of an unauthorized person into a protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations officer for additional details. * * * RETRACTION ON 4/2/14 AT 1657 EDT FROM JIM MORRIS TO JEFF ROTTON * * * Based on a review of the event, the event should have been reported in the safeguards event log, and this report is being retracted. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations officer for additional details. Notified R4DO (Gepford) and the Part 73.71 group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-03-13
49906 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-03-12 14:22 | 2014-03-12 21:18 | 2014-03-12 | SECONDARY CONTAINMENT INOPERABLE AND UNPLANNED ISOLATION OF BUILDING VENT RADIATION MONITOR "At 1422 EDT on March 12, 2014, Nine Mile Point Unit 2 declared secondary containment inoperable due to secondary containment differential pressure being positive. The positive differential pressure was related to sustained high winds from the northeast associated with Winter Storm Vulcan. The reactor building was isolated at 1630 EDT and secondary containment declared operable at 1700 EDT when Secondary Containment Vacuum was restored to greater than 0.25 inch of vacuum water gauge. The isolation of the reactor building resulted in the isolation of the reactor building vent rad monitor (Vent WRGMS [Wide Range Gas Monitors]) which is a loss of emergency assessment capability. "Secondary containment being inoperable is an 8-hour report for 10 CFR 50.72(b)(3)(v)(c), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control radioactive release.' "The unplanned isolation of the Vent WRGMS is an 8-hour report for 10 CFR 50.72(b)(3)(xiii), 'Any event that results in a major loss of emergency assessment capability.'" The NRC Resident Inspector has been informed. The licensee will notify the state. | 0 | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | LOSS COMM/ASMT/RESPONSE |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-03-12
49905 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2014-03-12 13:15 | 2014-03-12 18:15 | 2014-03-14 | LOSS OF COMMUNICATION - FEDERAL TELEPHONE SYSTEM (FTS) "At 1315 [EDT] on Wednesday March 12, 2014, while performing monthly communications testing, Pilgrim Nuclear Power Station (PNPS) discovered that portions of the Federal Telephone System (FTS) were not functioning as designed. Specifically, the Emergency Notification System (ENS), is not available from the Control Room or Technical Support Center/ Operations Support Center (TSC/OSC) while the Health Physics Network (HPN), the Reactor Safety Counterpart Link (RSCL), and the Protective Measures Counterpart Link (PMCL) are not currently available from the Technical Support Center/ Operations Support Center (TSC/OSC). All four of these systems were confirmed to be available from the Emergency Operations Facility (EOF). The initial investigation has determined that the failure has not impacted the entire FTS, but may have the potential to impair the licensee's ability to communicate in the event of an emergency. "Immediate actions are being taken to restore the system to functional status and applicable plant procedures have been entered to determine any further mitigating actions. Members of the Emergency Response Organization have been notified of the failures and the need to utilize commercial phone lines as a compensatory action. The NRC Operations Center has been contacted and informed of these communication system failures. "It cannot be determined at the time of this notification as to when the system will be restored to full functional status. "This event had no impact on the health and/or safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This notification is conservatively being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of certain emergency response communication capabilities as provided by the FTS." The NRC Resident Inspector has been notified. The licensee will notify the state. * * * UPDATE FROM KEN GRACIA TO HOWIE CROUCH @ 1712 EDT ON 3/14/14 * * * "Federal Telephone System (FTS) communications testing was completed at 1130 EDT on March 14, 2014. The FTS System has been restored to full functional status. The Emergency Response Organization (ERO) has been informed. "The licensee has notified the NRC Senior Resident Inspector and the Commonwealth of Massachusetts." Notified R1DO (Ferdas). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-12
49904 | 0 | VALCOR ENGINEERING CORPORATION |  |  |  |  | 2014-01-11 | 2014-03-12 18:24 | 2014-09-05 | PART 21 - AP-1000 SOLENOID OPERATED VALVES LEAKAGE The following was excerpted from a fax received from Valcor Engineering Corporation: "Background: "Valcor was chosen by WEC [Westinghouse Electric Corporation] as a supplier to the AP-1000 for the ASME Section Ill Class 1, 2 and 3 Solenoid Operated Valves. As part of the specification requirements Valcor is required to perform qualification testing in accordance with the requirements of IEEE-323-1974, IEEE-344-1987 and IEEE-382-1996. "Discovery: "On Saturday January 11th, 2014, Valcor's lab technician discovered that the hard faced seat of an AP-1000 Solenoid Operated qualification valve had a crack through the thickness of the valve seat to the outlet port that caused the valve to leak in the closed position beyond its Technical Specification requirement (WEC Specification APP-PV13-ZOD-101). The subject valve had undergone heat rise testing to determine actuator temperatures during its specified design basis conditions. As part of the qualification process (IEEE-323) and in accordance with the test procedure the subject valve is given a factory acceptance test (FAT) at each stage of the qualification program. "The valve design is unique to the model (V526-5631-36/40) in that the dimensional constrain resulted in a web thickness of the hard faced seat that is thinner than our standard historical valve designs. A total of eight (8) valves of this configuration (four (4) for Valve Model Number V525-5631-36 and four (4) for Model number V526-5631-40) have been delivered to Westinghouse for installation in the Sanmen and Haiyang nuclear power plants located in the People's Republic of China. Neither of these plants have loaded fuel or are operational. "The investigation, failure analyses, and stress analyses completed to-date have not provided a firm conclusion of the root cause of the crack. Westinghouse, the purchaser who imposed 10CFR21 on the procurement document of the valve models identified in question, has been informed of the condition and current status of investigation." Submitted by Jimmy Shieh Quality Assurance Director. * * * UPDATE PROVIDED BY JIMMY SHEIH TO JEFF ROTTON VIA FAX AT 0944 EDT ON 08/15/2014 * * * "Subject: An update to Interim Report initially filed on 3/12/14, revised 3/13/14 "Reference: SKA23651 previously submitted "Investigation activities since the Interim Report: "Computer Flow and Thermal Analysis conducted from March to April 2014. "Finite Element Stress Analysis rerun using Computer Flow and Thermal Analysis in April 2014. "Both analysis above suggest that the design is adequate and that stress induced by rapid temperature rise would not cause the seat to crack. "With Westinghouse assistance and permission [two] 2 production valves were disassembled and NDE (Visual, LP, radiographic, and Eddy current) of body seat area performed during May. The examinations did not identify any defect in the valve seat area. "Contrary to all stress/thermal analysis, cracking of valve seat was reproduced early June when one of the above mentioned bodies was subjected to the same thermal shock condition that caused the initial observed cracking. The second valve was tested at the same pressure and end temperature without the thermal shock. The valve seat remained intact without cracking. "Westinghouse has been supporting the Part 21 investigation that Valcor is leading. Westinghouse has reviewed all metallurgy, CFD, FEA, NDE, heat rise laboratory and other data Valcor collected during our thorough investigation. All of this information is currently being evaluated by Westinghouse. At this time, the only outstanding issue is for Westinghouse to review all AP1000 transient conditions that are applicable to PV13 solenoid valves. Westinghouse anticipates having the preliminary transient research completed imminently and estimates to take until Nov. 30, 2014 to have all calculations and transient research validated. "As stated in the original notification, the condition does not affect any operating plant. Affected valves are limited to overseas construction, none have been installed to date." Notified R2DO (Hopper) and NRR Part 21 Group via email. * * * UPDATE PROVIDED BY JIMMY SHEIH TO JEFF ROTTON VIA FAX AT 1620 EDT ON 09/05/2014 * * * "Westinghouse has informed Valcor that none of the affected valves have been installed and they are quarantined from accidental installation. Valcor therefore is not required to pursue 10CFR21 reporting further and we [Valcor] consider the report closed." Notified R2DO (Seymour) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-03-12
49903 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-12 14:00 | 2014-03-12 17:11 | 2014-03-12 | UNANALYZED CONDITION DUE TO A POSTULATED HOT SHORT THAT COULD AFFECT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience (NRC Event Number 49889) regarding the impact of unfused Direct Current (DC) circuits has determined the described condition to be applicable to Millstone Power Station Unit 3 (MPS3) resulting in an unanalyzed condition with respect to fire safe shutdown requirements. "In the postulated event, a fire induced hot short could adversely impact safe shutdown equipment. The MPS3 Main Turbine Emergency Bearing Oil Pump and Main Generator Emergency Seal Oil Pump control and indication circuits route to the main control room. It is postulated that a fire in one fire area can damage the cable and cause short circuits without protection that would overheat the cable and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by the approved fire protection program. "Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." The licensee notified the State of Connecticut and the town of Waterford. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-12
49902 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-12 14:00 | 2014-03-12 16:27 | 2014-03-12 | UNANALYZED CONDITION DUE TO A POSTULATED HOT SHORT THAT COULD AFFECT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience (NRC Event Number 49889) regarding the impact of unfused Direct Current (DC) circuits has determined the described condition to be applicable to Millstone Power Station Unit 2 (MPS2) resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. "In the postulated event, a fire induced hot short could adversely impact safe shutdown equipment. The MPS2 Main Turbine Emergency Lube Oil pump control and indication circuits route to the main control room. It is postulated that a fire in one fire area can damage this cable and cause short circuits without protection that would overheat the cable and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." The licensee notified the State of Connecticut and the town of Waterford. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-12
49901 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-03-12 08:41 | 2014-03-12 10:34 | 2014-03-12 | PYRO PANEL MAINTENANCE RESULTS IN LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 0841 [CDT] on March 12, 2014, the Unit 1 Pyro Panel (fire/smoke detection panel) was removed from service for required maintenance. The pyro panel was declared non-functional when it was removed from service. Compensatory measures have been established for all affected areas except the unit 1 Containment Building. Since a fire in the Containment Building is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). Containment temperature is being monitored while the pyro panel is out of service however this is not considered a satisfactory compensatory measure for maintaining effective assessment capability. A courtesy follow up notification will be sent when the pyro panel is returned to service and functional. "The NRC Resident Inspector has been informed." * * * UPDATE FROM DARRIN GARD TO CHARLES TEAL AT 1344 EDT ON 3/12/14 * * * The repairs to the Unit 1 Pyro Panel have been completed and the panel was returned to service on 3/12/14 at 1010 CDT. The NRC Resident Inspector has been informed. Notified R2DO (O'Donohue). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-12
49900 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-11 | 2014-03-12 09:59 | 2014-03-12 | AGREEMENT STATE REPORT - FIXED GAUGE WITH STUCK OPEN SHUTTER The following Agreement State Report was received from the State of Texas via telephone and email: The Texas Department of State Health Services received a report from the licensee concerning a stuck open shutter on a level gauge mounted on a tank. The gauge is in operation with the shutter in the normal open position. The failure to the shutter to close was discovered during routine testing. The licensee will contact the Texas Radiation Program Licensing for authorization to continue using the gauge until repaired. The device does not represent any harm to workers or to the public and a vendor will repair the gauge in 3-4 days. Follow up information will be provided in accordance with SA 300. The gauge shutter is normally open during operation. The device is a Thermo Fisher Scientific model 5201 with a 100 mCi Cs-137 source. TEXAS INCIDENT # I-9165. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-20
49899 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-11 | 2014-03-11 21:43 | 2014-03-12 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email from the State of Texas: "On March 11, 2014, the Agency [Texas Department of State Health Services] was notified of the theft of a Humboldt model 5001EZ moisture density gauge containing an americium-241 source and a cesium-137 source by the licensee. The licensee did not know the activity of the sources. The licensee stated a technician was working at a job site taking measurements every thirty minutes. The technician placed the gauge on the bed of their truck after taking a reading and left it there to talk to the site foreman. When they came back to the truck the gauge was missing. The technician and site foreman looked for the gauge, but did not find it. The technician notified his supervisor who notified the licensee's Radiation Safety Officer. The licensee stated they intend to notify the service providers they use of the theft. The licensee stated the operating rod for the cesium source was locked. Additional information will be provided as it is received in accordance with SA-300." * * * UPDATE FROM TUCKER TO KLCO ON 3/12/14 AT 0908 EDT VIA EMAIL * * * "On March 12, 2014 at 0745 [CDT], the Agency was notified by the licensee that the moisture density gauge had been recovered. The licensee had limited information on how the gauge was located and stated they will provide additional information as soon as it can be collected and verified. It did not appear to the licensee that any member of the general public received a significant exposure due to this event. Additional information will be provided to the HOO as it is received in accordance with SA-300." Notified the R4DO(Farnholtz), FSME Events Resource via email and Mexico. Texas Incident # I-9166 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-19
49898 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-03-11 10:01 | 2014-03-11 18:27 | 2014-03-11 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "An extent of condition review of all unfused ammeters circuits in Direct Current (DC) distribution systems at Columbia Generating Station (Columbia) identified areas in the plant which may be susceptible to secondary fires due to hot shorts from these unfused ammeters. It is postulated that a fire in one fire area can damage these circuits and cause short circuits without protection that would overheat the cables and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. "Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-11
49897 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2014-03-03 | 2014-03-11 14:00 | 2014-03-11 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED INDUSTRIAL GAUGE The following was received from the State of Mississippi via email: "[The] licensee reported a stuck shutter on an Ohmart Model SH-F2 level gauge, Source Holder Model No. SH-F2-30, during maintenance work to repair the gauge detector. The failure was identified on 3/3/2014 by the licensee while preparing/isolating the gauge for work to be performed on the gauge detector. A Vega Americas service engineer was on site at the time to complete the repair of the shutter mechanism. The shutter failure was identified to be caused from age and oxidation." The gauge contains 200 mCi of Cs-137. Mississippi Event Report Number: MS-14002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2014-03-19
49896 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2013-12-17 | 2014-03-11 13:40 | 2014-03-11 | AGREEMENT STATE REPORT - SHUTTER ON FIXED INDUSTRIAL GAUGE WAS BROKEN IN THE OPEN POSITION The following was received from the State of Mississippi via email: "[The] shutter on Ohmart SH-F2 fixed gauge, (sealed source Ohmart Model A-2102, sealed source serial number 2597CG, source holder model SHF-2-45) was broken in the 'open' position. Source holder shielded, removed from location and transferred to source storage location where repairs could be made by Vega Americas. After repair, gauge returned to safe operation on 3/7/14." The gauge contains 200 mCi of Cs-137. Mississippi Report Number: MS-14001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2014-03-19
49895 | 0 | ASCO VALVE INCORPORATED |  |  |  |  | 2014-03-11 | 2014-03-11 13:00 | 2014-06-16 | PART 21 - SCRAM SOLENOID PILOT VALVE NOT EXHAUSTING PROPERLY The following was excerpted from a fax received from ASCO Valve, Inc.: "Problem Description "GE Hitachi Nuclear Energy (GEH) customer Energy Northwest reported that an ASCO scram solenoid pilot valve (SSPV) Catalog number HVL266000010J 115/60, GE-H part number 107E6022P014, serial number A272718-054, CRD-SPV-118/1043 did not exhaust properly. The valve had been installed in Energy Northwest's Columbia facility for approximately 7 months and had been cycled 60-70 times. Energy Northwest's internal investigation revealed the pilot head assembly spring was not in the groove of the associated core. "Conclusion "Various tests were performed to rule out possible manufacturing non-conformances in the spring or core. The successful completion of these tests has established that when the spring is properly installed on the core, the spring will not come off in service. We have not yet identified any other conditions that could cause the spring to come off the core, except for improper assembly. "This configuration of spring and core design was used on the original 090405 scram valve. There has not been any design change to this core assembly since its inception in 1959. This spring/core assembly makes up the bulk of ASCO core solenoid offering. It is used across all of ASCO valve ranges in the Commercial, Nuclear, Military, and Petrochemical markets. ASCO has supplied over 10 million valves to these markets over the entire product offering. This Includes over 50,000 Nuclear Qualified Valves. With the exception of the 1994 and 2012 events, a review of ASCO return records found no other cases of this condition where a spring disengaged from the core. "Since ASCO does not have adequate knowledge of the actual installations and operating conditions of these valves, it was not able to be determined if this could create a 'Substantial safety hazard' as defined in 10 CFR Part 21. This information is intended to provide interim investigation results. "If you have any questions, you can contact Bob Arnone at 803-641-9395." * * * UPDATE FROM LARS GACAD TO JOHN SHOEMAKER VIA FACSIMILE ON 6/16/14 AT 0855 EDT * * * "Closure and Conclusion: Various tests were performed to rule out possible manufacturing non-conformances in the spring or core. The successful completion of these tests has established that when the spring is properly installed on the core, the spring will not come off in service. We have not yet identified any other conditions that could cause the spring to come off the core, except for improper assembly. "This configuration of spring and core design was used on the original 090405 scram valve. There has not been any design change to this core assembly since its inception in 1959. This spring/core assembly makes up the bulk of ASCO core solenoid offering. It is used across all of ASCO valve ranges in the Commercial, Nuclear, Military, and Petrochemical markets. ASCO has supplied over 10 million valves to these markets over the entire product offering. This includes over 50,000 Nuclear Qualified Valves. With the exception of the 1994 and 2012 events, a review of ASCO return records found no other cases of this condition where a spring disengaged from the core. Since ASCO does not have adequate knowledge of the actual installations and operating conditions of these valves. It was not able to be determined if this could create a 'substantial safety hazard' as defined in 10 CFR Part 21. This information is intended to provide interim investigation results. "If you have any questions, you can contact Bob Arnone at 803-641-9395." Notified R4DO (Hay) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-03-11
49894 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2014-03-11 06:00 | 2014-03-11 11:57 | 2014-03-11 | NOTIFICATION TO STATE OF MISSISSIPPI IN RESPONSE TO CONTAMINATED SPILLS/LEAKS PROCEDURE "This is a 4-hour notification to report a Notification to the State of Mississippi is being made in accordance with the Response to Contaminated Spills/Leaks procedure. "A surface contamination event has occurred at the Grand Gulf Nuclear Station that meets the State reporting criteria of 'An unmonitored and inadvertent contaminated leak or spill greater than 15 cubic feet-solid to the environment occurs.' "The source of the contamination is not known at this time, investigation to determine the source and extent of the event is in progress. The known contamination has been contained. Actions include sampling of storm drains to verify no unmonitored release outside the protected area, additional radiation protection monitoring of the area, removal of the contaminated liquid and soil, and covering of the affected ground. Installation of tenting over the area is in progress. There was no effect on plant operation. No one was injured during the event." The licensee has notified the NRC Resident Inspector, State, and local governments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-03-11
49893 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-11 09:31 | 2014-03-11 11:49 | 2014-03-11 | MILLSTONE STATION STACK RADMONITOR OUT-OF-SERVICE FOR PRE-PLANNED MAINTENANCE At 0931 EDT on 3/11/14, the Millstone Station Stack Radmonitor RM-8168 was removed from service for pre-planned maintenance. This resulted in a loss of assessment capability and is being reported under 10 CFR 50.72 (b)(3)(xiii). The licensee informed State/local agencies and the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-11
49892 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-03-10 | 2014-03-11 09:40 | 2014-03-11 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING YTTIUM-90 The following information was provided by the State of Pennsylvania via email: "Event type: [On March 10, 2014], A medical event involving the administration of yttrium-90 (Y-90) SirSpheres which is reportable under 10CFR35.3045(a)(3). Specifically, the licensee reported that an unintended organ received, as of yet, an undetermined dose during a prescribed treatment. "Notifications: On March 10, 2014, the Department [PA Department of Environmental Protection] received notification about this medical event. "Event Description: The patient underwent a Y-90 microsphere treatment. A gastric ulcer developed seemingly as a result of spheres migrating to the stomach. "Cause of the Event: Non-target flow of microspheres through an aberrant hepatic arterial vasculature supplying the stomach. "Actions: Details of the event are being developed. Further information will be given when received. The Department plans to do a reactive inspection." PA Report ID NO: PA-140007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-19
49891 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-03-11 07:00 | 2014-03-11 08:32 | 2014-03-11 | NORMAL VENTILATION PROCESS RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE Normal ventilation - normal and high range process radiation monitor, 3HVR*RE10A/B, has been removed from service for planned maintenance. The maintenance window is scheduled for 7 hours. The licensee notified the NRC Resident Inspector, the State of Connecticut Department of Environmental Protection, and Local police dispatch. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-11
49890 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2014-03-11 03:00 | 2014-03-11 03:38 | 2014-03-11 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On March 11, 2014 at 0300 [EDT], the Hope Creek Technical Support Center (TSC) ventilation system was removed from service to perform planned maintenance. The removal of the ventilation potentially affects the TSC habitability during a declared emergency requiring activation. Appropriate compensatory measures are in place while the ventilation is out of service. The Emergency Response organization duty team has been notified of the maintenance and the possible need to activate the TSC in an alternate location. The ventilation system is scheduled to be out of service for approximately 78 hours." The licensee will be notifying the NRC Resident Inspector and the Lower Alloways Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-11
49889 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2014-03-10 16:53 | 2014-03-10 22:43 | 2014-03-10 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "An extent of condition review identified that there were unfused 250 VDC circuits for the battery charger ammeters and the control circuits for various DC lube oil pumps which left the turbine building and went through the respective cable spreading room and up into the Control Room. These circuits are protected by 200 amp fuses and in some cases 100 amp fuses. The concern is that under the fire safe shutdown rules, it is postulated that a fire in one fire area can damage these circuits and cause short circuits without protection that would overheat the cables and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-10
49888 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-03-10 16:28 | 2014-03-10 19:20 | 2014-03-10 | REACTOR SCRAM DUE TO ACTUATION OF THE ALTERNATE ROD INSERTION SYSTEM "At 1628 EDT Nine Mile Point (NMP) Unit 2 experienced an actuation of the Alternate Rod Insertion (ARI) system which resulted in a reactor scram. Coincident with the scram, the Reactor Core Isolation Cooling (RCIC) system initiated. "Prior to the event, maintenance personnel were working in the vicinity of a reactor vessel level instrumentation rack and may have agitated the common drain line of the transmitters. A prompt investigation is underway to investigate the incident. "The actuation signal for the RCIC system was invalid because reactor vessel level did not reach level two and the actuation was not in response to actual plant conditions or parameters. "The reactor scram is reportable in accordance with 10 CFR 50.72(b)(2)(iv)(B) as, 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical.' "The event has been entered into the NMP corrective action program as CR-2014-001963. "The NRC Resident Inspector has been notified." The licensee has notified the State of New York. The reactor is shutdown with all rods inserted. Decay heat is being rejected to the condenser and reactor water level is being maintained by condensate, feedwater, reactor water clean up, and control rod drive systems. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-03-10
49887 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2014-02-27 | 2014-03-10 12:21 | 2014-03-10 | AGREEMENT STATE REPORT - UNDERDOSE OF Y-90 ADMINISTRATION TO LIVER The following was received from New York City Bureau of Rad Health via email: "[A] patient was receiving treatment of left lobe of liver with Y-90 Sir Spheres. Half way through the procedure the catheter became clogged. 30 mCi of Y-90 was prescribed, only 22.5 mCi was delivered. 7.5 mCi remained in the catheter. [The] initial report stated that treatment of right lobe of liver had been scheduled for April. [The] initial report stated that Physician decided to treat left lobe of liver with makeup dose of 7.5 mCi Y-90 at that time. "[The] ORH [Office of Radiological Health] inspector stated that multiple attempts were made to flush the catheter without success. The catheter was removed and the remainder of the dose was administered at the date of the initial clog with a micro-catheter. "[The] physician spoke to the vendor rep (company SureFire). [The] company stated that cause of the clog would be investigated when the Y-90 had decayed. "[The] referring physician was notified. "[This] incident is considered a reportable medical event because the administered dose differed from the prescribed dose by >20%. "[The] hospital states that if any future incidents such as this equipment malfunction occurs, they will keep the patient in treatment position to determine by measurement if proper dosage was delivered. If measurements indicate that inadequate dosage was delivered, they will draw another dose to supplement the original administration until the appropriate dose is administered to the patient." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-03-18
49886 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-03-06 15:45 | 2014-03-10 11:14 | 2014-04-29 | AGREEMENT STATE - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from the State of Texas via email: "On March 10, 2014, the Agency [State of Texas] received notice of a radiography source disconnect that occurred on March 6, 2014. The source was a 92.2 curie iridium-192 radiography source. The event occurred at a temporary field site just south of the border with New Mexico near Carlsbad, NM on the Texas side. No exposures to the public resulted from this event. No overexposures resulted from this event. The cause of the event is unknown at this time. The source was retrieved by the licensee. The licensee's initial report to the Agency [State of Texas] was later than 24 hours after the event. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident #: I-9163 * * * UPDATE AT 0912 EDT ON 04/17/14 FROM ART TUCKER TO S. SANDIN VIA EMAIL * * * "The Agency's investigation of this event has determined that there was no source disconnect, but that the radiographer failed to connect the source pigtail to the drive cable prior to connecting the drive assembly to the exposure device. Additional information will be provided in accordance with SA-300." Notified R4DO (Gaddy) and FSME via email. * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1656 EDT ON 4/29/2014 * * * "On April 29, 2014, the Agency received the final dose information for the radiographer who picked up the guide tube with the source still in it. A dose of 15.11 rem was assigned to his hand that picked up the guide tube and he received 509 millirem DDE on his whole body badge. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Haire) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-18
49885 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-03-10 05:30 | 2014-03-10 10:57 | 2014-03-10 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of Colorado via email: "At appx. 5:30 MST on 3/10/14 the licensee's employee noticed that the window in his vehicle had been broken and the contents stolen. This included a CPN Model MC-1-DR portable nuclear gauge (Serial Number : MD10800432) containing two licensed sources (10 mCi Cs-137 and 50 mCi Am:Be). "The vehicle was parked at the employees residence. The gauge was contained within a locked transport container. Although, the vehicle was locked there was no secondary tangible barrier preventing unauthorized removal of the gauge. "The event was reported to the Wheatridge police on the morning of 3/10/14 and to the Colorado Department of Public Health and Environment at appx. 8:15 a.m. MST 3/10/14. "The Colorado Department of Public Health and Environment received a follow up call at appx. 11:00 a.m. MST 3/10/14, indicating that the gauge was located by a member of the public and recovered by the licensee. "The gauge was still in the locked transport container when it was recovered and there was no signs of damage to the case or indications that an attempt was made to open the case. "A site visit will be conducted by a Colorado Department of Public Health and Environment inspector to interview staff and complete the investigation of the incident in the near future." Event Report ID Number: CO14-I14-03 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2014-03-18
49884 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-08 03:25 | 2014-03-08 10:25 | 2014-03-08 | UNIT 2 LOSS OF SECONDARY CONTAINMENT DUE TO DISCHARGE DAMPER FAILURE "On March 8, 2014 at 0325 [EST], Secondary Containment Zone 2 (Unit 2 Reactor Building) differential pressure went to 0.0 inches WG [water gauge] following a routine transfer of Unit 2 Reactor Protection System (RPS) Power supplies. Upon restoration from the RPS power supply transfer, one of the Reactor Building Exhaust Fans tripped due to a malfunction of its discharge damper. Zone 2 HVAC was restored at 0335 by placing the other train of fans in service. Zone I (Unit 1 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone 2 differential pressure recovered to SR 3.6.4.1.1 requirements of 0.25 inches WG within a few minutes and was verified to be stable. LCO 3.6.4.1 was entered at 0325 and exited at 0354. Tech Spec for Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge for all three Reactor Building Ventilation Zones. "There have been no further perturbations in differential pressure and secondary containment remains operable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a safety function. There is no redundant Susquehanna Secondary Containment System." The licensee notified the NRC Resident Inspector. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-08
49883 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-02-18 | 2014-03-07 16:52 | 2014-03-07 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of Texas via email: "On March 7, 2014, the Agency [Texas Department of Health] was notified by the licensee that one of its vehicles had been stolen on February 18, 2014. The vehicle contained a moisture density gauge, Troxler model 3340, serial number 17909, containing 1.48 GBq of Americium-241/Beryllium serial number 4713350 and 0.30 GBq of Cesium-137 serial number 507394. A local police report was filed. No recovery of vehicle or gauge. One violation cited for not reporting incident within regulatory timeframe. Any further information will be reported within SA 300 guidelines." Texas Incident #: I-9162 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-17
49882 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-03-07 13:58 | 2014-03-07 15:26 | 2014-03-07 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A construction supervisor failed a random fitness-for-duty test. The employee's access to the plant has been revoked. The NRC Resident Inspector has been notified. Notified R2DO (Rose). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2014-03-07
49881 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-03-05 | 2014-03-07 08:27 | 2014-03-07 | AGREEMENT STATE REPORT - UNDER DOSE INVOLVING YTTRIUM 90 MICROSPHERES The following information was received by email: "On March 6, 2014, UMass Memorial Health Care (license number 60-0096) reported [to the Massachusetts Radiation Control Program] that on March 5, 2014 they had under dosed a patient by more than 20% using Y-90 microspheres. Further pertinent data is: "Prescribed Activity: 26.4 mCi of Y-90 (in one fraction injection) Delivered Activity: 20.4 mCi of Y-90 (more than 20% different from prescribed) "Resulting in: Prescribed Liver dose: = 32.6 Gy Delivered Liver dose: = 25.2 Gy Dose difference in organ: = 740 rads (i.e., greater than 50 rem and 20% difference) "Note Also: Effective dose (requested): 32.6 Gy * 0.04 = 1.3 Sv Effective dose (delivered): 25.2 Gy * 0.04 = 1.0 Sv Effective dose difference: 1.3-1.0=0.3 Sv = 30 rem (greater than 5 rem difference)" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-03-17
49880 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-06 16:05 | 2014-03-06 20:41 | 2014-03-06 | SECONDARY CONTAINMENT AIRLOCK DOOR INTERLOCK MALFUNCTION "At 1605 EST on March 6, 2014, Operations determined that both the inner and outer secondary containment airlock doors, on the 50 foot elevation of the reactor building, had been simultaneously opened for approximately one minute on March 5, 2013. This event occurred while an employee was exiting secondary containment. The inner door failed to latch and opened as the employee was opening the outer door. Upon recognition of the condition the employee took action to secure both doors. The cause of this event was malfunction of the secondary containment airlock door interlock. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. With both doors open, Surveillance Requirement 3.6.4.1.3 of Technical Specification 3.6.4.1, Secondary Containment, was not met, rendering secondary containment inoperable. "Repairs to the secondary containment airlock door interlock have been completed. "This event did not result in any adverse impact to the health and safety of the public. "The NRC Senior Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-06
49879 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-03-06 09:06 | 2014-03-06 19:33 | 2014-09-09 | UNANALYZED CONDITION REGARDING POTENTIAL TORNADO MISSILE DAMAGE TO EMERGENCY DIESEL EXHAUST PLENUM "The condition described below is being reported as an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B) and per the guidance of NUREG-1022, Rev. 3. "On 03/06/2014 at 0906 PST, Diablo Canyon Power Plant (DCPP) identified a nonconforming condition involving the Emergency Diesel Generator (EDG) ventilation exhaust plenums installed in Unit 1 and Unit 2. Specifically, the radiator exhaust plenums and exhaust piping need to be re-evaluated to ensure adequate protection against flying debris that could be generated by a tornado. "The occurrence of such an event is highly unlikely and there is no imminent concern regarding severe weather involving tornados. The EDGs are located inside the power plant structure and are capable of performing their safety function. Compensatory measures are being developed to address the associated nonconformance. "This event does not adversely affect the health and safety of the public. "The licensee informed the NRC Resident Inspector." * * * UPDATE PROVIDED BY RUSS CRUZEN TO JEFF ROTTON AT 2245 EDT ON 09/09/2014 * * * "This condition does not adversely affect the health and safety of the public. "Based on an extent of condition review being performed for this event, the issue identified in the original event notification 49879 has also been determined to similarly affect the ventilation systems associated with the Unit 1 and 2 Vital 480 volt AC switchgear and battery/inverter equipment. "The condition described in this update is being reported as an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B) and as an event or condition that could have prevented the fulfillment of a safety function per 10 CFR 50.72(b)(3)(v)(A). "Compensatory measures are being developed to address the associated condition. "The licensee informed the NRC Resident Inspector." Notified R4DO (Azua) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2014-03-06
49878 | -1 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2014-03-06 10:26 | 2014-03-06 11:22 | 2014-04-03 | FEED TUBE LEVEL SENSOR FAILED AS AN ITEM RELIED ON FOR SAFETY "Feed tube level sensor was found to be in a state such that it has failed as an IROFS [Item Relied On For Safety] for a fire accident sequence leading to the loss of a criticality control. Another IROFS is in place and the accident sequence continues to meet performance requirements. Less than a safe mass was always maintained. This event is being reported because only one item relied on for safety, as documented in the Integrated Safety Analysis summary, remains available and reliable to prevent a nuclear criticality accident, and has been in this state for greater than eight hours. "Portion of the plant affected: FMO [Fuel Manufacturing Operation] Press." The licensee notified the North Carolina State Radiation Protection Branch, New Hanover County Emergency Management, and NRC Region II. * * * UPDATE ON 4/3/14 AT 1457 EDT FROM SCOTT MURRAY TO DONG PARK * * * "On 3/6/14, GNF-A [Global Nuclear Fuels - America] conservatively made a 1 hour event notification (EN 49878) due to a discovery that a feed tube level sensor had failed. After further review, it has been determined that a second control remained available, reliable, and the remaining IROFS was sufficient to meet performance requirements. As a result, the event notification is retracted." Notified R2DO (Vias) and NMSS EO (Lombard). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2014-03-06
49877 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2014-02-21 | 2014-03-05 17:05 | 2014-03-05 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT WITH Y-90 SIR-SPHERES MICROSPHERES The following information was received by email: "On February 21, 2014 a physician in the department of Interventional Radiology (IR) at Renown Regional Medical Center in Reno, NV prescribed a patient with 26.73 mCi of Y-90 to the liver. This isotope is listed on the RAM license 16-12-0016-01 as item K, sealed sources (Sirtex Medical Limited SIR-Spheres microspheres). This case was approached in the same manner as the previous 20+ cases. The physician felt that the entire dose was appropriately delivered, therefore he went to air and flushed the catheter. The case was ended without incident. After the dose calculations were performed, it was found out that only 54.2% of the dose was delivered. The technicians investigated the delivery system and found that the majority of the undelivered isotope was in/around the 3-way stop system. The company representative [SIRTex] was [at the licensee's site] and after lengthy discussion with the physician, it is felt that the stop might have been defective. The patient and the referring physician were notified." Nevada Event: NV140006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2014-03-13
49876 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-03-05 15:00 | 2014-03-05 16:08 | 2014-03-05 | OFFSITE NOTIFICATION DUE TO DRY SHIELDED CANISTER TEST RESULTS "This report is being made to provide information to the NRC regarding Monticello Dry Shielded Canister (DSC)-16. "On February 17, 2014, dye penetrant examinations were performed on the outer top cover plate (OTCP) to shell weld on dry shielded canister (DSC)-16. This was a re-examination of a linear indication identified on January 24, 2014. The results of the re-examination identified a 1.6 inch linear indication that remained after surface conditioning. This indication had not been previously detected by nonconforming nondestructive examination previously reported by TriVis Inc. "Xcel Energy is evaluating the condition and will remedy prior to moving the cask to the ISFSI [Independent Spent Fuel Storage Installation] pad. "The associated DSCs loaded during the current campaign successfully passed their helium leak tests. Helium leak checks are performed to demonstrate confinement and boundary integrity. Thus, public health and safety is not affected. "Since the licensee communication plan also notified other government agencies, this report is being made pursuant to 10CFR50.72(b)(2)(xi) and 72.75(b)(2)." The above referenced dry shielded canister is currently located on the refuel floor in the reactor building. The licensee notified the NRC Resident Inspector. | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | PRESS RELEASE/OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) | 72.75(b)(2) |  |  | 0 | 2014-03-05
49875 | -1 | WATERFORD | 3 |  |  | [3] CE | 2014-03-05 09:12 | 2014-03-05 14:10 | 2014-04-16 | POTENTIAL IMPACT ON UNFUSED DIRECT CURRENT AMMETER CIRCUITS IN THE MAIN CONTROL ROOM "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined that a similar condition is applicable to the Waterford 3 Nuclear Station resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R requirements. The original plant wiring design and associated analysis for an ammeter measuring current from the train AB Class 1E battery to its associated power distribution panel does not include overcurrent protection features to limit the fault current and is routed through multiple fire areas. The ammeter is located on the train AB power distribution panel in the train AB switchgear room. "In the postulated event, a fire could cause one of the ammeter wires to short to ground. Simultaneously, it is postulated that the fire could cause another DC wire from the opposite polarity on the same battery to also short to ground. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). There is no effect on plant operation. Fire watches have been implemented for affected areas of the plant as an interim compensatory measure." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 4/16/14 AT 1814 EDT FROM MARK CARTER TO DANIEL MILLS * * * "Subsequent engineering evaluation has determined that the circuit for an ammeter measuring current from its Class 1E battery to its associated power distribution panel is not routed through multiple fire areas. Therefore, the IER 13-54 related condition is not, and was not, an unanalyzed condition at Waterford 3 that significantly degraded plant safety, and thus not required to be reported under 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. Notified R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-05
49874 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-03-05 09:58 | 2014-03-05 13:20 | 2014-03-05 | INADVERTENT ACTUATION OF THE EMERGENCY NOTIFICATION SYSTEM "A planned actuation of the emergency sirens across the state of Ohio was scheduled as part of a Severe Weather Awareness activity. When Columbiana County, Ohio, was activating their county sirens at 0958 EST, they inadvertently depressed the button which activated all 120 sirens within the Beaver Valley Emergency Planning Zone, which included Beaver County, Pennsylvania and Hancock County, West Virginia sirens. "This event is reportable as a 4-hour Non-Emergency Notification 10 CFR 50.72(b)(2)(xi) as 'A News Release or Notification of Other Government Agency.' "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-03-05
49873 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2014-03-05 10:20 | 2014-03-05 11:20 | 2014-03-05 | DISCOVERY OF INDIVIDUAL PATHWAYS THAT COULD BYPASS FLOOD BARRIERS "During walk downs to ensure the availability of flood protection barriers, a condition was identified which had the potential to adversely impact the ability to address external flooding conditions. Several individual pathways between both unit's Turbine Building and Auxiliary Building were identified that could bypass flood barriers. In the aggregate however, the current equipment could become overwhelmed and the flooding in the Auxiliary Building could then potentially challenge equipment necessary to remove residual heat. "The identified pathways were for the most part unscheduled partially filled conduits. There were no isolation features on these pathways and no barriers to flooding were in place between the Turbine Building and Auxiliary Building thus the potential existed to bypass the existing flood barriers. Flooding of the Turbine Building conceivably could have resulted in the accumulation of water in sufficient quantities to fill the Turbine Building to the height of the external floodwaters which could enter the Auxiliary Building via one or more deficient flood barrier. These floodwaters would then potentially challenge equipment, located within the Auxiliary Building, which is required to remove residual heat. "This condition has been determined to be reportable per 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(b)(3)(ii)(B). This condition is a non-emergency condition. This condition has been entered into the Corrective Action Program. "Barriers are being installed in these pathways as they are identified or compensatory measures implemented." The walk downs were performed in response to Fukishima lessons learned. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2014-03-05
49872 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-03-04 13:30 | 2014-03-05 11:10 | 2014-03-05 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee had a confirmed positive for cocaine during a random fitness-for-duty test. The employee's access to the plant has been restricted. Notified R1DO (Bower). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2014-03-05
49871 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-03-04 23:34 | 2014-03-05 02:26 | 2014-03-05 | UNIT 1 MANUALLY SCRAMMED DURING A RAPID SHUTDOWN IN RESPONSE TO A TURBINE EHC FAILURE "At 2334 EST on 3/4/14 Unit 1 was manually scammed during a Rapid Plant Shutdown. The Rapid Plant Shutdown was initiated due to an Electro Hydraulic [Control] [EHC] System failure resulting in all Low Pressure Turbine lntercept Valves failing closed. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass Valves to the Main Condenser and normal level control using Feedwater." The licensee informed both State and local agencies and the NRC Resident Inspector. A press release will be issued by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-03-05
49870 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-03-04 19:17 | 2014-03-05 01:37 | 2014-03-05 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "At 1917 hours [CST] on March 4, 2014, the Unit 1B fuel pool radiation monitor spiked high due to an invalid actuation which caused the U1 and U2 reactor building ventilation system to isolate (the control room ventilation system also isolated as designed). The Standby Gas Treatment system was already in operation for a scheduled surveillance as of 1900 hours on March 4, 2014. During the ensuing pressure transient, the Reactor Building differential pressure momentarily went positive. As a result, Secondary Containment was declared inoperable. "Given the temporary loss in secondary containment, this event is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." After the transient, the reactor building ventilation system was shutdown for scheduled maintenance and the control room ventilation system was returned to its normal configuration. The Standby Gas Treatment system was operating to support planned reactor building ventilation system maintenance. Troubleshooting of the radiation monitor spike is underway. | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-05
49869 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-03-04 05:02 | 2014-03-04 06:04 | 2014-03-06 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the Oyster Creek Nuclear Generating Station has removed the Technical Support Center (TSC) ventilation system from service. The TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately twenty hours from 0500 [EST] to 2400, today, March 4, 2014. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. ''This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE AT 1532 ON 3/6/14 FROM SPAGNUOLO TO SNYDER * * * On 3/6/14 at 1532 EST the Technical Support Center was returned to service. Notified R1DO (Bower). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-04
49868 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-03-04 01:43 | 2014-03-04 05:05 | 2014-03-04 | UNIT 2 MANUAL REACTOR SCRAM FOLLOWING LOSS OF A UNINTERRUPTIBLE POWER SUPPLY [UPS] "At 0137 EST Nine Mile Point Unit 2 experienced a loss of an uninterruptible power supply 2VBB-UPS3B which resulted in a half scram and half isolations. This caused a loss of cooling water to the Reactor Recirculation Pumps and other indications for the loss of power. "At 0143 EST a Manual Reactor Scram was inserted due to the rise of temperatures on the Reactor Recirculation Pump seal cavity temperature and motor winding temperature. "The reactor building ventilation radiation monitor went non-functional when the reactor building isolated on the loss of UPS power. The standby gas treatment system was started as required and restored the reactor building differential pressure. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS Actuation and 8-Hour report for 10CFR50.72(b)(3)(xiii) Loss of Emergency Assessment Capability. "The NRC Resident inspector has been notified." All systems functioned as required following the manual scram. All control rods fully inserted. The cause of the loss of the UPS is under investigation. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | LOSS COMM/ASMT/RESPONSE |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-03-04
49867 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-03-04 00:25 | 2014-03-04 01:50 | 2014-03-04 | SECONDARY CONTAINMENT DECLARED INOPERABLE DURING SURVEILLANCE TESTING "On March 4, 2014 at 0025 EST, Secondary Containment drawdown testing surveillance failed to meet acceptance criteria of SR 3.6.4.1.5 due to maximum flow rate exceeding the allowable value. Secondary Containment drawdown testing was being performed on Reactor Building Zone 1 and Zone 3 with Zone 2 HVAC shutdown. "Upon failure of the surveillance, Secondary Containment ventilation was realigned to a previous successfully tested and known operable alignment for Zones 1, 2 and 3. This alignment consists of all Reactor Building Zones in service and Zone 3 aligned to the Railroad Bay. "Upon restoration of Secondary Containment ventilation to a known operable alignment, operability was restored and Secondary Containment LCO 3.6.4.1 was cleared at 0128 EST on March 4, 2014. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG-1022, Rev. 3, Section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-03-04
49866 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-03-02 16:30 | 2014-03-02 22:10 | 2014-03-02 | DISCOVERED A POSTULATED HOT SHORT OF A CABLE DURING EXTENT OF CONDITION REVIEW "On March 2, 2014, during an extent of condition review for a separate problem evaluation report (PER) for the Browns Ferry Nuclear Plant (BFN), it was discovered that a postulated worst case failure hot short of cable PP679-IA associated with 4kV Shutdown Board 'A' cross-tie breaker 1824 may cause spurious opening of breaker 1824. "4KV Shutdown Board 'A' breaker 1824 is required to be closed during an Appendix R safe shutdown event in fire area 2-3. The action taken by 0-SSI-2-3 is to assure breaker 1824 is closed after placing '43 switch' (Breaker Control Transfer switch) and '43AR switch' (Appendix R Isolation switch) in the emergency position. Cable PP679-IA is routed in fire area 2-3 and fire damage resulting in a hot short could prevent closing breaker 1824 upon demand. "Therefore, this condition could result in a loss of power to credited safe shutdown equipment used for Unit 1 that would challenge the ability to provide adequate core cooling during performance of BFN Safe Shutdown Instructions. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.'. This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(ii)(B). This item has been entered into the Corrective Action Program as PER# 853503. "The NRC Resident Inspector has been notified of this event." The licensee has established compensatory actions to ensure breaker 1824 remains closed. | 100 |  |  | 100 |  |  | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-03-02
49865 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-03-02 00:13 | 2014-03-02 00:45 | 2014-03-02 | UNUSUAL EVENT DECLARED DUE A FIRE ALARM IN THE CONTAINMENT BUILDING "An Unusual Event (NOUE) was declared at 0013 EST on 3/2/2014 due to a possible fire in the protected area inside containment which could not be verified within 15 minutes (EAL HU4). A containment building smoke alarm was received at 2120 on 3/1/14 after indications that a relief valve lifted during a safety injection accumulator fill evolution. Diverse containment instrumentation was checked and showed that containment dew point was elevated while containment temperature and pressure remained steady. The fire alarm was reset and did not reflash. A containment entry will be made to investigate the alarm. There are no requests for the local fire department to respond and there are no indications of a radiological release to the environment. "The NRC Resident Inspector has been notified." The licensee notified the Commonwealth of Pennsylvania Emergency Management Agency, Beaver County in Pennsylvania, the State of Ohio, Columbiana County in Ohio, the State of West Virginia and Hancock County in West Virginia. Notified DHS SWO, FEMA, NICC and Nuclear SSA (via email). * * * UPDATE FROM BRIAN STROBEL TO HOWIE CROUCH AT 0211 EST ON 3/2/14 * * * The licensee terminated the NOUE at 0205 EST after a containment entry determined no fire or indications of fire existed. Notified R1DO (DeFrancisco) IRD (Grant), NRR EO (Nieh), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-03-02
49864 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-03-01 11:25 | 2014-03-01 14:19 | 2014-03-01 | LOSS OF SAMPLE FLOW FOR MAIN STACK WIDE RANGE RADIATION MONITOR "At 1125 [EST] on Saturday, March 1st, 2014, the Peach Bottom Atomic Power Station Main Stack Wide Range Radiation monitor was declared inoperable due to a loss of sample flow. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). The inoperability would impact the ability to declare an Emergency Action Level at a level of an Alert or higher based on Main Stack radiation release. "The NRC Resident Inspector has been notified." | 51 | 100 | 0 | 51 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-03-01
49863 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-02-24 | 2014-02-28 16:35 | 2014-02-28 | AGREEMENT STATE REPORT - OPERATING ARM FOR NUCLEAR GAUGE BROKEN The following was received from the State of Texas via email: "On February 28, 2014, the Agency [State of Texas] received a reciprocity request from a company from the State of Tennessee to perform emergency repairs on a Berthold model LB 8010 nuclear gauge containing a 20 milliCurie cesium-137 source at a generally licensed facility in Texas. The Agency [State of Texas] contacted the Texas licensee and asked if there had been a shutter problem with the gauge. The licensee stated on February 24, 2014, while they were moving the gauge from one location to another, one of their employees noted the operating arm on the shutter appeared bent. The employee attempted to straighten the operating arm and it broke off the gauge. The gauge was placed in the licensee's storage location. The licensee contacted the manufacturer who repaired the gauge shutter on February 25, 2014. The licensee stated no personnel received any significant exposure from the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-03-10
49862 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-02-28 08:42 | 2014-02-28 11:02 | 2014-02-28 | PYRO PANEL REMOVED FROM SERVICE FOR MAINTENANCE "At 0842 CST on February 28, 2014, the Unit 1 Pyro Panel (fire/smoke detection panel) was removed from service for required maintenance. The Pyro Panel was declared non-functional when it was removed from service. Compensatory measures have been established for all affected areas except the Unit 1 Containment Building. Since a fire in the Containment Building is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). Containment temperature is being monitored while the pyro panel is out of service, however this is not considered a satisfactory compensatory measure for maintaining effective assessment capability. A courtesy follow up notification will be sent when the pyro panel is returned to service and functional. "The NRC Resident Inspector has been informed." * * * UPDATE FROM RICHARD LULLING TO CHARLES TEAL AT 2215 EST ON 2/28/14 * * * "At 1704 CST on 2/28/2014 the Unit 1 Pyro Panel was declared functional following the return of the fire indicating unit (FIU) to the original status. The Pyro Panel fire detection system was successfully tested following the maintenance. The emergency assessment capability for the site's Emergency Plan has been fully restored concerning a containment fire. "The Senior NRC Resident Inspector has been informed." Notified R2DO (McCoy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-28
49861 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2014-02-27 12:22 | 2014-02-27 18:56 | 2014-03-06 | DEGRADATION OF THE TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "At approximately 1222 EST on February 27, 2014, the site discovered degradation of the Technical Support Center (TSC) ventilation air handling unit. Maintenance is in progress. The functionality of the TSC ventilation system is in question. "The emergency assessment function could have been performed in the Control Room as addressed in emergency response procedures. "This event is reported in accordance with 10 CFR 50.72 (b)(3)(xiii)." A TSC ventilation fan was vibrating because of a thrown fan blade. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1105 EST ON 3/6/2014 FROM CHRIS TRENT TO JEFF ROTTON * * * "Turkey Point Nuclear Station declared the TSC functional but degraded due to its normal power supply breaker tripping unexpectedly. The TSC is capable of going on emergency recirculation on its alternate power supply. The TSC is currently in its normal standby alignment with its power being supplied from its alternate source breaker. Compensatory measures are in place IAW 0-ADM-117, Equipment Important to Emergency Response, and will remain in place until the cause of the normal power supply breaker tripping is identified and corrected. Emergency Preparedness department will be making a notification to ERO members to report to the TSC as their primary notification again." Notified R2DO (Rose). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-27
49860 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-27 08:09 | 2014-02-27 09:06 | 2014-02-27 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATION "SYSTEM AFFECTED: Battery 201B inoperable at 1040 EST on 2/26/14 "ACTUATIONS & THEIR INITIATION SIGNALS: None "CAUSES (IF KNOWN): Low cell voltage on cell 27 "EFFECT OF EVENT ON PLANT: Inoperable DC Bus "ACTIONS TAKEN OR PLANNED: Commence shutdown and cooldown to Mode 5 "ADDITIONAL INFORMATION: None" Plant shutdown was initiated by failure to meet the action statement of Technical Specification (TS) 3.8.2.3; restore cell 27 to operable within 2 hours. The failure to meet the action statement placed the plant in a 36 hr. to cold shutdown time clock. At 0809 on 2/27/14, the licensee commenced down powering the unit to meet the TS requirement. If the cell is not recovered, the licensee expects to achieve cold shutdown by 2300 on 2/27/14. Their 36 hr. clock expires at 0040 on 2/28/14. The plant is stable with all other safety busses available via onsite and offsite power. The licensee notified the State of Connecticut, Waterford dispatch and the NRC Resident Inspector. * * * UPDATE FROM THOMAS CLEARY TO CHARLES TEAL AT 1600 EST ON 2/27/14 * * * "At 1347 [EST] on February 27, 2014, Millstone Power Station Unit 2 exited the shutdown action statement for Technical Specification (TS) 3.8.2.3 'D.C. Distribution-Operating'. The 125-volt DC bus train has been restored to operable status. Operators had reduced plant power to approximately 16%. The plant is increasing power and is presently at approximately 27% power. "The NRC Resident Inspector has been notified." Notified R1DO (DeFrancisco). | 0 | 74 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-02-27
49859 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-02-27 03:30 | 2014-02-27 03:37 | 2014-02-27 | HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM DECLARED INOPERABLE "On February 24th at 0400 [EST], the Division 3 diesel (HPCS diesel) was declared inoperable for planned maintenance. Technical Specification (TS) 3.8.1 condition B was entered with a required action to restore the diesel to operable status within 72 hours. Shortly after starting the diesel for post maintenance testing, operations observed erratic voltage regulator operation. The diesel was secured at 1621 on 2/24/14 before completing the required post maintenance operability test and troubleshooting is ongoing. "At 0330 on 2/27/14, the High Pressure Core Spray System (HPCS) was declared inoperable and TS 3.5.1 condition B was entered. With the HPCS system declared inoperable, TS 3.8.1 condition B was exited in accordance with the following note modifying TS 3.8.1: 'Division 3 AC electrical power sources are not required to be OPERABLE when High Pressure Core Spray (HPCS) System is inoperable.' "The HPCS system is a single train system that is discussed in Chapters 6 and 15 of the Final Safety Analysis Report. The unplanned inoperability of the HPCS system is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D) as, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.' "The condition has been entered into the NMP corrective action program as CR-2014-001623. "The NRC Resident Inspector has been notified." * * * UPDATE FROM RODGER ORZELL TO JOHN SHOEMAKER AT 1210 EST ON 2/27/14 * * * The NMP Unit 2 Division 3 diesel testing was completed satisfactorily. The licensee declared the Division 3 diesel and HPCS systems operable at 1013 EST on 2/27/14 and exited TS 3.8.1 and 3.5.1. The licensee has notified the NRC Resident Inspector. Notified the R1DO (DeFrancisco). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-02-27
49858 | -1 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-02-26 18:02 | 2014-02-26 18:56 | 2014-03-12 | FAILURE OF A BARRIER IN PLACE Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM JOHN NIMTZ TO DANIEL MILLS AT 1324 EDT ON 3/11/14 * * * Further review determined that this condition was not a vulnerability in a safeguard system. The NRC Resident Inspector has been notified. Contact the Headquarters Operations Officer for additional details. Notified R3DO (Passehl), ILTAB (Wray), and Part 73.71 Group (Email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-02-26
49857 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2014-02-26 07:30 | 2014-02-26 18:18 | 2014-02-26 | 24 HOUR FITNESS-FOR-DUTY REPORT INVOLVING FALSE NEGATIVE ERRORS DURING QUALITY ASSURANCE TESTING "Contrary to the requirements in 10 CFR 26.137(b), a DHHS [Department of Health and Human Services] certified laboratory returned results for a blind specimen that were inconsistent with what was expected. On 02/25/2014, dilute blind specimens from the same lot # were sent to the three contracted DHHS laboratories. Upon review by the Callaway MRO [Medical Review Officer] at approximately 07:30 [CST] on 2/26/2014, it was discovered that one of the laboratories (Toxicology) reported results of negative. That result was inconsistent with the certification received from the blind provider (ProTox) certifying the specimen as negative and dilute. Later in the day on 2/26/14, the remaining two labs (Quest and CRL) also returned results of negative instead of negative and dilute. "10 CFR 26.719(c)(3), reporting requirements requires that 'If a false negative error occurs on a quality assurance check of validity screening tests, as required in  26.137(b), the licensee or other entity shall notify the NRC within 24 hours after discovery of the error.' "While it initially appears that the blind specimen certification provided by ProTox may be in error, since all three DHHS labs obtained the same testing result, additional investigation is necessary. This report is being made conservatively until the cause can be determined." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2014-02-26
49856 | 0 | NUCLEAR LOGISTICS, INC. |  |  |  |  | 2014-01-28 | 2014-02-26 17:19 | 2014-02-26 | PART 21 REPORT INVOLVING A POTENTIAL MANUFACTURING DEFECT IN REPLACEMENT MASTERPACT CRADLES The following information was received via facsimile: "Part 21 Report No: P21-01312014 "Subject: Report of potential defect per 10CFR Part 21 primary disconnect assembly "Pursuant to 10CFR 21.21(d)(3)(ii), AZZ/NLI is providing written notification of the identification of a defect. This letter is to notify you of a potential manufacturing defect concerning primary disconnect assemblies used on Masterpact replacement cradles. These assemblies are used in the replacement of the circuit breakers in low voltage switchgear. "The following information is required per 10CFR 21.21(d)(4), "(i) Name and address of the individual or individuals informing the Commission. Aron Seiken, Vice President Nuclear Logistics, Inc. 7410 Pebble Drive Ft. Worth, TX 76118 "(ii) Identification of the facility, activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. Facility: Nuclear Logistics, Inc. 7410 Pebble Drive Ft. Worth, TX 76118 "The specific part which fails to comply or contains a defect: "Primary disconnect (p/n AHX30701) for Square D replacement low voltage switchgear breaker cradles (model LGSB4). "(iii) Identification of the firm constructing or supplying the basic component which fails to comply or contains a defect. "The primary disconnect was manufactured by Square D Services (Schneider Electric) and supplied as a dedicated component by Nuclear Logistics, Inc. "(iv) Nature of defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "The cradle is an adaptor between the replacement circuit breaker and the existing switchgear cubicle. Part of the interfaces is the primary disconnects (fingers). The cradle primary disconnects connect to the bus stabs in the switchgear. The cradle primary disconnects are designed to account for vertical misalignment of the stabs in the switchgear. The primary disconnect fingers have vertical flexibility (float) that maintains the finger pressure on the bus stabs when the bus stabs are not completely aligned in the vertical axis. "The fabrication drawing for the primary disconnect fingers had an incorrect tolerance. If the fingers are made with a dimension at the low end of the specified tolerance, there will be interference with a mating part. This reduces or eliminates the vertical float for the fingers. If the cradle is installed in a switchgear cubicle with vertically misaligned bus stabs, the disconnect fingers may have inadequate contact pressure. This condition may result in a higher than normal contact resistance from the cubicle stab to the cradle primary disconnect. The higher contact resistance at any one finger contact could cause an unacceptable temperature rise at that connection point. At very high temperatures, the springs that maintain the finger contact pressure could relax, which would further increase the connection resistance and cause additional overheating. "This would not be an issue if there was no vertical misalignment of the switchgear cubicle stabs. See the additional clarifications in section (vi) below. "(v) The date on which the information of such defect or failure to comply was obtained. "The information that there is a defect was obtained on January 28, 2014. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for being supplied for, or may be supplied for, manufactured or being manufactured for one or more facilities or activities subject to the regulations in this part. "The issue is applicable to 1600amp cradles only. The same and similar disconnects are used in the different cradle designs identified below. A list of the cradle types, primary disconnect part numbers and affected facilities (plants) in Table 1 as follows: "TABLE 1 Plant Name / Cradle-Breaker Type / Primary disconnect part number / Quantity / Original breaker type-Notes OPPD-Ft. Calhoun/LGSB4 with Masterpact NW breaker/AHX30701/18/Original breakers: GE AK-50. OPPD replaced all AHX30701 with narrower disconnect p/n R300112 TVA-Browns Ferry/LGSB4 and LGSB21 with Masterpact NW breaker/AHX30701/28/Original breakers: GE AK-50. Entergy-River Bend/LGSB9 Masterpact NW breaker/R300112/5/ Original breakers: AKR-50. Narrower disconnect. FENOC-Beaver Valley/LGSB4 Masterpact NW breaker/AHX30701/20/Original breakers: GE AK-50 FPL-St. Lucie/LISB2 Masterpact NW breaker/AJF30101/15/Original breakers: ABB K-1600 FPL-Turkey Point/LISB2 Masterpact NW breaker/AJF30101/12/Original breakers: ABB K-1600 SCE-SONGS/LISB2 Masterpact NW breaker/AJF30101/8/Original breakers: ABB K-1600 Nextera Energy-Seabrook/LISB2 Masterpact NW breaker/AJF30101/4/Original breakers: ABB K-1600 "Additional details: "- This issue does not affect all of the cradles identified above. Since the issue is a result of incorrect manufacturing tolerances, it will not be present on all cradles. "- The overheating issue could be a problem with replacement circuit breakers for GE AK-50 circuit breakers. Due to the construction of the switchgear cubicles, there can be vertical misalignment of the stabs in the switchgear. If the primary disconnect float is not adequate, the overheating issue identified above could occur. "- The overheating issue is expected to be much less prevalent or non-existent on the replacements for GE AKR and ABB K-line circuit breakers. The construction of the switchgear cubicles results in good vertical alignment of the stabs in the switchgear, so the amount of cradle finger vertical float is not as critical. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "NLI has generated Technical Bulletin TB-14-001 to direct the plants for inspections to determine if the manufacturing defect is present in the specific applications. The Technical Bulletin will be issued to the potentially impacted plants by March 4, 2014. "NLl is in process of revising test plans to include verification of the proper operation of the primary disconnects during factory acceptance testing. The verification will be performed on 100% of supplied cradles. "Square D Services is revising manufacturing drawings to eliminate any tolerance stack up issue that could limit the vertical movement of the finger contacts of the primary disconnect assemblies. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "NLI Will submit NLI Technical Bulletin TB-14-001 to all facilities where the potentially impacted Masterpact breakers have been installed. The technical bulletin provides a summary of the issue and provides instructions for inspection and testing of the cradles. Please contact me with any questions or comments." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-02-26
49855 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-02-23 | 2014-02-25 15:00 | 2014-02-25 | AGREEMENT STATE REPORT - SHUTTER FAILURE ON BERTHOLD DENSITY GAUGE The following information was received from the Commonwealth of Pennsylvania via fax: "NOTIFICATIONS: Licensee notified the Department [PA DEP Bureau of Radiation Protection] via email and voice message after close of business on February 24, 2014. This event is reportable within 24-hours per 10 CFR 30.50(b)(2). "EVENT DESCRIPTION: During the pressure pumping operations at a well fracturing job site, personnel observed an unexpected fluctuation in density readings. The density gauge was inspected and attempts to turn the shutter handle to the closed position caused it to separate from the body of the gauge. It was observed that the roll pin, which attaches the shutter handle to the shutter shaft, had come out causing the shutter handle to separate from the shield housing. The pin was replaced, the handle reattached, and the gauge shutter was closed and locked. No elevated exposure to personnel is anticipated. The gauge was then removed from service, placed into storage, and the manufacturer was notified. Manufacturer: Berthold Model: LB 8010 Serial Number: 10049 Isotope: Cs-137 Activity: 20 mCi Source Serial Number: 0180/08 "CAUSE OF THE EVENT: The roll pin, which attaches the shutter handle to the shutter shaft, came out causing the shutter handle to be removed from the shield housing. More information will be forwarded upon receipt of final report. "ACTIONS: The density gauge has been removed from operations and is in storage in a Williamsport, Pennsylvania facility. The licensee is working with the manufacturer to investigate the event, make repairs, and determine root cause. The Department plans to do a reactive inspection." PA Event Report ID No: PA140006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-05
49854 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-25 08:33 | 2014-02-25 13:32 | 2014-02-25 | MILLSTONE STATION STACK RADMONITOR OUT-OF-SERVICE FOR PRE-PLANNED MAINTENANCE At 0833 EST on 2/25/14, the Millstone Station Stack Radmonitor RM-8169 was removed from service for pre-planned maintenance. This resulted in a loss of assessment capability and is being reported under 10 CFR 50.72 (b)(3)(xiii). At 1110 EST on 2/25/14, the maintenance was completed and the radmonitor restored to service. The licensee informed State/local agencies and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-25
49853 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-04-05 | 2014-02-25 08:56 | 2014-02-25 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILS TO RETRACT The following information was received from the Commonwealth of Pennsylvania via fax: "Notifications: This was originally reported to the NMED within 30-days per 10 CFR 34.101 (a)(2) on May 5, 2011 and was assigned NMED Number 110278; however, after further evaluation it was determined it should have also been reported under 10 CFR 30.50 which requires immediate reporting. "Event Description: TEI Analytical Services was performing gamma radiography of pipe welds at its facility in Washington, PA. During the first exposure, the radiography source assembly was unable to be retracted to its shielded position due to excessive bend in the guide tube. When retraction of the source was attempted resistance was encountered within 1/4 turn of full retraction. The source was returned to the collimator and a second attempt was made to retract the source. Again, resistance was encountered at the same location. Additional attempts to retract the source were terminated and the RSO was notified. "Equipment information: Exposure Device: Make: Source Production and Equipment Company Device Model: SPEC-150 Serial #:0418 Date Quarterly Inspection/Maintenance performed: 03/08/2011 Sealed Source: Isotope: Ir-192 Make: Source Production and Equipment Company Model: G-60 Serial #: SB2506 . Activity: 105 Ci (3885 GBq) "Cause of the Event: Exceeding the maximum 6 [inch] radius bend for guide tube. A longer tube would have prevented the event. "Actions: The device was operated by the RSO to retract the source conventionally and the resistance was significant. The RSO made one entry to the area to lower the stand height; thereby, decreasing the radius of the guide tube. Total time for the entry was 11 seconds including walking to the stand from the shieldwall and return. Time to lower stand was 2 seconds. The source was cranked back into the device and the event was terminated. The equipment was disassembled and inspected by the RSO. No physical damage was evident to the guide tube, or to the external/internal materials of the guide tube." PA Event Report ID No. PA110010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-05
49852 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-03-01 | 2014-02-25 08:56 | 2014-02-25 | AGREEMENT STATE REPORT - EXTERNAL CONTAMINATION IDENTIFIED ON A PACKAGE The following information was received from the Commonwealth of Pennsylvania via fax: "Notifications: Licensee emailed notification to the Department's [Pennsylvania Department of Environmental Protection] South Central Regional Office on March 2, 2011. This was initially evaluated as not exceeding the limits of  71.47; however, further assessment determined it as an immediate reporting event under 20.1906(d)(1). "Event Description: On March 1, 2011, a Nuclear Medicine Technologist from Geisinger logged in a package from Triad Isotopes radio pharmacy. Exposure on the surface of one of the containers labeled White I was measured to be 14 mR/hr. The contamination was found to be limited to the handle of the package. The inside of the container and its contents were not contaminated. The contents were removed and the empty contaminated package was double bagged and placed in decay storage. "According to calculations provided by the licensee, the initial net wipe reading of the handle area on the suspect package was 10,670 dpm for an area of 6 [inch] x 1.5 [inch] or 15 cm x 3. 8 cm. Assuming a 10% wipe efficiency, the activity per unit area was 1,840 dpm/cm2 (0.8 mCi/cm2), which exceeded the maximum permissible limit of 220 dpm/cm2 as noted in  71.47. "Cause Of The Event: Cross-contamination from the radio pharmacy. "Actions: The Department called Triad Isotopes on March 2, 2011. It was stated that the driver, vehicle, and all other areas that the driver and the package came into contact with, were surveyed and no contamination was found. Triad Isotopes confirmed that the shipment met the requirements of the Radioactive White I when it left and only contained 20 mCi of Tc-99m. No further actions were taken." PA Event Report ID No. PA110005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-03-05
49851 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2014-02-23 12:00 | 2014-02-23 12:23 | 2014-03-15 | INTEGRATED PLANT COMPUTER SYSTEM REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "[On] February 23, 2014, at approximately 1200 [EST], the Fermi 2 Integrated Plant Computer System (IPCS) was removed from service outside of the Control Room to support planned system maintenance. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform and [was rendered] out of service when the IPCS [was] removed from Emergency Response Facilities (ERFs). These systems will be unavailable to all Emergency Response Facilities (ERFs) for approximately 50 hours. During this time, dose assessment (Raddose) capability will only be available in the manual data input mode. The SPDS indications and Raddose remain available to the plant staff in the Control Room, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems as needed. A follow-up notification will be submitted when the IPCS is completely restored, including SPDS and ERDS, to the Operational Support Center, the Technical Support Center, and alternate facilities. This 8-hour non-emergency notification is being made per the requirements of 10 CFR 50.72(b)(3)(xiii), as an event that results in a major loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0905 EDT ON 03/15/14 FROM PAUL GRESH TO S. SANDIN * * * The following update was received from the licensee: "On February 23, 2014, at approximately 1200 [EST], the Fermi 2 Integrated Plant Computer System (IPCS) was removed from service to support planned system maintenance. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform and were out of service when IPCS was removed from service. "On March 15, 2014 at approximately 0800 [EDT], planned maintenance on ERDS, SPDS, and IPCS is complete, restoring full Emergency assessment capabilities to the control room and all onsite emergency response facilities." The licensee informed the NRC Resident Inspector. Notified R3DO (Passehl). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-23
49850 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2014-02-22 16:37 | 2014-02-22 19:32 | 2014-02-27 | OFFSITE NOTIFICATION CONCERNING A SMALL HYDRAULIC FLUID SPILL "[The New Jersey Department of Environmental Protection] and Ocean County Health [Department were] notified of a spill of approximately 1 cup of hydraulic fluid (oil) that leaked from a vehicle and entered a storm drain at approximately 1615 [EST]." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM JEREMY SHARKEY TO CHARLES TEAL AT 1954 EST ON 2/27/14 * * * "Upon subsequent review of the Material Safety Data Sheet associated with the fluid that leaked from the vehicle, it was determined that the fluid was not a hazardous substance as defined by the State of New Jersey (Appendix A of N.J.A.C. 7:1E). Additionally, it was determined that the fluid did not reach surface water. Based on this information, the New Jersey Department of Environmental Protection (NJDEP) was notified that the fluid that leaked from the vehicle did not reach surface water and was not a hazardous substance. The NJDEP notification was updated for the record. "For the above reasons, the 4 hour non-emergency ENS notification made under EN # 49850 is hereby retracted" The NRC Resident Inspector has been informed. Notified R1DO (DeFrancisco). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-02-22
49849 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-02-19 | 2014-02-21 16:28 | 2014-02-21 | AGREEMENT STATE REPORT - UNDERDOSE OF Y-90 TO A PATIENT The following information was obtained from the Commonwealth of Massachusetts via email: "Report of medical event. A dose that differs from the prescribed dose by more than 50 rem to an organ, the liver, and the total dose delivered differs from the prescribed dose by 20% or more. "The licensee reported to the Agency [Massachusetts Radiation Control Program] on 2/21/2014 that on 2/19/2014 licensee administered yttrium-90 SIR-Spheres to patient's left lobe of liver and that treatment was palliative in nature; that 7.2 millicuries of yttrium-90 was prescribed; and that 5.06 millicuries was administered resulting in an underdose of 29.7 percent. "The licensee reported that the dose administered differs from the dose prescribed by more than 50 rem to the liver and that licensee will determine what the likely dose difference actually was. "The licensee reported that during the procedure it was apparent that spheres were collecting on the tubing between the stop cock and the source vial and that when procedure was concluded, assays were performed of treatment apparatus and source vial and licensee determined that only 5.06 millicuries of the 7.2 millicuries prescribed was administered. "The licensee reported that the manufacturer, Sirtex, will be onsite on February 24th to begin a joint investigation. "The licensee reported that the referring physician has been notified and it is unknown at time of report whether referring physician has elected to notify patient. "The licensee reported that they do not anticipate any adverse effects on the patient's treatment outcome. "The licensee will submit a written report within 15 days in accordance with the requirements of 105 CMR 120.594(A)(4). "Root cause and corrective action are not known at this time and the Massachusetts Radiation Control Program continues to investigate." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-03-03
49848 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-02-21 08:39 | 2014-02-21 15:45 | 2014-02-21 | AUDIBILITY OF ALARM SYSTEM "A report was made to the facility Corrective Action Program (PIRCS) at 0839 [EST] on 2/21/2014 regarding difficulty hearing plant announcements and alarms in the recently renovated Building 110B restroom. Testing of the Public Address (PA) system confirmed that the PA system was difficult to hear. The speakers associated with the PA system are also used for annunciating the site criticality accident alarm evacuation warning. Subsequent testing of the criticality evacuation alarm indicated the alarm was difficult to hear as well. Safety management personnel were notified of the problem and the restroom was locked and posted with signs indicating the area was not to be occupied, pending resolution of the audibility issue. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2014-02-25
49847 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2014-02-13 | 2014-02-21 10:33 | 2014-02-21 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The following was received from the State of Maine via fax: "An emergency exit sign was lost. A portion of the Texas Instruments facility at 5 Foden Road in South Portland, Maine, where emergency exit signs are in use, was in the process of being renovated by a construction contractor. The contractor removed the sign from the wall unaware that this exit sign was not an electric exit sign. The sign was removed and its location has not been identified." Event Report ID No. ME-14-0001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2014-03-03
49846 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-02-21 01:30 | 2014-02-21 10:09 | 2014-02-21 | FAILED POWER SUPPLY AFFECTING RADIATION MONITORS "At 0130 CST, a degraded power supply resulted in multiple Area Radiation Monitors (ARMs) reading erroneously low. As a result, this condition is reportable under 10 CFR 50.72(b)(3)(xiii) as these ARMs are used to assess NUE and Alert thresholds. Portable Radiation Monitors have been placed in identified affected areas as a compensatory measure. "The health and safety of the public was maintained as the plant was in a normal condition with no initiating event in progress or signs of elevated radiation on any other unaffected radiation monitors. "The NRC Resident Inspector has been notified." | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-21
49845 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-02-20 06:55 | 2014-02-20 08:30 | 2014-02-20 | AUXILIARY BUILDING SERVICE WATER RETURN RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On February 20, 2014, at 0655 CST, Kewaunee Power Station rendered the Auxiliary Building Service Water Return Radiation Monitor (R-20) non-functional for planned maintenance. R-20 is used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that would result in an Alert or Unusual Event and is being conservatively reported under 10CFR50.72(b)(3)(xiii) as a loss of emergency assessment capability. "R-20 is planned to be restored to functional by 1430 CST today, 2/20/2014. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-20
49844 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-02-19 14:03 | 2014-02-19 20:31 | 2014-02-19 | FITNESS FOR DUTY - LICENSED EMPLOYEE SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A licensed employee supervisor had a confirmed positive test for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2014-02-19
49843 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-02-07 | 2014-02-19 17:41 | 2014-06-25 | AGREEMENT STATE REPORT - UNKNOWN RADIOACTIVE MATERIAL DISCOVERED IN GARBAGE TRUCK AT LANDFILL The following is a summary of information provided via email from the State of Arkansas: On February 7, 2014, the Environmental Manager of Republic Services, Inc. contacted the Arkansas Department of Health (ADH) to inform the State that a gate radiation monitor at a landfill near Bauxite, AR had alarmed for an incoming garbage truck. ADH sent three health physicists to inspect the truck. Initial surveys indicated the highest reading on contact on the bottom of the truck of 3.7 mR/hr. ADH was unable to identify the specific isotope. The truck was isolated and ADH returned on February 10, 2014 to survey and evaluate the material on the truck. ADH observed removal of the trash from the truck and identified a vacuum cleaner bag inside a bag of trash that contained the radioactive material. The vacuum cleaner bag was removed and placed in a five gallon plastic bucket which was posted and securely stored in a storage room at the landfill. The survey readings on the side of the bucket were 20 mR/hr. ADH returned on February 12, 2014 to survey the vacuum cleaner bag and evaluate for radioactive decay. The plastic bucket continued to read 20 mR/hr on contact. Further radiation surveys showed highest reading on contact with the plastic bucket were 42 mR/hr and 200 mR/hr localized near the bottom of the vacuum cleaner bag. ADH notified Republic Services, Inc. of the necessity to hire a consultant for identification and disposal of the radioactive material. ADH plans to be present when the consultant is onsite. Arkansas Report Number: AR-2014-002 * * * UPDATE FROM KAYLA AVERY TO DANIEL MILLS VIA EMAIL ON 6/25/14 AT 1107 EDT * * * "On March 7, 2014, Chase Environmental Group arrived at the Saline County Landfill, owned by Republic Services, Inc. that is located in Bauxite, Arkansas. The vacuum cleaner bag was opened and the Radioactive Waste Specialists attempted to analyze the material. However, the Exploranium meter could not identify the radionuclide. The material was packaged and transported by Chase Environmental Group to Teledyne Brown Engineering in Knoxville, Tennessee for sampling and disposal. A report from Chase Environmental Group was received on June 20, 2014, which stated that the material contained Cobalt-56, but the activity could not be determined. The Department [ADH] was also not able to determine where this radioactive material came from or how the material got into the public domain. "The Arkansas Department of Health considers this incident to be closed." Notified R4DO (Allen) and FSME Events Resource email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2014-02-27
49842 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-02-19 10:19 | 2014-02-19 15:32 | 2014-02-19 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION FAILURE "On 2/19/2014 at 1019 EST, the Technical Support Center emergency ventilation system failed to operate during TSC Ventilation Operability Check per EP-MA-124-1001-F-02 performed by Limerick Emergency Preparedness staff. Troubleshooting of this equipment deficiency found a blown control power fuse. The fuse failure is attributed to its age. The system has been restored to operational status as of 1430 EST on 2/19/2014. "If an emergency had been declared and TSC activation was required, the TSC would have been staffed and activated unless the TSC became uninhabitable due to ambient temperatures, radiological or other conditions. The Station Emergency Director would assess habitability in accordance with station procedures. TSC relocation of personnel would be directed as required until such time that the TSC emergency ventilation system was returned to service." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-19
49841 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-02-19 08:29 | 2014-02-19 14:29 | 2014-02-20 | LOSS OF PRIMARY CONTAINMENT OXYGEN AND HYDROGEN MONITORING "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0829 (PST), on 2/19/2014 the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was removed from service for planned maintenance activities. The Division 1 sample rack is expected to be out of service for 14 hours. The redundant Division 2 sample rack was previously removed from service for maintenance and remains out of service for repairs. Compensatory measures to monitor primary containment for hydrogen and oxygen are available via grab samples using chemistry procedures. "The NRC Resident Inspector has been notified." * * * UPDATE FROM NICHOLAS RULLMAN TO VINCE KLCO AT 1400 EST ON 2/20/2014 * * * "Following completion of surveillance activities, the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was returned to operable status at 1037 PST on 2/20/2014, restoring its required emergency assessment capability. "The NRC Resident Inspector has been notified." Notified the R4DO (Allen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-19
49840 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-02-18 18:20 | 2014-02-18 22:15 | 2014-02-18 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), Event or Condition that could have prevented fulfillment of a Safety Function needed to Control the Release of Radioactive Material. An employee entered a secondary containment [airlock] interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately 3 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, has remained less than -0.25 inches H2O at all times. Initial investigation determined that a mechanical interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the mechanical interlock." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-02-18
49839 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2014-02-17 | 2014-02-18 11:00 | 2014-02-18 | AGREEMENT STATE REPORT - POSSIBLE DISCONNECT OF INDUSTRIAL RADIOGRAPHY EQUIPMENT SOURCE The following information was provided by the State of Kansas via email: Industrial radiography equipment failed to function as designed which resulted in a possible source disconnect. The radiography equipment was located at a work site in Winfield, Kansas. The radiography equipment contained a 56 Curie Ir-192 source. The State of Kansas will update the event as more information becomes available. Kansas Item Number: KS140003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2014-02-26
49838 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-02-18 09:44 | 2014-02-18 13:18 | 2014-02-18 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "At 0944 CST, on February 18, 2014, both doors in the Secondary Containment Airlock were opened concurrently. The doors being open at the same time caused a failure to meet SR 3.6.1.4.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.1.4. Upon discovery, immediate action was taken to close the doors. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to operable status. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-02-18
49837 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-18 07:28 | 2014-02-18 11:55 | 2014-02-18 | RADIATION MONITORS WILL BE REMOVED FROM SERVICE FOR PRE-PLANNED MAINTENANCE "The four Main Steam Line Radiation Monitors 3MSS*RE75, 3MSS*RE76, 3MSS*RE77 and 3MSS*RE78 along with Terry Turbine Aux Feedwater Steam Exhaust Radiation Monitor 3MSS*RE79 will be removed from service to support a scheduled design change. "This condition is reportable per 10CFR50.72(b)(3)(xiii). "This equipment is expected to be restored to service within 72 hours." The licensee informed the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-18
49836 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-02-14 15:30 | 2014-02-18 10:28 | 2014-02-18 | AGREEMENT STATE REPORT - LOST CESIUM-131 SEEDS The following was received from the State of New York via email: "NYS DOH BERP [New York State Department of Health Bureau of Environmental Radiation Protection] received a call from Chief Physicist for Integrated Medical Professionals, PLLC. NYS RAM License No. 5335, Lake Success, NY. "A shipment of fifty-seven (57) Cs-131 seeds was sent to ISORAY MEDICAL, in Washington State (license WN-L0213-1). The shipment was received 2/14/14 and the receipt survey showed high radiation readings. The package was isolated and opened to reveal that the shipping pig was open inside of the outer package. Forty-four (44) seeds were found in the box. The shipment of seeds contained three activities, 1.28 millicurie, 1.1 millicurie, and 2.1 millicurie. It is not currently known which batch the missing seeds were from. The common carrier has been notified. Washington State DOH [Department of Health] has been notified. The root cause investigation is ongoing. A press release has not been issued. A reward has not been offered" Event Report ID: NY-14-01 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-02-26
49835 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2014-02-18 08:29 | 2014-02-18 10:35 | 2014-02-21 | POTENTIAL LOSS OF SNM Potential loss of Special Nuclear Material. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM CALVIN PITTMAN TO VINCE KLCO ON 2/21/14 AT 1530 EST * * * The Plant Shift Superintendent was notified by the common carrier that the shipment was delivered. The licensee notified the NRC Region 2 contact. Contact the Headquarter Operations Officer for additional details. Notified R2DO (Seymour), ILTAB (Bunch), NMSS EO (Sampson), IRD (Grant) and 73.71 Group via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST SNM OR SPENT FUEL SHIPMENT | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 73.71(a)(1) |  |  |  | 1 | 2014-02-26
49834 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-02-17 00:44 | 2014-02-17 10:42 | 2014-02-17 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "Reactor Building (Secondary Containment) pressure rose above the Technical Specification Surveillance requirement of 0.25 inches vacuum water gauge multiple times from 0044 [PST] to 0305 [PST] on 2/17/14. The alarm was received in the control room at 0305 [PST]. This is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. Reactor Building pressure has been restored to normal (greater than 0.25 inches of vacuum water gauge), returning Secondary Containment to operable status. Highest actual value indicated was +0.21 inches pressure water gauge. The cause of the event is under investigation. "There were no radiological releases associated with the event. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-02-17
49833 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-02-16 17:25 | 2014-02-16 21:37 | 2014-02-16 | CONTRACT WORKER TRANSPORTED TO HOSPITAL AFTER FALL "At time 1725 [EST] on 02/16/2014 a contract worker fell ten to fifteen (10-15) feet off of a ladder while descending the ladder above the 565 foot level in the Containment Building. The individual received lacerations to the forehead and potential other injuries. "For his work activities the individual was dressed in anti-contamination clothing. "The individual was transported via off-site ambulance in his anti-contamination clothing to H.B. Magruder hospital in Port Clinton, Ohio. A First Energy (FENOC) Radiation Protection (RP) Technician accompanied the injured person in the ambulance during the transfer to the hospital. A FENOC RP Supervisor along with the RP Technician assisted at the hospital while the injured individual received medical treatment. The protective anti-contamination clothing was removed from the individual. A full body frisk was performed and showed no contamination on the individual. "Smear readings on the anti-contamination booties and gloves showed [approximately] 1500 dpm / 100 square cm. The clothing was bagged and subsequent readings and surveys on the outside of the bag showed no readings above background. The bagged anti-contamination clothing will be transported back to Davis-Besse NPS by FENOC RP Supervision. The H.B. Magruder Hospital Treatment Room and the off-site ambulance also were frisked and showed no residual contamination." The licensee notified the State of Ohio and Lucas and Ottawa Counties. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2014-02-16
49832 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2014-02-16 12:16 | 2014-02-16 18:21 | 2014-02-17 | UNIT 2 EXPERIENCED A PARTIAL LOSS OF OFFSITE POWER WITH AUTOSTART OF DIVISION I AND III EDGS "An automatic initiation of Emergency Diesel Generators was received due to a loss of one of two off-site power sources. "On February 16, 2014 at 1216 [EST], Nine Mile Point Unit 2 experienced an automatic initiation of the Division 1 and 3 Emergency Diesel Generators [EDGs] due to a loss of Line 5. Line 5 is one of the two 115KV offsite power sources. "Line 5 was lost due to an offsite event that is currently being evaluated by the grid operator. "During the electrical transient, Nine Mile Point Unit 2 also experienced a feedwater level control lockup, requiring manual control. No Emergency Core Cooling Systems actuated, and feedwater level control was returned to automatic. Nine Mile Point Unit 2 remained at 100% power during the loss of Line 5, one of the offsite power sources. "The NRC resident has been notified." The licensee also notified the State of New York. Unit 2 is currently in a 24-hour Technical Specification Limiting Condition of Operation [TS LCO] Action Statement 3.8.1.A3. Once Division III is realigned to the "B" side Line 6 offsite power, Unit 2 will be in a 72-hour LCO. Both EDGs are currently running. There was no effect on Unit 1. * * * UPDATE PROVIDED BY MARK GREER TO JEFF ROTTON AT 1727 EST ON 2/17/2014 * * * "In addition to the initiation of Division 1 and 3 Emergency Diesel Generators, Service Water Radiation Monitor 2SWP*RE146A and Radwaste/Reactor Building Vent Gaseous Effluent Monitoring Systems were also lost. Compensatory actions were established as required by station procedures and the Offsite Dose Calculation Manual. The loss of these instruments is reportable as a major loss of Emergency Assessment Capability per 10CFR50.72(b)(3)(xiii). The Service Water Radiation Monitor 2SWP*RE146A was restored to service on February 16, 2014 at 1450 EST. The Radwaste/Reactor Building Vent Gaseous Effluent Monitoring Systems were restored to service on February 17, 2014 at 0240. It is recognized that this notification is not within eight hours of the event. "Line 5 is restored to OPERABLE February 17, 2014 at 1628. "The NRC Resident Inspector has been informed of this additional reportable condition [and the update on the lost off-site power source]. The condition has been entered into the corrective action program." The licensee also notified the State of New York Public Service Commission. The licensee exited the 72-hour LCO for the lost off-site power at 1628 on February 17, 2014. Notified R1DO(Krohn), NRREO (Monninger) and ILTAB (Whitney). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  |  | 0 | 2014-02-16
49831 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-02-14 22:45 | 2014-02-14 23:08 | 2014-02-15 | NOTICE OF UNUSUAL EVENT DUE TO EARTHQUAKE FELT ONSITE "An earthquake was felt in the control room at Virgil C. Summer Nuclear Station Unit 1 (VCSNS) at approximately 2223. The earthquake was confirmed with USGS at 2240. An unusual event in accordance with the emergency plan was declared at 2245 and NRC was notified at [2308 EST] via ENS per 10 CFR 50.72(a)(1)(i)." The plant is stable and continues to operate at 100% power. The licensee has completed preliminary building walkdown inspections with no damage noted. There were no injuries. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BETH DALICK TO JOHN SHOEMAKER AT 1108 EST ON 2/15/14 * * * "[V.C. Summer Nuclear Station] VCSNS has terminated the [Unusual] Event after walkdowns of the plant were satisfactorily completed and no aftershocks were felt. An update to ENS has also been made. The event was terminated at 1045 [EST] on 2/15/2014. The plant continues to operate at 100% power and the licensee has notified the NRC Resident Inspector. Notified R2RA (McCree), R2DO (Guthrie), NRR EO (Monninger), NRR (Uhle), IRD (Grant), DHS SWO, FEMA Ops, DHS NICC, and NuclearSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-02-14
49830 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2014-02-10 | 2014-02-14 16:39 | 2014-02-14 | PART 21 REPORT - FAILED PRESSURE REGULATOR DURING POST-INSTALLATION EDG PRESSURE TESTING "Component: Starting air pressure regulator (Nordberg P/N 1776 506). "Summary: Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 12/13/13 upon completion of a failure analysis performed on a pressure regulator part number 1776 506 (S/N 20776487) that was returned by Brunswick Nuclear Plant (BNP) following a failure that occurred during post-installation pressure testing on their emergency diesel generator [EDG] set. The downstream pressure would not maintain its set point and began to equalize to the inlet pressure. "This evaluation was concluded on 02/10/14 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. The failure to regulate downstream pressure is attributed to an o-ring within the piston guide assembly of the pressure regulating valve that was improperly installed at the factory. Failure of the o-ring's pressure boundary allows inlet pressure to leak to the outlet pressure side eventually causing equalization to occur. This equalization is undesirable since it could lead to pressures that exceed the capabilities of the engine's downstream air start solenoid valve; thereby potentially preventing the diesel engine from starting during an emergency event and performing its safety related function." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-02-14
49829 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-02-14 08:38 | 2014-02-14 14:00 | 2014-02-14 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE SUPERVISOR A non-licensed employee supervisor had a confirmed positive for marijuana during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2014-02-14
49828 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2014-02-14 03:25 | 2014-02-14 11:14 | 2014-02-24 | SHIELD BUILDING CONSTRUCTION OPENING "On 02/14/2014, an unfilled area was discovered in the concrete along the top of the shield building construction opening on the annulus side. The condition was discovered during the current steam generator replacement outage, and is likely due to not completely repouring the shield building wall opening in 2011. Analysis shows this condition is bounded by previous calculations that demonstrate the containment function is maintained such that the protection of the health and safety of the public was not in question. Further analysis is planned to reconfirm previous calculations. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM ROBERT OESTERLE TO VINCE KLCO ON 2/24/14 AT 1650 EST * * * "The FirstEnergy Nuclear Operating Company is retracting the 8-hour non-emergency notification made on 02/14/2014 (EN# 49828). "Engineering evaluation of the unfilled concrete area along the top of the shield building construction opening determined the condition did not prevent the shield building from performing all design functions as described in the Updated Safety Analysis Report. Therefore, this issue did not represent a condition that significantly degraded plant safety, and the notification made per 10CFR 50.72(b)(3)(ii)(B) is being retracted. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." Notified the R3DO (Kunowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-02-14
49827 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-02-14 01:13 | 2014-02-14 08:12 | 2014-02-14 | METEOROLOGICAL TOWER OUT-OF-SERVICE DUE TO WEATHER "On February 14, 2014 at 0113 EST, all Meteorological Tower data for wind direction was lost for Hope Creek and Salem Units 1 and 2. The loss of wind direction data occurred from environmental conditions during a period of heavy snowfall and ice accumulation. Valid wind direction from Meteorological Tower data input to the Hope Creek Safety Parameter Display System was observed to return at 0246 EST, and was confirmed by visual observation of wind direction onsite. "The loss of Meteorological Tower data had no effect on plant operations and all units [Hope Creek and Salem Units 1 and 2] remain at 100% power. "No personnel injuries resulted from the event. "The NRC Resident Inspectors has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-14
49826 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2014-02-14 01:13 | 2014-02-14 08:12 | 2014-02-14 | METEOROLOGICAL TOWER OUT-OF-SERVICE DUE TO WEATHER "On February 14, 2014 at 0113 EST, all Meteorological Tower data for wind direction was lost for Hope Creek and Salem Units 1 and 2. The loss of wind direction data occurred from environmental conditions during a period of heavy snowfall and ice accumulation. Valid wind direction from Meteorological Tower data input to the Hope Creek Safety Parameter Display System was observed to return at 0246 EST, and was confirmed by visual observation of wind direction onsite. "The loss of Meteorological Tower data had no effect on plant operations and all units [Hope Creek and Salem Units 1 and 2] remain at 100% power. "No personnel injuries resulted from the event. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-14
49825 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-12-15 | 2014-02-13 10:16 | 2014-02-13 | 60 DAY OPTIONAL TELEPHONE NOTIFICATION OF INVALID PCIS SYSTEM ACTUATION "This notification is being made in accordance with 10 CFR 50.73 (a)(2)(iv)(A) to provide information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment valves in more than one system. "On 12/15/2013, with the reactor at 100% power, invalid PCIS Group 3 actuation occurred from a momentary spike of the 'B' Refuel Floor radiation monitor which reached the instrument's high radiation trip set point. A radiation protection technician was dispatched to the refuel floor and dose rates in the vicinity of the 'B' radiation monitor detector were verified to be normal and below the alarm set points. The radiation monitor was verified to be indicating normal expected radiation levels. The detector and trip unit were replaced, a functional check and calibration of the radiation monitor was completed satisfactory and the instrument channel was returned to service. The issue has been entered into the station's corrective action program. "Both trains of Standby Gas Treatment System started as designed and Reactor Building ventilation isolated as a result of the invalid PCIS actuation. "The PCIS functioned successfully providing a complete Group 3 isolation. The PCIS Group 3 isolation involves the following systems: "Drywell and Suppression Chamber Air and Vent: V16-19-6, 6A, 6B, 7, 7A, 7B, 8, 9, 10, 23 Containment Makeup: V-16-20-20, 22A, 22B Containment Air Sampling: VG-23, 26, V109-76A, 76B Containment Air Compressor Suction: V72-38A, 38B Containment Air Dilution: VG-9A, 9B, 22A, 22B, NG-11A, 11B, 12A, 12B, 13A, 13B "Since no actual high radiation condition existed which required the PCIS Group 3 isolation, and the actuation was not in response to actual plant conditions satisfying the requirements for isolation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public. "In accordance with 10 CFR 50.73(a)(1) a telephone notification is being made instead of submitting a written Licensee Event Report. The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-02-13
49824 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-02-12 11:13 | 2014-02-12 16:17 | 2014-02-12 | CIRCULATING WATER DISCHARGE MONITOR OUT OF SERVICE "At 1113 CST on February 12, 2014, R-21 Circulating Water Discharge Monitor failed during routine surveillance testing and was declared nonfunctional. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs) - NUE (Notification of Unusual Event) and Alert classifications - when out of service. This results in a Loss of Emergency Assessment Capability while R-21 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "There are no radioactive leaks that will impact the Circulating Water System as evidenced by normal readings on R-21 prior to its failure. In addition all other liquid effluent radiation monitors that monitor releases to the Circulating Water Discharge are in-service and have normal readings. Corrective maintenance is in progress and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 10 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-12
49823 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-12 10:47 | 2014-02-12 15:48 | 2014-02-12 | HIGH RANGE STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE At 1047 EST on 2/12/14, Millstone Unit 2 removed the Stack High Range Radiation Monitor, RM 8168, from service for pre-planned maintenance. Functional test was completed and operability was restored at 1426 EST on 2/12/2014. The licensee informed the Connecticut Department of Environmental Protection, Waterford Dispatch and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-12
49822 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-02-11 06:00 | 2014-02-12 15:07 | 2014-02-12 | AGREEMENT STATE REPORT - LOST MEDICAL PACKAGE The following information was received via email: "On February 11, 2014, the RSO of Eisenhower Medical Center, LN2425-33, contacted [the California Department of Health, Radiologic Health Branch] RHB about a Bracco CardioGen Rb-82/Sr-82 generator that was packaged for shipment to the manufacturer for disposal. The package was left unattended/unsecured in an unrestricted area on February 10, 2013 between 1600 PST and 1800 PST awaiting [common carrier] pickup . The package was sealed with radioactive material labels. When the first technician arrived at the facility at approximately 0600 [PST], the box was missing and no paperwork from [the common carrier] had been left. [The common carrier] was contacted and they had no records of a pick-up. [The common carrier] has initiated an investigation. "The licensee reported the following information for the package: "Surface dose rate 19.4 mR/hr and 1 meter dose rate 323 microR/hr; "Surface wipe 713 dpm/100cm2; and "Total mCi 99.9 (3.60 GBq). "On February 12, 2014, the RSO contacted RHB and stated that someone from housekeeping placed the package in the dumpster which was picked up on February 11 and sent to the Riverside County Landfill. The landfill and Riverside County HAZMAT were informed. The licensee personnel then proceeded to the landfill to attempt to recover the package. The package has not been recovered as of this time." California Report #: 021114 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-02-20
49821 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-02-12 07:11 | 2014-02-12 14:18 | 2014-02-12 | SECONDARY CONTAINMENT BOUNDRY DOOR FOUND AJAR "On February 12, 2014 at 0711 EST, secondary containment (Unit 1 reactor building) boundary door-612 was found propped ajar with a secondary containment boundary sign stuck in the door jam, holding the door open. Upon discovery, the sign was removed from the door jam and the door was verified closed. A status walk down was performed and no other doors were found in this condition. "Although secondary containment differential pressure was maintained throughout the time period that the door was open, the door serves as a secondary containment boundary and is required to be closed for secondary containment operability. "Secondary containment alignment for removal of the 818 foot elevation (refuel floor) hatch removal had been performed at 0105 EST, February 12, 2014 and the last record of access to the area by security card reader occurred at 0044 EST by the operator performing the ventilation alignment. The potential duration of inoperability based on the available information is approximately 6.5 hours. Past operability evaluation is being performed. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev. 3 section 3.2.7 as a loss of a safety function. There is no redundant Susquehanna secondary containment system." The licensee notified the NRC Resident Inspector. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-02-12
49820 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-02-12 08:15 | 2014-02-12 09:27 | 2014-02-12 | SERVICE WATER RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "Planned preventive maintenance on service water piping will remove the service water radiation monitor from service. As a result, this represents a loss of emergency assessment capability under NUREG 1022, Revision 3, since the radiation monitor is used to assess NUE [Notification of Unusual Event] and Alert thresholds. The planned maintenance is expected to last 8 hours. During this time, the site Chemistry Department will perform sampling at this location every 30 minutes. The sampling is documented in a station procedure and allows the ability to detect NUE levels in a timely manner. As a result of sampling, reasonable assurance exists to monitor and detect rising radiation levels in order to protect the health and safety of the public. "The NRC Resident Inspector will be notified prior to removing the service water radiation monitor from service." | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-12
49819 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-02-11 14:30 | 2014-02-11 20:35 | 2014-02-11 | DRYWELL TO TORUS VACUUM BREAKER FAILURE DURING SURVEILLANCE TESTING "While cycling AO-2382A (TORUS-DW VAC BREAKER) for required surveillance testing, [the vacuum breaker] did not indicate fully closed on all available indicators. The procedure for this condition was utilized to continue to cycle the vacuum breaker to achieve closed indication on all available indicators. The vacuum breaker was cycled a total of four (4) times and dual indications were present for approximately six (6) minutes. During the six (6) minutes that the vacuum breaker indications did not show fully closed, the Technical Specification Limiting Condition for Operation (TS LCO) requirement was not met. The Monticello Safety Analysis assumes all eight (B) vacuum breakers are closed, therefore this condition is being reported per 10CFR50.72(b)(3)(ii)(B) and per 10CFR50.72(b){3)(v)(D). The vacuum breakers are all capable of performing their design function and all safety related equipment is operable." The NRC Resident Inspector has been notified. The same vacuum breaker failed its surveillance test in a similar fashion on February 7, 2014 (See EN #49808). The surveillance test for this vacuum breaker is due again on February 18, 2014. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-02-11
49818 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-02-11 18:00 | 2014-02-11 19:28 | 2014-02-11 | NONCONSERVATIVE OPERATOR MANUAL ACTIONS IDENTIFIED IN APPENDIX R ANALYSIS "Preliminary Westinghouse transient analysis calculations of Watts Bar Nuclear (WBN) Unit 1 fire protection features revealed that there is less time than previously credited to perform certain operator manual actions (OMA) to prevent Pressurizer (PZR) overfill during an Appendix R fire. "Specifically, an assumed Appendix R fire in rooms 713.0-A28, 737.0-A1A, 757.0-A2, 757.0-A5, 757.0-A9, 772.0-A1, 772.0-A2, or 772.0-A5 could result in spurious operation of multiple components in the normal and emergency charging flow paths. Westinghouse's analysis indicates the required time to isolate the normal charging path is approximately two minutes, securing the second charging pump is approximately four minutes and isolating the emergency charging path is approximately 12.5 minutes. "Based on this preliminary analysis, WBN procedures are non-conservative since they require these actions to be completed in 18 minutes. "TVA has verified that potentially impacted Appendix R equipment remains functional; however, a compensatory fire watch has been established for the above listed areas. This immediate action will ensure that the approved Appendix R Fire Safe Shutdown Plan can be achieved." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2014-02-11
49817 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-02-09 06:00 | 2014-02-11 18:40 | 2014-02-11 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following Agreement State report was received via email: "On February 10, 2014, [the California Department of Health, Radiologic Health Branch] RHB Richmond received a call from MISTRAS Group, Inc. RSO, regarding a source disconnect. On February 9, 2014, at 0600 [PST], during radiography at Chevron Refinery, using IR-100 camera, containing 31 Curies, Ir-192, s/n 6614, the source pigtail connector became disconnected from the drive cable. Following good health physics practices, the RSO retrieved and secured the source into the shielded position. Exposures to personnel [were] less than 50 millirem for this event." California Report #: 021114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-02-19
49816 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-02-09 10:35 | 2014-02-11 18:03 | 2014-02-11 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA LEFT UNATTENDED The following Agreement State report was received via email: "On February 10, 2014, [the California Department of Health, Radiologic Health Branch] RHB Richmond received a call from the MISTRAS Group RSO, indicating that a radiographer had inadvertently left behind a radiography camera when he drove off the parking lot at the Chevron Richmond Refinery. On February 9, 2014, at 1035 [PST] after the radiographer finished radiography using IR100 Camera containing 31 Curies Ir-192, s/n 6614, he left the radiography camera on the bumper of the truck; later, assuming that he left the camera inside the truck, he drove off and the camera fell onto the pavement. According to the radiographer, the camera was left unattended for a short period of time. Later, a Chevron Richmond employee noticed the camera in the parking lot and contacted the Chevron facility Manager. Chevron management contacted Mistras RSO and he drove to the refinery and took possession of the camera." California Report #: 021014 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-02-19
49815 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-01-24 | 2014-02-11 17:37 | 2014-02-11 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING UNINTENDED DOSE "During a liver radio embolization procedure with Y-90 SIRTEX Sir-Spheres on January 24, 2014 an unanticipated shunting occurred and was identified during the procedure. The procedure for the right liver lobe was stopped when the shunting was identified. The licensee runs contrast between vial doses to verify proper delivery of the microspheres. After imaging of the patient, the licensee determined on January 27, 2014 that the unintended dose to the gastric fundus was 11 Gray. The licensee reported the medical event to ODH BRP [Ohio Department of Health - Bureau of Radiation Protection] by telephone on February 11, 2014 at 3:30pm [EST]. "The referring physician and patient were notified on January 24, 2014. The patient is asymptomatic (no adverse effects) and is currently receiving medical monitoring." Ohio Report #: OH140002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-02-19
49814 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-02-10 16:50 | 2014-02-10 20:58 | 2014-02-10 | SINGLE FAILURE VULNERABILITY AFFECTING EMERGENCY DIESEL GENERATOR OPERABILITY The licensee also reported an additional 8 hour Non-emergency report in accordance with 10CFR50.72(b)(3)(v)(D) "On February 10, 2014, [at 1650 CST] Monticello station personnel identified a vulnerability where a single failure could result in the Emergency Diesel Generators (EDGs) picking up load on the essential busses in a time frame longer than what is required by Monticello Technical Specification Surveillance Requirement [TS SR] 3.8.1.12. This surveillance requires that on a simulated or actual loss of off-site power signal in conjunction with an actual or simulated ECCS initiation signal, the Emergency Diesel Generators auto-start from standby condition and energize permanently connected loads in approximately 10 seconds. The single failure vulnerability could result in the EDGs energizing the connected loads in a slightly longer time period based upon actual test data (< 11 seconds). "As a result, Technical Specification SR 3.8.1.12 was declared not met and both EDGs were declared inoperable. Monticello has subsequently isolated the single failure vulnerability and declared the EDGs operable. The station remained in a safe condition during the discovery of this vulnerability. Both EDGs remain available and functional [and operable], off-site power remains available, and the plant continues to operate in a normal condition with no initiating events present." The single failure vulnerability was associated with the 1AR 13.8KV transformer logic. The 1AR transformer is one of three off-site power sources. 1R and 2R meet the TS requirements for Off-site power. The licensee notified the NRC Resident Inspector and the State of Minnesota Duty Officer. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2014-02-10
49813 | 0 | ABB INC |  |  |  |  | 2014-02-10 17:36 | 2014-02-10 17:36 | 2014-02-10 | PART 21 REPORT - INSTRUCTION LEAFLET FOR SUBJECT RELAYS MAY BE DEFICIENT The following Part 21 Report was received via facsimile: "On December 12, 2013, ABB determined that that its Instruction Leaflet 41-682.11 (effective September 2002) for the subject relays may be deficient with regards to the external diagram connection. "With the relay connected per the typical connections shown in the instruction leaflet and the relay having verified a synchronous condition for a period of time ranging from several minutes to hours, the main element contact identified as 'CVX-1' may become stuck in the closed position. Again, this situation is dependent on each customer's control power connection scheme and may be more prevalent in certain applications, such as fast bus transfer or tie breaker applications. In cases where the contact remains closed, it may result in an unwanted connection of two asynchronous systems when the command to connect them is issued, leading to equipment damage and possible bodily injury or death. We will be updating our instruction leaflet in February 2014, to reflect the addition of an interposing contact in the control circuit to prevent this condition. "ABB's records indicate that 15 relays were supplied to Exelon (Clinton Nuclear Station), 4 relays were supplied to Duke Energy (Oconee Nuclear Station) and 10 relays were supplied to ABB d.o.o. (Slovenia). "ABB has determined, as of the date of this notification, that it does not have the capability to perform an evaluation to determine if a defect exists, and therefore in accordance with 10 CFR 21.2l(b), is making this notification simultaneously to our customers so they may evaluate the deviation or failure to comply, in accordance with 10 CFR 21(a)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-02-10
49812 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-02-09 00:30 | 2014-02-10 16:53 | 2014-02-10 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA LEFT UNATTENDED The following Agreement State report was received via email: "[The California Department of Health, Radiologic Health Branch] RHB Richmond received an incident report from the Qualspect Manager, via an email that a radiography camera had been left unattended. On February 9, 2014, between 0030 and 0245 [PST], Qualspect employees were conducting a radiography operation using [a camera containing an] Ir-192 104 Curie [source], camera s/n 4850, at the Valero Benicia Refinery. During the operation a few Qualspect rope [access] employees were in the area, their presence distracted the two radiographers thinking that another radiographer was in the area, so they left to process film. While the film was being processed, the camera was [left] dangling at 2 feet from the floor and unattended. A Valero Benicia Refinery employee discovered the suspended camera and brought it to the Qualspect employees' attention. Shortly thereafter, the Qualspect employees took possession of the camera." The California RHB considers this a major event and is conducting an investigation. There were no personnel overexposures. California Report #021014 Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2014-02-18
49811 | 0 | US ARMY 20TH CBRNE COMMAND |  |  |  |  | 2014-02-10 | 2014-02-10 14:26 | 2014-02-10 | SOURCE LOST DURING SHIPMENT "A shipment of licensed material was shipped from our CBRNE Analytical and Remediation Activity, CARA, located in Pine Bluff, AR on 3 February 2014 was not received by the consignee, Frontier Technology Corporation, 1641 Burnett Drive, Xenia, OH 45385, [Ohio license # - 03214290000] "The source, a 1.3 mCi Frontier Model 100 Cf-252 source Serial Number 4151, was shipped in a DOT Spec 7A Type A container. The transportation index on the package was 2. "This was one of two items shipped from CARA, Pine Bluff, AR [scheduled to arrive on February 10, 2014]. The second source, serial number 4152, was received by Frontier Technology Corporation today along with an unrelated package containing what appeared to be environmental samples in a combination package." Common Carrier has not claimed that they have lost physical control. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-02-18
49810 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2014-02-09 01:00 | 2014-02-09 08:10 | 2014-02-09 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "On 02/09/2014, at 0100 [EST], a major portion of Peach Bottom Atomic Power Station's [PBAPS] offsite communication capability was discovered to be non-functional due to an offsite communications equipment failure outside the control of PBAPS. Peach Bottom continues to investigate and resolve the cause of this loss of offsite communications. Peach Bottom Main Control Room ENS and offsite communication lines have been restored and are currently available. The Technical Support Center is limited to satellite phones for offsite communications. On-site communications were not affected. "This report is being submitted pursuant to 10CFR 50.72(b)(3)(xiii) as a result of a major loss of offsite communications capability. "The NRC [Resident Inspector] has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-09
49809 | 0 | WEIR VALVES AND CONTROLS, USA INC |  |  |  |  | 2014-02-07 | 2014-02-07 19:13 | 2014-02-07 | PART 21 INTERIM REPORTING REGARDING TRICENTRIC TRIPLE OFFSET BUTTERFLY VALVES The following is a summary of information provided via facsimile: "Based on recent testing conducted on a 24 inch Class 150 TRICENTRIC [triple offset butterfly valve] to evaluate bearing coefficients of friction (COF), it has been determined that there exists an unseating load that has not been accounted for on our TRICENTRIC Triple Offset Product Line. "Weir has not experienced a field failure of the product, but recent testing by a customer indicated anomalies that required review by Weir. The review of the unseating anomaly relates to two inputs; the inputted seating torque and increases in differential pressure across the disc after initial closure. Weir has developed a conservative approach for calculating this additional loading. "Weir has reviewed data from customers for several recent orders, and has determined that there is a minimal risk of failure of an item to perform its safety function. However, based on the safety related functions of these items, Weir cannot provide absolute assurance of operability on items in service without confirming with the end user. Weir will be releasing an industry notice that will address our initial findings, continue with the detailed investigation, and advise customers concerning the recommended corrective actions." Known customer - PSEG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-02-07
49808 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-02-07 10:05 | 2014-02-07 17:52 | 2014-02-07 | SINGLE DRYWELL TO TORUS VACUUM BREAKER NOT GOING FULLY CLOSED DURING SURVEILLANCE TEST "After cycling AO-2382A (Drywell to Torus Vacuum Breaker) for surveillance testing, it did not indicate fully closed. The procedure for this condition was entered and after cycling the valve several times, the vacuum breaker indicated full closed. During the approximately eight minutes that the indication showed that it was not closed, the Technical Specification Limiting Condition for Operation (LCO) requirement was not met. After validation that the vacuum breaker had opened as required, and was closed successfully, the safety function was restored. The health and safety of the public was not jeopardized as the plant was in a normal condition and an initiating event was not in progress. "The USAR [Updated Safety Analysis Report] assumes all eight vacuum breakers to be closed. This condition therefore put the nuclear power plant in an unanalyzed condition and is reportable per 10CFR50.72(b)(3)(ii)(B). "This condition, at time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident and is reportable per 10CFR50.72(b)(3)(v)(D). The licensee notified the NRC Resident Inspector, the State of Minnesota Duty Officer, and the local counties. | 70 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-02-07
49807 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2013-12-11 20:11 | 2014-02-07 16:31 | 2014-02-07 | 60 DAY REPORT FOR AN INVALID MAIN STEAM LINE ACTUATION "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This telephone notification is being made pursuant to the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of the Palo Verde Nuclear Generating Station Unit 2 'A' train Main Steam and Feedwater Isolation System (MSFIS) logic. "On December 11, 2013, at approximately 2011, Mountain Standard Time, Unit 2 was shut down in Mode 4 with Reactor Coolant System (RCS) temperature at approximately 425 degrees Fahrenheit and 1900 pounds per square inch absolute. While starting up the plant following completion of repairs to the 1A reactor coolant pump, an invalid actuation of the 'A' train MSFIS fast close logic occurred due to a random electrical failure in the 'A' train MSFIS logic cabinet. This resulted in the closure of all four Main Steam Isolation Valves and the two 'A' train Economizer Feed Water Isolation Valves. No other engineered safety feature actuations occurred and none were required. The invalid actuation was initiated by a ground fault in a 30-volt direct current power supply in the 'A' train MSFIS Logic cabinet. Repairs were completed on December 12, 2013. "This was a complete actuation of 'A' train MSFIS equipment and all the affected equipment responded as designed. RCS temperature and pressure were maintained stable using atmospheric dump valves. Feed water to the steam generators was being provided by Auxiliary Feed Water and was not affected by the event. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-02-07
49806 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-02-07 06:20 | 2014-02-07 12:16 | 2014-02-07 | SHIELD BUILDING VENT GAS RADIATION MONITOR FAILURE "At 0620 CST on February 7, 2014, 1R-22 Shield Building Vent Gas Radiation Monitor failed and was declared nonfunctional. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs); NUE (Notification of Unusual Event) and Alert classifications when out of service. It is also used for offsite dose projection calculations. This results in a Loss of Emergency Assessment Capability while 1R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 Shield Building Ventilation Stack is also monitored by high range monitor, 1R-50, which is used for the same purpose in Site Area or General Emergency classifications. 1R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 1R-22 prior to its failure. Corrective maintenance is in progress and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-07
49805 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-02-06 | 2014-02-07 08:44 | 2014-02-07 | AGREEMENT STATE REPORT - SOURCE DISCONNECT AND RETRIEVAL The following information was obtained from the State of Texas via email: "On February 7, 2014, the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) a source disconnect had occurred on February 6, 2014. The disconnect occurred while radiographers were working at a field location using a QSA model 880D exposure device with a 39 curie iridium-192 source. "The radiographers were working in a shooting bay and had been working for about five hours when the problem occurred. The RSO stated the radiographer had extended the source to the collimator and was attempting to retract the source when the source moved a few inches and then could not be moved in any direction. The radiographer contacted the RSO who directed them to secure the area and wait for his arrival. "The RSO and an assistant arrived at the facility and attempted to retract the source, but could not. The RSO stated the guide tube had a sharp bend near the area of the collimator and believed that could have damaged the guide tube causing the hang-up. The RSO disconnected the guide tube from the exposure device and using a remote handling tool, slid the guide tube down the drive cable. When the end of the drive cable was exposed, the RSO noted the source was not attached. He then shook the source from the guide tube and onto the ground. The source was covered with bags of lead shot. "The RSO connected the source to the drive cable and was able to retract the source into the exposure device. The exposure device and drive cable connectors were tested using a go-no-go device and both passed. The highest exposure received from the source retrieval was 38 millirem. No overexposures occurred and no member of the general public was exposed due to this event. The RSO stated the guide tube would be returned to the manufacturer for inspection. Additional information will be provided as it is received in accordance with SA-300." TX Incident: I-9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-02-17
49804 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-02-07 06:00 | 2014-02-07 08:19 | 2014-02-07 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO CONTAINMENT ISOLATION VALVE OVER LEAK RATE LIMIT "This event is being reported in accordance with 10CFR 50.72(b)(2)(i), 'Initiation of a Shutdown Required by Technical Specifications.' "At 2043 hours [EST] on February 06, 2014, the Perry Nuclear Power Plant entered Technical Specification 3.6.1.3 Primary Containment Isolation Valves (PCIVs), action C.1, due to leakage identified during local leak rate testing of the containment penetration for the Containment and Drywell Purge system. Leakage was identified on the outboard containment isolation valve resulting in the plant exceeding the limit for secondary containment bypass leakage. The Containment and Drywell Purge system penetration is normally isolated and remains isolated in accordance with Technical Specifications. Action C.1 requires restoration of the leakage rate within four hours. At 0043 hours on February 7, 2014, the plant entered Technical Specification 3.6.1.3, 'Primary Containment Isolation Valves (PCIVs)', action E as the leakage rate was not restored. Action E requires the plant be in Mode 3 in 12 hours and Mode 4 in 36 hours. "At 0600 hours on February 07, 2014, the Perry Nuclear Power Plant initiated a shutdown in accordance with Technical Specification 3.6.1.3, action E. Repairs to restore the penetration leakage to within allowable limits are in progress." The NRC Resident Inspector has been notified. * * * UPDATE PROVIDED BY DAVE ODONNELL TO JEFF ROTTON AT 1220 EST ON 02/07/2014 * * * "At 0943 hours [EST] the reactor shutdown to comply with Technical Specification 3.6.1.3 action E was terminated [with the reactor at 42% power]. A blind flange was installed downstream of the outboard containment isolation valve. Local leak rate testing of the containment penetration for the Containment and Drywell Purge system verified that leakage was within the limits for secondary containment bypass leakage. "The NRC Resident Inspector has been notified." The licensee has commenced increasing reactor power. Notified R3DO (Orlikowski) | 45 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-02-07
49803 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-02-07 03:00 | 2014-02-07 03:04 | 2014-02-07 | UNAVAILABILIITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 03:00 EST on Friday, February 7, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 16:00 EST on Friday, February 7. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE PROVIDED BY BRAD LEWIS TO JEFF ROTTON AT 1605 ON 02/07/2014 * * * "TSC ventilation system was returned to service following successful maintenance and post maintenance testing at 14:30 EST on Friday, February 7, 2014. The licensee has notified the NRC Resident Inspector." Notified R3DO (Orlikowski) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-07
49802 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2014-02-06 15:53 | 2014-02-06 20:17 | 2014-02-06 | UNANTICIPATED AUXILIARY FEEDWATER PUMP START AFTER SECURING EMERGENCY DIESEL GENERATOR "This report is being made in accordance with 10CFR50.72(b)(3)(iv)(A) for an Auxiliary Feedwater System Actuation. "The monthly surveillance on 31 Emergency Diesel Generator (EDG) was conducted on 6 February 2014. The EDG was unloaded and its output breaker opened at 1553 [EST]. At this time, the Non-SI Blackout Logic Defeated indication in the control room changed state from 'not illuminated' (logic defeated) to 'illuminated' (logic not defeated) without operator action. The steam-driven 32 Auxiliary Boiler Feed Pump (ABFP) auto started but did not inject water into the steam generators. The discharge valves are normally closed. Operators verified normal steam generator levels and level control and that all 480VAC Safeguards buses remained energized, then secured 32 ABFP and placed it back into AUTO. "Indian Point 3 remains at full power in Mode 1. This event did not cause any change in power. "The Senior NRC Resident and the NY State Public Service Commission have been informed." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2014-02-06
49801 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2014-02-06 12:54 | 2014-02-06 19:17 | 2014-04-04 | EMERGENCY EQUIPMENT COOLING WATER IN MANUAL OVERRIDE DUE TO HUMAN PERFORMANCE ERROR "At 1254 [EST] on February 6, 2014, while shutting down Division 2 Emergency Equipment Cooling Water (EECW), a human performance error occurred resulting in the Division 2 EECW isolation override switch being placed in manual override. Division 2 EECW remained running and continued to operate normally. The Division 2 EECW system cools various safety related components including the High Pressure Coolant Injection (HPCI) system room cooler. With the Division 2 EECW isolation override switch in manual override, Division 2 EECW may have been prevented from performing its safety function during a loss of power event. An unplanned HPCI inoperability occurred due to the Division 2 EECW inoperability which may have prevented HPCI from performing its safety function. A 14 day Limiting Condition for Operation (LCO) was entered for HPCI via T.S. LCO 3.5.1 and subsequently exited 36 seconds later upon returning the Division 2 EECW isolation override switch to normal. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on a loss of a single train safety system. The NRC Resident Inspector has been notified." The licensee reported that the individuals involved have been removed from licensee duties pending further investigation. * * * RETRACTION FROM PAUL GRESH TO DONALD NORWOOD AT 0931 EDT ON 4/4/14 * * * "The Fermi 2 Engineering staff has completed a comprehensive evaluation of the momentary mispositioning of the Division 2 EECW system overide switch initially reported on February 6, 2014. "The evaluation determined that HPCI room temperature would remain below the HPCI room steam leak detection isolation logic setpoint in the unlikely event that the momentary mispositioning resulted in the temporary interruption of the cooling water flow to the HPCI system room cooler. Over the brief period of time for which EECW would have been unavailable to support the effective operation of the room cooler, its function was not necessary for HPCI to perform its required safety functions. Therefore, event notification 49801 is retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (Passehl). | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-02-06
49800 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-12-11 08:18 | 2014-02-06 11:00 | 2014-02-06 | INVALID ACTUATION OF PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) VALVES DURING I&C MAINTENANCE "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made per 10 CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid closure of Unit 2 Primary Containment Isolation System (PCIS) valves. On December 11, 2013, at 0818 EST, an instrument technician was adjusting the output voltage of the 'A' 120-volt Reactor Protection System (RPS) motor-generator (MG) set, which is the normal power supply for the 'A' RPS bus. As the adjustment potentiometer was being moved, output voltage momentarily dropped below the setpoint of an Electrical Protection Assembly (EPA) on the 'A' RPS bus. The EPA tripped and removed power from the 'A' RPS bus. Removing power from the RPS bus resulted in PCIS valves receiving a close signal. Affected valves or systems were a Reactor Water Sample valve, Main Steam Line Drain valves, Containment Atmospheric Control System valves, Drywell Equipment Drain and Floor Drain valves, and a Reactor Water Cleanup System valve. "Other systems affected were Standby Gas Treatment, Control Room Emergency Ventilation, and Radiation Monitoring on Main Steam Lines, Main Stack, Reactor Building Vent, and Main Condenser. All actuations that resulted from the loss of power to RPS Bus 'A' were completed as expected. "This event resulted from the attempt to adjust the voltage control potentiometer on the RPS MG set. When a technician attempted to adjust the potentiometer, the movement caused the RPS MG set to momentarily and unexpectedly experience a low voltage on the output, tripping the output breakers. "Power was restored to the affected RPS bus by 0858 EST on December 11, 2013, and all affected systems were subsequently returned to service. "Since no actual plant or process conditions existed which would have caused the various actuations described above, this event is being reported per 10 CFR 50.73(a)(1) as an invalid actuation. "This issue has been entered into the site Corrective Action Program (CR 651284) for evaluation and implementation of further corrective actions. "The NRC Resident Inspector has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-02-06
49799 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-02-06 07:30 | 2014-02-06 08:21 | 2014-02-06 | RADIATION MONITOR OUT OF SERVICE FOR MAINTENANCE "At approximately 0730 CST on February 6, 2014, 1R-22 Shield Building Vent Gas Radiation Monitor will be removed from service for planned maintenance. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs), NUE (Notification of Unusual Event) and Alert classifications when out of service. It is also used for offsite dose projection calculations. This results in a Loss of Emergency Assessment Capability while 1R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 Shield Building Ventilation Stack is also monitored by high range monitor, 1R-50, which is used for the same purpose in Site Area or General Emergency classifications. 1R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 1R-22 prior to removing it from service. This planned maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-06
49798 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2014-02-06 | 2014-02-06 07:04 | 2014-02-06 | AGREEMENT STATE REPORT - TROXLER GAUGE STOLEN FROM TRUCK AT RESIDENCE The State of Florida was notified at 0630 EST on 2/6/14, that the cab of a gauge user's truck was broken into and the case containing a Troxler Moisture-Density Gauge was stolen overnight at the gauge user's residence located in West Palm Beach, FL. The gauge, a model 3440, was properly stowed and locked in its case. This gauge contained 5.7 mCi of Cs-137, and 39.1 mCi of Am-241:Be. Local Law Enforcement is on-scene conducting an investigation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2014-02-14
49797 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-02-05 10:30 | 2014-02-05 17:07 | 2014-02-05 | AGREEMENT STATE REPORT - MALFUNCTIONING SOURCE SHUTTER FAILED TO CLOSE The following information was received via facsimile from the State of Nebraska: "The Nebraska Department of Health and Human Services was notified by a representative of the Omaha Public Power District that a Kay Ray fixed gauge Model Number 7080 source shutter failed to close. The device contains approximately 25.5 millicuries of Cesium-137. The gauge is mounted between two fly ash hoppers approximately 20 feet off of the floor. The source closure mechanism on the gauge is connected to a handle located at floor level by a flexible cable. The closure cable is secured so that when the floor handle is operated, the control cable slides inside of the sheath opening/closing the shutter. The shutter closure cable became loose where the sheath attaches to the source closure mechanism which prevented the shutter from closing. The licensee disconnected the lower part from the cable and the on/off handle. By holding on to the lower part of the sheath and sliding the internal cable, the licensee was able to close the shutter. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2014-02-13
49796 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-02-05 13:00 | 2014-02-05 16:17 | 2014-02-05 | DEGRADED CONDITION DISCOVERED ON PRESSURIZER NOZZLE WELD DURING TESTING "On February 5, 2014, during planned inspections, an ultrasonic examination performed on weld PCS-6-PRS-1C1-1 (RV-1041) revealed two axial indications in the root area of the weld. The weld containing the indications is the nozzle to safe end dissimilar metal weld on the flange for pressurizer safety valve RV-1041. These two indications do not meet applicable acceptance criteria under ASME, Section XI, IWB-3600, 'Analytical Evaluation of Flaws,' or ASME Section Xl, Table IWB-3410, 'Acceptance Standards,' and will require a repair or replacement activity in order return the weld to an acceptable condition. "The plant was in cold shutdown at 0% power for a planned refueling outage at the time of discovery. Replacement or repair actions will be completed prior to plant startup from the outage. "This condition has no impact to the health and safety of the public. "The licensee notified the NRC Senior Resident Inspector. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A), since indications were found that did not meet acceptance criteria referenced in ASME Code, Section XI." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-02-05
49795 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2014-02-05 10:00 | 2014-02-05 15:28 | 2014-02-05 | TONE ALERT SYSTEMS OUT OF SERVICE "On Wednesday, February 5, 2014, at 1130 EST, Oswego County notified Nine Mile Point [NMP] of a loss of the tone alert system at approximately 1000. The loss of the tone alert was identified by the National Weather Service - Binghamton forecast office when it was determined that the phone line to the site was out of service. Site Emergency Procedures define a loss of the tone alert system for greater than one hour as a significant loss of emergency communications. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the NMP and JAF [James A. FitzPatrick] nuclear power plants. This failure meets NRC 8-Hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper-reach system, which is a reverse 911 feature available from the county 911 center. "The county alert sirens, which also function as part of the public prompt notification system, remain operable. "At 1328 on February 5, 2014, Nine Mile Point was notified by Oswego County that the tone alert system was returned to service, effective as of 1325." The licensee informed the NRC Resident Inspector and the State of New York. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-05
49794 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2014-02-05 10:00 | 2014-02-05 15:15 | 2014-02-05 | TONE ALERT SYSTEM OUT OF SERVICE "At 1130 [EST] on February 5, 2014, with the James A. FitzPatrick Nuclear Power Plant (JAF) at 100% reactor power, Oswego County Emergency Management notified JAF that the tone alert radios had been out of service since 1000. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the Nine Mile Point and JAF nuclear power plants. This failure meets NRC 8-hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The county alert sirens, which also function as part of the public prompt notification system, remain operable. "The loss of the tone alert radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the prompt notification system be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for route alerting of the affected areas of the EPZ. "At 1328 on February 5, 2014, JAF was notified by Oswego County Emergency Management that the tone alert radios had been returned to service at 1325." The licensee notified the NRC Resident Inspector, the State of New York and local authorities of the outage. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-05
49793 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-02-03 | 2014-02-05 13:52 | 2014-02-05 | TEXAS AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Texas via email: "On February 5, 2014, the Agency [Texas Department of Health] received notice that on February 3, 2014, the licensee was unable to retract an 84.5 curie iridium-192 source. The camera and guide tube had fallen from a 22 inch pipe while in use. This caused damage to the guide tube near the camera. The source was retrieved according to license conditions. The retrieval employee received 9 millirem from the retrieval. No member of the public was exposed at rates above limit. The damaged equipment was retired from service and will be replaced. The camera was an INC IR-100 with serial number 7231 and the source had serial number 11337C. Additional information will be provided when it is received in accordance with SA-300." Texas Incident Number: I-9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-02-13
49792 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2013-10-14 | 2014-02-04 14:38 | 2014-02-04 | SUSPECTED LOCKING MECHANISM FAILURE ON AN INDUSTRIAL RADIOGRAPHY CAMERA The following was received from the State of Nevada via email: "The plunger lock on Camera 880 D (SN: D9686) spun freely in the locked position and could not be unlocked. It was tagged as inoperable and locked away in the safe. "On November 15, 2013, the camera was shipped to QSA Global, Inc., for repair. The camera was repaired on November 19, 2013 and returned to the licensee. It was then verified that all its parts including the plunger, lock and locking mechanism were working correctly. The camera was inspected and found to be fine on January 22, 2014, by one of our staff from the Radiation Control Program. The incident is closed." Item Number: NV140004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2014-02-12
49791 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-02-04 07:38 | 2014-02-04 11:37 | 2014-03-05 | OFFSITE NOTIFICATION DUE TO FATALITY ON SITE "At 0738 CST on 2/4/2014, the control room received a report that a supplemental radiological technician was found unresponsive on the refueling floor in the Reactor Building. The individual was located in a contaminated area and was dressed out when he was found. At 0745 CST, the individual was reported to be deceased by the EMT's. The Nemaha County Sheriff Department was contacted and responded to the site. OSHA is also being contacted. A news release is planned. No release has been made at this time. "The fatality does not appear to be work related at this time however an investigation is in progress. The individual was found to be not contaminated and was transferred off site. "The NRC Resident Inspector has been notified of this event." * * * UPDATE FROM DAVID MADSEN TO CHARLES TEAL AT 1618 EST ON 3/5/14 * * * "Correction: The report that the individual was deceased was made to the Control Room by an RP Technician not an EMT. The Nemaha County Sheriff made the official declaration of death." The licensee will notify the NRC Resident Inspector. Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-02-04
49790 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-04 08:54 | 2014-02-04 10:26 | 2014-02-04 | STACK RADIATION MONITOR NON-FUNCTIONAL FOR PRE-PLANNED MAINTENANCE The Millstone Station Stack Radiation Monitor, RM-8169, was removed from service at 0854 EST for pre-planned maintenance. The Stack Radiation Monitor will be restored to service after maintenance. The licensee informed the Connecticut Department of Environmental Protection, Waterford Dispatch and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-04
49789 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-02-03 12:00 | 2014-02-03 18:39 | 2014-02-04 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO A REFRIGERANT LEAK IN THE HVAC SYSTEM "The facility Technical Support Center (TSC) was rendered non-functional due to a malfunction in the TSC HVAC system. A leak in the refrigerant tubing has resulted in a loss of refrigerant and affected the system's ability to provide proper climate control. Repairs are being planned and will commence today. The out of service time is greater than one hour which by the station's Technical Requirements Manual is an 8 hour non-emergency report. "Compensatory measures per site procedure FNP-0-EIP-6.0 (TSC Setup and Activation) for maintaining emergency assessment, off-site response, and off-site communication capabilities are available. These measures include the conditional relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC to be uninhabitable. "A follow up notification will be made when the TSC is declared functional." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 0100 EST ON 02/04/14 FROM RICK LULLING TO S. SANDIN * * * The following was received as a courtesy notification follow-up: "At 2320 CST on 2/3/2014 the TSC HVAC was declared functional following post maintenance testing. Satisfactory pressure testing, system evacuation, and system re-charging were performed following the repair to two tubing leaks. Emergency assessment, off-site response, and off-site communication capabilities have been fully restored to the Technical Support Center. The Emergency Director, and NRC Senior Resident Inspector have been informed." Notified R2DO (McCoy). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-03
49788 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-02-03 10:03 | 2014-02-03 10:26 | 2014-02-03 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS RELEASE THAT COULD AFFECT NORMAL OPERATION At 1003 EST, Unit 1 declared an Unusual Event - EAL HU 3.1 (Toxic/corrosive/asphyxiate/flammable gas release that could affect normal operations) due to smoke in the Unit 1 "B" Battery room. The Unit 1 standby UPS inverter cabinet was smoking and leaking fluid. The fire brigade responded and declared the room uninhabitable due to smoke. The standby inverter was de-eneergized and the smoke subsided. The standby inverter was not in service and no plant equipment was lost. Unit 2 was not affected. Request for offsite assistance was sent to the local fire department but was not needed. The licensee notified the NRC Resident Inspector, the State of North Carolina, and local emergency response organizations. Notified Federal Agencies [DHS SWO, FEMA Operations Center, NICC Watch Officer, and NuclearSSA] via email. * * *UPDATE PROVIDED TO JEFF ROTTON FROM MARTIN HAMM AT 1045 EST ON 02/03/2014* * * Licensee terminated from the Unusual Event at 10:25 EST. Licensee notified the NRC Resident Inspector, the State of North Carolina and local emergency response organizations. Notified Federal Agencies [DHS SWO, FEMA Operations Center, NICC Watch Officer and Nuclear SSA] via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-02-03
49787 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2014-02-03 00:43 | 2014-02-03 02:41 | 2014-02-04 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION SYSTEM OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0043 [CST] on Monday, February 3, 2014, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system was removed from service for planned preventative maintenance activities on the TSC ventilation system condensing unit. The TSC air handing and filtration units will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 88 hours. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Preparedness (EP) procedures and checklists. If radiological conditions require TSC facility evacuation during ventilation system maintenance; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with established procedures. "The licensee notified the NRC Resident Inspector." * * * UPDATE ON 2/4/14 AT 1939 EST FROM DAN MILLER TO DONG PARK * * * "At 1800 CST on February 4, 2014, Dresden TSC ventilation was restored. The Dresden TSC ventilation is functional at this time. "The NRC Resident Inspector has been notified." Notified R3DO (Orlikowski). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-02-03
49786 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-02-02 11:29 | 2014-02-02 18:16 | 2014-02-02 | UNIT 2 AUTOMATIC REACTOR TRIP "On February 2, 2014, at 11:29 PST, Diablo Canyon Power Plant Unit 2 500kV line differential relay actuated. This action tripped the turbine and opened the generator output breakers to isolate the generator. With the turbine tripped and Unit 2 operating above the P-9 50% power permissive, a reactor trip was initiated from the reactor protection system. All systems operated as designed with no problems observed. All three Unit 2 Auxiliary Feedwater pumps started, the Containment Fan Cooling units started and ran in slow speed, and the standby Auxiliary Saltwater train started, all as expected. "Unit 2 is stable at normal operating temperature and pressure. All power transferred to the plant startup source without incident. Condenser vacuum was maintained. "The preliminary cause of the differential relay actuation was a flashover of Phase B 500 kV to ground across the Phase B lightning arrestor during a rainstorm. "Decay heat is being removed by steam dumps to the condenser. No relief valves lifted during the transient. The steam generators are being supplied by the auxiliary feedwater pumps. There were no injuries to personnel. Unit 1 was not affected. "NRC Senior Resident Inspector and Region Branch Chief have been informed of this event. "A press release is planned for local media." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2014-02-02
49785 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2014-02-01 21:30 | 2014-02-02 11:21 | 2014-02-02 | CONTAMINATED PLANT EMPLOYEE RECEIVED MEDICAL TREATMENT INSIDE THE RESTRICTED AREA "An employee with a laceration to his ear reported to the on-site dispensary yesterday evening. The plant nurse administered first aid. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination was present on the employee's boots, 2,136 dpm/100cm2. The plant nurse allowed the employee to return to work. The employee remained inside the Restricted Area over the course of the event." The source of the contamination is Uranium Ore Concentrates inside the process building. The licensee will request a bioassay when the employee returns to the site. The licensee informed R2 (Hartland) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2014-02-02
49784 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-02-02 08:59 | 2014-02-02 11:01 | 2014-02-02 | MANUAL REACTOR TRIP FOLLOWING LOSS OF THE "A" MAIN FEEDWATER PUMP "On 2-2-2014 at 0859 [EST], with Unit 2 operating at 100% power, a manual reactor trip was initiated by the control room staff following a trip of the 'A' main feedwater pump and automatic start of the 'C' feedwater pump due to crew concerns that both motors of the 'C' feedwater pump had not actuated. When the 'C' feedwater pump auto started, the running indicator light for one of the 'C' feedwater pump motors failed to illuminate. Both motors of the 'C' feedwater pump had started as designed. Following the reactor trip, all control rods fully inserted into the core and Unit 2 was stabilized in Mode 3 at normal reactor coolant system temperature and pressure. Decay heat is being removed using the normal condenser steam dump system. Unit 2 is in a normal shutdown electrical alignment with power being supplied from the Reserve Station Service Transformers. This event is reportable per 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system. "Following the reactor trip, the auxiliary feedwater pumps automatically started as designed and provided makeup flow to the steam generators. The steam generator levels were returned to normal operating level and the auxiliary feedwater pumps were returned to the normal standby automatic alignment. This event is reportable per 10CFR50.72(b)(3)(iv)(A) for actuation of an ESF system. "Unit 1 is operating at 100% power and was not affected by the event." The licensee informed the NRC Resident Inspector and will inform the Louisa County Administrator. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-02-02
49783 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-02-01 10:00 | 2014-02-01 14:12 | 2014-03-13 | CONTROL ROOM DOOR BLOCKED OPEN FOR PLANNED MAINTENANCE "Door in Control Room boundary blocked open for scheduled maintenance. No impact as door is opened under administrative control OP3314F, Section 4.24. Door has been closed following maintenance. "Door opened under administrative control could have prevented the fulfillment of Safety Function to Mitigate the Consequences of an Accident. "A door credited for Control Room Boundary was blocked open under administrative controls as part of a Pre-Planned maintenance activity. Technical Specification 3.7.7, Control Room Emergency Ventilation System, is applicable and allows 'The Control Room Envelope (RE) boundary may be opened under administrative control' "NUREG 1022, Revision 3, states inoperability of a single train system is reportable even though the plant's Technical Specifications may allow the condition to exist for a limited time. Although the plant was operated within the licensing basis, since the Control Room Envelope was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector, State government, and Local government. * * * UPDATE AT 1030 EDT ON 03/13/14 FROM THOMAS CLEARY TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this call is to retract the report made on February 1, 2014, NRC Event Number 49783. Event Report number 49783 describes a condition in which the Millstone Power Station Unit 3 (MPS3) Control Room Envelope was voluntarily rendered inoperable under administrative control. "Using the criteria of NUREG-1022 Rev. 3, this condition report is not related to inoperability being due to one or more personnel errors, including procedure violations; equipment failures; inadequate maintenance; or design, analysis, fabrication, equipment qualification, construction, or procedural deficiencies and was declared inoperable as part of a planned evolution for maintenance or surveillance testing and done in accordance with an approved procedure and the plant's technical specifications. Therefore, this condition Is not reportable and NRC Event Number 49783 is being retracted. "The basis for this conclusion will be provided to the NRC Resident Inspector." The licensee notified the NRC Resident Inspector. Notified R1DO (Ferdas). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-02-01
49782 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-31 | 2014-01-31 15:02 | 2014-01-31 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE COULD NOT BE RETRACTED The following was received from the state of Texas via email: "On January 31, 2014, the Agency [Texas Department of Health] was notified by the licensee that while performing radiography at a field location a radiography crew was unable to retract a 19 curie iridium - 192 source into a SPEC 150 exposure device. The radiographers were testing a pipe when a second pipe fell on the guide tube and crimped it enough that the source could not pass by it. The radiographers contacted their manager and informed them of the problem. Two individuals qualified to retrieve sources went to the location. They were able to reshape the guide tube enough to retract the source. The work was being conducted in a shielded shooting bay, therefore there was no exposure to any member of the general public. The highest exposure to anyone involved with the event was 60 millirem. No overexposure occurred. The guide tube was disposed of. The exposure device was tested with a new guide tube and functioned normally. The exposure device was returned to service. Additional information will be provided as it is received in accordance with SA-300." Texas incident # I-9152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-02-10
49781 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2014-01-31 | 2014-01-31 13:39 | 2014-01-31 | PART 21/50.55 - AP1000 UPDATED REACTOR COOLANT PUMP LOCKED ROTOR ANALYSIS The following was received via facsimile: "The purpose of this letter is to provide the Commission with the prescribed interim report as required per 10 CFR 21.21(a)(2) of a deviation identified by Westinghouse Electric Company LLC. This also will serve as an interim report under 10 CFR 50.55 (3)(ii) to the extent applicable. "A postulated reactor coolant pump (RCP) locked rotor (LR) transient has been explicitly analyzed for the AP1000 steam generator (SG) structural design, as documented in the latest AP1000 Design Control Document (DCD), Revision 19. This includes the calculation of LR hydrodynamic forces (HF) on the SG using the BANG UP code. This activity was performed based upon the unique features of the AP1000 design. However, the other AP1000 reactor coolant system (RCS) structural component analyses have not considered the locked rotor transient for hydrodynamic forces, even though a determination has been made that the effects of these loads could be more bounding than the limiting design-basis loss of coolant accident (LOCA) hydrodynamic forces (based on the BANG UP calculation of pressure pulsations through the RCS). "Westinghouse has not yet completed its evaluation as to whether there is a reportable condition as defined in 10 CFR 21 (or 10 CFR 50.55 to the extent applicable) if the deviation is left uncorrected. "Westinghouse expects to complete this evaluation by September 30, 2014. We will inform the staff if there are any changes to this schedule, prior to that date." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | CONSTRUCT DEFICIENCY | [8 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) | 50.55(e) |  |  | 0 | 2014-01-31
49780 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-31 10:01 | 2014-01-31 11:44 | 2014-01-31 | MANUAL REACTOR TRIP "This 4-hour notification is being made to report that Salem Unit 2 has performed an unplanned manual reactor trip. The trip was initiated due to reactor coolant temperature approaching the minimum temperature for criticality, 543 degree F, due to boration to achieve shutdown margin requirements following identification of a misaligned control rod. "All control rods inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Engineered Safety Features] systems functioned as expected with no equipment actuated. The 21 safety injection pump was out of service for scheduled maintenance during the event as was the 2R41 plant vent radiation monitor. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees F with decay heat removal via the main steam dump and auxiliary feedwater systems. Unit 2 has no active shutdown technical specification action statements in effect. "There was no major secondary equipment tagged for maintenance prior to the event." Prior to the event, the licensee was conducting their monthly control rod surveillance. No primary or secondary relief valves lifted during the transient. The electrical grid is stable and the plant is in its normal shutdown electrical lineup. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector, the State of New Jersey, the State of Delaware and the Lower Alloways Creek Township. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2014-01-31
49779 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-31 03:30 | 2014-01-31 04:09 | 2014-01-31 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO DEGRADATION OF THE PRESSURIZER PROPORTIONAL HEATERS GROUP 1 Operators commenced a Technical Specification required shutdown due a 480 volt supply breaker trip resulting in degradation of the Pressurizer Proportional Heaters Group 1. The licensee plans on making a containment entry to investigate the cause of the breaker trip. The B-Emergency Diesel-Generator is currently inoperable for planned maintenance. Unit 2 is currently ramping down and proceeding to a shutdown. The plant is in a normal electrical configuration. There is no indication of any primary to secondary leakage. Unit 3 is unaffected. The licensee notified the NRC Resident Inspector. | 0 | 31 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-01-31
49778 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-01-30 13:20 | 2014-01-30 19:03 | 2014-01-31 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTIVATION OF ONE EMERGENCY SIREN "One siren false actuation. At approximately 1415 CST on January 30, 2014, the licensee was notified of a false activation of emergency siren (G-14). The site contacted the siren vendor. It was determined that the siren had falsely actuated 5 to 6 times and has since been deactivated. The Goodhue County Sheriff's department received calls from some area residents. The siren remains out of service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ). NRC Resident Inspector has been informed.'' * * * UPDATE FROM MARK LOOSBROCK TO HOWIE CROUCH AT 1743 EST ON 1/31/14 * * * "Based upon further review, the event time of the false siren actuation was approximately 1320 CST. The previously reported event time of 1415 CST was the confirmation time of the siren vendor responding to the siren actuation. This does not represent a significant loss in emergency notification. The siren system has significant overlap between sirens. For any failed siren, backup methods are implemented per our emergency plan to ensure timely public notification." The licensee notified the NRC Resident Inspector of this update. Notified R3DO (Sheldon). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-30
49777 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-30 13:45 | 2014-01-30 17:09 | 2014-01-30 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM THAT COULD HAVE ALLOWED UNAUTHORIZED ACCESS The licensee discovered a vulnerability in a safeguard system that could have allowed unauthorized access to the Protected Area for which compensatory measures were not in place. Compensatory measures have been employed. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-01-30
49776 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2014-01-29 09:53 | 2014-01-29 18:33 | 2014-01-31 | LOSS OF TECHNICAL SUPPORT CENTER VENTILATION FAN "This telephone notification is provided in accordance with Exelon Reportability manual SAF 1.10, 'Major Loss of Emergency Preparedness Capabilities', and 10 CFR 50.72(b)(3)(xiii). "On January 29th at 09:53 CST, it was determined that the onsite Technical Support Center (TSC) Ventilation System Supply Fan had failed (due to failed fan belts as a result of degraded alignment), resulting in loss of ventilation for the TSC. Repairs have been initiated, however repairs will not have been completed within the time required to staff the TSC. There is currently no emergency event in progress requiring TSC staffing. The Main Control Room remains available as an Emergency Response Facility (ERF), should an event occur requiring Emergency Response Facilities to be staffed. "The licensee has notified the Senior Resident Inspector of the issue." * * * UPDATE FROM MARK SMITH TO VINCE KLCO AT 0217 EST ON 1/31/2014 * * * "After repairs were completed, the TSC Ventilation was restored to service at [2350 CST on 01/30/2014]. "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Sheldon). | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-29
49775 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-29 12:00 | 2014-01-29 15:39 | 2014-02-02 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following was received from the state of Texas via email: "On January 29, 2014, the Agency [Texas Department of State Health Services] received notice from the Licensee that a Troxler model 3430 moisture/density gauge had been stolen along with a truck. The serial number is 35379. It was not believed that the gauge was the target of the theft. The truck was stolen from the parking lot while the driver was running an errand. The gauge as manufactured contains an 8 millicurie cesium-137 source and a 40 millicurie americium/beryllium source. An investigation into this event is ongoing. It is unlikely that a member of the public will be exposed to hazardous radiation as the sources are still locked in the shielded position. Additional information will be supplied as it is received in accordance with SA-300." The local police and the Texas Association of Pawnbrokers were notified. Texas incident # I 9150 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-02-06
49774 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-29 11:15 | 2014-01-29 14:58 | 2014-03-13 | SECONDARY CONTAINMENT BOUNDARY WAS TEMPORARILY BLOCKED OPEN "Title: Door Opened Under Administrative Control Could Have Prevented Fulfillment of Safety Functions to Control the Release of Radioactive Material and Mitigate the Consequences of an Accident "On January 29, 2014, it was determined a door credited as a Secondary Containment Boundary was temporarily blocked opened multiple times since January 25, 2014 under administrative control. Technical Specification 3.6.6.2 'Secondary Containment' is applicable and requires the system to be restored to operable status within 24 hours. In each instance where the door was blocked open, the requirements of Technical Specification 3.6.6.2 were entered and complied with. "NUREG 1022 Revision 3 states inoperability of a single train system is reportable even though the plant's Technical Specifications may allow the condition to exist for a limited time. Although the plant was operated within the licensing basis, since Secondary Containment was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to control the release of radioactive material and mitigate the consequences of an accident. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector has been notified." * * * UPDATE AT 1030 EDT ON 03/13/14 FROM THOMAS CLEARY TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this call is to retract the report made on January 29, 2014, Event Number 49774. Event Report number 49774 describes a condition in which the Millstone Power Station Unit 3 (MPS3) Secondary Containment was voluntarily rendered inoperable under administrative control. "Using the criteria of NUREG-1022 Rev. 3, this condition report is not related to inoperability being due to one or more personnel errors, including procedure violations; equipment failures; inadequate maintenance; or design, analysis, fabrication, equipment qualification, construction, or procedural deficiencies and was declared inoperable as part of a planned evolution for maintenance or surveillance testing and done in accordance with an approved procedure and the plant's technical specifications. Therefore, this condition is not reportable and NRC Event Number 49774 is being retracted. "The basis for this conclusion will be provided to the NRC Resident Inspector." The licensee informed the NRC Resident Inspector. Notified R1DO (Ferdas). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-01-29
49773 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-01-29 09:00 | 2014-01-29 11:06 | 2014-01-29 | INDICATIONS IDENTIFIED ON CONTROL ROD DRIVE MECHANISM HOUSINGS "On January 29, 2014, during planned inspections of control rod drive mechanism (CRDM) upper housings, it was determined that the inspection results for some housings did not meet the applicable acceptance criteria. That is, evaluations of the housing indications are being performed under ASME Code, Section XI, IWB-3600, 'Analytical Evaluation of Flaws,' and indications were identified that exceed acceptance criteria specified in the Code. None of the indications were through-wall and there was no evidence of leakage. "The housing indications, varying in depth and length characteristics, were identified in 17 of the 45 CRDM housings inspected. All 45 CRDM housings were inspected, which constituted 100% extent of condition inspection. "The plant was in cold shutdown at 0% power for a planned refueling outage at the time of discovery. Replacement or repair actions are in progress and will be completed prior to plant startup from the outage. "This condition has no impact to the health and safety of the public. "This report is being made in accordance with 10CFR 50.72(b)(3)(ii)(A), since indications were found that did not meet acceptance criteria referenced in ASME Code, Section XI. "The licensee notified the NRC Senior Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-01-29
49772 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-01-28 10:30 | 2014-01-28 15:09 | 2014-01-28 | AGREEMENT STATE REPORT - EXTERNAL RADIATION LEVELS ON PACKAGE EXCEEDED LIMITS The following was received from the State of New Jersey via email: "Event Type: "External radiation levels on packages containing Type A quantity material received exceeded the limits of 10 CFR 71.47 (200 millirem/h) on the external surface of the package. The maximum reading on one of the packages was 360 millirem/h. "Event Description: "A total of 4 packages (Sr-82/Sr-85) were received from Brookhaven National Laboratory Upton, NY. "As per the licensee's incoming procedures, the TI [Transportation Index], surface and contamination readings were taken. The packages exceeded the regulatory surface limit of 200 mR/hr. No other issues were found on the packages. "The licensee immediately contacted the Brookhaven Labs and informed them of the surface readings exceeding the regulatory limit of 200 mR/hr. The carrier's Dangerous Goods Division and the NJDEP were also notified. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-02-05
49771 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-01-28 07:34 | 2014-01-28 09:09 | 2014-01-28 | SERVICE WATER EFFLUENT RADIATION MONITOR NON-FUNCTIONAL DUE TO PREPLANNED MAINTENANCE "On Jan. 28, 2014, at 0734 CST, [Radiation Monitor] R-20, Service Water Sampling Effluent Line (Auxiliary Building Service Water Header) was declared non-functional due to planned maintenance. R-20 is used for Emergency action level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that would result in an Alert or Unusual Event and is being conservatively reported under 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability. "R-20 is planned to be returned to functional [status] by 1300 CST today, 1/28/2014." The spent fuel pool is the only heat load requiring Service Water for cooling and no spent fuel pool activities are in progress or planned. The NRC Resident Inspector has been informed by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-28
49770 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-01-24 | 2014-01-27 17:05 | 2014-01-27 | AGREEEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE The following was received from the State of Ohio via email: "On Jan. 27, 2014, the RSO of Flower Hospital provided a telephone report of medical event that occurred on Jan. 24 and 27, 2014. "A patient was being treated with a Varian GammaMed Plus HDR with 4.7 Ci of lr-192 in a vaginal cylinder. The written directive was for three fractions of 500 cGy for a total of 1,500 cGy. Then during the delivery of the second fraction the licensee realized that they were only delivering a planned dose of 166 cGy. The licensee completed the second fraction as planned. The treatment planning was entered as one third of the 500 cGy for three fractions instead of three fractions of 500 cGy. The license will modify the treatment plan to give the full prescribed 1500 cGy to the patient. "The patient was notified on Jan. 27, 2014. "This is a reportable medical event under OAC 3701:1-58-101 (A)(1)(c.) for a fractionated dose that differs by more than 50%." Ohio Report #: OH140001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2014-02-04
49769 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2014-01-27 14:40 | 2014-01-27 16:35 | 2014-01-27 | MARYLAND AGREEMENT STATE REPORT - STOLEN LEAD PAINT ANALYZER The following information was received from the State of Maryland via email: "The Maryland Radiation Program received a telephone call around 3:55 p.m. [EST] from [the RSO] of Arc Environmental (MD-07-199-01) informing the Department [Maryland Department of the Environment] that an XRF (RMD LPA1) was stolen from 2611 East Monument Street, Baltimore, Maryland where they were performing an inspection. The theft occurred at about 2:40 p.m. when the two inspectors, [names deleted], were leaving the site. They thought the other had put the XRF in the vehicle, and when they realized they did not have it, returned to the site, but the XRF was gone. They will provide the Department a copy of the police report when it is available. MDE may put out a press release on 1/28/14 if the device is not recovered." Per the vendor documentation, the LPA1 nominally contains 12 mCi of Co-57. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2014-02-04
49768 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-01-25 16:30 | 2014-01-27 15:29 | 2014-01-27 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM THAT COULD HAVE ALLOWED UNAUTHORIZED ACCESS The licensee discovered a vulnerability in a safeguard system that could have allowed unauthorized access to the Protected Area for which compensatory measures were not in place. Compensatory measures were immediately employed upon discovery. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-01-27
49767 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-27 09:37 | 2014-01-27 11:02 | 2014-01-29 | RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE Supplementary Leakage Collection and Release system (SLCRS) Radiation monitor, 3HUR-RE10A/B, is being removed from service for planned maintenance. Radiation monitor is scheduled to be returned to service on February 2, 2014. The Licensee notified the NRC Resident Inspector, the State Department of Environmental Protection, and the town of Waterford. * * * UPDATE FROM TOM CLEARY TO CHARLES TEAL AT 1241 EST ON 1/29/14 * * * The licensee called to correct the identification number of the SLCRS radiation monitor. The SLCRS radiation monitor identification number should be 3HVR 19A/B. Notified R1DO (Burritt). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-27
49766 | 0 | US AIR FORCE |  |  |  |  | 2013-10-01 | 2014-01-27 08:39 | 2014-01-27 | LOSS OF RADIOACTIVE MATERIAL The following report was received via email; "1. IAW 10 CFR 20.2201(a)(1)(ii), we are providing a written report for the loss of radioactive material. The loss of material was reported on 27 Jan 14; 1) telephonically to NRC Operations Center, Event No. 49766 and 2) via E-mail to NRC, Region IV (Ms. Cook). The following information addresses the reporting requirements: "a. Description of the licensed material: The subject device contained nickel 63 (Ni-63), one source, at 15 millicuries. The source is encapsulated in a hollow brass cylinder which in turn is sealed in a ceramic shield as referenced in Sealed Source & Device Registry (SS&DR) NR-0163-D-102-E (19 Oct 2010). The subject device was generally licensed (GLD) and used by USAF Security Forces Personnel (75th SFS) of Hill AFB, Ogden, UT. "b. Description of circumstances for loss: The missing Ionscan 500DT was added to the Installation Radiation Safety Officers inventory of all GLDs on Hill AFB in October 2007. The serial number of the missing source is 50083. It was surveyed semi-annually through May 2013. During the November 2013 leak test/inventory of GLDs, the device was not at the security gate where it has always been. The 75 SFS storage warehouse was checked and it was not there either. "c. Statement of disposition: 75 SFS personnel were asked multiple times about the disposition of the item. On 11 December 2013, they reported the Ionscan was no longer in their possession. They reported that the item was dropped and damaged during transport. An Airman was assigned to locate a disposal location that would be able to take the item and was directed to dispose of it there. Later the Airman reported that he had done this. The Airman was in the process of being dismissed from the Air Force at that time and is no longer in the Air Force for questioning on how he disposed of the item. Therefore, the final disposition of the item is unknown at this time. "d. Exposures to individuals: Because the device contains Ni-63, which is sealed and incorporated into the Ion Mobility Spectrometer assembly, the radiation level surrounding the device would be indistinguishable from background. "e. Actions taken: Requests have been made of multiple levels of 75 SFS command to obtain more specifics on the event. No additional information has been received to-date. "f. Procedures/measures to rectify future loss: The installation radiation safety officer will reinforce the policies outlined in Air Force Instruction (AFI) 40-201, Managing Radioactive Materials in the United States Air Force for proper disposal of generally licensed devices." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-02-04
49765 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-01-27 00:45 | 2014-01-27 05:05 | 2014-06-06 | TURBINE AND RAD WASTE BUILDINGS RADIATION MONITORS INOPERABLE DUE TO PLANNED MAINTENANCE "At 0045 PST on 1/27/14, the Turbine Building Exhaust Low and Intermediate radiation monitors and the Rad Waste Building Exhaust Low and Intermediate radiation monitors were declared inoperable because of planned maintenance for replacement of the monitors. Compensatory measures have been implemented per station procedures; however, the time required for installation, testing, and acceptance of the new equipment is expected to last several weeks. Therefore, this radiological monitoring equipment outage is being reported as a major loss of assessment capability under regulation 10 CFR 50.72(b)(3)(xiii). Compensatory measures will be in place throughout the duration of the planned equipment outage." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 6/6/2014 AT 2008 EDT FROM JOHN KAINEG TO DONG PARK * * * "At 1416 PDT on 5/31/14, the Turbine Building Exhaust Low and Intermediate radiation monitors were declared operable, and at 1312 PDT on 6/06/14 the Rad Waste Building Exhaust Low and Intermediate radiation monitors were declared operable after outages due to equipment replacements. "The NRC Resident Inspector has been notified." Notified R4DO (Taylor). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-27
49764 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-01-24 15:00 | 2014-01-24 17:24 | 2014-01-24 | MASSACHUSETTS AGREEMENT STATE REPORT - MISADMINISTRATION OF I-131 The following information was obtained from the Commonwealth of Massachusetts via facsimile: "30 mCi of I-131 (NaI) was administered to the wrong patient. Blocking agent has been prescribed by doctor. Patient is described as in their 70s. Doctor and patient have been informed. 15 day report will follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-02-03
49763 | 0 | PALISADES | 1 |  |  | [1] CE | 2014-01-24 16:10 | 2014-01-24 16:58 | 2014-01-24 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM THAT COULD HAVE ALLOWED UNAUTHORIZED ACCESS The licensee discovered a vulnerability in a safeguard system that could have allowed unauthorized access to the Protected Area for which compensatory measures were not in place. Compensatory measures were immediately employed upon discovery. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-01-24
49762 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-01-22 | 2014-01-24 10:56 | 2014-01-24 | PENNSYLVANIA AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received via fax from the Commonwealth of Pennsylvania: "Notifications: Licensee reported this event to the Department's [Pennsylvania Department of Environmental Protection] Southeast Regional Office on January 23, 2014. This is an immediate reporting event under 35.3045(a)(1)(i). "Event Description: On January 22, 2014, the licensee experienced a medical event in which 76% of a yttrium-90 (Y -90) TheraSphere liver cancer therapy dose was delivered to the patient. Both the patient and referring physician were notified of the under dose. "Cause of the Event: Occlusion. The remaining activity appeared to have precipitated out and remained in the catheter. "Actions: Awaiting the required 15 day written report from the licensee. The Department will provide updated information as received. "Media attention: None at this time." Event number: PA140005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-02-03
49761 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2014-01-23 | 2014-01-23 16:21 | 2014-03-21 | AGREEMENT STATE REPORT - MISSING DEVICE CONTAINING AMERICIUM-241 The following information was obtained from the Commonwealth of Massachusetts via email: "Immediate report in accordance with 105 CMR 120.281(A)(1) of missing device containing a 100 millicurie americium-241sealed source. "After [a] billing inquiry by Massachusetts Radiation Control Program [the Program] [to] the licensee about generally licensed devices registered with [the] Program, the licensee reported on January 23, 2014 that one Industrial Dynamics Co., LTD Model FT-12 device [a fill level gauge], S/N 102282, containing a 100 millicurie americium-241 sealed source, cannot be located or is missing. "The licensee informed the Program that the device is obsolete and has been out of service for about 15 years and may have been returned to manufacturer or might be in storage at licensee's facilities. The licensee informed [the] Program that it is making the effort of contacting a person that may have known about the device and is conducting a search of it's storage facilities. "The Program notified the licensee of it's responsibility for providing [a] written report in accordance with the requirements of 105 CMR 120.281(B). "Root cause and corrective actions are not known at this time and the Program intends to make site visit. "This event remains open." * * * UPDATE FROM ANTHONY CARPENITO TO CHARLES TEAL ON 2/18/14 AT 0828 EST * * * The following information was obtained from the Commonwealth of Massachusetts via email: "The Commonwealth of Massachusetts performed an on-site inspection on 2/17/14. Licensee has been in contact with the gauge manufacturer and has been searching numerous potential storage locations on licensee's property which covers multiple city blocks to determine possible long ago return to manufacturer or possible long-term on-site storage. There is no change in status and the device is still missing. The investigation is ongoing and the event remains OPEN." Massachusetts Event Number: 14-1155 Notified R1DO (Krohn) and FSME Event Resource via email. * * * UPDATE FROM ANTHONY CARPENITO TO JOHN SHOEMAKER ON 3/21/14 AT 1235 EDT * * * The following information was obtained from the Commonwealth of Massachusetts via email: "[The] licensee confirmed via telephone on 3/21/14, that subject gauge was still missing. Based on current information, the Agency [Commonwealth of Massachusetts] presumes gauge lost. The Agency considers this matter to be closed." Massachusetts Event Number: 14-1155 Notified R1DO (Welling) and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2014-01-31
49760 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-11-22 | 2014-01-23 13:24 | 2014-01-23 | PENNSYLVANIA AGREEMENT STATE REPORT - LOST THEN FOUND BRACHYTHERAPY SEEDS The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "Notifications: On November 22, 2013, the DEP [Pennsylvania Department of Environmental Protection] Southwest Regional Office was notified that some palladium-103 (Pd-103) brachytherapy seeds were inadvertently disposed but then recovered by the licensee. On January 22, 2014, the Department was provided the actual activity amount and made the determination that this event qualifies as a reportable event under 10 CFR 20.2201(a)(1)(i). "Event Description: On November 20, 2013, a box containing Pd-103 brachytherapy seeds was delivered to the Nuclear Medicine Department. On November 22, 2013, the Medical Physicist, prior to the implant procedure, noticed that all the seeds were not present. It was later acknowledged that all 90 seeds equaling 170 mCi of Pd-103 were inadvertently disposed. "Cause of the Event: Human error. The seeds were not removed from the shipping box prior to the box being disposed of. "Actions: On November 22, 2013, the Medical Physicist retrieved the missing box containing all the seeds. No exposure to anyone is expected while the seeds were missing. The regional office will further determine, with the licensee, the root cause of this event and the corrective actions to prevent this from reoccurring. "Media attention: None at this time." Event Report ID No: PA140001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-01-31
49759 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2014-01-22 13:15 | 2014-01-23 11:30 | 2014-01-23 | INOPERABLE CRITICALITY WARNING SYSTEM LOCAL ALARM IN WILMINGTON FIELD SERVICES CENTER BUILDING NUMBER 1 "On 1/22/14 at 1:15 PM [EST], it was discovered during routine testing on an outdoor Criticality Warning System (CWS) Data Acquisition Module (DAM #21), that the module had inadequate voltage to properly sound a portion of the local alarm horns in the Wilmington Field Services Center (WFSC) building #1. While another module provides overlapping detector coverage, it does not provide overlapping horn audibility in the affected areas. The cause of the event is believed to be related to a battery component failure. "Personnel were immediately removed from the affected areas and repairs initiated to restore normal operation of the system. "The module was repaired and the system returned to normal on 1/22/14 at approximately 3:00 PM. The affected outdoor CWS horns were retested to ensure proper system operability. There are no active fissile material operations at the WFSC, thus no unsafe condition existed. "Longer term preventive actions are being evaluated. "This event is being reported pursuant to the requirements of 10CFR70.50 (b)(2)." The licensee will be notifying NRC NMSS Licensing Project Manager, NRC Region II Inspection Coordinator, State of North Carolina Radiation Protection Branch, and the New Hanover Emergency Response Branch. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2014-01-23
49758 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-01-22 19:56 | 2014-01-22 23:36 | 2014-01-22 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "A spurious closure of a Secondary Containment isolation damper caused a trip of the Fuel Building ventilation system and a loss of Secondary Containment differential pressure. Secondary Containment differential pressure exceeded -0.25 inches of water vacuum rendering Secondary Containment inoperable between the time of 1956 and 2003 [CST]. The damper re-opened, fuel building ventilation was restarted and Secondary Containment differential pressure was restored to normal. This event is reportable under 10CFR50.72(b)(3)(v)c. "The Licensee will be notifying the NRC Resident Inspector". Investigation for the spurious closure of a Secondary Containment isolation damper is in progress. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-01-22
49757 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2014-01-22 12:05 | 2014-01-22 17:35 | 2014-01-22 | SAFEGUARDS REPORT-ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2014-01-30
49756 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-22 | 2014-01-22 17:13 | 2014-01-22 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RADIOLOGICAL WORKER The following information was obtained from the State of Texas via email: "On January 22, 2014, the Agency [Texas Department of Health] was notified by the licensee's Radiation Safety Officer that they had received a report from their dosimetry processor indicating one of their employees had received 11.27 rem DDE [Deep-Dose Equivalent] on their OSL [optically stimulated luminescence] dosimeter for the exposure period of December 1, 2013 to December 31, 2013. This brought the individuals exposure for the year 2013 to 14.250 rem DDE. The RSO stated they had interviewed the employee, who is a radiography trainee, and was not able to discredit the exposure. The radiographer trainer the trainee worked with was also interviewed and did not have an explanation for the exposure. The trainee has been removed from all duties requiring exposure to radiation. The RSO stated they will contact the Radiation Emergency Assistance Center/Training Site, (REAC/TS) the morning of January 23, 2014, to have a cytogenetic blood testing performed of the individual. "The RSO stated the trainee's exposure total for the same exposure period, as measured by their self-reading dosimeter, was 165 millirem. The RSO stated the trainee had not been involved in any reported source recoveries or misconnects. The RSO stated they had not observed any medical conditions that would support the reported exposure. The RSO does not believe the exposure is real, but since he has not identified another explanation for the reading he will treat it as real until proven otherwise. Additional information will be provided as it is receive in accordance with SA-300." Texas Incident #: I-9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-01-30
49755 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2014-01-20 | 2014-01-22 15:58 | 2014-03-21 | AGREEMENT STATE REPORT - LOST GENERAL LICENSED DEVICE The following information was received from the Commonwealth of Virginia by email: "Event description: On January 20th the Radioactive Materials Program (RMP) received a call from Simms Metal Recycling in Petersburg, that a load of scrap metal being received set off the radiation monitoring detector. A DOT exemption form was completed and the scrap load returned C&C Cullet, Inc. in Ashland, where it originated from. They dumped the scrap load and found the item using a survey meter, which indicated 87 microrem/hr. Pictures were sent to the RMP and upon review concluded that the device was a liquid scintillation analyzer. The RMP contacted the manufacturer, Perkin Elmer, and began a conversation regarding the analyzer. The analyzer is secured at C&C Cullet, Inc. as an investigation is ongoing to determine the serial number and owner of the analyzer. It is believed to contain an 18 mCi source of either Ba-133 or Ni-63. There are no health or safety impacts as the source is secured in the analyzer." Virginia Event: VA-14-01 * * * UPDATE FROM MIKE WELLING TO CHARLES TEAL ON 1/28/14 AT 1541 EST * * * The following was received from the Commonwealth of Virginia via email: "On Tuesday January 28th, the source was removed by the manufacturer for disposal. The company will try to ascertain a serial number from the source to determine the General Licensee whom the device was provided to." Notified R1DO (Burritt) and FSME Event Resource via email. * * * UPDATE FROM MIKE WELLING TO CHARLES TEAL ON 3/21/14 AT 1036 EDT * * * The following was received from the Commonwealth of Virginia via email: "On Tuesday January 28th, the source was removed by the manufacturer for disposal. The source serial number (432228) was ascertained by the manufacturer which allowed for tracking to Virginia State University (VSU) as the recipient of the device. The source activity was incorrectly stated at 18 mCi in the initial report, the actual activity is 18 microcuries (uCi) of Ba-133. "An investigation was performed by VSU in regards to when and how the device was disposed of. VSU stated the device was given to the Department of General Services (DGS) as surplus equipment in 2012 and was then subsequently sold as scrap metal. The RMP will contact DGS and discuss the proper disposal methods of radioactive material." Notified R1DO (Welling) and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2014-01-30
49754 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2014-01-21 21:25 | 2014-01-22 00:33 | 2014-01-22 | DUAL UNIT TRIP ON THE LOSS OF THE "21" 13KV BUS "Dual Unit Trip due to loss of '21' 13 KV bus . All safety functions are met for both units. Unit 1 remained with normal heat removal. Unit 2 lost power to its normal heat sink and is stable on Auxiliary Feed water and Atmospheric Dump Valves for temperature control. Both trips were automatic trips. Due to loss of power a Under Voltage actuation occurred on both units ('14' and '24' 4Kv bus). Due to loss of main feed on Unit 2 a Auxiliary Feed water Actuation System [AFW] actuation occurred on Unit 2. Cause is under investigation." All control rods fully inserted on the loss of power to the Control Rod Drive Mechanisms [CRDMs]. Both Units Reactor Coolant Pumps [RCPs] remained running during the transient. The normal Unit 2 heat sink was unavailable due to the loss of the operating circulating water pumps resulting in a loss of condenser vacuum. The Unit 2 AFW actuation included one of two steam-driven pumps and the motor-driven pump. Both Units Emergency Diesel Generators started and loaded and have since been secured. Both Units are stable and will remain in mode 3 (Hot Standby) pending the results of the investigation. The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-22
49753 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-01-21 13:40 | 2014-01-21 21:14 | 2014-01-21 | VENT STACK RADIATION MONITORS OUT OF SERVICE "At 1340 [EST] on 1/21/2014, Susquehanna Control Room Operators received an alarm due to the lockup of a monitoring panel utilized for Vent Stack Radiation Monitors (known as SPINGs - System Particulate, Iodine, and Noble Gas). There are two monitor panels, one in the control room and one in the Technical Support Center (TSC). Both panels are fully redundant. At the time, the control room panel was out of service for maintenance. "This event rendered all five SPINGs inoperable. Additionally, control room alarm capability was not available. The associated Technical Requirement (TROs) were entered for this inoperability. In order to clear the lockup, the TSC terminal needed to be powered down and rebooted. "The TSC monitoring terminal was restored to operable status at 1352 and the associated TROs were cleared. The SPING function and control room alarm functions were inoperable for a total of 12 minutes. "In accordance with the guidance of NUREG 1022, Revision 3, Item 3.2.13, this event is being reported as an 8 hour ENS notification due to a loss of emergency assessment capability. The loss of the Stack Monitoring System was not part of a pre-planned evolution. This equipment is relied upon by control room operators and emergency response personnel to implement procedures addressing classification, assessment, and protective actions associated with the emergency plan." The licensee notified the NRC Resident Inspector. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-21
49752 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-21 | 2014-01-21 15:24 | 2014-01-21 | AGREEMENT STATE REPORT - LOST PROCESS GAUGE "On January 21, 2014, the Agency [State of Texas] was notified by the licensee that while conducting a routine source inventory, it could not find a beverage fill device containing a 100 millicurie americium-241 source. The licensee stated the unit was removed from the production line several years ago and placed in storage. The licensee stated the source shutter on the device was locked in the closed position when it was placed in storage. The licensee stated the unit has the appropriate labels on it. The licensee does not believe the lost source presents a risk of exposure to any individual as long as the device is not altered. "The licensee is interviewing employees and contractor personnel in an attempt to locate the source. The licensee stated the source was inventoried in 2013, but could not provide a specific date. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-9147 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-01-29
49751 | 0 | CCI THERMAL TECHNOLOGIES INC. |  |  |  |  | 2014-01-16 | 2014-01-21 12:37 | 2014-01-21 | PART 21 - NONCONFORMANCE OF AN ELECTRICAL TUBULAR WATER HEATER The following information was received via facsimile: "Subject: Non-Conformance on [CCI Thermal Technologies] Purchase Order 244232-1-MRA-MEEW-00001 Element "We notify you that we have initiated a notification process today to: "Bechtel Project Quality Manager EQB1A/Watts Bar Nuclear Plant Hwy 68 Spring City, TN 37381 "Regarding finding on January 16, 2014 related to non-conforming items shipped under purchase order 244232-1-MRA-MEEW-00001 Element. "Manufactured by: "CCI Thermal Technologies Inc. 2721 Plymouth Dr. Oakville, [Ontario] [Canada], L6H5R5 "Non-conforming items are under investigations with further pending review of action with the issuance party on the purchase order indicated." The nonconformance is related to a borated water storage tank electrical heater that was shipped in 2011 for use on Watts Bar Unit 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-01-21
49749 | 0 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2013-11-15 | 2014-01-21 10:20 | 2014-01-21 | PART 21 - LOOSE BATTERY VENT ASSEMBLIES The following (in part) was received via facsimile: "The purpose of this letter is to provide the NRC preliminary notification in general conformity to the requirements of 10CFR Part 21.21 (a)(2). On November 15, 2013 C&D Technologies, Inc. (C&D) was informed by Nuklearna Elelktrarna Krsko (NEK) of Slovenia that the vent assemblies in a lot 66 units of LCY-39 batteries were not engaging properly to form a seal between the vent assembly and the battery cover. This issue was detected and corrected prior to installation and use of the batteries. "The vent assembly is a safety related component with the primary function of preventing spark or flame propagation back into the cell from external sources. Lack of engagement or seal between the vent assembly and cover may provide a path for flame or spark propagation. Subsequent evaluation of the design of the cover to vent assembly seal has shown that under certain combinations of assembly, gasket and cover dimensions a clearance fit is formed that may exist in installed batteries. To date no other user of LCY-35, 37, or 39 batteries that use these covers and vent assemblies has reported a similar situation, however, the possibility exists that this issue may exist in products used by US licensees. And may pose a safety hazard. Thus, C&D is submitting this report to the NRC and notifying C&D's customers that use LCY batteries of this report, and actions to be taken to eliminate the possible safety hazard. "U.S. Licensees using batteries possibly containing the clearance fit have been notified of the filing of this report with recommendations that they inspect their batteries for any signs of problems. A procedure (attached) will allow users to detect clearance fits between the vent assembly and cover. Replacement parts will be provided by C&D for affected cells that will eliminate the possibility of clearance fits." The affected US facilities are: Oconee Nuclear Station, Indian Point Energy Center, Arkansas Nuclear One, Beaver Valley Nuclear Generating Station, St. Lucie Nuclear Power Plant, Vogtle Electric Generating Plant, Edwin I. Hatch Power Plant, and Wolf Creek Generating Station. The affected foreign facilities are: Bruce, Laguna Verde, Krsko and Pickering. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2014-01-21
49748 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2014-01-21 06:40 | 2014-01-21 08:41 | 2014-01-21 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "On Tuesday, January 21 at 0640 CST, the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service approximately 8 hrs. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." * * * UPDATE FROM SAM GOLDSMITH TO CHARLES TEAL AT 1347 EST ON 1/21/14 * * * The TSC system maintenance is complete and returned to service as of 1140 CST on 1/21/14. The NRC Resident Inspector has been informed. Notified R3DO (Valos). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-21
49747 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2014-01-20 22:30 | 2014-01-21 05:48 | 2014-01-23 | TECHNICAL SUPPORT CENTER EMERGENCY DIESEL GENERATOR OUT OF SERVICE "On 1/20/14 at 2230 CST, an interruption in the control power to the TSC diesel generator was discovered. Investigation revealed a blown fuse supplying the TSC diesel generator control panel. The blown fuse has resulted in the TSC diesel generator starting batteries depleting. The fuse has since been replaced, and the TSC diesel generator starting batteries are currently recharging. The TSC diesel generator remains non-functional until the starting batteries are charged. This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the unplanned loss of the backup power supply to the Emergency Response Facility (ERF). The NRC Resident Inspector has been informed. An update notification will be made when the TSC diesel generator has been restored to fully functional status." * * * UPDATE FROM NATHAN PIEPER TO HOWIE CROUCH AT 1551 EST ON 1/23/14 * * * At 1400 CST, the licensee restored the TSC emergency diesel generator to functional status. The NRC Resident Inspector was notified by the licensee. Notified R3DO (Valos). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-21
49746 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2014-01-21 01:40 | 2014-01-21 02:19 | 2014-01-21 | OFFSITE NOTIFICATION DUE TO TRITIUM DISCOVERED IN GROUNDWATER "This notification is being made pursuant to [10 CFR] 50.72(b)(2)(xi), notification of other government agency. Notification to other government agency, State of Ohio, was made at 0140 [EST] on 1/21/14. "At 1310 on 1/20/2014, a leak was identified on a feed water Venturi. In response to the water leak, samples were taken to check for the spread of tritium. A positive result for tritium was identified in the under drain system in the Auxiliary Building which requires communications as part of the NEI ground water protection initiative. The positive sample results were obtained at 2330 on 1/20/14. Actions are in progress stop the leak (perform leak injection)." The EPA limit for groundwater is 20,000 pCi/l. The samples taken by the licensee indicated 46,000 pCi/l. The licensee has notified the NRC Resident Inspector and will notify local counties. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-21
49745 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2014-01-20 02:16 | 2014-01-20 05:28 | 2014-01-20 | LOSS OF SHIELD BUILDING GASEOUS RADIATION MONITOR "2R-22, Unit 2 Shield Building Ventilation Gaseous Radiation Monitor was removed from service at 0216 CST on 01/20/2014 due to a broken belt. 2R-22 is important to the site's emergency plan for Notification of Unusual Event and Alert classifications in the event of an unplanned gaseous release from the Unit 2 Shield Building stack. It is also used for offsite dose projection calculations. There is no backup instrumentation or compensatory measure to perform these functions while 2R-22 is out of service. This results in a loss of emergency assessment capability, thus is reportable per 10CFR 50.72(b)(3)(xiii). "2R-22 readings were normal prior to the equipment failure. Unit 2 Shield Building Ventilation Stack is also monitored by high range monitor, 2R-50, which is used for the same purpose in Site Area or General Emergency classifications. 2R-50 is being monitored and is indicating normal values. This event did not result in the unplanned release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "Immediate efforts are underway to repair 2R-22. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-20
49744 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-01-18 10:20 | 2014-01-18 14:48 | 2014-01-20 | UNIT 2 PYRO PANEL NON-FUNCTIONAL DUE TO UNKNOWN EQUIPMENT PROBLEMS "At 10:20 [CST] on January 18, 2014, the Unit 2 Pyro Panel (fire/smoke detection panel) was declared non-functional due to an unknown equipment problem. Compensatory measures (e.g. continuous roving fire watches) have been established for all affected areas with the exception of the Unit 2 Containment Building. Containment fire watches have been established per the FSAR, which includes monitoring various temperatures, pressures, and other parameters for Containment, and systems associated with containment. However, this is not considered a satisfactory compensatory measure for maintaining effective assessment capability. Since a fire in Containment is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability, and is being reported per 10CFR50.72(b)(3)(xiii). "The NRC Senior Resident Inspector has been informed." * * * UPDATE FROM RICK LULLING TO DANIEL MILLS AT 0700 EST ON 1/20/14 * * * "At 0404 CST on 1/20/14 the Unit 2 Pyro panel was declared functional following the replacement of the fire indicating unit (FIU) and the power supply, and successful post maintenance testing. The emergency assessment capability for the site's Emergency Plan has been fully restored concerning a Containment fire." The licensee notified the NRC Resident Inspector. Notified R2DO (King). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-18
49743 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-01-18 08:40 | 2014-01-18 12:18 | 2014-01-18 | REACTOR TRIP DUE TO TURBINE TRIP "At 0840 [CST], Comanche Peak NPP [CPNPP] Unit 1 turbine tripped causing a reactor trip. All rods inserted. No evolutions were in progress at time of trip. The cause of the trip is under investigation. A Generator Negative Sequence Current High Alarm was received immediately prior to turbine trip. "Both Motor Driven Auxiliary Feed Water Pumps and the Turbine Driven Auxiliary Feed Water Pump started in response to Steam Generator Lo-Lo Levels. "Currently, Unit 1 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007A and the Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves). "Normal plant response was observed and all systems actuated as expected. No radiological release is in progress. "There was no impact to CPNPP Unit 2, and off-site power remains available." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-18
49742 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-01-18 10:16 | 2014-01-18 10:47 | 2014-01-18 | ALERT DECLARED DUE TO FIRE IN 480V BUS "[At 1016 EST, an] Alert [was declared] based on EAL # HA 2.1 Fire or explosion resulting in either: visible damage to any table H-1 structure or system/component required for safe shutdown of the plant, or control room indication of degraded performance of any safe shutdown structure, system, or component within any table H-1 area. "Fire in 480V bus 1D2. Reactor was manually tripped" 480 VAC safety related transformer fire in switchgear room. Plant reduced power and tripped the reactor manually. Reactor trip was uncomplicated. Fire was extinguished when the 480 VAC bus was de-energized. The licensee has notified the NRC Resident Inspector, the State of North Carolina, and other local authorities. Notified DHS SWO, DOE Ops Center, FEMA Operations Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and NuclearSSA via e-mail. * * * UPDATE FROM JOEL DUHON TO JOHN SHOEMAKER AT 1602 EST ON 1/18/14 * * * Harris Nuclear Plant secured from the Alert at 1551 EST, on 1/18/14. The plant is stable, the fire is out, the TSC and EOF have been secured and plant recovery has been transferred to the outage control center. There were no personnel injuries or radiological releases. Radiation monitor RM-*1TS-3653C (Technical Support Center Radiation Monitor) is out of service. The licensee has notified the NRC Resident Inspector. Notified the R2DO (King), R2RA (McCree), NRR (Leeds), IRD MOC (Grant), OPA (Brenner), NRR EO (Lee) Notified DHS SWO, DOE Ops Center, FEMA Operations Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and NuclearSSA via e-mail. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  | 0 | 2014-01-18
49741 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-01-18 03:38 | 2014-01-18 07:45 | 2014-01-20 | OFFSITE NOTIFICATION DUE TO DISCHARGE CANAL TEMPERATURE DROP "At 0338 CST, Xcel Energy Environmental Services made a report to the State of Minnesota due to cooling water return to the Mississippi River via the plant's discharge canal dropping by more than 5 deg F per hour. The cause of the temperature drop was due to a required time limited reactor shut down. The reactor is currently shut down with all systems responding as expected. "This notification is being made under 10 CFR 50.72(b)(2)(xi) based on a notification to another government agency. "The NRC Resident Inspector has been notified" * * * UPDATE FROM JON LAUDENBACH TO VINCE KLCO ON 1/20/14 AT 1259 EST * * * "At 1130 EST on 1/20/2014, XCEL Energy Environmental Services made a report to the State of Minnesota (Minnesota Pollution Control Agency and the Minnesota Department of Natural Resources) due to the recorded total fish loss (207) as a result of the Monticello Plant's discharge canal temperature change per above. "This is an update notification only and has no safety significance and no impact on the health and safety of the general public." The licensee notified the NRC Resident Inspector. Notified the R3DO (Skokowski). | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-18
49740 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-01-18 04:01 | 2014-01-18 05:56 | 2014-01-18 | UNUSUAL EVENT DUE TO FIRE IN THE PROTECTED AREA "At 0346 CST [the Unit 1 control room] received a fire alarm in the plant computer room. Upon investigation [the licensee] discovered [the plant computer] room with heavy smoke present and the halon system actuated. [Plant operators] entered '0P0P04-ZO-0008, Fire and Explosion'. Entered Unusual Event at 0401 CST. Fire brigade present at Unit 1 electrical auxiliary building. At 0412 CST the fire was declared to be under control with no visible signs of flame noticed by the fire brigade. Unusual Event based on HU2 (fire or explosion) in the (Protected Area or Switchyard) which affects normal plant operations." At 0446 CST the fire was declared to be extinguished. No plant equipment or indications were affected. The licensee has notified the NRC Resident Inspector, the State of Texas, and other local authorities. Notified DHS SWO, FEMA Operations Center, NICC Watch Officer, and NuclearSSA via e-mail. * * * UPDATE FROM TRIPP FRAHM TO DANIEL MILLS AT 0957 EST ON 1/18/14 * * * "At 0957 EST, [on 1/18/14, the] Unusual Event [was] terminated. Fire damage assessment not complete. Working with site engineering, fire protection, and maintenance personnel to restore all fire detection and protection systems. Continuous fire watch being maintained. Priority is to restore fire detection and protection systems to affected area, followed by repairs to damaged equipment." The licensee has notified the NRC Resident Inspector, the State of Texas, and other local authorities. Notified R4DO (Keller), NRR (Uhle), R4RA (Dapas), NRR EO (Lee), and IRD MOC (Grant). Notified DHS SWO, FEMA Operations Center, NICC Watch Officer, and NuclearSSA via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-01-18
49739 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-01-17 17:36 | 2014-01-17 23:11 | 2014-01-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO REACTOR PRESSURE BOUNDARY LEAKAGE "Leakage into the Reactor Building Closed Cooling Water (RBCCW) system has been determined to be Reactor Pressure Boundary leakage as identified by the plant's Technical Specification [LCO 3.4.4]. Based on this, the LCO is not met and a plant shutdown is required. The shutdown commenced at 2029 CST. "All of the leakage has been retained within the RBCCW system. There has been no radioactive release from the Monticello plant and all other systems remain operable and available. The unit continues to be operated in a safe and predictable fashion as it is being removed from service. "The NRC Resident Inspector has been notified." The leakage rate was 0.12 gallons per minute at power. | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2014-01-17
49738 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-17 14:00 | 2014-01-17 14:54 | 2014-01-17 | FUEL OIL FOUND DURING CORE DRILLING "On January 17, 2014, at 1400 EST Sequoyah (SQN) notified the Tennessee Department of Environment and Conservation (TDEC) of a condition that was identified on December 4, 2013, while conducting core samples. The core drilling contractor detected a petroleum odor, notified the SQN Environmental Group who observed the core drilling and confirmed a slight petroleum odor from a core boring in which water was detected at approximately 41 feet below the ground surface. At that time, as a result of the type of core drilling that was conducted, TVA could not verify if there were petroleum products in the groundwater. "SQN obtained geoprobe boring samples to determine the extent and the depth of the petroleum. Petroleum product was detected in the soil between 30 and 35 feet in depth. This condition has been determined to be associated with a legacy diesel fuel oil leak at SQN in the 1990's and was previously reported. SQN previously completed a remediation project from 1992 - 2010, with oversight from TDEC. The petroleum product appears to be isolated at approximately 30 to 35 feet in depth, is in a perched water table not utilized for drinking water, and appears to be isolated to the diesel building area. To verify the petroleum product is isolated; TVA is conducting additional geoprobe boring to help define the limited area impacted by the legacy diesel fuel oil leak. "The Sequoyah NRC Resident Inspectors have been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-17
49737 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-01-16 | 2014-01-17 12:58 | 2014-01-17 | AGREEMENT STATE - STUCK OPEN SHUTTER ON LEVEL GAUGE The following was received from the State of Georgia via email: "Licensee's Radiation Safety Officer for PQ Corporation with Georgia Radioactive Materials License GA 976-1 reported to the Georgia Radioactive Materials Program [GRMP] on 1-16-14 that an Industrial Source Holder shutter failed to close (used for level measurements) leaving the source in the exposed position. This was discovered when the licensee was performing a semiannual shutter check and inventory for their gauges and source holders. Once this was discovered by the licensee, the entrances to the unoccupied building where the source holder is located was taped off to prevent any unauthorized entrance to the building. The licensee then contacted Thermo Fisher who will be sending a technician to repair the malfunctioning source holder on 1-28-14. The licensee indicated to the GRMP that the building will remain inaccessible until Thermo Fisher arrives to perform repairs on the source holder. The Licensee will inform the GRMP once the repairs have been completed. "Source Holder: TN Technologies, Inc. "Model: 5205 "Source: Cs-137 "Source Activity: 200 mCi "Source S/N: B597" Complaint ID: 72888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-01-27
49736 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-17 11:43 | 2014-01-17 12:50 | 2014-01-17 | OFFSITE NOTIFICATION DUE TO ONSITE DEATH OF AN EMPLOYEE "On January 17, 2014, at approximately 0931 EST, with Watts Bar Nuclear Unit 1 at 100% power and Unit 2 under construction, an off duty security officer was found unresponsive in a personal vehicle in an owner controlled parking lot located outside of the Protected Area. "An emergency medical team responded and the individual was transported off site to a nearby medical facility where he was pronounced dead at 1143 EST. The individual was not contaminated and there were no radiological or industrial safety issues associated with Watts Bar Nuclear Plant. Due to notification of local sheriff and OSHA, this report is submitted pursuant to 10 CFR 50.72(b)(2)(xi), as a notification to a government agency. "NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Under Construction |  | Power Operation | Under Construction |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-17
49735 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-01-17 09:25 | 2014-01-17 12:45 | 2014-01-17 | PYRO PANEL TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0925 [CST] on January 17, 2014, the Unit 1 pyro panel (smoke detection panel) was removed from service for required maintenance. The pyro panel was declared non-functional when it was removed from service. Compensatory measures have been established for all affected areas except the Unit 1 Containment Building. Since a fire in Containment is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). Containment temperatures are being monitored while the pyro panel is out of service, however, this is not considered a satisfactory compensatory measure for maintaining effective assessment capability. "The site NRC Resident Inspector has been notified." * * * UPDATE FROM DARRIN GARD TO CHARLES TEAL AT 2202 EST ON 1/17/14 * * * The pyro panel was restored to service as of 1650 CST. The licensee has notified the NRC Resident Inspector. Notified R2DO (King). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-17
49734 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-15 18:00 | 2014-01-17 11:41 | 2014-06-23 | AGREEMENT STATE REPORT - PROSTATE SEED IMPLANT MISADMINISTRATION The following was received from the State of Arkansas via email: "Central Arkansas Radiation Therapy Institute, Inc. (CARTI), ARK-0654-02200, reported a medical event involving a patient treated for prostate cancer. The treatment plan included implanting 128 I-125 brachytherapy seeds (6 seeds were not implanted), containing a total activity of 1.592 GBq (43.036 mCi), in the patient's prostate for a prescribed therapeutic radiation dose of 14,400 cGy. It appears that approximately 40 of the total number of seeds were implanted into the prostate gland. The seeds were implanted on December 31, 2013. On January 15, 2014, the patient returned to the facility for a post implant CT scan. The scan showed that the implanted seeds, although in an appropriate pattern, were placed outside the intended target. "The State performed an on-site review on January 16, 2014, of the event and discussed the initial details of the event. "The licensee is continuing to investigate the cause and is preparing a written report. "The State is continuing to investigate and will update this report when the report is received from the licensee. "This event is reportable under 10 CFR 35.3045 of the NRC Regulations and RH-8800 of the Arkansas State Board of Health Rules and Regulations for Control of Sources of Ionizing Radiation." State Event Report Number: AR-2014-001 * * * UPDATE PROVIDED VIA EMAIL BY STEVE MACK TO JEFF ROTTON AT 1557 EDT ON 06/23/2014 * * * "Doses: The D90 for the prostate pre-plan was 167.86 Gy and the D90 for the prostate post-plan is 25.31 Gy. "Estimated mean doses to other organs and tissues were, Seminal Vesicles 13.99 Gy, Rectum 45.80 Gy, Bladder 3.89 Gy, and the Penile Bulb 185.24 Gy. "Root cause of the event: The licensee stated: 'the facts of the case lead us to believe that the complexity of the patient anatomy contributed to anatomical misidentification by the attending urologist, i.e. mistaking the penile bulb with the prostate gland.' "Corrective Actions "Multiple corrective actions were implemented including: (1) Centralizing prostate seed implant programs to fewer facilities under the Radioactive Material License, (2) At those facilities continuing to perform prostate seed implants, ensure consistent adherence to the seed implant procedural and policies at each facility, (3) Re-evaluation of the prostate seed implant procedures by the radiation oncologists, (4) Require quality assurance documents on the ultrasound equipment utilized for prostate seed implants, and (5) Require training and proficiency records for operating room staff assisting with prostate seed implants. "Manufacturer and model number of the seeds: The seeds used during this misadministration were Oncura, OncoSeed, Model 6711, containing 0.336 mCi of I-125. Thirty-four (34) seeds of 128 were implanted into the prostate. "The Department [Arkansas Department of Health] considers this event to be closed." Notified R4DO (Allen) and FSME Resources via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2014-01-27
49733 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-16 | 2014-01-16 16:40 | 2014-01-17 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following was received from the State of Texas via email: "On January 16, 2014, the licensee notified the Agency [State of Texas] that it had lost a Troxler Model 3440 moisture/density gauge containing one 40 millicurie americium-241/beryllium source and one 8 millicurie cesium-137 source. One of the licensee's technicians left a construction job site approximately 25 miles west of Austin just off of Hwy. 71 and was driving back to the licensee's office. Near the intersection of Burnet Road and Waterford Center Boulevard in Austin, the technician saw a bucket had fallen out of the back of the truck so he stopped to retrieve it. At that time he saw the tailgate was down and the gauge was missing. He immediately called the job site superintendent. The construction site area and part of Hwy. 71 were searched but the gauge was not found. The licensee's radiation safety officer (RSO) reported that the technician stated he had secured the gauge and closed the tailgate before leaving the site. The licensee will notify local law enforcement and will continue to look for the gauge. The Agency [State of Texas] has notified several area fire departments and the Texas Association of Pawnbrokers. More information will be provided as it is obtained per SA-300." Texas Incident Number: I-9146 * * * UPDATE FROM ROBERT FREE TO CHARLES TEAL ON 1/17/14 AT 1705 EST * * * The gauge was found at the entrance of the construction site by a construction supervisor. The gauge was not damaged. The licensee has possession of the gauge. Notified R4DO (Kellar), FSME Event Resource via email, and Mexico via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-01-24
49732 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-17 10:00 | 2014-01-16 15:50 | 2014-01-16 | 60-DAY REPORT FOR INVALID SYSTEM ACTUATION OF EMERGENCY DIESEL GENERATORS "The following 60-day report is being made under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of the Unit 2, Division 1 and Division 2, Emergency Diesel Generators (EDG) that occurred on November 17, 2013, at 1000 CST. As allowed by 10 CFR 50.73(a)(1) this notification is being made via telephone. "(a) The specific train(s) and system(s) that were actuated. "On November 17th, during the required twenty-two year replacement of the ATWS [anticipated transient without scram] level transmitters, the Unit 2, Division 1 and Division 2, Emergency Diesel Generators (EDG) auto-started as a result of maintenance activities. The failure to remove trip relays, in addition to the sequence for the timing of the replacements, resulted in an unexpected and invalid low water level trip. Subsequently, this resulted in an automatic initiation of the Unit 2, Division 1 and 2, EDGs. "(b) Whether each train actuation was complete or partial. "Upon receiving the invalid low water level signal, both divisions of EDGs responded as expected for existing plant conditions. Therefore, the actuation was considered a complete actuation of both Division 1 and Division 2 EDGs. "(c) Whether or not the system started and functioned successfully. "Both Divisions of EDGs auto-started, achieved rated speed, and idled based upon offsite power being available to the safety related busses. Therefore, this is being considered a successful actuation of the Division 1 and Division 2 EDGs. "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-01-16
49731 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2014-01-16 13:23 | 2014-01-16 14:36 | 2014-01-16 | SAFEGUARDS REPORT - MISSING SECURITY WEAPON Security weapon missing during inventory. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2014-01-16
49730 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-01-15 07:32 | 2014-01-15 17:18 | 2014-01-15 | FITNESS-FOR-DUTY INVOLVING A CONTRACT SUPERVISOR A contract supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. The licensee has notified the NRC Resident Inspectors. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2014-01-15
49729 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-01-15 09:07 | 2014-01-15 16:37 | 2014-01-15 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "Reactor Building (Secondary Containment) pressure increased to above the Technical Specification Surveillance requirement of 0.25 inches vacuum water gauge briefly (5 minutes or less). This is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. Reactor Building pressure has been restored to normal (greater than 0.25 inches vacuum water gauge), returning Secondary Containment to operable status. Highest actual value was 0.21 inches vacuum water gauge. "There were no radiological releases associated with the event." The differential pressure change is believed to have been caused by a momentary shift in Heating and Ventilation Systems dampers. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-01-15
49728 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-15 09:15 | 2014-01-15 16:25 | 2014-01-15 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSED SUPERVISOR A licensed supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2014-01-15
49727 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2014-01-15 07:23 | 2014-01-15 15:47 | 2014-02-07 | DRYWELL RADIATION MONITOR INOPERABLE "At 0723 [CST] hours on January 15, 2014, the 2A Drywell Radiation Monitor was declared inoperable after exhibiting erratic performance. This monitor provides the input into one division of the primary containment isolation logic for a Group II isolation. As a result, the channel was placed in a tripped condition in accordance with Technical Specification 3.3.6.1, Condition B. "Given both divisions are required to complete the Group II isolation logic, this condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The 2A Drywell Radiation Monitor has been repaired and restored to an operable condition. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM JAMES BURKE TO JOHN SHOEMAKER AT 1447 EST ON 2/7/14 * * * "The purpose of this notification is to retract the ENS notification made on January 15, 2014 (ENS 49727). Upon further investigation it was verified that the Drywell Radiation Monitors do not mitigate the consequences of an accident as discussed in Chapters 6 and 15 of the Updated Final Safety Analysis Report and the Technical Specifications Bases for 3.3.6.1. Therefore, the threshold for reporting the issue as an event or condition that could have prevented the fulfillment of a safety function was not met (NUREG 1022 Revision 3 - Event Report Guidelines Section 3.2.7). "The NRC Resident Inspector has been notified." Notified the R3DO (Orlikowski). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-01-15
49726 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-15 10:19 | 2014-01-15 13:29 | 2014-01-15 | HIGH RANGE STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "Millstone Unit 2 [removed the] High Range Stack Radiation Monitor, RM 8168, [from service for] pre-planned maintenance. RM 8168 [was] restored to operable at 1157 [EST] on 1/15/2014." The licensee informed State and local agencies and the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-15
49725 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2014-01-14 15:00 | 2014-01-15 13:05 | 2014-01-15 | FISH LOSS AT CLINTON POWER STATION "The following report is being made in accordance with Clinton Power Station Operating License, Appendix B, Environmental Protection Plan. "On 1/14/14, an inspection of the Clinton Lake was conducted via boat of inaccessible areas. The inspection revealed more than one hundred deceased fish over several locations. The species predominantly observed were buffalo fish and carp, with some game fish identified. While no direct cause was identified for the fish loss, the fish loss closely coincides with two recent unplanned plant shutdowns that occurred in December 2013." The licensee informed the State and the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2014-01-15
49724 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-15 09:48 | 2014-01-15 12:29 | 2014-01-15 | NORMAL VENTILATION RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "[The] Normal Ventilation Normal Range Process Radiation Monitor 3HVR*RE10B [was] removed from service for planned maintenance. [The affected Radiation Monitor] will be returned to service following maintenance." The licensee informed State and local agencies and the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-15
49723 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-16 14:20 | 2014-01-14 18:33 | 2014-01-14 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "On 10/16/2013 at 14:20 [CDT], the Technical Support Center (TSC) Emergency Makeup Filter Flow Control Damper (OVV145Y) was discovered degraded and non functional during planned maintenance activities. The degraded damper adversely impacted the TSC ventilation system function. "On 10/16/2013 at approximately 15:00 [CDT], administrative actions were developed and briefed to isolate instrument air to the degraded nonfunctional damper OVV 145Y providing the capability to restore TSC Emergency Makeup Filter functionality. Isolating instrument air to the degraded damper places the damper in the failed open position, thereby restoring TSC Emergency Makeup Filter functionality. "On 10/16/2013 at 20:25 [CDT], instrument air was isolated to the degraded damper OVV 145Y under administrative controls restoring TSC Emergency Makeup Filter functionality. This action was taken after determining no adverse affects on system operation. "On 10/30/2013, degraded damper OVV145Y was repaired, instrument air restored and post maintenance testing completed, thereby restoring the degraded TSC emergency Makeup Filter Unit flow control damper functionality. This event is reportable per 10CFR50.72(b)(3)(xiii) for a major loss of emergency assessment capability because the emergent degraded TSC flow control damper OVV145Y adversely impacted the function of TSC Emergency Makeup Filter and was not restored within the TSC activation time (60 minutes). "This event was originally determined not reportable because the capability to restore within the TSC activation time (60 minutes) existed from the time of discovery. Upon further review it was determined to be reportable because the degraded damper 0VV145Y was not restored to service within the TSC activation time (60 minutes). "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-14
49722 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-01-14 13:30 | 2014-01-14 16:14 | 2014-01-14 | OFFSITE NOTIFICATION TO SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL (SCDHEC) "Offsite notification to South Carolina Department of Health and Environmental Control (SCDHEC). At approximately 1330 EST on January 14, 2014, site personnel discovered a fork lift leaking hydraulic oil in the protected area. The estimated amount of hydraulic oil spilled is between 10-15 gallons. Approximately 3 gallons of hydraulic oil from the spill entered a nearby storm drain that discharges into Outfall 13. At 1530 [EST] an initial notification was made to SCDHEC. The spill has been contained and clean up efforts are underway. "The NRC Residents have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-14
49721 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-01-13 | 2014-01-14 15:59 | 2014-01-14 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE-DENSITY GAUGE The following information was received from the State of Georgia via email: "On January 13, 2014, NOVA Engineering and Environmental, LLC had a Troxler 3440 gauge stolen out of the bed of the truck. There have been a couple thefts at this site leading up to this incident (2075 Princeton Ave., College Park, Georgia). The truck was parked at an active construction site (new elementary school) and the vehicles are required to park some distance away from the construction. During [the] NOVA gauge operator time at the site he stated he saw the gauge in the bed of the truck and sometime later he left this site to go to another. Upon arrival, he realized the chain had been cut and the gauge box was gone. "[The] NOVA RSO confirmed that the gauge box was only secured with one chain and that there was a lock on the box. A police report has been filed and will be available to be viewed in three to five days. At this moment, all gauges are locked in storage at the company's office. Gauges are only allowed to be removed if there is an assignment. Prior to this, the gauge stayed in the bed of the truck and went to all job sites even if there wasn't an assignment for it. "A leak test was done on November 27, 2013 and the result report was created on December 13th 2013 by Atlantic Supply with no areas of concern. Gauge Information: Model Number: Troxler 3440 Serial Number: 22661 Isotope: Am-241 and Cs-137 Source serial numbers: 47-18503 (Cs-137) and 75-4417 (Am-241) Activity: 8mCi Cs-137 and 40mCi Am-241" GA Complaint ID: 72861 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2014-01-22
49720 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2014-01-13 10:22 | 2014-01-13 13:09 | 2014-01-17 | EMERGENCY RESPONSE FACILITIES OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because work activities affect the functionality of emergency response facilities. This condition does not affect the health and safety of the public or station employees. "At approximately 1022 [EST] on January 13, 2014, planned maintenance activities began on the Emergency Operations Facility (EOF) heating ventilation and air conditioning (HVAC) system. The scope of the maintenance is to obtain samples of the charcoal filter. The planned work activity duration is expected to be approximately 20 hours ending on January 14, 2014. In addition, a multi-day (5 days) maintenance activity will begin on January 13, 2014 on the Technical Support Center (TSC) HVAC system, involving flow-balancing the system, which may involve intrusive maintenance during certain intervals. This intrusive maintenance will render the TSC HVAC system non-functional. This planned work activity is expected to be completed on January 17, 2014. The EOF and TSC HVAC systems will be restored periodically throughout this maintenance period. "If an emergency is declared requiring emergency facility activation during this period, the emergency facilities will be staffed and activated using existing emergency planning procedures. If relocation of the emergency facilities becomes necessary, the Emergency Director will relocate the emergency response organization to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "An update will be provided once the EOF and TSC ventilation systems have been restored to normal operation and all planned maintenance is complete. The NRC Resident Inspector has been notified." * * *UPDATE PROVIDED BY KEVIN ABELL TO JEFF ROTTON AT 1043 EST ON JANUARY 17, 2014 * * * The planned maintenance is complete and the EOF and TSC have been restored to normal operation. The licensee notified the NRC Resident Inspector. Notified R2DO (King) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-13
49719 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-13 08:00 | 2014-01-13 09:24 | 2014-01-13 | RADIATION MONITOR OUT OF SERVICE FOR MAINTENANCE The normal ventilation high range process radiation monitor, 3HVR*10A, was removed for service for planned maintenance. The radiation monitor will be returned to service following maintenance. The NRC Resident Inspector has been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-13
49718 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-13 04:00 | 2014-01-13 04:28 | 2014-01-13 | LOSS OF TECHNICAL SUPPORT CENTER DUE TO PLANNED MAINTENANCE "A condition is being reported per TRM 13.13.1, Emergency Response Facilities, Action 8.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities performed on TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity. The NRC Resident Inspector has been notified." * * * UPDATE FROM KEVIN LOWE TO DANIEL MILLS ON 1/18/14 AT 0533 EST * * * The TSC has been returned to functional status. The Licensee notified the NRC Resident Inspector. Notified R2DO (KING). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-13
49717 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-01-12 03:23 | 2014-01-12 06:44 | 2014-01-16 | MANUAL REACTOR TRIP FOLLOWING CONTROL ROD POSITION DEVIATION "After achieving criticality a deviation between control rods was observed by plant personnel. When attempting to level the control rods, one rod could not insert to the level of the rest of the group. A manual reactor trip was initiated by the operating crew. All tripable control rods fully inserted into the core." The trip was uncomplicated and the licensee is investigating the cause of the control rod position deviation. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT MOECK TO JOHN SHOEMAKER AT 1320 EST ON 1/16/14 * * * Report was updated to indicate 8-hour reportable criteria for Valid Specified System Actuation (Reactor Protection System). The licensee will notify the NRC Resident Inspector. Notified the R4DO (Kellar). | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-12
49716 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-01-11 16:05 | 2014-01-11 22:25 | 2014-01-11 | DIGITAL RADIATION MONITORING SYSTEM COMMUNICATION FAILURE "At 1605 EST on January 11, 2014, Beaver Valley Power Station (BVPS) Unit 2 determined that the Digital Radiation Monitoring System (DRMS) had a communication loop failure resulting in a loss of control room radiation monitor indication and alarm capability. BVPS Unit 2 DRMS was declared nonfunctional. Repair efforts were initiated and compensatory measures were established. "At 2040 EST on January 11, 2014, BVPS Unit 2 DRMS was returned to service and declared functional. "The failure of the BVPS Unit 2 DRMS communication loop resulted in a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." The licensee notified Pennsylvania, West Virginia and Ohio emergency management agencies as well as local authorities of this notification. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-11
49715 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2014-01-11 11:00 | 2014-01-11 13:24 | 2014-01-11 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "On January 10, 2014, at 0919 CST, the plant voluntarily entered multiple required action statements in Technical Specifications 3.3.1 Reactor Trip System Instrumentation and 3.3.2 Engineered Safety Feature Actuation System to conduct surveillance testing of the B-train Solid State Protection System (SSPS). During testing, abnormal indications were received. As a result of the abnormal indications, the SSPS has not been returned to operable status within the required completion time of 24 hours. At 1100 CST on January 11, 2014, Unit 2 commenced a plant shutdown required by technical specifications and will be in Mode 3 by 1519. Therefore, this is reportable under 10 CFR 50.72(b)(2)(i), plant shutdown required by technical specifications. "The NRC Resident Inspector has been notified." | 0 | 51 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-01-11
49714 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-01-11 01:00 | 2014-01-11 03:33 | 2014-01-11 | OFFSITE NOTIFICATION DUE TO DECREASING DISCHARGE TEMPERATURE "At 0205 CST [on 1/11/14], Xcel Energy Environmental Services made a report to the State of Minnesota due to cooling water return to the Mississippi River via the plants discharge canal dropping by more than 5 degrees F in an hour. The cause of the temperature drop was due to an emergent reduction in reactor power and generator load in response to a degrading condenser vacuum. "This notification is being made under 10 CFR 50.72(b)(2)(xi) based on a notification to another Government Agency. "The NRC Resident Inspector has been notified." | 60 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-11
49713 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-01-10 19:48 | 2014-01-10 20:11 | 2014-01-10 | UNUSUAL EVENT DECLARED DUE TO EXPLOSION WITHIN PROTECTED AREA BOUNDARY The licensee declared a Notice of an Unusual Event per EAL HU2.2 "Explosion with Protected Area Boundary" following an apparent fault and explosion on the M29 transformer (a non-safety related transformer). This resulted in a loss of one electrical bus at the ocean discharge station; however, no safety-related electrical loads were effected and both units remained at 100 percent electrical power. Station personnel reported that there was no smoke in the area of the M29 transformer and the event may have been a flashover explosion in the area of the transformer. All safety systems remain available. Licensee is investigating the cause of the explosion, and no offsite assistance was required. The licensee has notified the NRC Resident Inspector, the State of North Carolina, and other local authorities. Notified DHS SWO, FEMA Operations Center, NICC Watch Officer, and NuclearSSA via e-mail. * * * UPDATE ON 01/10/14 AT 2343 EST FROM MIKE MORRIS TO RYAN ALEXANDER * * * "Notification of an Unusual Event is being terminated [at 2320 EST] because the condition no longer exists. The source of the apparent explosion was a failed insulator on a breaker and is known to present no danger to public health and safety. Both Units are stable and a recovery organization is in place." The licensee has notified the NRC Resident Inspector regarding the termination of the event. Notified R2DO (Hopper), NRR EO (Lubinski), IRD Manager (Gott), DHS SWO, FEMA Operations Center, NICC Watch Officer, and Nuclear SSA via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-01-10
49712 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2014-01-10 12:14 | 2014-01-10 13:27 | 2014-01-10 | OFFSITE NOTIFICATION DUE TO TEMPORARY BYPASS OF NORMAL OUTFALL DURING SEVERE WEATHER "On January 10, 2014, Florida Power and Light reported to the Florida Department of Environmental Protection that the St. Lucie Nuclear Plant temporarily bypassed the normal storm collection outfall path at 17:45 EST on January 9, 2014. The bypassed flow of water was a result of severe rainfall at the station and a blockage in the normal outfall path. "This non-emergency notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to the notification of the Florida Department of Environmental Protection." The licensee originally made the offsite notification to the State of Florida agency associated with the emergency declaration and severe weather event on January 9, 2014 (see Event Notification 49707). The licensee has notified the NRC Resident Inspector. | 100 | 93 | 0 | 100 | 93 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-10
49711 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2014-01-09 | 2014-01-10 09:45 | 2014-01-10 | AGREEMENT STATE REPORT INVOLVING STUCK SHUTTER ON LEVEL GAUGE "On January 10, 2014, the Agency received a report from the licensee's Radiation Safety Officer (RSO) stating the shutter on a Ohmart Vega model SGLG gauge containing a 500 millicurie cesium - 137 source was found stuck in the open position. Open is the normal operation position of the gauge shutter. The RSO stated a contractor was performing a calibration of a level detector on January 9, 2014, when they could not get the gauge shutter to close. The contractor sprayed the shutter with a light oil and attempted to rotate the handle and operating arm. While trying to free the shutter, the operating arm separated from the gauge. The contractor was able to insert the operating rod into the gauge, but the shutter would not move. The manufacturer has been contacted to assist in the repair or replacement of the gauge. No exposure resulted from this event and the current position of the gauge shutter does not create any additional exposure risk to any personnel. A contact dose rate survey of the gauge was conducted and the highest reading observed was 1.2 millirem per hour. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-9145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-01-20
49710 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-01-09 23:17 | 2014-01-10 06:39 | 2014-01-16 | DEGRADED FITTINGS CONNECTED TO CONTAINMENT PENETRATION "During an engineering walk down inside containment a minor leak from a pipe fitting was discovered on the primary sampling piping connected to penetration M-45. There was previously identified minor leakage from a fitting on this same penetration outside of containment in the auxiliary building. The containment isolation valves are currently tagged closed." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT MOECK TO JOHN SHOEMAKER AT 1320 EST ON 1/16/14 * * * "Additional testing was performed on penetration M-45 which determined that the penetration met the required leakage limits. Therefore this issue does not represent a degraded condition for the containment and is not reportable. The previous notification is being retracted." The licensee has notified the NRC Resident Inspector. Notified the R4DO (Kellar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-01-10
49709 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-01-09 17:43 | 2014-01-10 02:14 | 2014-01-10 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "Reactor Building (Secondary Containment) pressure increased to above the Technical Specification Surveillance requirement of 0.25 inches vacuum water gauge briefly (two minutes or less) on two occasions. This is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. Reactor Building pressure has been restored to normal (greater than 0.25 inches vacuum water gauge) returning Secondary Containment to operable status. The cause of the event is under investigation. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-01-10
49708 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2014-01-09 22:34 | 2014-01-10 00:27 | 2014-01-10 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 2234 hours EST on 01/09/2014, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. At the time of the event, Steam Generator Water level Protection Channel Testing was in progress. While testing was in progress with the 'C' Steam Generator Channel 1 Water Level Protection channel in trip for testing, a Turbine Trip occurred. The cause of the Turbine Trip is under investigation. "The [Turbine Driven and Motor Driven] Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. The pressurizer Power Operated Relief Valves (PORVs) and the Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "Currently, the unit is stable in Hot Standby (Mode 3). "This event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B) due to the valid Reactor Protection System Actuation. "This event is being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of Auxiliary Feedwater System. "At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified. State and local authorities will be notified. Estimated restart date is 1/12/2014" | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-10
49707 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2014-01-09 18:03 | 2014-01-09 18:56 | 2014-01-10 | UNUSUAL EVENT DECLARED DUE TO SEVERE RAIN STORM "On January 9, 2014 St. Lucie Unit 1 declared an Unusual Event based on a severe rain storm, a natural occurrence affecting the Protected Area. Specifically, visual sightings by station personnel that water levels are approaching storm drain system capacity. Countermeasures are being deployed and are currently operating satisfactorily. Both units continue to operate at full power. All safety systems remain available. The licensee has notified the NRC Resident Inspector, state, and other local authorities. Notified R2DO (Hopper), NRR EO (Lubinski) and IRD. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, and Nuclear SSA via email. * * * UPDATE FROM RACHEL SMITH TO GEROND GEORGE ON 01/10/2014 AT 0043 EST * * * "On January 10, 2014 at 0001 EST, St. Lucie Unit 1 terminated an Unusual Event. Site storm drain system functioning as required. Severe weather has passed, site water levels have returned to normal." Notified R2DO (Hopper), NRR EO (Lubinski) and IRD. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2014-01-09
49706 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2014-01-09 11:35 | 2014-01-09 15:21 | 2014-01-09 | ENTRY INTO & EXIT FROM TECHNICAL SPECIFICATION 3.6.5.1.1 DUE TO OPEN AIR LOCK DOORS "Station Personnel simultaneously opened the inner and outer air lock doors from Unit 2 (U2) Reactor Enclosure to the Refuel Floor. Reactor Enclosure Secondary Containment Integrity was declared Inoperable per U2 TS 3.6.5.1.1, due to failure to meet surveillance requirement U2 TS 4.6.5.1.1.b.2, due to the report of both containment airlock doors on 352' momentarily open at the same time. Reactor Enclosure D/P[differential pressure] remained steady at 0.35 inches vacuum water gauge. "Reactor Enclosure Secondary Containment Integrity was declared Operable following verification that at least one air lock door to each access of secondary containment was closed per U2 TS 4.6.5.1.1.b.2. Total [Limiting Condition for Operation] time was approximately 5 seconds." The NRC Resident Inspector has been informed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2014-01-09
49705 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-01-09 | 2014-01-09 15:29 | 2014-01-09 | UNANALYZED CONDITION IDENTIFIED FROM OPERATING EXPERIENCE REVIEW "A review of industry operating experience regarding the impact of unfused [safety-related] direct current ammeter circuits in the main control room has determined the described condition [having the ammeters installed] to be applicable to River Bend Station, resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. River Bend Station does have unfused ammeter leads. This normally is not a concern, since two failures are required to cause the problem described in the document referenced above; an ammeter lead must short to ground, and another lead of the opposite polarity must also short to ground. Either of these events by itself will set an alarm, but not cause equipment damage. This allows for locating and repairing the problem before the second failure occurs. However, during a fire, there is a greater chance that these two failures could happen simultaneously, or before a single failure can be repaired. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures have been implemented." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-01-09
49704 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-01-09 05:18 | 2014-01-09 06:42 | 2014-01-09 | TECH SPEC REQUIRED SHUTDOWN DUE TO INOPERABLE RAW WATER PUMPS. "At 0315 CST T.S. 2.0.1 was entered for all four Raw Water pumps being declared inoperable. The pumps were declared inoperable due to inability to close one of the sluice gates. There are six sluice gates and one is not functional. "At 0518 the technical specification required shutdown commenced." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM AMY BURKHART TO NESTOR MAKRIS ON 01/09/14 AT 1915 EST * * * "At 0900 CST 1/9/14 Fort Calhoun Station Unit 1 was manually tripped and entered Mode 3. Reactor Coolant System (RCS) cooldown to less than 300 deg F was commenced at time 1030 CST 1/9/14. The RCS temperature was less than 300 deg F at time 1433 CST. A press release has been issued." The licensee informed the NRC Resident Inspector. Notified R4DO [Hagar] | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2014-01-09
49703 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-01-09 03:15 | 2014-01-09 06:42 | 2014-01-09 | INTAKE STRUCTURE SLUICE GATE INOPERABLE " At 2230 CST on 1/8/14 during operator rounds it was self identified there was a block of ice formed on the shaft and top of one of the intake structure sluice gates. This has bent the sluice gate operating shaft. At 0315 CST on 1/9/14 it was verified this gate could not be closed. "There are six intake sluice gates that are required to be able to close to act as flood barriers. The other 5 sluice gates are not affected by this condition." The licensee informed the NRC Resident Inspector. | 96 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2014-01-09
49702 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-01-08 10:10 | 2014-01-08 19:49 | 2014-03-13 | LOSS OF ASSESSMENT CAPABILITY - NON-FUNCTIONAL AREA RADIATION MONITORS "At [1010 PST] on 1/08/14, during performance of a surveillance the power supply for ten area radiation monitors in the Reactor Building was found with voltage out of specification. As a result, the affected area radiation monitors were declared non-functional. This condition represents a major loss of assessment capability and is being reported as such under 10 CFR 50.72 (b)(3)(xiii). As directed by station procedures, compensatory measures have been enacted until the power supply is restored. "The Resident Inspector has been notified." * * * UPDATE FROM JASON LOVEGREN TO JIM DRAKE ON 01/10/2014 AT 0214 EST* * * "The power supply voltage has been restored to specification per applicable station procedures. All affected area radiation monitors have been declared functional. Compensatory measures have been suspended." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 3/13/14 AT 1853 EDT FROM JOHN KAINEG TO DONG PARK * * * "Licensee is retracting this event notification based on the following: "Energy Northwest performed an evaluation for the reported out-of-specification voltage condition for the power supply to several radiation monitors in the Reactor Building. The evaluation concluded that the voltage deviation from the -24 VDC set point was small and within the calculated uncertainty for the instrument, and did not result in equipment failure. Therefore, it was concluded that the radiation monitors were functional and that the reported major loss of assessment capability did not occur." The licensee has notified the NRC Resident Inspector. Notified R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-08
49701 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-01-07 14:39 | 2014-01-08 17:35 | 2014-01-08 | OFFSITE NOTIFICATION FOR SPILL IN THE RIVER BEND OWNER CONTROL AREA "On January 8, 2014, at 1439 CST, River Bend Station management determined that a spill discovered on the morning of January 7 was reportable in accordance with NEI 07-07 (Nuclear Energy Institute), Ground Water Protection Initiative. The spill was the result of freeze damage that occurred on a valve connected to the cooling tower blow-down line. Dams were installed to prevent the water from reaching any storm drains, and the spill was confined to the owner-controlled area. Since this system has the potential to contain diluted radioactive plant effluent, samples were collected for analysis. The leak was immediately reduced to a small drip and actions are in progress to completely isolate and repair the valve. The effluent was determined today to contain 4584 pico-curies per liter of tritium, but no detectable gamma activity. The calculated volume of the leak was between 100 and 1200 gallons. This exceeds the NEI reporting criterion of 100 gallons from a source containing licensed material. The Louisiana Department of Environmental Quality was notified at 1549 CST today. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as an event requiring notification of the state government. "The NRC resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-08
49700 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2014-01-07 12:10 | 2014-01-07 16:07 | 2015-02-09 | REACTOR BUILDING STACK MONITOR TEMPORARILY OUT OF SERVICE FOR MAINTENANCE "At 1210 PST on January 7, 2014 the Reactor Building Stack Radiation Monitor- Intermediate Range detector was declared non-functional due to scheduled maintenance on supporting equipment. The monitor is expected to be out of service for approximately 1 hour. Preplanned compensatory actions have been implemented. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "At 1238 PST on January 7, 2014 the Reactor Building Stack Radiation Monitor -Intermediate Range detector was declared functional following scheduled maintenance on supporting equipment. Emergency Assessment Capability has been restored. Preplanned compensatory actions have been secured. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM MATT REID TO DANIEL MILLS AT 1636 EST ON 02/09/2015 * * * "Licensee is retracting this event notification based on the following: Regulatory guidance in NUREG-1022 Revision 3 allows for not reporting EP equipment outages that are planned (i.e., maintenance) when outage time is not expected to exceed or does not exceed 72 hours, and when there are viable compensatory measures in place. Verification of the Control Room Logs indicates Columbia had viable compensatory measures in place during the maintenance outage and the outage duration was less than 72 hours. Columbia met the conditions in NUREG-1022; therefore, this event did not represent a loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. Notified R4DO (Allen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-07
49699 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-07 07:45 | 2014-01-07 13:12 | 2014-01-07 | UNANALYZED CONDITION CAUSED BY HIGH ENERGY LINE BREAK BARRIER DOOR OPEN DURING MAINTENANCE "At approximately 0745 on January 7, 2014, a review of maintenance activities performed on October 3, 2013 on Salem Unit 2, identified an instance in which a High Energy Line Break (HELB) barrier access door was not properly controlled during a Turbine Driven Auxiliary Feedwater Pump room maintenance activity. A HELB event occurring in a room with its barrier door open could adversely affect equipment in an adjacent room. The steam supply to the Turbine Driven Auxiliary Feedwater Pump was not isolated in support of the maintenance activities and the room HELB barrier door was not properly controlled during maintenance in the room. Consequently, a HELB event occurring in the Unit 2 Turbine Driven Auxiliary Feedwater Pump room with the impaired barrier door, could have rendered the Turbine Driven Auxiliary Feed water Pump and both of the Motor Driven Auxiliary Feedwater Pumps in the adjacent room inoperable. "This event is being reported under the requirements of 10 CFR 50.72(b)(3)(ii)(B) as "the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." An ENS notification is required if an unanalyzed condition occurred within 3 years of the date of discovery even if the event is not on-going at the time of discovery. "The Licensee has notified the NRC Resident." The licensee also will notify the Lower Alloways Creek Township. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-01-07
49698 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2014-01-06 21:15 | 2014-01-06 21:55 | 2014-01-06 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL DUE TO A FAILED MAIN FEEDWATER REG VALVE "On January 6th, 2014 at 2115 EST Indian Point Unit 3 experienced an Automatic Reactor Trip due to '33 Steam Generator Steam flow/Feed flow Mismatch.' Operators entered emergency procedure E-0, Reactor Trip or Safety Injection. All control rods fully inserted, all safety systems responded as expected, and off-site power remained in-service. No primary or secondary safety valves actuated due to the trip. This is reportable under 10CFR50.72(b)(2)(iv)(B). The main condenser is being used for heat sink. Unit 2 remains stable at 100% power. The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10CFR50.72(b)(3)(iv)(A). "Investigation is underway to determine the cause of the 33 Steam Generator Mismatch condition." The licensee will inform local and other government agencies and issue a press release. The licensee has informed the State of New York and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-06
49697 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2014-01-06 16:59 | 2014-01-06 19:09 | 2014-01-06 | AUTOMATIC REACTOR TRIP DUE TO MAIN TRANSFORMER FAULT "At 1659 EST hours on January 6, 2014, Beaver Valley Power Station Unit 1 automatically tripped from 100% power. The cause of the reactor trip was a main transformer differential trip. All rods fully inserted into the core and the plant is stable in Mode 3. All three auxiliary feedwater pumps automatically started as expected. Normal and Emergency Busses are being powered by Offsite Power. The cause of the main transformer differential trip is being investigated. All other equipment functioned as expected. At 1757 EST hours the Emergency Operating Procedures were exited. "Resident inspector has been notified." Decay heat is being removed via the turbine bypass valves to the condenser. No primary or secondary safety valves lifted. Unit 2 was unaffected. Licensee notified the States of Pennsylvania, Ohio, and West Virginia and the Counties of Beaver, PA, Hancock, OH, and Columbiana, OH. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-01-06
49696 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2014-01-04 | 2014-01-06 13:21 | 2014-01-06 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER MECHANISM FAILURE The following information was provided by the State of Iowa via email: "On 1/6/2014 the RSO for MidAmerican Energy Company (Louisa Generating Station), License # 0040-1-70-FG, informed IDPH [Iowa Department of Public Health] that a shutter for a fixed gauge (Texas Nuclear, Model # 5192, s/n B-2723, Source Model # 57157C, containing < 50 mCi of Cs-137) vibrated out of its bracket. This event occurred on 1/4/2014 at approximately 0730 [CST]. The fixed gauge is located on a coal hopper and used for level indication. At the time of the incident the plant is online and the hopper is in use. The fixed gauge is located approximately 50 feet from the catwalk. Since the facility is online, the hopper is in use and no work can occur inside hopper, there is no exposure pathway for any individuals. The licensee has informed all of their employees that no work will be allowed in the hopper until the shutter has been repaired/reinstalled. The licensee has contacted their fixed gauge service provider (RM Wester) to perform repairs/modifications to the fixed gauge so there is no reoccurrence of this event. They are scheduled to be onsite 1/8/2014. "IDPH considers this event closed." Item No.: IA140001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2014-01-14
49695 | 0 | MALLINCKRODT PHARMACEUTICALS |  |  |  |  | 2014-01-06 08:13 | 2014-01-06 13:07 | 2014-01-14 | MOLLY-TECH GENERATOR LOST SOURCE DURING SHIPMENT "The Mo-Tc Generator (Mallinckrodt Tracking number 2241132 on box and generator, and DU [Depleted Uranium] number 4283 stamped on DU shield) was offered for shipment on 27DEC13 to courier [common]. The generator was sent to customer Pharmalogic MT Inc in Missoula, Montana. The customer did not receive the generator and contacted Mallinckrodt [on December 28, 2013]. A search was conducted and on 06JAN14, [common carrier] informed Mallinckrodt that they believe they did not have the generator of concern at any of their sites. Typical shipment routing is from Maryland Heights, Missouri to St. Louis Lambert airport to Memphis, Tennessee. After Memphis we [Mallinckrodt] are not aware if a second stop occurs prior to arrival in Missoula, Montana. Mallinckrodt conducted an onsite search and was not successful at finding the generator. "At time of shipment, the generator activity was 11 curie of Mo-99, and 8.1 mCi of depleted Uranium-238. The shipping box read 10.9 mR/hr on contact with the outer surface. Estimated on contact exposure rate levels on the outside of the generator at time of shipment was 180 mR/hr. "At time (06JAN14) of declaration of the generator being lost, the activity levels were estimated to be 882 mCi of Mo-99, 882 mCi of Tc-99m, and 8.1 mCi of depleted U-238. Estimated exposure rate levels were 0.9 mR/hr on the outside surface of the shipping box, and 14 mR/hr on the outside surface of the generator. "This event was also reported to Ken Lambert (Voice Mail), NRC Sr. Health Physicist in Region III." During shipment pickup on December 27, 2013 by the common carrier , the package did not get properly scanned into the common carrier tracking system, and no shipping Bill of Lading, Air Way Bill number, or shipping documentation of any sort was provided to the shipper and was attributed to a new common carrier employee. * * * UPDATE PROVIDED BY GARY BOSGRAAF TO JEFF ROTTON AT 1027 EST ON JANUARY 14, 2014 "On 27DEC13 (Day of initial event), another generator that day was shipping to Cardinal Health in Pompano Beach, Florida. Numerous changes were made to generator orders over the holiday due to reduced pharmacy needs. This particular customer has their standing order for their generator flown on American Airlines on a standing order basis every Friday. Any other orders they want would ship [common carrier]. They made changes to their generator for the 27th which resulted in this particular order defaulting to their [common carrier] routing. "When the generator for Pompano Beach was processed on the 27th their routing for this generator was [common carrier]. When a generator is routed [common carrier] the DG [Dangerous Goods] statement and the label will generate automatically when it is processed at the drop station which is what happened here. The technician noticed that this particular order goes American every Friday and changed the order to ship with the airline. The [common carrier] paperwork was not pulled and another technician mistakenly put the [common carrier] label on the Missoula, MT generator. We know this by looking at the history of the order for Pompano Beach. It shows it being processed as a [comon carrier] order but the route being changed to ship with American. "The generator then shipped down to the [common carrier] facility in Pompano Beach where it remained until Friday 10JAN14 when it was reported to Mallinckrodt." Notified R1DO (Rogge), R3DO (Skokowski), R4DO (Kellar) and FSME Events Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-01-14
49694 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2014-01-06 02:45 | 2014-01-06 10:31 | 2014-01-06 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE EXCEEDED TECHNICAL SPECIFICATION "At 0245 CST secondary containment differential pressure exceeded the Technical Specifications limit due to a personnel error manipulating an incorrect component. This caused entry into LCO 3.6.4.1 for secondary containment inoperability. An event or condition that could have prevented fulfillment of a safety function requires an 8 hour report per 10CFR50.72(b)(3)(v)(C) for Control of Rad Release and 10CFR50.72(b)(3)(v)(D) for Accident Mitigation. The error was corrected and secondary containment pressure was restored to greater than or equal to 0.25 inch vacuum water gauge and secondary containment was declared operable at 0302 CST. The NRC Resident has been informed of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-01-06
49693 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2014-01-06 08:51 | 2014-01-06 10:09 | 2014-01-06 | RADIATION MONITOR TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "The Supplementary Leakage Collection and Release System ventilation process flow radiation monitor 3HVR*RE19A has been removed from service for pre-planned maintenance. The monitor will be returned to service after maintenance is complete." The NRC Resident Inspector, state, and local agencies have been informed. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-06
49692 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2014-01-06 03:30 | 2014-01-06 06:56 | 2014-01-06 | LOSS OF THREE EMERGENCY PLAN SIRENS "While operating in Mode 1 at 100% rated thermal power, the City of Burlington Kansas emergency dispatch center notified Wolf Creek Nuclear Operating Corporation (WCNOC) Security that two emergency plan sirens in Burlington, Kansas and one emergency plan siren in New Strawn, Kansas failed to function when they were actuated to call out a local fire response . These three sirens also function as part of the Emergency Plan Alert and Notification System. WCNOC Emergency Plan personnel have been notified of the three siren failures and the cause is under investigation. "Wolf Creek Generating Station (WCGS) remains at 100% rated thermal power. "The WCGS NRC Resident [Inspector] has been notified and local government." * * * UPDATE AT 1408 EST ON 01/06/14 FROM PIERCE MOORE III TO JEFF ROTTON * * * "At 0922 CST, the three sirens were returned service. "WCGS NRC Resident has been notified. " Notified R4DO (Hagar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-06
49691 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-01-03 23:00 | 2014-01-04 01:22 | 2014-01-04 | SIREN ACTIVATION CAUSED BY EQUIPMENT MALFUNCTION "Limerick Generating Station Main Control Room was informed that a Limerick Emergency Preparedness Zone (EPZ) Siren located in South Coventry, Chester County Pennsylvania area was sounding by an off-duty plant employee and confirmed by the Chester County 911 Dispatch Center. Notification occurred at 2300 hours on 1/13/14. This notification is being made in accordance with SAF 1.9 due to a spurious actuation of Limerick Emergency Preparedness Zone (EPZ) Siren. "The siren maintenance contractor has been contacted to investigate and silence the sounding alarm. "No actual Plant emergency exists. The siren activation was caused by equipment malfunction. "[The] remaining 164 of 165 Limerick EPZ Sirens remain functional, no other reportability threshold(s) have been met or exceeded." The licensee has notified the NRC Resident Inspector and state and local authorities. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-01-04
49690 | -1 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-03 15:00 | 2014-01-03 22:07 | 2014-01-30 | ABGTS POTENTIALLY INOPERABLE FOR BOTH UNITS UNDER WORST-CASE CONDITIONS "At 1500 EST on 01/03/2014, TVA determined that during certain conditions, Service Air usage (air used for non-safety related tools/equipment) could result in introducing air into the Auxiliary Building Secondary Containment Enclosure that could, in worst-case conditions, exceed the margin required to maintain the Auxiliary Building Gas Treatment System (ABGTS) operable for Sequoyah Units 1 and 2. ABGTS is required to be operable for both units by Technical Specifications. This is an unanalyzed condition that could prevent both trains of ABGTS from performing [their] safety function[s]. Service air has been isolated to the Auxiliary Building and is under administrative controls until further analysis [is] complete. This is additional information discovered during follow-up evaluation regarding the issue identified in LER 50-327/2013-004. Further analysis will be performed to determine safety significance." There is 1600 scfm margin in the ABSGTS. The Service Air compressors have an 1850 scfm capacity. The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM BRUCE BUCH TO DANIEL MILLS AT 1428 EST ON 1/30/2014 * * * "Sequoyah Nuclear Plant, Units 1 and 2, are retracting the 8 hour non-emergency notification January 3, 2014 at 2207 EST (EN# 49690). "The notification on January 3, 2014, reported under certain conditions, service air usage could result in the Auxiliary Building Secondary Containment Enclosure (ABSCE), in worst case conditions, exceeding the margin required to maintain the Auxiliary Building Gas Treatment System (ABGTS) operable and prevent both trains of ABGTS from performing its safety function(s). "Subsequent engineering analysis concluded acceptable margin was available. Both trains of ABGTS would have remained operable and capable of performing its design function(s) at all times. The engineering analysis results are captured in the licensee's corrective action program. Based on the new analysis, the condition reported in EN #49690 did not result in an unanalyzed condition that significantly degraded plant safety. This event report is being retracted. "The NRC Resident Inspector has been briefed on the analysis results and informed of this retraction." Notified R2DO (McCoy). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2014-01-03
49689 | 0 | WAUPACA FOUNDRY |  |  |  |  | 2014-01-02 15:30 | 2014-01-02 20:41 | 2014-01-02 | FIXED SOURCE SHIELDING FAILURE "This letter is a follow up to our phone conversation dated January 2, 2014, with a contact time of 2041 EST which involved damage to one of our fixed nuclear sources (Model TN5200 s/n B3493). This report is being filed in compliance to 10 CFR 30.50(b)(2)(ii). "On January 2, 2014, on or about 1535 pm CST it was noted that the shell of our #2 cupola had overheated during startup of the equipment. Previously at 1130 CST, the shell temperature was noted at 145 degrees F. At the time of the event, the shell temperature was noted at 990 degrees F. The person taking the temperatures was using a hand held laser temperature device and took the temperature remote to the shell. The person taking the temperatures immediately contacted a Radiation Safety Officer (RSO). The RSO then conducted a visual inspection of the gauge and noted a puddle in front of the gauge. All personnel were evacuated from the vicinity of the cupola shell. An additional RSO was contacted at 1602 CST via phone. He then proceeded to conduct an evaluation of the area at approximately 1630 CST. "The nuclear source noted above is used to measure scrap metal level in the cupola and is located directly against the cupola shell, down in an enclosed moat. This in turn resulted in the high ambient temperatures causing the lead shielding of the nuclear source to melt out the front of the gauge. The amount of lead melted out is estimated to be the equivalent of shot glass. "The manufacturer of the gauge was contacted at 1732 CST and informed of the event. The RSO will contact the manufacturer again tomorrow during normal business hours to arrange for the removal and replacement of the gauge. "The gauge is a Thermal Fisher Model TN5200, serial number B3493 containing Cs-137 with an activity of 100 mCi. "The evaluation of the gauge was compared to survey readings previously taken on September 14, 2013 by the RSO in conjunction with the required six month inventory requirements. Survey readings conducted this evening were done using a Ludlum Model 3 calibrated on December 20, 2013. "There were no over exposures during this event due to the remote reading of the temperature and the quick evacuation of the area. Follow up surveys did note an area by the receiver of the damaged gauge (approximately 21 feet away) to be 0.4 mR which is higher than the previous reading in September of 0.1 mR. Crews were instructed to not enter the moat nor attempt to repair the receiver due to the inability to lock out the shutter at this time. "All other areas noted in the vicinity of the gauge as well as above and below the gauge were the same as or below the September readings. "The cause of the event as to the shell overheating will be further investigated tomorrow, January 3, 2014. The results of the investigation will be included in a letter within 30 days to [U.S.NRC] Region Ill." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-01-10
49688 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2013-11-03 03:23 | 2014-01-02 12:14 | 2014-01-02 | 60-DAY REPORT INVOLVING AN INVALID PARTIAL ACTUATION OF UNIT 1 EDG "1A" DUE TO A FAILED RELAY "This report is being made under 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of Emergency Diesel Generator (EDG) 1A in lieu of a 60-day LER. Per NUREG-1022, the following information is provided: "The specific train and system that were actuated: "At 0323 hours [EST] on November 3, 2013, the St. Lucie Unit 1 train 'A' EDG automatically started. Troubleshooting revealed that the ESF-A group 7 actuation relay (K507A) failed, providing an invalid Engineered Safety Feature (ESF) 'start' signal to EDG 1A, and the EDG started and operated in the standby mode. The failed relay was replaced, and the post maintenance test was successful. "Was train actuation complete or partial? "This was a partial actuation of the 'A' train emergency power system as the 1A EDG output breaker did not close, by design, with power on the emergency busses. "Did the system start and function correctly? "The failed 7A actuation relay provided an invalid start signal to EDG 1A that properly responded to the start signal. The EDG output breaker closing logic prevented closure because the 4160 VAC emergency bus was energized at the time the actuation relay failed. The system started and functioned as would be expected for the existing plant conditions." The licensee informed the NRC Resident Inspector. Notified R2DO (Haag). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-01-02
49687 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-01-01 11:00 | 2014-01-01 15:21 | 2014-01-02 | TSC VENTILATION SYSTEM NON-FUNCTIONAL "At 11:00 EST on Wednesday, January 1, 2014, during a scheduled functional test of the Cook Nuclear Plant (CNP) Technical Support Center (TSC) ventilation system, the following two dampers failed to properly open when the system was placed in emergency mode (ventilation flow directed through the emergency filtration unit): 12-HV-TSC-SD-5, TSC Ventilation Emergency Flow To & From Air Conditioner 12-HV-TSC-AC-1 Volume Damper 12-HV-TSC-SD-7, TSC Ventilation Emergency Filtration Unit 12-HV-TSC-FIL Inlet Volume Damper "The TSC ventilation system is therefore non-functional. This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to an emergency response facility being non-functional. Repair activities are in progress for repair of the two dampers. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM DAN KURTH TO CHARLES TEAL AT 0220 EST ON 1/2/14 * * * After repairs were completed, the TSC was restored to service at 0130 EST on 1/2/14. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-01-01
49686 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-12-27 | 2013-12-31 16:35 | 2013-12-31 | AGREEMENT STATE REPORT - NUCLEAR MEDICINE ADMINISTERED TO WRONG PATIENT The following Agreement State Report was received via facsimile: "Notifications: York Hospital [a PA DEP licensee] left a voice message on Friday, December 27, 2013 after business hours; the voice message was reviewed by the South Central Regional Office on Monday, December 30, 2013. This is an immediate reporting event under 35.3045(a)(2)(iii). "Event Description: On Friday, December 27, 2013 a nuclear medicine technologist at York Hospital injected the wrong patient with 500 microcuries (microCi) of indium-111 (ln-111) Oxine leukocyte (ln-111 Oxine WBC or ln-111 WBC). This was to be part of a radiolabeling leukocyte component procedure for another patient that was in an adjacent room. The nuclear medicine technologist noticed swelling at the injection site and notified a nurse. Physicians and patient were informed of the incident on December 27th. Additional information regarding the dimensions of the tissue volume affected by the extravasation has become available from non-nuclear imaging performed subsequent to the ln-111 WBC injection. The shallow dose to the skin was estimated to be approximately 210 rad (2.1 Gy). "In addition, a request has been made for approval to conduct follow-up whole body imaging of the residual ln-111 in the patient's body, towards providing additional information utilizable in refining further the shallow and whole body dose estimate. "CAUSE OF THE EVENT: Human error. The nuclear medicine technologist did not check the patient's wrist-band, nor did they correlate the name and birth date provided verbally from the wrong patient, as to being not the appropriate patient for the ln-111 WBC injection. "ACTIONS: A reactive inspection by the PA DEP South Central Region took place on Monday, December 30th. The nuclear medicine technologist was immediately placed on administration leave by the licensee. Further investigations by PA DEP and the licensee are underway." PA Event Report ID No: PA130030 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-01-08
49685 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-12-31 09:33 | 2013-12-31 14:51 | 2014-01-03 | UNANALYZED CONDITION DUE TO REMOVAL OF MULTIPLE STEAM GENERATOR LATERAL SUPPORT SHIMS AND BUMPERS "Prairie Island Unit 2 is currently in Mode 3 with RCS [Reactor Coolant System] at Tave 547 degrees and 2235 psig and preparing for reactor startup following steam generator replacement outage 2R28. "At 0933 December 31, 2013 it was discovered that multiple upper lateral support shims and bumpers were removed from both 21 and 22 steam generators. This resulted in both loops being declared inoperable and entry into Tech. Spec. [Technical Specification] LCO [Limiting Condition of Operation] 3.4.5 Condition D. It also placed the Unit 2 Reactor Coolant System in an unanalyzed condition for Seismic and LOCA analyses and required this 8 hour report under 10 CFR 50.72(b)(3)(ii)(B). "During this condition both reactor coolant loops were in operation, adequately removing decay heat and keeping Prairie Island in a safe condition. "Tech Spec [LCO] 3.4.5 Condition D requires 3 immediate actions: 1. Place the rod control system in a condition incapable of rod withdrawal; action is completed. 2. Suspend operations that would cause introduction into the RCS, coolant with boron concentration less than required to meet shutdown margin; action is completed. 3. Initiate action to restore one RCS loop to operable status and operation; action was immediately initiated. "Actions have been initiated to reinstall all shims and bumpers in both steam generators. Once these actions are completed and verified the unanalyzed condition will be corrected and Technical Specification [LCO] 3.4.5 Condition D will be exited. These actions are expected to be completed by 1600 on December 31, 2013." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1653 EST ON 1/3/2014 FROM TERRY BACON TO MARK ABRAMOVITZ * * * "Technical Specification 3.4.5 Condition D was exited on December 31, 2013 at 1728 [CST], when 21 and 22 Steam Generator Upper Lateral Supports were restored to the proper configuration to meet seismic acceptance criteria. Additionally, based on further analysis, it was determined that with both Reactor Coolant Loops inoperable that this condition is a loss of safety function and reportable under 50.72(b)(3)(v)(B). "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Kunowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2013-12-31
49684 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-31 11:12 | 2013-12-31 12:09 | 2013-12-31 | STACK RADIATION MONITOR NON-FUNCTIONAL FOR PRE-PLANNED MAINTENANCE The Millstone Station Stack Radiation Monitor, RM-8169, was removed from service at 1112 EST for pre-planned maintenance. The expected return to service time is 1400 EST. The licensee informed the Connecticut Department of Environmental Protection, Waterford Dispatch and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-31
49683 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-12-27 | 2013-12-31 10:37 | 2013-12-31 | AGREEMENT STATE REPORT- IRRADIATOR MALFUNCTION The following information was received by facsimile: "The Radiation Safety Officer reported a source rack travel event that occurred the evening of December 27, 2013. After an irradiation run, the 3 source racks in a panoramic irradiator were lowered into the pool; source rack 3 was completely lowered but source racks 2 and 1 only lowered 8 and 6 feet, respectively, below the water line causing a travel fault. MDS Nordion was immediately notified and provided guidance to Steris Isomedix staff. The highest exposure rate at the surface of the pool was 18 mR/hr. After investigation, it was determined that the pool water skimmer basket dislodged and became stuck behind source rack 1; source rack 1 pushed into source rack 2 which pushed into source rack 3. The basket was freed from the source rack using remote manipulation tools around [0100] on December 28. The highest worker exposure (from a pocket dosimeter) was less than 1 mrem. A full written report of this event including corrective actions will be submitted to the Department [New York State Department of Health]." ú New York Event: NY-13-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2014-01-08
49682 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-12-31 10:50 | 2013-12-31 10:50 | 2013-12-31 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 1050 EST on Tuesday, December 31, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accidents conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 1600 EST on December 31, 2013. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE ON 12/31/13 AT 1731 EST FROM BUD HINCKLEY TO DONG PARK * * * The TSC ventilation system maintenance and testing was completed satisfactorily and the system was restored to service at 1730 EST on 12/31/13. The licensee will notify the NRC Resident Inspector. Notified R3DO (Kunowski) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-31
49681 | 0 | UNIVERSAL WELL SERVICES |  |  |  |  | 2013-12-30 13:30 | 2013-12-31 10:35 | 2013-12-31 | DAMAGED GAUGE SHUTTER HANDLE The licensee reported a shutter handle was bent during fracking field operations that are located in Marion County, West Virginia. The shutter is stuck closed in a safe operations position in a fixed location and presents no danger to personnel. The malfunctioning device is a Berthold Model LB8010; Shield serial number (#10102); Source serial number (0561/10); Source of 10 milliCuries of Cesium-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2014-01-08
49680 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-12-27 | 2013-12-30 12:04 | 2014-02-06 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The following information was received via email from Arkansas Department of Health: "The licensee notified the [Arkansas] Department [of Health] on December 27, 2013 via email that a Ronan source holder model SA1-F37 shutter failed. The source holder serial number is M4785, and the source contains 100 mCi of Cesium-137. The problem was discovered during shutter checks. [According to the licensee], it appears the shutter handle is spinning on the shaft that rotates [to] open [and] close the shutter. [This] may be a result of a sheared pin that connects the handle to the shaft. Per the RSO, the gauge is still in use, and there have been no exposures to employees or members of the public. The RSO has notified applicable facility personnel. "The licensee indicated the manufacturer was contacted on December 27, 2013 and repairs should be performed the week of January 6th-13th. "The State of Arkansas is awaiting a written report after repairs. The State's event number is ARK-2013-013." * * * UPDATE AT 0844 EST ON 02/06/14 FROM TAMMY KRIESEL TO S. SANDIN VIA EMAIL * * * "The following updates and closes Event Number 49680. "The manufacturer, Ronan Engineering Company, sent a report to the Arkansas Department of Health dated January 9, 2014 and received on February 5, 2014 indicating repair was completed. The root cause was a top rubber seal had 'dry rotted and allowed contaminates to seep into the shutter cavity. Over time, contaminates built up to a point of binding up the shutter.' The damaged seal was replaced and the source holder was reassembled. On January 16, 2014 a routine inspection was conducted at the facility. At the time of inspection, the gauge was functioning properly. "The Department [Arkansas Department of Health] considers this event closed." Notified R4DO (Azua) and FSME Events Resource (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2014-01-07
49679 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-12-30 04:25 | 2013-12-30 06:18 | 2014-01-15 | AGREEMENT STATE REPORT - ATTEMPTED THEFT OF LICENSED NUCLEAR MATERIAL The following information was provided by the State of Texas via email: "On December 30, 2013, the Agency [Texas Department of Health] was notified by the licensee's Radiation Safety Officer (RSO) they had received a call from their security company stating the alarm at their facility had activated. The security company also called local law enforcement (LLE) who had responded. The RSO stated when they arrived at the location, they found a hole had been cut in the side of the metal building where the storage area for their exposure devices is located. The lock on the outer storage vault had been cut, but the lock on the inner vault was still intact. The RSO stated it appeared no radioactive material was removed from the facility. The RSO stated the building lights, which are always on, were off when he arrived. The RSO stated LLE is sending a team to take finger prints in the area. The RSO stated the hoods off of six of their trucks had been removed and are missing. The RSO stated he was waiting for LLE to complete their work before he opens the storage vault. The RSO stated he will update this Agency as soon as they complete their inspection of the facility. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9144 * * * UPDATE AT 0716 EST ON 12/30/13 FROM ART TUCKER TO S. SANDIN * * * The following update was received via email: "On December 30,2013, at 0552 hours, the licensee's Radiation Safety Officer (RSO) contacted the Agency and stated they had accounted for all of their sources, none were missing. The RSO stated Local Law Enforcement (LLE) had completed processing the scene. The RSO stated one of their trucks had been stolen. The truck has a tracking device on it and they had located the truck using the device. The RSO stated the truck was located about five mile from the licensee's address. Local Law enforcement is investigating. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Whitten), FSME (McIntosh), FSME Events Resource (email) and ILTAB (email). NOTE: This report is provided per the Increased Control Orders. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 1 | 2014-01-13
49678 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-29 07:44 | 2013-12-29 15:25 | 2014-02-27 | SWITCHGEAR ROOM DOOR DISCOVERED UNLATCHED "A condition was discovered on December 29, 2013 that could have prevented the fulfillment of safety functions to shutdown the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. "On December 29, 2013, a water tight door between the East Switchgear and Service Building was discovered not dogged (unlatched). Upon discovery, the safety function was immediately restored by properly dogging (latching) the subject door. "The subject door between the East Switchgear and Service Building protects both trains' of safety related switchgears. The access Key Log indicates the door was in the condition for approximately 60 minutes. If the door is inoperable, then T.S. 3.0.3 applies. "This condition is being reported pursuant to 10CFR50.72(b)(3)(v)(A) and 10CFR50.72(b)(3))(v)(D). "The NRC Resident lnspector has been notified [by the licensee]." The licensee has notified state and local authorities. The door is required to be properly secured to protect the East Switchgear from a potential High Energy Line Break and was left improperly dogged by a security officer while making rounds. Millstone Unit 3 did not enter T.S.3.0.3 and continues to operate at 100%. * * * RETRACTION FROM GARY CLOSIUS TO JOHN SHOEMAKER AT 1402 EST ON 2/27/14 * * * "Upon further review the fact that the switchgear room door was closed but not latched did not render the switchgear within the room inoperable, and therefore, there was no loss of safety function. The engineering evaluation determined the switchgear would have been protected for high energy line break, flooding, and tornado pressure drop events. Additionally, the carbon dioxide fire suppression capability would have also been maintained. The details of the engineering review will be provided to the NRC Senior Resident Inspector. " Notified R1DO (DeFrancisco). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-12-29
49677 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2013-12-26 13:01 | 2013-12-26 16:29 | 2013-12-26 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO BLOWN FUSE "On December 26, 2013 at 1301 EST, Nine Mile Point Unit 1 (NMP1) commenced a reactor shutdown in accordance with Technical Specification (TS) 3.2.7.c as a result of Main Steam Isolation Valve (MSIV) 111 being declared inoperable due to a surveillance test failure when power was lost to the control circuit. The cause of the power loss was a blown fuse due to a short in the test circuitry. TS 3.2.7.c requires that a normal orderly shutdown be initiated within one hour and have the reactor in cold shutdown condition within ten hours. The blown fuse was replaced, test circuit isolated, power to the control circuit restored and MSIV 111 was declared operable at 1549 EST. Power ascension is in progress." Post maintenance operability test have been completed and the surveillance will be completed at a later time. The licensee has notified the NRC Resident Inspector and the State of New York. | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-12-26
49676 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-12-13 | 2013-12-26 14:35 | 2013-12-26 | AGREEMENT STATE REPORT - PACKAGE DELIVERED TO INCORRECT ADDRESS The following report was received via e-mail: "This morning we [Oklahoma Department of Environmental Quality] were informed that a package containing a Siemens 20 mCi Ge-68 sealed source used for attenuation correction in a PET scanner was delivered to the wrong address by [a carrier] on Dec. 13. The package was signed for, but the person who signed is not an employee of the licensee: Tahlequah City Hospital (OK-15626-01). It is not presently known who the package was delivered to, but whoever it was realized that it was not intended for them and took it to the hospital where they left it on the loading dock without informing the hospital staff. The package remained on the loading dock until late afternoon on the 13th when it was noticed by shipping and receiving personnel who took it inside with the other deliveries. They did not notice the radiation labels on the package and did not inform radiology of its arrival. Instead it was placed in an unrestricted area until Dec. 20 when Siemens contacted the Nuclear Medicine staff to schedule a time to install the new source. The staff then searched Shipping/Receiving and found the package. The package was intact and had not been opened." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2014-01-03
49675 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-12-06 | 2013-12-24 14:48 | 2013-12-24 | AGREEMENT STATE REPORT - LICENSED MATERIAL RECOVERED AT A LANDFILL NOTIFICATIONS: "On December 6, 2013 the PA Department of Environmental Protection (PA DEP) was notified of a radiation alarm at Modern Landfill in York, PA. A health physics consultant for the landfill had responded and determined that two bare molybdenum-99 (Mo-99) generator cores were the cause of the alarm. The Mo-99 generators had their labels intact and noted an activity of 18 curies (Ci) on 10/29/2013 and 11/06/2013. Expiration dates were 11/12/2013 and 11/19/2013 respectively. Per 10 CFR 20.2201, decay correcting the activity would prompt a 30-day report per 10 CFR 22.2201(a)(ii); however, after further investigation and discussion with the licensee, a conservative (immediate) report per 10CFR 20.2201(a)(i) may be required. EVENT DESCRIPTION: "The December 6th initial notification to the PA DEP/BRP was due to a load of solid waste possibly containing Mo-99, versus Tc-99m which is often found to set off landfill radiation alarms. Upon off-loading the waste and discovery of two bare Mo-99 generator cores and investigation the following week, the serial number on each of the Mo-99 generator labels revealed they were from a Pennsylvania nuclear pharmacy licensee, Cardinal Health (C. H.), PA-0385. A reactive inspection was initiated. The RSO for C.H. concluded that the generators may have been stolen after their expiration date, and thus would involve a decayed activity of 510 mCi. This is greater than 1,000 times the quantity specified in 10 CFR 20 Appendix C for Mo-99 (that is, greater than 100 mCi). PA DEP/BRP is expecting the licensee to assess the range of whole body and extremity doses to the individual(s) that disassembled these Mo-99 generators using conservative bounding assumptions. No one has admitted to the removal of the Mo-99 from the C.H. facility. CAUSE OF THE EVENT: "Possible theft as a crime of opportunity for scrap lead shielding. ACTIONS: "A reactive inspection by the PA DEP Regional Office has already occurred and further evaluation of the potential individual radiation exposure and needed corrective actions are ongoing." PA Event Report ID No: PA130029 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-01-01
49674 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-23 15:00 | 2013-12-23 16:32 | 2013-12-23 | HISTORICAL GAPS IN HIGH ENERGY LINE BREAK BARRIER "At 1930 EST on June 7, 2012, it was determined that a series of gaps in a high energy line break (HELB) barrier rendered equipment in the west 480 VAC switchgear room inoperable. There is evidence that this condition had existed since initial construction. The openings were sealed and the equipment restored to operable status at 1605 EST on June 8, 2012. This condition was previously reported to the NRC pursuant to 10 CFR 50.73(a)(2)(i)(B) in LER 2012-001-00. Upon further engineering analysis, it was determined that for limited exposure times safety functions could have been prevented for certain postulated high energy line breaks. Therefore, this condition is also being reported pursuant to 10 CFR 50.73(a)(2)(v)(A),(D), and 10 CFR 50.72(b)(3)(v). The NRC Senior Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-12-23
49673 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-12-23 08:28 | 2013-12-23 13:11 | 2013-12-23 | LOSS OF COMMUNICATIONS WITH VIRGINIA STATE EOC DUE TO POWER OUTAGE "At 0828 EST on 12/23/2013, the Surry Power Station control room was notified that the Virginia State Emergency Operations Center (EOC) had lost all power and all offsite communications. This included commercial phone lines, automatic ring downs, and the State ringdown loop (lnsta-phone). At 0900 EST, all communications were restored once emergency generators were placed in service at Virginia State EOC. The Virginia State EOC initially lost offsite power and all communications were supplied by an Uninterruptable Power Supply (UPS). Subsequently, the UPS batteries depleted and all communications were lost. At that time, (0828 EST) the Virginia State EOC personnel notified the Surry control room and supplied individual cellular phone numbers as an alternative method of contacting the Virginia State EOC. "This event is reportable in accordance with 10CFR50.72(b)(3)(xiii), any event that results in a major loss of offsite communications capability, (e.g., Emergency Notification System)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-23
49672 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-12-23 08:23 | 2013-12-23 13:00 | 2013-12-23 | LOSS OF COMMUNICATIONS WITH VIRGINIA STATE EOC DUE TO POWER OUTAGE "At 0828 EST on 12/23/2013, the North Anna control room was notified that the Virginia State Emergency Operations Center (EOC) had lost all power and all offsite communications. This included commercial phone lines, automatic ring downs, and the State ring down loop (lnsta-phone). At 0900 EST, all communications were restored once emergency generators were placed in service at Virginia State EOC. The Virginia State EOC initially lost offsite power only but all communications were supplied power by an Uninterruptable Power Supply (UPS). Subsequently, the UPS batteries depleted and all communications were lost. At that time (0828 EST) Virginia State EOC personnel notified the North Anna control room and supplied individual cellular phone numbers as an alternative method of contacting the Virginia State EOC. "This report is reportable in accordance with 10CFR50.72(b)(3)(xiii), any event that results in a major loss of offsite communications capability, (e.g. Emergency Notification System)." The licensee has notified the NRC Resident Inspector and Louisa County. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-23
49671 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-12-20 13:03 | 2013-12-20 20:10 | 2013-12-20 | BOTH CONTROL ROOM AIR CONDITIONING SUBSYSTEMS INOPERABLE "While the B control room chiller was out of service for planned maintenance, the A control room chiller was manually secured due to excessive fluctuations in load and running current. TS 3.7.2.2 Action a.2 was entered at 1303 [EST] for both control room air conditioning subsystems inoperable. Control room temperature is being maintained below the TS limit of 90 degrees F. "The required TS Action is to restore one control room AC subsystem to operable status within 72 hours." The licensee will notify the NRC Resident Inspector and the Lower Alloways Creek township. * * * UPDATE ON 12/20/13 AT 2234 EST FROM JOHN PANAGOTOPULOS TO DONG PARK * * * The B control room chiller was returned to service at 2120 EST. The A control room chiller remains out of service resulting in a 30-day TS LCO. Notified R1DO (Dimitriadis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-12-20
49670 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-11-25 | 2013-12-20 14:57 | 2013-12-20 | AGREEMENT STATE REPORT - SOURCE HOLDER GRIPPER MALFUNCTION The following information was submitted by the Commonwealth of Virginia via email: "On November 25th, the Virginia Department of Health Radiological Duty Officer received a call from the General Electric (GE) service provider representative that a PET/CT machine at Rockingham Memorial failed. The representative responded and found that the source holder was open exposing the source. The representative troubleshot the holder and found that the gripper was not functioning properly. The source was removed and the coach was sent back to Wisconsin for service at GE's facility. "The Virginia Radioactive Materials Program has been working with GE regarding the cause for the failure. At this time, GE is reviewing service reports to evaluate whether this is an isolated incident. "The unit was repaired and returned to Rockingham Memorial." Virginia Event Report ID: VA-13-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-12-30
49669 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-10-09 | 2013-12-20 14:57 | 2013-12-20 | AGREEMENT STATE REPORT - BROKEN SOURCE HOLDER CABLE The following information was submitted by the Commonwealth of Virginia via email: "On October 9th, the PET/CT unit reported a problem with the pin source holder indicating the holder was open. The licensee closed the scan room door and contacted General Electric (GE) service provider to provide emergency service. On October 10th, a GE representative investigated the unit and found the source holder cable was broken. A new cable was ordered and replaced on October 11th. The source was replaced, and the unit was tested and placed back in service. The Virginia Radioactive Materials Program has been working with GE regarding the cause for the failure. At this time, GE is reviewing service reports to evaluate whether this is an isolated incident." Virginia Event Report ID: VA-13-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-12-30
49668 | 0 | CONAGRA FOODS |  |  |  |  | 2013-12-18 16:00 | 2013-12-20 15:00 | 2013-12-20 | LOST FILL LEVEL MONITORS ConAgra Foods, Inc. reported that while performing a physical walkdown verification to meet reporting requirements for 2013, three Peco Controls Corporation model Gamma 101P fill level monitors could not be located. After further checking, one of the unaccounted for monitors was found to be in the possession of a vendor where it had been sent in exchange for a replacement. However, two of the monitors remain unaccounted for at this time. Details on the two monitors are as follows: Peco Controls Corporation, Model - Gamma 101P, Serial Number - G001768549, with a 100 mCi Am-241 source. Peco Controls Corporation, Model - Gamma 101P, Serial Number - G002318648, with a 100 mCi Am-241 source. ConAgra states that these monitors had not been in service for several years. The report issued for 2012, which was dated 12/20/2012, indicated that all monitors were accounted for at that time. ConAgra is continuing to search for the two unaccounted for monitors. The licensee notified R3(Pelke). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-12-30
49667 | 0 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2013-10-22 | 2013-12-20 11:45 | 2014-07-18 | PART 21 REPORT - CRACKING IN KCR-13 STANDBY BATTERY JARS The following was received via facsimile: "The purpose of this letter is to provide the NRC a report in general conformity to the requirements of 10CFR Part 21.21 (a)(2). On October 22, 2013, C&D Technologies, Inc. (C&D) was informed by Entergy Nuclear Northeast that a KCR-13 battery installed at the Indian Point Nuclear Energy Center had developed a small crack in the polycarbonate jar material. The jar is a safety related component with the primary function of containing electrolyte. C&D does not believe that significant quantity of electrolyte was lost through this crack, because there was a normal level of electrolyte in the battery. This unit has been replaced, and the unit was sent by Entergy to an outside lab, Lucius Pitkin (LPI) of New York, NY, for analysis. As C&D did not have access to the components of the allegedly defective battery, and a report has not yet been issued by Lucius Pitkin, C&D cannot perform a root cause technical evaluation and affirm whether there is any defect in the component or manufacturing process, or whether the reported condition may have been due to user abuse of product, improper maintenance or other negligence or error. No formal report from Entergy or LPI Is expected before the expiration of the 60 day limit from the date C&D was notified of the issue. Thus, C&D is submitting this interim report to the NRC and notifying C&D's customers that use C&D KCR-13 batteries of this interim report. [C&D is also] initiating an action plan to evaluate the reported potential defect and determine whether it could pose a substantial safety hazard for any U.S. licensee using such batteries. "Concurrent actions underway to complete the evaluation: a) On receipt of the final report by LPI/Indian Point by C&D, C&D shall evaluate the findings and the causes for failure. Maximum time 14 days from receipt of the report. b) In conjunction with the licensees identified in section vi, C&D will recommend maintenance assessment of all KCR-13 batteries at these locations to determine their status, and specifically the presence of any evidence of potential defects via visual examination. For any cells exhibiting the presence of potential defect, C&D shall further recommend that they be returned for analysis. Estimated completion date of analysis is thirty (30) days from the receipt of the returned batteries." KCR-13 batteries are used in Indian Point and Monticello Nuclear Plants. For further information contact: Robert Malley VP Quality and Process Engineering Office Phone 215-619-7830 Email bmalley@cdtechno.com * * * UPDATE AT 1110 EST ON 02/24/14 FROM CHRISTIAN RHEAULT TO S. SANDIN VIA FAX * * * The following updated information was received from C&D Technologies: "Subject: Updated Interim Report - Inability to Complete 10CFR Part 21 Evaluation regarding cracking in KCR-13 Standby Battery Jars "As previously stated, C&D did not have access to the components of the allegedly defective battery, and a report has not yet been issued by Lucius Pitkin. C&D cannot perform a root cause technical evaluation and affirm whether there is any defect in the component or manufacturing process, or whether the reported condition may have been due to user abuse of product, improper maintenance or other negligence or error until a final report Is issued by Lucius Pitkin. Although several requests to both Indian Point and Lucius Pitkin have been made, a receipt date for the analysis results is still indeterminate." If you have any questions or wish to discuss this matter or this report, please contact: Robert Malley VP Quality and Process Engineering Office Phone 215-619-7830 Email bmalley@cdtechno.com Notified R1 (DeFrancisco), R3DO (Kunowski) and Part 21 Group (via email). * * * UPDATE AT 0927 EDT ON 5/9/2014 FROM ROBERT MALLEY TO MARK ABRAMOVITZ * * * The following report was received via fax: "C&D has recently received and is evaluating the report from Lucius Pitkin and will perform a root cause technical evaluation and affirm whether there is any defect in the component or manufacturing process, or whether the reported condition may have been due to user abuse of product, improper maintenance or other negligence or error. The planned final evaluation should be completed by May 31, 2014 at which time it is anticipated that a final report will be issued." Notified the R1DO (Lilliendahl), R3DO (Riemer), and Part 21 Group (via e-mail). * * * UPDATE AT 1640 ON 7/18/2014 FROM CHRISTIAN RHEAULT TO DONALD NORWOOD * * * The following is a synopsis of information received via facsimile: The information provided in the C&D facsimile serves as C&D's final analysis of the issue. Conclusion: While the images do show indications of environment stress cracking (ESC) and fatigue, the lack of chemical evidence of the actual agent makes it difficult to determine the source of the material. Polycarbonate (the container material) has known stress cracking agents for example esters, aliphatic hydrocarbons, aromatic hydrocarbons, halogenated hydrocarbons, ketones, etc. and the C&D Installation and Operation Manual clearly states that the only approved material for contact with the jar and cover (other than materials used in the construction of the battery) for cleaning purposes is water and sodium bicarbonate. If one of the previously mentioned materials came into contact with the jar, it could have caused the ESC that was observed. The standing recommendation to system operators is to limit any chemical that can come into contact with the battery to only approved materials. In the event that an unapproved material contacts the battery, the unit should be cleaned and observed for any subsequent damage caused by the agent. Notified R1DO (Cahill), R3DO (Pelke), and Part 21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-12-20
49666 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-12-19 22:33 | 2013-12-20 11:23 | 2013-12-20 | VALID ACTUATION OF MAIN STEAM ISOLATION VALVES THAT WAS NOT PART OF A PREPLANNED SEQUENCE "While in Mode 3 in preparing the Unit 2 secondary plant for startup, conditions occurred where it became necessary to break vacuum on the main condenser. Procedures directed closing of the main steam isolation valves. Instead of shutting each main steam isolation valve individually, a manual main steam isolation actuation was initiated through the solid state protection system (SSPS) to close the valves. This actuation of SSPS was a valid signal. The actuation was not part of a preplanned sequence. "This notification is supported by the guidance of NUREG-1022, Revision 3, 'Event Reporting Guidelines 10CFR50.72 and 50.73.' In part, the guidance states: 'The Commission is interested in both events in which a system was needed to mitigate the consequences of an event (whether or not the equipment performed properly) and events in which a system actuated unnecessarily.' "The manual actuation was not initiated to mitigate the consequences of an actual event. However, the method of closing the main steam valves for this condition did not specifically require that the valves should be closed by initiating a main steam isolation signal and therefore, the safety system was unnecessarily actuated. "Therefore, this notification is being made pursuant to 10 CFR 50.72(b)(3)(iv)(A) as an event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) that was not part of preplanned sequence during testing or reactor operation. The system listed in paragraph (b)(3)(iv)(B) is (2) main steam isolation valves." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-12-20
49665 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-12-19 15:11 | 2013-12-19 19:18 | 2014-02-14 | LOSS OF REACTOR BUILDING VENTILATION "At 1511 [EST] on December 19, 2013, bus 10A404 (D channel 4 kv 1E vital bus) deenergized while transferring infeed breakers after degraded voltage testing. Reactor building ventilation fans tripped resulting in a loss of secondary containment negative pressure. Filtration Recirculation and Ventilation System (FRVS) was manually started and secondary containment negative pressure was restored at 1525 [EST]. "Secondary containment pressure is stable with differential pressure negative. "The technical specification requirement is to maintain secondary containment at a negative pressure for secondary containment integrity. Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The standby reactor building ventilation fans did not automatically start and [the reason for that] is being investigated." The licensee notified the NRC Resident Inspector and will notify the Lower Alloways Creek township. * * * UPDATE AT 1326 EST ON 2/14/14 FROM LINDSAY KOBERLEIN TO S. SANDIN * * * The licensee is retracting this report based on the following: "Hope Creek Generating Station Unit 1, is retracting the 8-hour non-emergency notification made on December 19, 2013, at 1918 EST (EN# 49665). "The notification on December 19, 2013, reported that secondary containment was declared inoperable when reactor building ventilation system (RBVS) fans tripped resulting in the loss of secondary containment negative pressure. "Subsequent engineering evaluation concluded that the safety function of secondary containment was not lost. The Hope Creek post-LOCA Exclusion Area Boundary, Low Population Zone, and Control Room dose calculation assumes that primary containment leakage is released directly to the environment with no credit for hold up or filtration for the first 375 seconds after the accident, i.e., the Hope Creek accident analysis does not assume that secondary containment is under vacuum at the start of an accident. In addition, the accident analysis relies upon the operation of the safety related Filtration Recirculation and Ventilation System (FRVS), which was fully operable. Upon receipt of an accident signal, FRVS would have automatically started and restored secondary containment negative pressure within the time limits of the design assumptions. The trip of the non-safety related RBVS and the failure of the stand-by RBVS fans to start did not result in an adverse impact on the dose consequence analysis. Although secondary containment was declared inoperable, the safety function was not lost and secondary containment was capable of performing its design function of minimizing any ground level release of radioactive material by providing a leak tight boundary so that FRVS may draw a vacuum In the Reactor Building and filter radioactive material at all times. The engineering evaluation is captured In the licensee's corrective action program. Based on the engineering evaluation, the condition reported in EN #49665 did not result in the loss of a safety function needed to control the release of radioactive material. This event report is being retracted. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." Notified R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-12-19
49664 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2013-12-17 | 2013-12-19 16:42 | 2013-12-19 | PART 21 - FISHER TYPE 377 TRIP VALVES NOT PROCESSED AS REQUIRED "Fisher Information Notice: FIN 2013-05 "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert Dominion Virginia Power, Omaha Public Power District and Florida Power and Light that as of 17 December 2013, Fisher Controls International LLC ('Fisher') became aware of the possibility of a situation which may affect the performance of the applicable equipment. Fisher is informing you of this circumstance in accordance with Section 21.21 (b) of 10CFR Part 21. "Applicability: This notice applies only to the subject equipment supplied by Fisher, identified in the above referenced orders. "Discussion: The Type 377 Trip Valve assembly was subjected to the processing requirements of Fisher Controls FMP2K27 (Control of Commercial Grade Items to be Dedicated for Use in Nuclear Safety-Related Applications) and was supplied as a safety related component. However, for the above referenced orders, Fisher supplied various other parts, in addition to the Type 377 Trip Valve, that were not processed as required by the requirements of 2K27; thus, such parts were supplied as commercial items. "Action Required: Each recipient needs to: (i) evaluate the situation for each application of the Type 377 Trip Valve; (ii) determine what portions of the Trip Valve system are 'essential to function'; and (iii) determine what commercial parts may be installed in the Type 377 Trip systems in their respective plants. "10CFR21 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR Part 21. "If there are any technical questions or concerns, please contact: "George Baitinger Manager, Quality Fisher Controls International LLC 205 South Center Street Marshalltown, La 50158 Fax: (641) 754-2854 Phone: (641) 754-2026 George.Baitinger@Emerson.com" North Anna, Surry, Fort Calhoun, and St. Lucie plants are affected by this Fisher Information Notice. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-12-19
49663 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-12-19 07:52 | 2013-12-19 16:21 | 2013-12-19 | TWO OF THREE EMERGENCEY DIESEL GENERATORS INOPERABLE AT THE SAME TIME "On 12/19/13 Unit 1 Emergency Diesel Generator (EDG) 1-2 was inoperable for scheduled maintenance. "During an operational walk-down of the Unit 1 EDG 1-3, the associated fuel oil priming pump discharge fitting and pump housing were inadvertently damaged. "Pacific Gas and Electric Company declared EDG 1-3 inoperable on 12/19/13 at 0752 PST. "Since both Unit 1 EDGs were inoperable at the same time, this condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-12-19
49662 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2013-12-19 13:20 | 2013-12-19 16:04 | 2013-12-19 | UNANALYZED CONDITION AFFECTING UNIT 2 EMERGENCY DIESEL GENERATORS "At 1320 ET on December 19, 2013, Florida Power and Light identified that atmospheric conditions that had sustained high winds exceeding approximately 50 miles per hour from the ENE direction could result in inadequate heat removal to support continuous operation of the Unit 2 emergency diesel generators. Upon identification of this condition, an adverse condition monitoring plan was issued requiring implementation of compensatory measures to assure adequate emergency diesel generator cooling to support continuous operation of the U2 emergency diesel generators, should weather forecasts identify conditions that would likely result in this condition. "This condition is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified of this condition." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-12-19
49661 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-12-19 08:38 | 2013-12-19 12:58 | 2013-12-20 | BOTH DIVISIONS OF PRIMARY CONTAINMENT OXYGEN AND HYDROGEN ATMOSPHERIC MONITORS INOPERABLE FOR MAINTENANCE "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0838 PST on 12/19/2013, the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was removed from service for planned maintenance activities. The Division 1 sample rack is expected to be out of service for 14 hours. The redundant Division 2 sample rack was previously removed from service for maintenance and remains out of service for repairs. Compensatory measures to monitor primary containment for hydrogen and oxygen are available via grab samples using chemistry procedures. "The NRC Resident Inspector has been notified." * * * UPDATE FROM QUOC VO TO VINCE KLCO AT 0130 EST ON 12/20/13 * * * "Following completion of surveillance activities, the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was returned to operable status at 2114 PST on 12/19/2013, restoring its required emergency assessment capability. "The NRC Resident Inspector has been notified." Notified the R4DO (Lantz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-19
49660 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-12-18 15:00 | 2013-12-18 18:56 | 2013-12-18 | SAFETY FUNCTION FOR THE HPCI SUCTION AUTOMATIC LOW CST LEVEL SWAP OVER INOPERABLE "During the performance of surveillance testing on 12/17/2013 for the HPCI CST low water level switch instrument functional test, the safety function for the low CST level suction swap-over was lost. "While performing testing, 23LS-75B setpoint was found to be below the TS required value with 23LS-74B already declared inoperable. Tech Spec 3.3.5.1 Condition D was entered and within 1 hour of finding 23LS-75B setpoint below the TS required value, this switch was adjusted to within tolerance as allowed by procedure and tested satisfactory. Both switches were inoperable concurrently for a period of less than 1 hour from time of discovery of 23LS-75B being out of tolerance. "This issue has been discussed with the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-12-18
49659 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-12-18 14:09 | 2013-12-18 18:50 | 2013-12-18 | LOSS OF UNIT 2 SECONDARY CONTAINMENT INTEGRITY "Station Personnel simultaneously opened the inner and outer air lock doors from Unit 2 Reactor Enclosure to the Refuel Floor. Reactor Enclosure Secondary Containment Integrity was declared inoperable per U2 TS 3.6.5.1.1, due to failure to meet surveillance requirement U2 TS 4.6.5.1.1.b.2, due to the report of both containment airlock doors on the 352 foot elevation being momentarily open at the same time. Reactor Enclosure D/P [differential pressure] remained steady at 0.35 inches vacuum water gauge. "Reactor Enclosure Secondary Containment Integrity was declared Operable following verification that at least one air lock door to each access of secondary containment was closed per U2 TS 4.6.5.1.1.b.2. Total LCO time was approximately 5 seconds." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-12-18
49658 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-12-18 | 2013-12-18 17:06 | 2014-05-09 | AGREEMENT STATE REPORT - MULTIPLE STUCK SHUTTERS AT A PAPER MILL PLANT The following report was received via email: "The following are the preliminary findings of the Arkansas Department of Health, Radioactive Materials Program, involving multiple stuck shutters at a paper mill plant. "An onsite inspection of this licensee was conducted on December 17, 2013. During this inspection, it was discovered that since 2008, multiple shutters were found to have been stuck open and were not able to be locked out. Based on the records reviewed at the time of inspection, it appears that there were a total of 17 gauges with stuck shutters since May 2010. It appears at this time that all but nine (9) of these gauges have been repaired, dismounted and/or disposed. Currently, these nine gauges (9) are still in use with the shutters stuck in the open position. In accordance with RH-1502.f.2. (equivalent 10 CFR 30.50(b)(2)), each stuck shutter event should have been reported to the State of Arkansas within 24 hours. The licensee failed to notify the State of Arkansas of all of these events. "The information concerning the 17 gauges is as follows: Radionuclide Manufacturer Model # Activity Cesium-137 Berthold LB 7440 50 mCi Cesium-137 Berthold LB7440 100 mCi Cesium-137 Berthold LB 7440 30 mCi Cesium-137 Berthold LB 7440 250 mCi Cobalt-60 Berthold LB 300L 0.2 mCi Cobalt-60 Berthold LB 300L 0.5 mCi Cobalt -60 Berthold LB 300L 0.19 mCi Cobalt-60 Berthold LB 300L 0.7 mCi Cobalt-60 Berthold LB 300L 4.14 mCi Cobalt-60 Berthold LB 300L 0.46 mCi Cobalt-60 Berthold LB 300L 1.8 mCi Cobalt-60 Berthold LB 300L 1.51 mCi Cesium-137 Berthold LB 330 24 mCi Cobalt-60 Berthold LB 300L 1.8 mCi Cobalt-60 Berthold LB 300L 0.46 mCi Cobalt-60 Berthold LB 300L 1.51 mCi Cobalt-60 Berthold LB 300L 0.22 mCi "The licensee is in the process of submitting additional records. Information related to the gauge serial numbers and event date will be provided in another update. The Department is continuing to investigate and will provide updates as information is received." * * * UPDATE FROM KAYLA AVERY TO HOWIE CROUCH VIA EMAIL ON 1/24/14 AT 1629 EST * * * "The Arkansas Department of Health, Radioactive Materials Program, received an incident report from Domtar A.W., LLC on January 17, 2014. All stuck shutters were discovered in May of 2010, when a new consultant was hired who properly performed the shutter checks. Since that time, there were a total of 22 stuck shutters. Some of these shutters were stuck open from seven months to two years before being replaced or repaired. The licensee has confirmed that no Domtar workers, contractors or members of the public received any radiation exposure from these gauges. The following devices had stuck shutters: Radionuclide Manufacturer Model Activity Date of Repair Cs-137 Berthold LB7440 50 mCi 12/14/10 Cs-137 Berthold LB7440 50 mCi 12/15/10 Cs-137 Berthold LB7440 50 mCi 12/14/10 Cs-137 Berthold LB7440 50 mCi 12/15/10 Cs-137 Berthold LB7440 250 mCi 08/10/11 Cs-137 Berthold LB7440 100 mCi 12/16/10 Cs-137 Berthold LB7440 30 mCi 08/09/11 Cs-137 Berthold LB7440 100 mCi 06/28/11 Cs-137 Berthold LB7440 50 mCi 06/30/11 Cs-137 Berthold LB7440 30 mCi 06/29/11 Cs-137 Berthold LB7440 100 mCi 08/11/11 Cs-137 Berthold LB7440 30 mCi Disposed on 05/24/12 Cs-137 Berthold LB7440 100 mCi 08/12/11 Co-60 Berthold LB300L 2.5 mCi total 12/17/13 for 1 shutter ** Co-60 Berthold LB300L 5.03 mCi total 12/17/13 for 2 shutters** Co-60 Berthold LB300L 2.19 mCi total 12/17/13 for 2 shutters** "** These gauges contain three (3) sources with three (3) shutters, which had been all stuck open. Currently, one of these gauges still has two (2) shutters stuck open, and two of the gauges still each have one (1) shutter stuck open. Therefore, a total of four (4) shutters are currently stuck open. The licensee has committed to the Department that these gauges will be replaced on 01/23/14, 02/20/14 and 04/17/14 during mill outages. The licensee is required to notify the Department when the replacements are complete. The Department will provide another update when this information is received." Notified R4DO (Spitzberg) and FSME Events Resource (email). * * * UPDATE AT 1612 EDT ON 05/09/14 FROM KAYLA AVERY TO S. SANDIN VIA EMAIL * * * This update provided device serial numbers and closed out this incident. Radionuclide Manufacturer Model Serial Number Activity Date of Repair Cs-137 Berthold LB7440 37624-12097 50 mCi 12/14/10 Cs-137 Berthold LB7440 37624-11867 50 mCi 12/15/10 Cs-137 Berthold LB7440 700799-2813 50 mCi 12/14/10 Cs-137 Berthold LB7440 37624-12090 50 mCi 12/15/10 Cs-137 Berthold LB7440 37624-12273 250 mCi 08/10/11 Cs-137 Berthold LB7440 37624-12098 100 mCi 12/16/10 Cs-137 Berthold LB7440 37624-12271 30 mCi 08/09/11 Cs-137 Berthold LB7440 37624-12281 100 mCi 06/28/11 Cs-137 Berthold LB7440 *** 50 mCi 06/30/11 Cs-137 Berthold LB7440 37624-12279 30 mCi 06/29/11 Cs-137 Berthold LB7440 37624-12278 100 mCi 08/11/11 Cs-137 Berthold LB7440 *** 30 mCi Disposed on 05/24/12 Cs-137 Berthold LB7440 37624-12272 100 mCi 08/12/11 Co-60 Berthold LB300L 7687 2.5 mCi total 12/17/13 for 1 shutter ** Co-60 Berthold LB300L 8654 5.03 mCi total 12/17/13 for 2 shutters** Co-60 Berthold LB300L 9507 2.19 mCi total 12/17/13 for 2 shutters** "** These gauges contain three (3) sources with three (3) shutters, which had been all stuck open. Currently, one of these gauges still has two (2) shutters stuck open, and two of the gauges still each have one (1) shutter stuck open. Therefore, a total of four (4) shutters are currently stuck open. The licensee has committed to the Department that these gauges will be replaced on 01/23/14, 02/20/14 and 04/17/14 during mill outages. The licensee is required to notify the Department when the replacements are complete. The Department will provide another update when this information is received." Notified R4DO (Whitten) and FSME_Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2013-12-26
49657 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-12-18 08:30 | 2013-12-18 15:39 | 2013-12-18 | BOTH DOORS IN SECONDARY CONTAINMENT AIRLOCK OPENED CONCURRENTLY "At 0830 CST on December 18, 2013, both doors in the Secondary Containment Airlock were opened concurrently. The doors being open at the same time caused a failure to meet SR 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.4.1. Upon discovery, immediate action was taken to close the doors. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to an operable status. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-12-18
49656 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2013-12-16 | 2013-12-18 14:09 | 2013-12-18 | AGREEMENT STATE REPORT - LOST VIAL OF THALLIUM-201 "The Radiation Safety Officer at GE Healthcare (Mediphysics) [IL-01109-01] Arlington Heights, IL called the Agency [IL Emergency Management Agency] on December 18, 2013 to report an incident concerning an over pack shipment intended for their pharmacy in Atlanta, Georgia. On Sunday December 15, a package containing 12 shielded vials of TL-201, 31 milliCi each, was transferred to Delta Airlines Freight services at Chicago's O'Hare international airport for shipping to Atlanta. The package arrived at Atlanta's Hartsfield International Airport the next day and was unloaded. However during the trip from the air plane cargo hold to the freight hub, the package tumbled off the conveyance and was broken open. This occurred on Sunday night, December 16. That night and the next morning a 3rd party contractor hired by the airlines/airport collected the vials and its packaging and placed the material into an over pack and secured the drum until it could be claimed by GE Healthcare. Based on the description and measurements performed by the company which were provided to GE Healthcare, it appeared none of the glass vials within their shielded containers were broken. As such it was determined that the vials were to be repackaged and forwarded to the pharmacy for evaluation. When repackaging at the freight hub was attempted by the GE Atlanta pharmacist on Tuesday, December 17, it was confirmed that no contamination was present on the packaging or the interior containers, however, it became clear that only 11 of the 12 vials were present in the salvage drum, contrary to the contractor's initial assertions. GE Healthcare contacted the Georgia agreement state program regarding the matter. The contractor is conducting additional visual and radiological surveys of the tarmac and freight hub. As of today (12/18/13), calculations show that a single vial contains approximately 16 milliCi of TL-201. If intact and still shielded as the other vials which were found, GE Healthcare estimates that the vial would have a dose rate of approximately 350 microR/hr at one foot. "A report on the matter from GE Healthcare is anticipated. They have indicated that they would keep us appraised of developments as this matter moves forward. The Agency has been in touch with a representative of the Georgia program regarding potential additional actions to recover the vial. Given the 72 hour half life of the material, there will be no TL-201 present within the next 30 days. Also given that no contamination was detected on the packaging and the other 11 containers of Tl-201 were found intact, there is reason to assume the missing container was still intact at the time of the accident and the search is being conducted accordingly." Illinois Event Number: IL13036 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2013-12-26
49655 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-12-18 | 2013-12-18 15:31 | 2013-12-18 | AGREEMENT STATE REPORT - LOST MATERIAL SHIPMENT An outgoing shipment of a Strontium (Sr-82, 23.6 mCi; Sr-85, 54 mCi) Generator, from the University of California Davis to Los Alamos, NM, cannot be located by the shipping company. Shipment tracking shows the items last seen in Memphis, TN. It is suspected the shipment is only temporarily misplaced due to holiday shipping traffic and the shipping company is continuing attempts to locate the shipment. California Report #121713. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-12-26
49654 | 0 | U. S. ARMY |  |  |  |  | 2013-12-13 09:30 | 2013-12-18 13:50 | 2013-12-18 | STOLEN CHEMICAL AGENT MONITORS The US Army in Warren, Michigan, reported that 3 improved chemical agent monitors were stolen from a storage facility at Fort Bragg, NC. Each of the 3 detectors contained a sealed 15 mCi Ni-63 source. The detectors were stored in building N-5342 and the locks on the building, storage area, and storage locker were damaged. The Fort Bragg Criminal Investigation Unit is conducting an investigation. The US Army has also notified NRC Region 3. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-12-26
49653 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-07-26 23:35 | 2013-12-18 13:12 | 2013-12-18 | PAST SUSPENSION OF SECURITY MEASURES Security measures temporarily suspended. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-12-18
49652 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2013-12-18 13:00 | 2013-12-18 13:01 | 2013-12-19 | TECHNICAL SUPPORT CENTER INOPERABLE FOR PLANNED MAINTENANCE "NRC Operations Center notification for planned routine preventative maintenance on the Technical Support Center HVAC. Expected start of the preventative maintenance is 12/18/13 at 1300 EST. Planned completion is 12/19/13 at 0100 EST. This maintenance renders the TSC non-functional. The planned TSC alternate location will be the Control Room." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 12/19/13 AT 1621 EST FROM NICHOLAS DESANTIS TO DONG PARK * * * At 1405 EDT, maintenance was completed, and the TSC was declared functional. The licensee will notify the NRC Resident Inspector. Notified R2DO (Freeman). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-18
49651 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-12-18 09:39 | 2013-12-18 12:22 | 2013-12-18 | LOSS OF UNIT 1 SECONDARY CONTAINMENT INTEGRITY "Station Personnel simultaneously opened the inner and outer air lock doors from Unit 1 Reactor Enclosure to the Radwaste Enclosure. Reactor Enclosure Secondary Containment Integrity was declared inoperable per U1 TS 3.6.5.1.1, due to failure to meet surveillance requirement U1 TS 4.6.5.1.1.b.2, due to the report of both containment airlock doors on 217 [foot elevation, being] momentarily open at the same time. Reactor Enclosure D/P [delta pressure] remained steady at 0.35 inches vacuum water gauge. "Reactor Enclosure Secondary Containment Integrity was declared Operable following verification that at least one air lock door to each access of secondary containment was closed per U1 TS 4.6.5.1.1.b.2. Total LCO time was approximately 5 seconds." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-12-18
49650 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-12-18 09:32 | 2013-12-18 12:21 | 2013-12-18 | OFFSITE NOTIFICATION DUE TO CONTRACT EMPLOYEE COLLAPSING WITHIN THE PROTECTED AREA "On December 18, 2013, at approximately 0700 EST, with Watts Bar Nuclear Unit 1 at 100% power and Unit 2 under construction, a contract employee on his way to his job site collapsed. The emergency team responded and the individual was transported via ambulance offsite. The individual was declared deceased at Rhea County Medical Center. The individual was not contaminated. Due to a required report to OSHA at 0932 EST, this report is submitted pursuant to 10 CFR 50.72(b)(2)(xi), as a notification of other government agency. "NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-12-18
49649 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2013-11-21 | 2013-12-18 12:22 | 2013-12-18 | AGREEMENT STATE REPORT - HDR BRACHYTHERAPY SOURCE PLACED INCORRECTLY "Description of incident: HDR brachytherapy treatment of the bronchial, tracheal area. The source was placed incorrectly, resulting in underdose to intended treatment area. "An additional treatment fraction will be prescribed to compensate for underdose to intended treatment area. Underdose was discovered on 1st of 3 fractions, prior to delivery of 2nd fractions. "Sequelea: No adverse effects expected as a result of medical event, since the patient is terminally ill. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-12-26
49648 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-12-17 19:57 | 2013-12-18 03:41 | 2013-12-18 | REACTOR PROTECTION SYSTEM (RPS) ACTUATION WITH THE REACTOR IN HOT SHUTDOWN "Pursuant to 10CFR50.72(b)(3)(iv)(A), notifications are being performed for a valid actuation of the reactor protection system resulting in a full scram. The actuation was a result of the reactor mode switch being placed from the refuel position to the shutdown position without the scram bypass jumpers installed. The reactor was subcritical with all rods inserted at the time of the actuation. All systems functioned as designed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-12-18
49647 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-12-17 13:32 | 2013-12-17 22:13 | 2013-12-17 | LOSS OF CONTAINMENT ISOLATION CAPABILITY DUE TO SURVEILLANCE PROCEDURE ERROR "During performance of 06-IC-1E31-Q-1016-02 RCIC Steam Supply Pressure Low, the RCIC Containment Isolation Valve 1E51F063, RCIC STM SPLY DRWL INBD ISOL, closed. The procedure for this surveillance (which had recently been revised) should have directed the opening of the breakers for isolation valves 1E51F063 and 1E51F076, RCIC STM LINE WARMUP VLV, which are the division two inboard containment isolation valves for the RCIC system. The procedure incorrectly directed the breakers to be opened for the 1E51F064, RCIC STM SPLY DRWL OTBD ISOL, and 1E51F076. The 1E51F076 is a division two valve and the 1E51F064 is a division one valve. Both the 1E51F076 and 1E51F064 were open at the time their breakers were opened, which resulted in the loss of isolation capability for this containment penetration." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-12-17
49646 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2013-12-17 10:50 | 2013-12-17 17:25 | 2013-12-17 | TECHNICAL SUPPORT CENTER DEGRADED DUE TO LOSS OF AIR FILTRATION "At approximately 1050 EST on December 17, 2013, during a check of facility equipment, the Technical Support Center (TSC) was found to be degraded due to the loss of the air filtration system. The air filtration system was restored and the TSC made fully functional at approximately 1300 the same day. "The emergency assessment function could have been performed in the control room as addressed in emergency response procedures. This event is reported in accordance with 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-17
49644 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-12-16 20:00 | 2013-12-17 15:11 | 2013-12-17 | FITNESS FOR DUTY REPORT - LICENSED OPERATOR TESTED POSITIVE FOR ALCOHOL A licensed operator had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to the plant has been restricted. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2013-12-17
49643 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2013-12-16 | 2013-12-17 14:19 | 2013-12-18 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL MISADMINISTRATION The following report was received via email: "Description of Event: [The Georgia Department of Natural Resources] Received a call from the RSO [Radiation Safety Officer] of RCG [Radiotherapy Clinics of Georgia] on December 17, 2013 at 0930 EST, informing the Department of a possible misadministration that occurred at the Snellville location. "The wrong [High Dose Rate] HDR treatment plan was selected and used on a patient resulting in some possible injury to the patient. An investigation is currently being initiated to determine the cause and effects of the error. The licensee will provide an official report to the Department within 15 days." Georgia Incident Number 121613. * * * UPDATE RECEIVED FROM DAVID CROWLEY TO JOHN SHOEMAKER AT 2034 EST ON 12/18/13 * * * "[The Georgia State Investigator] received the initial call on 12/17/2013 at 0930 EST. The incident regarded an Ir-192 HDR afterloader and had occurred on 12/16/2013. . "[The initial report stated:] It was determined that the wrong treatment plan was given and a misadministration had occurred. The correct site and applicator were used; however, a gynecological treatment plan ran in place of the intended skin treatment plan. No symptoms were evident at this time, but the patient was alerted to look for a reddening of the skin. "The RSO did not communicate much information and left many details open until they could submit the final report. [The Georgia State Investigator] forwarded this information to the [NRC] upon documenting it. "[A Georgia State Investigator] performed a reactive site [follow-up] inspection on 12/18/2013 to discern more information about the incident. One of the contributing causes appears to be similar last names on the two patient plans. No other verification of the treatment plans seemed to be conducted other than selecting the name; which the physicist inadvertently clicked on the wrong patient name in this selection process. "113 seconds passed before the error was caught and the physicist pressed for manual interrupt of the treatment. The treatment was intended for the skin on the temporal region of the patient's head. This used a skin plaque type applicator. Instead, a gynecological plan ran in the system but with the skin plaque applicator in place on the correct location of the patient. "The error caused the Ir-192 source to hit a dead end at the first channel due to it having a shorter channel length than the other plan anticipated. From what the physicist could determine it was stuck in that position for nearly the entire time. "The prescribed procedure was for 40 (4000 rem) Gy to be delivered in a fractionated schedule. An actual delivered dose is yet to be calculated and will determine whether a corrective fractionation schedule will be prescribed to correct for this since most of the dose was deposited in the vicinity of the treatment site. This determination will be included in the final report. At this time, the only expected acute effects to the patient may be reddening of the skin in the immediate location of the source. "The source had an 8.0 Ci Ir-192 source from Alpha Omega Services, Inc. (Serial#: 24-01-2470-001-110113-12043-45). This was in a mobile HDR unit made by Varian (Model: Gamma Med(+)iX / Serial#: H640510-GM). "Corrective actions are still being discussed and will be clearly identified in the final report to prevent future occurrences." Notified the R1DO (Dimitriadis), FSME Events Resource and FSME (McIntosh) via email only. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2013-12-25
49642 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-17 10:15 | 2013-12-17 13:38 | 2013-12-17 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PREPLANNED MAINTENANCE At 1015 EST on 12/17/13, the Unit 2 high range stack radiation monitor RM-8168 was removed from service for preplanned maintenance. The maintenance was completed and the radiation monitor returned to service at 1300 EST. The licensee notified the NRC Resident Inspector and the State and Local Governments. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-17
49641 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-10-21 04:19 | 2013-12-17 13:07 | 2013-12-17 | 60 OPTIONAL REPORT - INVALID PARTIAL REACTOR PROTECTION SYSTEM ACTUATION "Invalid partial Reactor Protection System (RPS) actuation results in; Closure of Containment Isolation Valves (CIVs) in multiple systems, including isolation of the Reactor Water Clean-Up (RWCU) System. "On October 21, 2013, at 0419 EST, Unit 2 received a Reactor Auto SCRAM System 'B' trip signal in the main control room. Initial investigations at the local RPS Motor-Generator (MG) set room discovered breaker 52-3D tripped in cabinet 2C71-P003D. This resulted in a half-scram and the closure of CIVs in multiple systems, including closure of the RWCU system outboard isolation valve, 2G31-F004. These trips are normal responses to the loss of the 'B' RPS. The operating crew entered abnormal operating procedures, including those for loss of RPS and for loss of the RWCU system, and confirmed that all isolations and trips occurred as expected. Additionally, the crew restored the 'B' RPS bus from its alternate source, reset the half scram, returned the CIVs to their normal positions, and placed RWCU in service. "Upon investigation, the determination was made that the trip and reset setpoints for under-voltage relay 2C71 -K752D had drifted. Consequently, once the drift reached the trip setpoints during the event, breaker 52-3D tripped, resulting in the loss of the 'B' RPS bus. Because a malfunctioning subcomponent caused the partial RPS trip rather than a valid CIV actuation signal, the resulting isolation is considered an invalid actuation. "Further evaluation into the cause of the drift revealed solder joint cracks in the relay circuit board and an inadequate previous refurbishment of the subject relay. The drifting relay was removed and a refurbished relay was installed in location 2C71-K752D. Plans are to replace both units' RPS Power Monitoring relays with a different design. Until that design change is implemented, the frequency of calibration for these relays is being increased from every 182 days to every 91 days." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-12-17
49640 | 0 | CONNECTICUT RADIATION DIVISION |  |  |  |  | 2013-12-16 22:00 | 2013-12-17 11:15 | 2013-12-30 | LEAD ANALYZER STOLEN FROM CAR A lead analyzer was stolen from the trunk of a car belonging to an employee of the New Haven Health Department. The device was a RMD XRF Lead Analyzer, Model LPA-1, serial #3520, and contained a Co-57, 10-12 mCi source. The missing device was reported to the New Haven, CT police department. * * * UPDATE FROM ANDREW ZWICK TO VINCE KLCO ON 12/30/13 AT 0830 EST * * * Notified by the State of Connecticut that the lead analyzer has been recovered and is in the possession of local law enforcement. Notified the R1DO (Dwyer), and FSME Resources and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-12-25
49639 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-12-16 17:00 | 2013-12-16 22:29 | 2013-12-16 | POTENTIAL FOR SPURIOUS START OF VARIOUS PUMPS DURING POSTULATED FIRE EVENTS "A circuit analysis review for Appendix R Operator Manual Action deficiency extent of condition identified that fire damage to cable ES194-I is not isolated by the local control power transfer switch utilized in the Safe Shut-down Instruction. Fire damage to the non-isolated cable ES194-I in Fire Areas 01-03, 02-01, and 02-03 could cause the RHR Pump 2C to spuriously start (or restart after the Operator local trip action) when 4kV Shutdown Board B is credited for these Fire Areas. An undesired spurious start of RHR Pump 2C could overload the credited Diesel Generator or take away the necessary load capacity to allow operation of other Appendix R fire safe shutdown credited loads. "The fire damage postulated would require a short to ES194-I from a separate cable conductor energized with the positive potential of the battery supplying 4kV Shutdown Board B (i.e., normally Shutdown Battery B). It is postulated for a fire-event that the necessary short to ES194-I could come from a cable-to-cable short or from a short to ground as the fire event may cause a separate conductor energized with the positive potential of the associated battery to short to ground. "Similar conditions also exist for: RHR Pumps 1A, 1B, 1D, 2A, 2B, 3A, and 3C due to fire damage to cables in one or more Fire Areas. "Compensatory actions in the form of an Operator Work Around [OWA] to remove the affected RHR Pump breaker close circuit control power fuses during the affected Safe Shut-down Instructions, a caution order on the appropriate transfer switches referencing the OWA, and fire watches in the affected Fire Areas to mitigate this condition are in place in accordance with the BFNP [Browns Ferry Nuclear Plant] Fire Protection Report. "This condition is being reported pursuant to 10CFR50.72(b)(3)(ii)(B) and 10CFR50.72(b)(3)(v). "The NRC Resident Inspector has been notified." The licensee is also reporting under 10CFR50.72(b)(3)(v)(D) Accident Mitigation. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2013-12-16
49638 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-12-16 16:27 | 2013-12-16 21:37 | 2013-12-16 | UNANALYZED CONDITION DUE TO UNFUSED DIRECT CURRENT AMMETER CIRCUITS "At 1627 CST on December 16, 2013 Farley Nuclear Plant determined that the following was an unanalyzed condition: "As a result of recent industry operating experience (OE 305419, EN 49411, EN 49419) regarding the impact of un-fused Direct Current (DC) ammeter circuits in the Control Room, Farley performed a review of ammeter circuitry for similar issues. The review determined the described condition to be applicable to Farley resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The wiring design for the ammeters contains a shunt in the current flow from each DC battery and battery charger, but the ammeter wiring attached to the shunt does not contain fuses. "It is postulated that a fire could cause one of the ammeter wires to short to ground. Concurrently, the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a ground loop through the un-fused ammeter cable. The potential exists that the cable could heat up, causing a secondary fire in the ammeter raceway. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown per 10 CFR 50 Appendix R. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-12-16
49637 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-12-16 14:54 | 2013-12-16 21:37 | 2013-12-17 | LOSS OF CONTAINMENT SMOKE DETECTION CAPABILITY "At 1454 CST on December 16, 2013, the Unit 1 pyro panel (smoke detection panel) was declared non-functional due to an unexpected failure. Viable compensatory measures have been established for all affected areas except the Unit 1 Containment Building. Since a fire in Containment is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). Containment temperatures are being monitored while the pyro panel is out of service, however, this is not considered a satisfactory compensatory measure for maintaining effective assessment capability." The NRC Resident Inspector has been notified. * * * UPDATE AT 2046 EST ON 12/17/13 FROM DARRIN GARD TO DANIEL MILLS * * * The Unit 1 pyro panel has been returned to service as of 1554 CST on 12/17/13, which restores Unit 1 containment fire detection capability. The NRC Resident Inspector has been notified. Notified R2DO (Freeman). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-16
49636 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-12-14 | 2013-12-16 20:02 | 2014-05-29 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following was received via facsimile: "Event Narrative: While performing radiography operations at Microsoft Bld. 32 in Redmond, Washington, the radiography source could not be retracted from the collimator back into camera. The Radiation Safety Officer (RSO) of Mistras then called the Washington State Department of Health (DOH) emergency line (206 Nuclear) and an inspector was dispatched to the scene. At the scene was the RSO, Assistant RSO (trained in source recovery), assistant radiographer, and another radiographer. Assistance was being provided via telephone by QSA Global. It is not known yet if previous attempts brought the source through the camera and into the crank cable tube. However, while attempting to remedy the situation the (0-200 mR) pocket dosimeter of the radiographer had gone off scale. The radiographer was removed from the scene and his TLD has been sent in via overnight mail for emergency processing. The collimator was attached to the camera with a 2-3 inch long fitting (there was no guide tube). After disconnecting the crank cable from the camera, the crank cable was pulled back to the crank (while observing survey meters), and it was discovered that the connector at the end of the cable where it was attached to the pig tail was broken. The camera and collimator were loaded onto a dry wall cart and covered with several bags of lead shot. A moving 2 mR/hr barrier was established around the cart during this movement. The apparatus was then moved to a remote area of the parking lot. Once in the parking lot, 2 mR/hr barricades were set up. Eight foot long tools were made in order to unscrew the fitting from the collimator. Once the fitting was removed, the connector end of the pigtail was exposed and could be pulled out (with eight foot grappler) of the collimator and inserted into another camera. This procedure was practiced several times with a dummy source prior to the actual transfer. The highest dose received on the retrieval team was 93 mR. An investigation is about to begin, and Mistras was performing reenactments earlier today. More information pending." * * * UPDATE ON 12/19/13 AT 1439 EST FROM STEPHEN MATTHEWS TO DONG PARK * * * The retrieval team leader received 43 mR with pocket dosimeter, the licensee RSO received 93 mR with pocket dosimeter, the assistant radiographer received 85 mR with pocket dosimeter, and the radiographer received 40 mR with pocket dosimeter. Notified R4DO (Lantz) and FSME Events Resource via email. * * * UPDATE ON 5/29/2014 AT 1616 EDT FROM STEPHEN MATTHEWS TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "This incident has been closed as of May 29, 2014. The two sides of the crankshaft fractures were analyzed to determine the nature of the fracture mechanism. A reenactment was performed at the licensees facility. Radiographers were re-trained with respect to not attempting retrieval procedures without training or contacting the RSO, and supervision of assistants has been adequately addressed by the licensee. Details of any of these issues are available upon request." Washington Incident #WA-13-062 Notified the R4DO (Vasquez) and FSME Resources (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-12-24
49635 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2013-12-16 | 2013-12-16 15:12 | 2013-12-17 | MARYLAND AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was obtained from the State of Maryland via email: "At 12:17 PM on December 16, 2013, the Radiation Safety Officer of Maryland Q.C. Laboratories, called [the State of Maryland] to report an incident that occurred today in their radiography vault. She reported that they were performing industrial radiography using a 34.7 Ci Ir-192 source, QSA model A424-9 in a model 880 D camera, when a steel pipe fell on the guide tube preventing the source from retracting into the shielded position. She stated that attempts to retract the source were not successful. She further stated that QSA Global will arrive at the licensed facility tomorrow to recover the source. The source is in a tungsten collimator inside the vault. The assistant radiographer reported 10 mRem on his SRD. For security, Maryland Q.C. locked the door to the vault and will post a 2-man crew at the facility until QSA arrives. Maryland Health Physicist Bob Nelson is on site at this time conducting an investigation. He reports that the dose rates outside the vault are less than 1.0 mRem per hour." * * * UPDATE FROM ALAN JACOBSON TO CHARLES TEAL AT 0937 EST ON 12/17/13 * * * "The Maryland Health Physicists conducting the investigation at Maryland QC Laboratories reported on 12/17/2013 at 0930 hours that the source has been safely retrieved and stored in the camera." Notified R1DO (Dimitriadis) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2013-12-24
49634 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-12-14 15:03 | 2013-12-14 19:32 | 2013-12-14 | UNANALYZED CONDITION AFFECTING UNIT 1 EMERGENCY DIESEL GENERATOR "At 1503 PST on December 14, 2013, Pacific Gas and Electric Company identified that, if atmospheric conditions were to develop that had both sustained high winds exceeding 60 miles per hour from the NW to NNE direction, and ambient air temperature exceeding 97 degrees Fahrenheit, the combination of these conditions could result in inadequate heat removal to support continuous operation of the Unit 1 emergency diesel generators. Upon identification of this condition, shift orders were issued requiring implementation of existing procedural guidance to open plant doors to allow additional air flow that would provide adequate emergency diesel generator cooling to support continuous operation of the U1 emergency diesel generators. "This report addresses a condition as described in 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified of this condition." This condition was discovered during a license basis verification review. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-12-14
49633 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-12-14 03:37 | 2013-12-14 06:57 | 2013-12-14 | MANUAL SCRAM DUE TO RISE IN REACTOR PRESSURE DURING TURBINE VALVE TESTING "Today at approximately 0337 [EST], during quarterly turbine valve testing with reactor power at 100% of rated thermal power, the plant experienced reactor pressure control abnormalities. Reactor pressure rose to 1042 psig [at which point] the Operators inserted a manual SCRAM. The cause of the rise in reactor pressure is currently under investigation. "All control rods inserted into the core. Main steam isolation valves remained open, [however], bypass valves did not open as expected. The plant is in its normal electrical lineup and decay heat is being removed via isolation condensers. No electronic (EMRVs) or safety valves lifted during the transient. The plant is currently shutdown and all parameters are stable. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" The licensee notified the NRC Resident Inspector and will be notifying the State. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-12-14
49632 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-12-13 17:57 | 2013-12-13 20:07 | 2013-12-13 | MANUAL REACTOR TRIP DURING FEED PUMP SWAP "During a feed pump shift from the motor driven reactor feed pump to the 'A' turbine driven reactor feed pump during power ascension, reactor pressure vessel (RPV) water level was approaching the Reactor Protective System (RPS) automatic scram set point when a manual reactor scram was inserted. "All control rods fully inserted. RPV water level is being maintained by the normal condensate booster / feedwater systems. RPV pressure is being maintained via normal main steam system. There were no actuations of any Emergency Core Cooling System and no Safety Relief Valves actuations. All systems responded as expected." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-12-13
49631 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-11-25 15:00 | 2013-12-13 19:44 | 2014-01-21 | BREACH SIZES EXCEEDED FOR CONTROL ROOM ENVELOPE "On December 13, 2013 it was determined that a reportable condition has existed at Columbia Generating Station since 1500 hours [PST] on November 25, 2013. "At 1500 hours on November 25, 2013, the Control Room Envelope (CRE) was declared inoperable based on the inability to ensure that the Control Room Emergency Filtration (CREF) System would be able to maintain a positive differential pressure with all areas surrounding the CRE boundary. Columbia does not have the installed instrumentation to directly monitor the differential pressure between the Main Control Room (MCR) and certain areas adjacent to the MCR. The pressure in the adjacent areas is controlled by placing conservative limits on allowed breach size for these adjacent areas. "On November 25, 2013, it was identified that the combined breach size associated with several doors in these adjacent spaces resulted in exceeding the allowed limit. Based on exceeding the allowed breach size limit to the adjacent areas, the Control Room Envelope was declared inoperable, and Technical Specification Action Statement 3.7.3.B.1 was entered. "An additional breach was discovered on 12/05/13 from a hole in ductwork passing through the cable spreading room, which is one of the adjacent areas to the CRE boundary, and that condition was added to the existing action statement 3.7.3.B.1. These are conditions that could have prevented fulfillment of a safety function of structures that are needed to mitigate the consequences of an accident and are reportable under 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BRIAN HEAVILIN TO VINCE KLCO ON 1/21/2014 AT 1720 EST* * * "In the case of this event, the Control Room Envelope (CRE) was declared inoperable and Technical Specification Action Statement 3.7.3.B.1 was entered conservatively based upon limited knowledge at the time of discovery. There is no installed differential pressure indication between the CRE and this area adjacent to the Main Control Room (MCR), therefore conservatively this adjacent area is included in the CRE, and leakage is administratively controlled. The leakage between the MCR and the adjacent area included in the CRE exceeded this administrative limit. "Testing performed on November 20, 2013, prior to the December 13, 2013 reported events, as well as testing after the event, January 10, 2014, has demonstrated that the leakage identified does not prevent the Control Room Envelope (CRE) from establishing and maintaining the required differential pressure to ensure fulfillment of its required safety function for Control Room Habitability. "The ability of the Control Room Emergency Filtration (CREF) system to perform its function of pressurizing and maintaining the Main Control Room positively pressurized with respect to its surroundings was not lost due to the leaking doors and duct specified in the event. Performance of the surveillance without these breaches sealed validated this conclusion. "The event described above should not have been reported, as the Control Room Envelope was always operable and capable of fulfilling its safety function with the existing breaches and did not constitute a reportable event as conditions that could have prevented fulfillment of a safety function of structures that are needed to mitigate the consequences of an accident under 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified the R4DO (Spitzberg). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-12-13
49630 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-12-13 16:00 | 2013-12-13 17:51 | 2013-12-13 | ELEVEN INDIVIDUALS NOT PROPERLY SUBJECTED TO THE RANDOM FITNESS FOR DUTY PROGRAM "In 2010, changes within the Dominion FFD [Fitness for Duty] program resulted in 11 supplemental personnel not being included in the current random FFD testing program. Two individuals are actively badged at Surry Power Station (SPS) and North Anna Power Station (NAPS). Both individuals accessed the protected area at SPS recently. The other nine individuals were not badged but perform duties that require them to be subject to the FFD program. The affected individuals are now included in the random testing program. An extent of condition was performed and no other contractor records were found to be affected. "This event is reportable per 10CFR26.719(b)(4), 'Any programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program." The error occurred when, in 2010, it was decided that contract employees would no longer be placed in a select labor pool. When this occurred, FFD personnel no longer monitored that particular labor pool in the belief that it no longer existed. Upon discovery that the labor pool did, in fact, still exist the licensee determined that the eleven personnel should have been included in the random testing program. See similar North Anna report EN #49629. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2013-12-13
49629 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-12-13 16:00 | 2013-12-13 16:43 | 2013-12-13 | ELEVEN INDIVIDUALS NOT PROPERLY SUBJECTED TO THE RANDOM FITNESS FOR DUTY PROGRAM "In 2010, changes within the Dominion FFD [Fitness for Duty] program resulted in currently 11 individuals not being subjected to random FFD testing although required. Two individuals are actively badged at Surry Power Station and North Anna Power Station (NAPS). Both individuals accessed the protected area at NAPS recently. The other nine individuals were not badged but perform duties that require them to be subject to the FFD program. The affected individuals are now within the random testing program. "This event is reportable per 10CFR26.719(b)(4), 'Any programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program.'" A work review will be conducted for the two actively badged individuals. The program error has been corrected. The licensee has notified the NRC Resident Inspector and the Louisa County Administrator. See similar Surry report EN #49630. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2013-12-13
49628 | 0 | TRIVIS INC. |  |  |  |  | 2013-12-13 | 2013-12-13 14:37 | 2014-01-29 | PART 21 REPORT - NON-DESTRUCTIVE TESTING DID NOT MEET PROCEDURAL REQUIREMENTS The following information was summarized from the report submitted by TriVis via facsimile: David Bland, President of TriVis Inc. reported that two contract Non-Destructive Evaluation (NDE) Level II examiners, employed by TriVis, failed to meet NDE procedural requirements for weld testing on the Outer Top Cover Plate (OTCP) on six Transnuclear Model NUHOMS-61BTH Dry Shield Canisters (DSC) at the Monticello Nuclear Generating Plant. An NRC inspector observed part of this activity and questioned whether the dwell times for the penetrant and developer used by a NDE Level II employee of TriVis were sufficient to meet procedural requirements. Upon evaluating recorded video of the work location, it was determined that the dwell times for both the penetrant and the developer of the OTCP weld on DSC #16 were not in compliance with the TriVis NDE LPT [Liquid Penetrant Test] Procedure. An extent of condition review of previous LPT exams conducted on DSCs 11 through 16 revealed additional examinations that were not in compliance with the dwell times specified by the procedure as well as other procedural discrepancies. All six DSCs were declared inoperable at the time of discovery. All work activities associated with dry fuel storage at Monticello were stopped. A timeline and corrective actions are being developed by TriVis and the licensee. The two NDE Level II examiners were not previously employed by TriVis and did not perform any other NDE activities at Monticello. Evaluations will be completed by January 31, 2014 or a follow-up interim report will be submitted. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MIKE SOUTH TO DANIEL MILLS ON 1/29/14 AT 0945 EDT * * * The following information was selected from the report submitted by TriVis via facsimile: "TriVis has completed its evaluation of the activity and determined that it is limited to procedural non-compliance on DSCs 11 through 16 at [Monticello] only. Based on the results of the evaluation, TriVis believes the procedural non-compliance did not adversely affect the health and safety of the public and does not constitute a substantial safety hazard." Notified R3DO (Sheldon), and NRR Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-12-13
49627 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-12-13 11:06 | 2013-12-13 13:40 | 2013-12-13 | OFFSITE NOTIFICATION DUE TO FUEL OIL SPILL TO THE ENVIRONMENT "At 1106 [CST], the control room was informed that a diesel fuel spill to the environment was a reportable event. Earlier in the day, a container tipped over in the bed of a truck eventually spilling diesel fuel onto the ground inside the owner controlled area. Approximately 2 and one half gallons spilled out. The lid of the container was apparently defective. "No fuel oil made contact with any surface water. "The area was cleaned up. "The Kansas Department of Health and Environment and the National Response Center were notified. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-12-13
49626 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-12-12 04:36 | 2013-12-12 12:44 | 2013-12-13 | BOTH TRAINS OF PRIMARY CONTAINMENT HYDROGEN AND OXYGEN MONITORS OUT OF SERVICE FOR MAINTENANCE "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). At 0436 (PST), on 12/12/2013 the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was removed from service for planned maintenance activities. The Division 1 sample rack is expected to be out of service for 14 hours. The redundant Division 2 sample rack was previously removed from service for maintenance and remains out of service for repairs. Compensatory measures to monitor primary containment for hydrogen and oxygen are available via grab samples using chemistry procedures." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM QUOC VO TO HOWIE CROUCH AT 1705 EST ON 12/13/13 * * * "Following completion of maintenance activities, the Division 1 sample rack for monitoring primary containment oxygen and hydrogen atmospheric concentrations was returned to operable status at 1150 PST on 12/13/2013, restoring its required emergency assessment capability. "The NRC Resident Inspector has been notified." Notified R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-12
49625 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-12-11 08:40 | 2013-12-11 15:56 | 2013-12-11 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE "A licensed employee had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2013-12-11
49624 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-11 15:32 | 2013-12-11 15:51 | 2013-12-11 | MISSING LICENSED MATERIAL "Two Trijicon gun scopes, source ID# 6-53953 and 110-59164, both non-exempt sources, were identified as being missing from a Security rifle scopes inventory. Each scope had a [tritium] activity quantity of 57.766 milliCuries (mCi) and 60.528 milliCuries (mCi), respectively. The radioactive material is an integral part of the scope from manufacture. Scope source ID# 110-59164 was recovered, and scope source ID# 6-53953 remains unrecoverable. "The activity quantity for the these gun scope exceeds the 10 times the 10 CFR 20, Appendix C quantity, but is [less than] 1,000 times the regulatory criteria of Appendix C and therefore is being reported in accordance with 10 CFR 20.2201(a)(ii). "The licensee informed the State of Connecticut, and the NRC Resident Inspector." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-12-11
49623 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-12-10 | 2013-12-11 15:32 | 2014-01-21 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RADIOGRAPHER AND MEMBER OF THE PUBLIC The following information was obtained from the State of Texas via email: "The owner of J-CAP manufacturing [located in Seminole, TX] reported at 14:10 CST [on 12/11/13] that an incident [involving industrial radiography of a pressure vessel occurred at his facility on December 10, 2013]. Individual reported that his site foreman was working with the industrial radiographer who was performing radiography of a pressure vessel. The radiographer approached the source collimator to change the film and the radiographer realized the source was still in the open - exposed position. The amount of exposure is still in question and the site foreman was escorted by his employer to the hospital for evaluation. The employee reported he was in the area for 5- 8 minutes and approximately 12-24 inches from the source. The employee was not working for the industrial radiography company, thus this is an exposure to the public. The radiographer also received a dose. The Radiation Safety Officer for Wilco NDT [licensed in Farmington, NM] was contacted by the Agency [Texas Department of State Health Services] to verify the incident. RSO for Wilco NDT reported that he contacted the State of New Mexico to report the incident and is currently working on sending [the radiographer's] monitoring badge to be read. RSO is still trying to contact his radiographer and review details of the incident. A calculated dose for the time period of 8 minutes with a distance of 1 foot from the Ir-192 source with 67 curies of activity was 40 rem/8 minutes. Investigation is ongoing and further details will be supplied as in accordance with SA300." Texas Incident #: I-9142 * * * UPDATE FROM IRENE CASARES (VIA EMAIL) TO HOWIE CROUCH AT 1758 EST ON 12/13/13 * * * "On December 13, 2013, at 1632 hours [CST], the licensee notified the Agency [that] their dosimetry processor had completed reading the radiographers' badges. One badge read 34 millirem DDE, and the other 30 millirem, DDE. "Two Agency inspectors are scheduled to interview all parties involved in the event [on] Tuesday, December 17, 2013. "Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Werner) and FSME EO (Holian). * * * UPDATE FROM IRENE CASARES TO VINCE KLCO ON 1/21/14 AT 1214 EST * * * The following information was obtained from the State of Texas via email: "Update to Event 49623: The initial report stated a possible public exposure of 40 rem, upon further investigation and interviews the dose was much lower. The dose for whole body was calculated to be 515 mrem for the public exposure and 2.06 rem for the radiographer's exposure in 5 minutes of exposure time. The initial report was stated that Wilco NDT reported the incident to State of New Mexico and State of Texas. During investigation [it] was understood that Wilco NDT did not report to any Agency. The J-Cap Manufacturing company reported the incident. The incident is not an immediate report event after complete investigation. . . " Notified R4DO (Spitzberg) and FSME EO (Holian). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2013-12-19
49622 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-12-10 05:20 | 2013-12-10 18:37 | 2013-12-10 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The California Radiologic Health Branch reported a stolen moisture density gauge from a licensee in Walnut Creek, CA. The gauge was recovered in about 4 hours, in Lafayette, CA, after being abandoned by the thieves. The state assisted local law enforcement in Walnut Creek and Lafayette, CA with the gauge recovery. The gauge was recovered in good condition and there are no known exposures or spread of contamination. The gauge has been returned to the licensee for storage in a secure location. The gauge is a Instro Tek, model 3500 Explorer, Serial #1644, containing 10 mCi Cs-137 and 40 mCi Am/Be-241 sources. California State Report #121013 and Lafayette, CA police report #13-21268. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-12-18
49621 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2013-12-10 12:00 | 2013-12-10 16:43 | 2013-12-13 | AGREEMENT STATE REPORT - COMPOSITE LISTING OF MISSING TRITIUM EXIT SIGNS The following forty eight (48) lost licensee tritium signs were submitted by the State of Nebraska via email: 1. ShopKo Store #47 located in Lincoln, NE; (1) SRB Technologies; Model Safety-10; S/N ST18770; H-3; 21 Ci. (10) Safety Light; Model #2040; S/N A44267, A44269, A44272 thru A44274, A44276, A42278 thru A44281; H-3; 11.5 Ci each. Nebraska Event - NE130006. 2. ShopKo Store #48 located in Norfolk, NE; (6) Safety Light Model #2040; S/N Unknown; H-3; 11.5 Ci. Nebraska Event - NE130007. 3. ShopKo Store #56 located in Omaha, NE; (29) SRB Technologies; Model Safety-10; S/N 24303 thru 24318, 24327 thru 24333, 24398, 24299, 24400, 24401, 24399H-3; 21 Ci each. (2) Safety Light Model #2040; S/N AON845, AON847; H-3; 12 Ci each. Nebraska Event - NE130008. * * * UPDATE ON 12/13/13 AT 0921 EST FROM TRUDY HILL TO DONG PARK * * * The following thirteen (13) lost licensee tritium signs were submitted by the State of Nebraska via email: 1. ShopKo Store #53 located in North Platte, NE; (13) Safety Light Model #2040; S/N Unknown; H-3; 11.5 Ci. Nebraska Event - NE130009. Notified R4DO (Walker), FSME Events Resource and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2013-12-18
49620 | 0 | FLANDERS FILTERS |  |  |  |  | 2013-11-19 12:00 | 2013-12-10 15:10 | 2013-12-10 | PART 21 - POSSIBLE DEFECT IN A HIGH EFFICIENCY PARTICULATE AIR FILTER The following information was received by facsimile: "This serves as notification to the U.S. Nuclear Regulatory Commission (NRC) of a possible deviation or defect in nuclear qualified High Efficiency Particulate Air (HEPA) Filters manufactured by Flanders Filters. "Flanders Nuclear HEPA Model T-007-W-43-05-NU-51-23-GG-FU5 failed requalification testing at Edgewood Chemical Biological Center (ECBC). This failure was related to the 'Resistance to Pressure' test required per ASME AG-1, Section FC5140. "On November 19, 2013, Flanders received a report from ECBC indicating failure of this filter model to re-qualify per the requirements of ASME AG-1, Section FC. Flanders is investigating the failure, but at this time do not believe Flanders has the ability to determine if this could create a substantial safety hazard because we do not have specific knowledge regarding the actual application the filters are being used in at each site. "Customers supplied this model Filter, or filters with the same media type and pack style, since the last qualification of the media type and pack style on July 18, 2012 are being notified. "In accordance with 10CFR Part 21.21(d)(4), Flanders will provide written notification to the NRC within 30 Days with additional information including corrective actions where applicable." The customers include the following: SCANA; Nuclear Fuel Service; Premier Technology Incorporated of Blackfoot, Idaho; and Energy Northwest. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-12-10
49619 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-12-09 09:06 | 2013-12-09 10:19 | 2013-12-09 | SMOKE DETECTION PANEL REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "At 0906 CST on December 9, 2013, the Unit 1 pyro panel (smoke detection panel) was removed from service for planned repairs. The pyro panel is expected to be out of service for approximately 8 hours. Viable compensatory measures have been established for all affected areas except the Unit 1 Containment Building. Since a fire in Containment is an entry condition for the site's Emergency Plan, this is considered a loss of emergency assessment capability and is being reported per 10CFR50.72(b)(3)(xiii). Containment temperatures are being monitored while the pyro panel is out of service, however this is not considered a satisfactory compensatory measure for maintaining an effective assessment capability. "A follow-up notification will be provided upon restoration of Containment Building smoke detection capability. "The NRC Resident Inspector has been notified." * * * UPDATE FROM JOHN ANDREWS TO JOHN SHOEMAKER AT 1345 EST ON 12/9/13 * * * "The Unit 1 pyro panel (smoke detection panel) has been returned to service after planned repairs. The loss of emergency assessment capability reported per 10CFR50.72(b)(3)(xiii) has been restored. The NRC Resident [Inspector] will be notified of the update." Notified R2DO (Masters). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-09
49618 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2013-12-09 08:00 | 2013-12-09 09:20 | 2013-12-09 | UNUSUAL EVENT DECLARED DUE TO UNIT 2 AUXILIARY TRANSFORMER EXPLOSION "At approximately 0748 [CST] on 12/9/2013, an electrical fault occurred resulting in a fire and explosion on the ANO [Arkansas Nuclear One] Unit 2 Unit Auxiliary Transformer. This caused a unit trip and a loss of power to Startup 3 Transformer, which is one of the two offsite power feeds to ANO Unit 2. ANO Unit 2 is currently in a stable shutdown condition. With Startup 3 and Unit Aux Transformer unavailable, power was lost to the Reactor Coolant Pumps and Circulating Water Pumps. RCS [Reactor Coolant System] natural circulation is in progress removing core decay heat. Emergency Feedwater actuated due to low steam generator levels and is supplying both steam generators. The unit is steaming to the atmosphere. 2A-1 and 2A-3 are powered from SU [Startup] 2 Transformer. 2A-4 is powered from 2K-4B Emergency Diesel Generator. "ANO Unit 1 is currently operating at 98% power. The auto transformer tripped off line with the fault in ANO Unit 2 Unit Auxiliary Transformer. This has caused Startup Transformer 1 to be inoperable. This places ANO Unit 1 in a 72 hour Technical Specification action statement (T.S 3.6.1 for Loss of the SU-1 Transformer). "No significant injuries were reported as a result of this condition and offsite agencies have been notified. "At 0800 on 12/9/2013 Unit 2 declared a Notification of Unusual Event based on EAL HU4 Fire or Explosion inside Protected Area not extinguished in 15 minutes. "At 0917 on 12/9/2013, the fire on Unit 2 Unit Auxiliary Transformer is OUT." The Licensee notified the NRC Resident Inspector. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and Nuclear SSA vial email. * * * UPDATE FROM DAN BREEDLOVE TO VINCE KLCO AT 1336 EST ON 12/9/2013 * * * At 1215 CST, ANO terminated from the Unusual Event as per HU4 stable plant conditions. ANO Unit 2 is stable and will be cooled down to Mode 5 via natural circulation and decay heat is being removed via emergency feedwater and downstream dump valves to atmosphere. There is no radiological release and no personnel injuries. The licensee has notified the NRC Resident Inspector, Arkansas Department of Emergency Management, Arkansas Department of Health, and other local authorities. Notified R4DO (Vasquez), NRR EO (King) and IRC MOC (Morris). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and Nuclear SSA vial email. * * * UPDATE FROM ALBERT MARTIN TO VINCE KLCO AT 1812 EST ON 12/9/2013 * * * "Outside agencies (National Response Center, Arkansas Department of Emergency Management, Corps of Engineers, and U.S. Coast Guard) were contacted due to a minor unknown amount of oil that entered the plant discharge to Lake Dardanelle. The oil was from the faulted Unit 2 Unit Auxiliary Transformer. The majority of oil was contained within the containment around the transformer or the oily water separator it drains to. Local inspection revealed only a small amount of what was released actually passed the containment booms that are continuously in place on the discharge canal. The oil boom was verified to be in good condition. The oil was verified to be mineral oil. The release was verified to be terminated. An additional oil boom was deployed. Reference [ANO] Condition Report CR-ANO-C-2013-03071." The licensee notified the NRC Resident Inspector. Notified the R4DO (Werner) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 4 | AR | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2013-12-09
49617 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-12-08 20:27 | 2013-12-09 01:15 | 2013-12-09 | MANUAL SCRAM DUE TO LOSS OF DIVISION 1 480 VAC POWER CAUSING LOSS OF INSTRUMENT AIR TO CONTAINMENT AND SCRAM AIR HEADER While operating at rated electrical power, the station experienced a transformer fault which resulted in a loss of Division 1 480 VAC power. This resulted in the operators inserting a Manual Scram due to loss of Instrument Air to Containment and the scram air header. On the scram, all control rods fully inserted and no safety relief valves lifted. Reactor vessel level is being maintained by normal feedwater and decay heat is being removed via steam to the main condenser through the steam bypass valves. The plant is currently in Mode 3 and proceeding to Mode 4 to comply with Technical Specification requirements. The plant is in a normal shutdown electrical lineup with the exception of the loss of Division 1 480 VAC power. Reporting in accordance with 10CFR50.72(b)(3)(v)(C) due to loss of normal ventilation to secondary containment which resulted in a positive secondary containment pressure for approximately 15 minutes. Secondary Containment required pressure was restored at 2043 CST. Reporting in accordance with 10CFR50.72(b)(3)(v)(D) due to loss of Division 1 480 VAC power resulting in loss of a single train of Low Pressure Core Spray. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2013-12-09
49616 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-12-08 08:00 | 2013-12-08 10:53 | 2013-12-12 | LOSS OF ASSESSMENT DUE TO TECHNICAL SUPPORT CENTER UNINTERRUPTABLE POWER SUPPLY PLANNED REPLACEMENT "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 0800 Mountain Standard Time on December 8, 2013, Palo Verde Nuclear Generating Station (PVNGS) removed the Technical Support Center (TSC) uninterruptable power supply (UPS) from service for a planned replacement. The outage disables the Emergency Response Facility Data Acquisition and Display System (ERFDADS) inside the TSC, remote meteorological data display in the emergency response facilities and control rooms, and transmission of plant data to the Emergency Operations Facility (EOF) and to the NRC's Emergency Response Data System (ERDS). The outage is expected to be completed within five days. "The TSC and EOF remain functional during the outage. The outage does not affect the availability of normal power to the TSC or back-up power from the TSC diesel generator. Existing telecommunication systems provided for the emergency response organization (ERO) remain functional to provide the ERO within the TSC and EOF the necessary emergency assessment capabilities, as described in the PVNGS Emergency Plan. The ERFDADS system in each of the three unit control rooms and unit satellite TSCs remain functional and are not affected by the TSC UPS outage. Compensatory measures exist within emergency plan implementing procedures to obtain meteorological tower data locally and from the National Weather Service. "The ERO has been briefed on the effects of the planned TSC UPS outage. "The NRC Resident Inspector has been informed. "PVNGS will inform the NRC after the outage has been completed and the functionality of affected equipment has been restored." * * * UPDATE FROM DAVE HECKMAN TO HOWIE CROUCH AT 1632 EST ON 12/12/13 * * * "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This notification is an update to EN 49616 which provided notification of pre-planned maintenance activities on the Palo Verde Nuclear Generating Station (PVNGS) Technical Support Center (TSC) uninterruptable power supply (UPS) that disabled various Emergency Plan (E-Plan) data systems. "At approximately 0915 Mountain Standard Time on December 12, 2013, PVNGS restored the affected data systems to service such that the functions of the E-Plan can now be performed without the use of alternate methods. "The NRC Resident Inspector has been informed. " Notified R4DO (Werner). | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-08
49615 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2013-12-07 23:55 | 2013-12-08 06:09 | 2013-12-08 | AVERAGE POWER RANGE MONITORS DECLARED INOPERABLE DUE TO NON-CONSERVATIVE POWER VALUE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(A), event or condition that at the time of discovery could have prevented the fulfillment of a safety function of systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition. A scheduled load reduction for surveillance testing and control rod sequence exchange was in progress. During the control rod sequence exchange, the core monitoring software system (3DMonicore) was used to obtain a 'case' which records various calculated and actual core parameters (i.e. core thermal power, Power Range Monitor indication). The 'case' data is used to evaluate the Technical Specification (TS) Surveillance Requirement (SR) acceptance criteria for SR 3.3.1.1.2 to verify the absolute difference between the average power range monitor (APRM) channels and the calculated power is less than or equal to 2% rated thermal power (RTP) while operating at greater than or equal to 25% RTP. The 'case' showed that all 3 A RPS Trip System APRM channels exceeded the allowable 2% difference threshold in the non-conservative direction (i.e. APRM power reading less than calculated thermal power, difference of 2.9, 3.1, and 2.5% respectively). TS 3.3.1.1 requires at least 2 operable APRM channels per trip system (there are 2 RPS trip systems, A and B). At least 1 of 2 TS required APRM channels are required to maintain the Safety Function (i.e. SCRAM). In this situation, none of the A RPS TS required APRM channels met their SR and were declared inoperable. TS 3.3.1.1 allows delaying entry into the associated Condition and Required Action for this inoperability for up to 2 hours when the inoperability is solely due to APRM indication not within the 2% limit; therefore no TS Required Action tracking timeclocks were entered. A confirmatory 'case' was performed that validated that the subject SR was not met. Prompt action was taken to restore the APRM indications to within limits (this action took approximately 22 minutes to complete) and the subject APRMs were declared operable, restoring the A RPS Safety Function." The licensee notified the NRC Resident Inspector and the Illinois Emergency Management Agency. | 0 | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2013-12-08
49614 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-12-07 09:50 | 2013-12-07 17:31 | 2013-12-07 | SECONDARY CONTAINMENT FAILS RETEST OF DRAWDOWN SURVEILLANCE TEST "On December 7, 2013 at 0950 [EST], Susquehanna Steam Electric Station [SSES] Secondary Containment drawdown testing failed to meet acceptance criteria of Tech Spec Surveillance Requirement SR 3.6.4.1.5 due to inleakage flow rate exceeding the allowable value. "SSES previously entered SR 3.0.3 at 0900 [EST] on 11/15/2013, due to not meeting the requirements of SR 3.6.4.1.4 and 3.6.4.1.5 because of an untested alignment of the Unit 1 Reactor Building Railroad Bay (101 bay). Corrective maintenance was performed on several boundary components (doors and hatches) along with multiple inspections. The test being performed on 12/7/2013 was to be a retest for the previously failed surveillance [performed on 11/20/13]. LCO 3.6.4.1 was entered at 0950 [EST] in support of this test. During the test, it was determined that the maintenance performed did not produce the desired outcome. As a result, the retest was not successful. "The 101 Bay ventilation was realigned to the previously known operable configuration. Upon completion of this realignment, LCO 3.6.4.1 was cleared at 1349 [EST] and operability restored. Note that SR 3.0.3 remains in effect for the unsuccessful, untested configuration. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." See EN #49565 for the previous surveillance test failure, performed on 11/20/13. The licensee has notified the NRC Resident Inspector. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-12-07
49613 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-12-06 12:48 | 2013-12-06 17:52 | 2014-01-17 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "At 1248 EST, Unit 2 High Pressure Coolant Injection (HPCI) system was being tested for routine quarterly flow verification using surveillance test procedure SO-252-002. When HPCI turbine speed was lowered to approximately 2400 RPM, oscillations on turbine speed, flow and discharge pressure were observed. HPCI turbine speed was raised to approximately 2700 RPM and the oscillations stopped. "Unit 2 HPCI system had been declared inoperable and LCO 3.5.1 entered at 1200 EST for the surveillance test. [This is a 14 day LCO.] "Review by Engineering determined that cause of the oscillations warrant further evaluation and HPCI remains inoperable. "HPCI is a single train Emergency Core Cooling Safety system. This event results in the loss of an entire safety function which requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v). "There are no other ECCS systems presently out of service." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DARVIN DUTTRY TO JOHN SHOEMAKER AT 1201 EST ON 1/17/14 * * * "NUREG-1022, Revision 3, states, 'if the retraction or cancellation of a report under this criterion is due to a revised operability determination, the retraction or cancellation should discuss the basis for why the operability determination was revised, and why it is believed that system operability was never lost (i.e., in lieu of the initial determination).' "As indicated in the initial report, Engineering determined that the cause of the oscillations required further evaluation and HPCI remained inoperable. Additional evaluation by Engineering resulted in a conclusion that HPCI was OPERABLE with the observed oscillations at the low flow conditions. Details are as follows: "HPCI speed/flow oscillations at low flow conditions can occur due to inherent instability at these conditions. This phenomenon is understood and documented in industry OE [Operating Experience], EPRI [Electric Power Research Institute] maintenance guidelines, and station procedures. HPCI system operation and control during the surveillance were as expected and demonstrated proper response and stable operation, with the only exception being the described oscillations at the low flow condition. This was confirmed by a review of the system response on the start-up traces. A system walkdown confirmed no abnormality with the control system equipment or governor setting. No tuning adjustments were considered to be necessary based on the low magnitude of the oscillations and their negligible impact on system operation. Unit 2 HPCI was declared OPERABLE and LCO 3.5.1 was cleared at 2308 [EST] on December 6, 2013. "Based on the above additional information, PPL [Pennsylvania Power and Light] is retracting this report." The licensee has notified the NRC Resident Inspector. Notified the R1DO (Rogge). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-12-06
49612 | 0 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2013-12-06 | 2013-12-06 17:00 | 2013-12-06 | UNLABELED PACKAGE CONTAINING RADIOACTIVE MATERIAL The Missouri Baptist Medical Center, in Saint Louis, MO, received an unlabeled package from a supplier in Valencia, CA, which contained 2 spot markers, each containing 50 microCi of Co-57. The package was an expected shipment; however, there was no labeling on the outside of the package indicating the presence of radioactive material. The radiation reading on the outside of the package was 1 mR/hr. The package was opened to verify contents and the material is being maintained in a secure location. No personnel over exposures occurred. The supplier was notified by the licensee of the mislabeling. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | OTH | AGR | 20.1906(d)(2) |  |  |  | 0 | 2013-12-16
49611 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-12-05 17:27 | 2013-12-05 19:16 | 2013-12-12 | 73.71 SAFEGUARDS REPORT - SAFEGUARDS INFORMATION NOT PROPERLY STORED Discovered safeguards information not properly stored. Compensatory measures are being taken. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM DAVID SPARGO TO CHARLES TEAL AT 1143 EST ON 12/12/13 * * * The licensee determined that the information discovered was not safeguards information so they are retracting this event. The licensee has notified the NRC Resident Inspector. Notified R4DO (Werner) and 73.71 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-12-05
49610 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2013-10-09 | 2013-12-05 16:35 | 2013-12-05 | PART 21 - FAILURE OF RELAY LOGIC CARD MODULES IN 2 OUT OF 4 VOTERS FOR POWER RANGE MONITORS The observed aging characteristics of the Solid State Relays on two particular Voter Relay Logic Cards Modules present a future challenge to the Power Range Neutron Monitoring System's ability to reliably insert the Average Power Range Monitor High-High/INOP scram and/or the Oscillating Power Range Monitor Scram to the Reactor Protection System in plant conditions warrant such action. For Relay Logic Cards that have been in operation for over 10 years, Relay Logic Card Module replacement should be scheduled and accomplished at the first reasonable opportunity. For Relay Logic Cards in operation for less than 10 years, a program should be implemented to replace Relay Logic Card Modules before the 10 years is reached. Plant affected; Nine Mile Point 2, Fermi 2, Grand Gulf, Limerick 1 & 2, Peach Bottom 2 & 3, Susquehanna 1&2, Brunswick 1 & 2, Hatch 1 & 2, Browns Ferry 1, 2, & 3, Monticello, and Columbia. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-12-05
49609 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-12-04 13:35 | 2013-12-05 11:07 | 2013-12-05 | FITNESS FOR DUTY - ALCOHOL FOUND IN PROTECTED AREA "On December 4, 2013, at approximately 1335 EST with Watts Bar Nuclear Unit 1 at 100% power and Unit 2 under construction, a small whiskey bottle was found by a Unit 2 construction employee within the protected area. Site Security took possession of the bottle and it was removed from the protected area. The seal on the container did not appear to have been broken. An investigation has been initiated by Site Security. This condition has been documented in TVA's corrective action program as Service Request 818776. This report is submitted pursuant to 10 CFR 26.719 (b)(1) based on the presence of alcohol within the protected area. "The licensee notified the NRC Resident Inspector." Unit 2 does share the same protected area boundary as Unit 1. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Under Construction |  | Power Operation | Under Construction |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2013-12-05
49608 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-12-05 03:25 | 2013-12-05 05:40 | 2013-12-05 | AUTOMATIC REACTOR SCRAM FOLLOWING TURBINE TRIP ON HIGH MOISTURE SEPARATOR LEVEL "While operating at 76% power on 12/5/13 at 0325 EST, the main turbine tripped on moisture separator hi level. The reactor scrammed along with the main turbine trip. All safety systems responded as designed and expected. There was no radiological release. There were no injuries. "During the scram, all rods inserted into the core. Plant is stable in Mode 3 in its normal S/D [shutdown] electrical line up. Decay heat is being removed via the turbine bypass valves dumping steam to the main condenser. "At 0505 EST while securing from cooldown in an attempt to start a recirc pump, BPVs [Bypass Valve] opened causing reactor level swell and subsequent shrink. During this time, RPV [Reactor Pressure Vessel] level lowered to below RPV level 3 and caused a RPS [Reactor Protection System] actuation. RPV level was recovered and is now stable in normal band." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 12/5/13 AT 1000 EST FROM LINDSAY KOBERLEIN TO DONG PARK * * * "This update to ENS #49608 adds reporting criterion 10CFR50.72(b)(3)(iv)(A) for the RPS actuation at 0505 EST during post-scram recovery." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek township. The licensee will be making a press release. Notified R1DO (Cook). | 0 | 0 | 0 | 76 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-12-05
49607 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-12-04 15:40 | 2013-12-04 21:32 | 2013-12-04 | A POTENTIAL ELECTRICAL HOT SHORT IN THE RHR SHUTDOWN COOLING CONTROL CABLE COULD RESULT IN AN INTER-SYSTEM LOCA "As a result of questions raised by inspectors as part of the 2013 Triennial Fire Protection Inspection, a vulnerability from a postulated fire in the Unit 1 Cable Spreading Room was identified. This vulnerability involved the assumption of a fire occurring in Fire Area 0024A (Cable Spreading Room) which would create an inter-cable vulnerability that could result in an inter-system LOCA [Loss of Coolant Accident]. Hatch's licensing basis included credit for the use of disconnect or remote shutdown panel 'Emergency' switches located on the respective remote shutdown panels to isolate the circuits in the cable spreading room thereby eliminating this vulnerability. However, the presence of these switches does not fully address this vulnerability. The Unit 1 RHR [Residual Heat Removal] shutdown cooling isolation valves 1E11-F008 and 1E11-F009 need to be de-energized in order to preclude the opening of these valves should this vulnerability occur on Unit 1. Since the Unit 2 RHR shutdown cooling isolation valves 2E11-F008 and 2E11-F009 are already closed and deactivated, they are not presently impacted by this additional vulnerability. "Immediate actions were taken to de-energize the valves in the 'closed' position which removed the vulnerability. The postulated intersystem LOCA represents an unanalyzed condition that significantly degraded plant safety." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-12-04
49606 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-12-04 13:50 | 2013-12-04 15:14 | 2013-12-05 | UNUSUAL EVENT - LOSS OF STARTUP POWER DUE TO A CUT CABLE "At 1343 CST on 12/04/2013, Comanche Peak Nuclear Power Plant experienced a loss of safeguards electrical power when 345KV transformer XST2 lost power from offsite while 138KV transformer XST1 was out of service for maintenance. Non-Safeguards electrical power remained energized. Both Units remain at power in Mode 1. Both units Emergency Diesel Generators automatically started and all safeguards busses were re-energized from the Emergency Diesel Generators. All ESF systems functioned as expected and the Turbine Driven Auxiliary Feedwater Pump automatically started as designed. Operators reduced reactor power to maintain reactor power less than 100 percent rated thermal power." At 1350 CST, the licensee declared an Unusual Event due to losing both startup transformers. The cause of the loss of the second start up transformer was a cut cable. No one was injured during this event. The licensee informed State and Local Government Agencies and the NRC Resident Inspector. Notified other Federal Agencies (DHS SWO, FEMA Ops, DHS NICC, and Nuclear SSA via email). * * * UPDATE AT 1718 EST ON 12/4/2013 FROM MATT KARL TO STEPHEN SANDIN * * * Correction to initial event report description; actual loss of electrical power time was 1341 CST. Include 8-HR Non-Emergency report for Specified System Actuation for automatic start of Auxiliary Feedwater and Emergency Diesel Generators. Notified the R4DO (Vasquez). * * * UPDATE FROM DAVE BUTLER TO JOHN SHOEMAKER AT 1840 EST ON 12/05/13 * * * Comanche Peak terminated from the Unusual Event at 1717 CST on 12/05/13. Offsite power has been restored to both safeguard busses on both units via the transformer XST2. Work continues on transformer XST1. Comanche Peak Units 1 and 2 continue to operate at 100% power. The licensee has notified the NRC Resident Inspector. Notified R4DO (Vasquez), NRR EO (Bahadur), IRD MOC (Gott), and DHS SWO, FEMA Ops, DHS NICC, and Nuclear SSA via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-12-04
49605 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-12-03 13:30 | 2013-12-03 20:04 | 2013-12-04 | LOSS OF EMERGENCY COMMUNICATIONS CAPABILITY- EP CONFERENCING LINES UNAVAILABLE "At approximately 1330 [EST] on Tuesday, December 03, 2013, while performing a table top drill, Pilgrim Nuclear Power Station (PNPS) discovered that EP [Emergency Preparedness] bridge conferencing lines were unavailable. The conference lines affected included the mitigation line, plant data phone, radiation data phone, emergency conferencing line, and the back up conference bridge line. Reviews to determine the cause of the event and efforts to restore the system are ongoing. "The licensee has determined the Emergency Plan to be functional based on other communication methods that are available between onsite and offsite facilities. These include direct telephone lines, portable handheld radios, satellite phones and cell phones. Immediate actions to establish compensatory conferencing lines have been completed. On-going actions are in-progress to ensure procedure instruction is provided at each facility to enable use of the compensatory conference lines. "At the time of this report, the plant is currently operating at 82% power due to a planned power maneuver unrelated to the reported communication event. "The licensee has notified the NRC Senior Resident Inspector [and will notify the Commonwealth of Massachusetts]. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of emergency response communication capability." * * * UPDATE AT 1718 EST ON 12/4/2013 FROM STAN PAUL TO MARK ABRAMOVITZ * * * The primary communications method has been restored. The backup communications method should be restored tomorrow. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Cook). | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-03
49604 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-12-03 10:22 | 2013-12-03 15:53 | 2013-12-03 | STACK RADIATION MONITOR NON-FUNCTIONAL FOR PRE-PLANNED MAINTENANCE The Millstone Station Stack Radiation Monitor, RM-8169, was removed from service at 1022 EST for pre-planned maintenance. At 1304 EST, the monitor was returned to service. The licensee informed the Connecticut Department of Environmental Protection, Waterford Dispatch and NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-03
49603 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-12-03 08:22 | 2013-12-03 12:30 | 2013-12-07 | REACTOR BUILDING STACK RADIATION MONITOR NON-FUNCTIONAL DUE TO SCHEDULED MAINTENANCE "During scheduled maintenance, at approximately 0822 PDT on December 3, 2013 the Reactor Building Stack Radiation Monitor - Intermediate Range detector was declared non-functional due to scheduled maintenance on supporting equipment. "To compensate for the loss of assessment capability due to the non-functioning radiation monitoring equipment, an additional Health Physics (HP) Technician trained to acquire offsite dose assessment information on offsite releases is available. The additional personnel are pre-staged in support of the radiation monitoring system outage and will be mobilized in accordance with guidance in the compensatory measure instructions. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). A follow up notification will be made when the equipment has been returned to service. "The licensee has notified the NRC Resident Inspector." The planned outage is scheduled for approximately 90 hours. * * *UPDATE PROVIDED BY DAVID HOLICK TO JEFF ROTTON AT 0652 EST ON 12/07/2013 * * * "At 2104 PST on 12/6/13, planned maintenance on the Reactor Building Stack Radiation Monitor - Intermediate Range detector was complete, the instrument was retested satisfactorily, and the instrument was declared functional. This restored the emergency assessment capability in accordance with 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." Notified the R4DO(Vasquez) and R1DO(Cook). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-03
49602 | 0 | MALLINCKRODT, INC |  |  |  |  | 2013-11-12 | 2013-12-03 11:50 | 2013-12-03 | MISSING DEPLETED URANIUM-238 SHIELDS Between October 2012 and May 2013, the two customers located in Ridgeland, SC and Tampa, FL shipped depleted shielded Tc-99m generators back to Mallinckrodt in Missouri using courier service companies. The Ridgeland, SC customer, Palmetto Isotopes, shipped three containers; one on 4/29/13 and two on 5/1/13 using the courier ACI. The Tampa, FL customer, West Coast Nuclear Pharmacy, shipped one container on 10/11/12 using the courier Medical Delivery Services. Mallinckrodt has no record of these shields being returned to their facility. Each container has 3.09 mCi of depleted U-238 as a shield. Mallinckrodt uses between 4000 - 5000 total containers to support their customer's needs. A container is declared missing after performing a complete inventory, contacting their customers to verify the Bill of Laden (BOL) information and contacting the couriers who conduct a search and provide a written response to Mallinckrodt. The typical turn-around time for the above is approximately 100 days. The serial numbers, i.e., DU tracking # on box and safe serial # stamped on shield, of the missing sources are as follows: Palmetto - DU tracking # 2185528, safe s/n 608, DU tracking # 2186644, safe s/n 930, DU tracking # 2189415, safe s/n 4947 West Coast Nuclear Pharmacy - DU tracking # 2178372, safe s/n 2146 The licensee contacted R3 (Lambert). This report is similar to EN #47106. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-12-11
49601 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2013-12-02 23:24 | 2013-12-03 04:05 | 2013-12-03 | TECH SPEC REQUIRED SHUTDOWN DUE TO DROPPED CONTROL ELEMENT ASSEMBLY "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "All times described are approximate Mountain Standard Time. "At 2324 on December 2, 2013, Palo Verde Nuclear Generating Station (PVNGS) Unit 3 commenced a reactor shutdown required by Technical Specification (TS) 3.1.5, Control Element Assembly (CEA) Alignment. TS Limiting Condition for Operation (LCO) 3.1.5, requires 'All full strength CEAs shall be OPERABLE, and all full strength and part strength CEAs shall be aligned to within 6.6 inches (indicated position) of all other CEAs in their respective groups.' "Regulating CEA number 69 dropped to the fully inserted position at 1830 on December 2, 2013, when the circuit breaker for CEA 69 tripped open. The other 88 CEAs in the reactor were unaffected and remained fully withdrawn. Unit 3 entered LCO 3.1.5 Condition A for one misaligned CEA and reduced power to 78% within one hour in accordance with Required Action A.1. "The CEA was unable to be restored to its required position within two hours in accordance with Required Action A.2 to restore CEA alignment. "At 2030, Unit 3 entered Condition C of LCO 3.1.5 because of the inability to restore CEA alignment. Condition C requires the unit to be in Mode 3 in 6 hours. "At 0033 on December 3, 2013 the Power Switch Assembly was replaced and tested satisfactorily. The shutdown was terminated at this time while at approximately 48% power. At 0039, Unit 3 began to withdraw CEA 69. CEA 69 was realigned with its group at 0143 and LCO 3.1.5 conditions A and C were exited. "The event did not result in the unplanned release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." | 0 | 0 | 48 | 0 | 0 | 78 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-12-03
49600 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2013-12-02 17:58 | 2013-12-02 23:26 | 2013-12-02 | AUTOMATIC REACTOR TRIP FOLLOWING THE LOSS OF THE 1A REACTOR COOLANT PUMP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On December 2, 2013, at approximately 1758 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station (PVNGS) Unit 2 control room received reactor protection system alarms for low departure from nucleate boiling ratio and an automatic reactor trip occurred. Prior to the reactor trip, Unit 2 was operating normally at 100% power. Plant operators entered the emergency operations procedures and diagnosed an uncomplicated reactor trip but noted the 1A reactor coolant pump (RCP) was not running. All CEAs fully inserted into the core. Following the reactor trip, indications on the train A logarithmic (log) power nuclear instrument initially responded normally but then did not trend as expected. All other nuclear instruments responded normally and the train A log power channel was declared inoperable and technical specification limiting conditions for operation 3.3.10 and 3.3.11 were entered. No emergency classification was required per the PVNGS Emergency Plan. "The Unit 2 safety related electrical busses remained energized from normal offsite power during the event. Due to planned maintenance on one switchyard breaker, the Ruud offsite power line was disconnected from the PVNGS switchyard when the Unit 2 main generator output breakers opened. There was no impact to the required circuits between the offsite transmission network and the onsite Class 1E Electrical Power Distribution System; the offsite power grid is stable. "No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 2 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. Preliminary information indicates the reactor trip resulted from an electrical protection trip of the power supply circuit breaker for the 1A RCP. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 2 reactor trip." There was no impact on either Unit 1 or Unit 3. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-12-02
49599 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-12-02 22:00 | 2013-12-02 22:01 | 2013-12-04 | TECHNICAL SUPPORT CENTER (TSC) NON-FUNCTIONAL DUE TO PLANNED MAINTENANCE "On December 2, 2013, activities are scheduled that will render the Technical Support Center (TSC) non-functional by removing the normal and emergency ventilation system from service. These activities are being performed in support of planned preventive maintenance. In preparation for these normal and emergency ventilation system outages, the TSC emergency responders were notified that if an emergency occurred during this outage the Emergency Coordinator and the TSC staff involved with classification, notification and PARS should report to the Work Execution Center. All other TSC personnel should report to the Operational Support Center. The duration of this TSC outage is expected to be less than 36 hours. The NRC Operations Center will be provided an update to this notification when the TSC normal and emergency ventilation is restored. This 8 hour notification in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee notified the NRC Resident Inspector." * * * UPDATE ON 12/4/13 AT 0440 FROM BRIAN LEWIN TO DONG PARK * * * The TSC is fully functional. The licensee will notify the NRC Resident Inspector. Notified R3DO (Riemer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-12-02
49598 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-12-02 | 2013-12-02 16:58 | 2013-12-02 | AGREEMENT STATE REPORT - CONTAMINATED PACKAGE RECEIVED DURING SHIPMENT The following information was received from the State of Tennessee via email: "Tennessee's Division of Radiological Health was notified on Monday, December 2, 2013, by the RSO of RbM Services, regarding a contaminated package containing a Bracco CardioGen-82 generator. At 8:30 a.m. EST, a wipe test revealed 2937 dpm on the package exterior. The contamination was removed and the package was opened. The generator itself was not leaking; no contamination was found. The package was shipped via [a common carrier] and the shipper was G.E. Healthcare. Both were notified. The truck and the driver were surveyed, no contamination was found. The isotope involved is not known at this time. The state will follow-up and keep NRC informed of the status of our investigation." Tennessee Report ID No.: TN-13-186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-12-10
49597 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-10-24 | 2013-12-02 16:58 | 2013-12-02 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE INVOLVING A RADQUAL FLEXIBLE RULER The following information was received from the State of Tennessee via email: "Tennessee's Division of Radiological Health was notified on Monday October 28, 2013 by the RSO from the University of Tennessee [UT] Knoxville, regarding the failure of a RadQual BM83-20 flexible ruler Co-57 source. In late October, a UT nuclear medicine technician put down the ruler source, and one of the rubber caps came off. This resulted in three of the metal sources inside coming out. The sources were not leaking and no radiation contamination occurred. It appeared as though the glue from the end caps had failed. The source contained 460 micro-Ci of Co-57. Manufacturer is International Isotopes Idaho, Inc., serial # BM8305710071101. The Radiation Safety Department collected the source to be disposed of in the future." Tennessee Report ID No.: TN-13-185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-12-10
49596 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-12-02 08:53 | 2013-12-02 16:52 | 2013-12-02 | FITNESS-FOR-DUTY - CONFIRMED POSITIVE TEST FOR ALCOHOL A non-licensed employee supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's unescorted access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 41 | 0 | 100 | 41 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2013-12-02
49595 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2013-09-24 08:00 | 2013-12-02 13:52 | 2013-12-02 | DEFICIENCY IDENTIFIED IN QUALITY ASSURANCE PROGRAM "This is a 10 CFR 50.55(e) initial notification for a significant breakdown in the Quality Assurance (QA) Program of Chicago Bridge & Iron (CB&I) Lake Charles facility, a sub-supplier of CB&I. CB&I Lake Charles supplies safety-related structural sub-modules for the Vogtle 3 & 4 construction project. "In September 2013, CB&I Lake Charles issued a root cause analysis report for deviations associated with sub-modules being supplied to domestic AP1000 construction projects. An evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10 CFR 50.55(e)(4)(iii) and 10 CFR 50.55(e)(5)(i)." The licensee will notify the NRC Resident Inspector. Reference similar Summer Event (EN#49582). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 50.55(e) |  |  |  | 0 | 2013-12-02
49594 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-11-29 19:40 | 2013-12-02 12:25 | 2013-12-02 | AGREEMENT STATE REPORT INVOLVING THE FAILURE OF AN IRRADIATOR SOURCE RACK TO FULLY LOWER The following information was received from the State of Texas via email: "On December 2, 2013, the Agency [Texas Department of State Health Services] received information from the licensee that on November 29, 2013, at 1940 hrs. CST, the drive mechanism on a Nordion JS-8900 (continuous) pool-type irradiator had failed to completely lower one of the source racks into the fully safe position at the bottom of the pool. Source rack one was completely lowered into the pool by venting the source hoist air cylinder. The licensee reported that the preliminary root cause seems to be debris in the air system which caused the solenoid to get stuck and prevented the source hoist piston from completely lowering the source rack. The solenoid valve spools were replaced, the source cycled several times, and normal operation continued. There were no exposures as a result of this incident. An investigation into this event is ongoing. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-12-10
49593 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-12-02 09:04 | 2013-12-02 11:03 | 2013-12-02 | MANUAL SCRAM FOLLOWING TRIP OF BOTH REACTOR RECIRCULATION PUMPS "At 0904 [EST] on Monday, December 2, 2013, Nine Mile Point Unit 2 was manually scrammed from approximately 40% thermal power due to the loss of both reactor recirculation pumps during a planned downpower evolution. Manual scram of the unit is procedurally required upon loss of both recirculation pumps to avoid potential power/flow oscillations. The reactor recirculation pumps failed to transfer to the low frequency motor generators when downshifted from fast speed. The cause of the loss of both reactor recirculation pumps is not known at this time. [Nine Mile Point Unit 2] NMP2 has commenced cooldown in preparation for the forced outage to investigate and commence repairs. "10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours of any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." All control rods fully inserted. No safety systems actuated. Decay heat is being removed via the main condenser. The "A" recirculation pump was restarted in low speed at 1045 EST. Unit 2 is in a normal shutdown electrical lineup. The licensee informed the NRC Resident Inspector and will inform the New York State Public Services Commission. | 0 | 0 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-12-02
49592 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-12-01 06:13 | 2013-12-01 10:02 | 2013-12-01 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "While operating at 100% power on 12/01/2013, at 0613 EST, the main turbine tripped on moisture separator hi level. The reactor scrammed along with the main turbine trip. All safety systems responded as designed and expected. There was no radiological release. There were no injuries." During the scram, all rods inserted into the core. The plant is stable in mode 3 in its normal shutdown electrical line up. Decay heat is being removed via the turbine bypass valves dumping steam to the main condenser. The licensee notified the NRC Resident Inspector and will be notifying Lower Alloways Creek township. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-12-01
49591 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-30 15:53 | 2013-11-30 22:43 | 2013-11-30 | HIGH PRESSURE COOLANT INJECTION SYSTEM SURVEILLANCE TEST FAILURE "At 1553 CST on November 30, 2013, during the performance of the High Pressure Coolant Injection (HPCI) fast initiation test, HPCI did not produce the required flow rate as specified by Technical Specification Surveillance Requirement 3.5.1.6. The HPCI subsystem is designed to ensure adequate core cooling when operated with other available Emergency Core Cooling Systems (ECCS), and during this event, all other ECCS systems remained operable. The cause of this event is currently under investigation. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. "The NRC Resident Inspector has been notified." The flow rate achieved during the test was 3000 gpm and the required minimum flow rate is 5000 gpm. | 0 | 16 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-11-30
49590 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-28 02:58 | 2013-11-28 10:56 | 2013-11-28 | SECONDARY CONTAINMENT DECLARED INOPERABLE WHILE TWO SECONDARY CONTAINMENT DOORS WERE SIMULTANEOUSLY OPEN "At 0258 CST on November 28, 2013, two individuals were removing materials from the main steam isolation valve room (X-Area) and defeated an interlock which allowed them to open two secondary containment doors simultaneously. The X-Area personnel access doors connect secondary containment to the turbine building and are part of the secondary containment boundary. "At the time of this event, Dresden Unit 2 was in Mode 4 and secondary containment was not required. However, Dresden Unit 3 was in Mode 1 which requires secondary containment to be operable. Throughout this event, secondary containment differential pressure was maintained within technical specifications surveillance requirement 3.6.4.1.1 limits, and the individuals remained in the area with the capability to close the personnel access doors. "This condition represents a failure to meet surveillance requirement 3.6.4.1.2, since both doors in a singular access opening were allowed to open. As a result, entry into technical specification 3.6.4.1 condition A was made, for Unit 3, due to secondary containment being inoperable. The doors were secured at 0311 and secondary containment was declared operable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of the safety function. "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-28
49589 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2013-11-27 14:46 | 2013-11-27 18:14 | 2013-11-27 | NON-OCCUPATIONAL DEATH ON-SITE "At approximately 1446 hours (CST) on November 27, 2013 a badged employee was discovered non-responsive inside a vehicle within the Owner Controlled Area. [The vehicle was located outside the protected area and in the parking lot]. On-site and off-site emergency personnel responded to the medical issue. The individual was pronounced dead at 1604 hours. No radioactive material or contamination was involved. The death was not work-related nor the result of an occupational event. "This event is being reported under 10CFR50.72(b)(2)(xi). "The NRC Resident lnspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-11-27
49588 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-11-27 10:01 | 2013-11-27 14:58 | 2013-11-27 | UNIT 1 REACTOR BUILDING SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE OUT OF SPECIFICATION "On November 27, 2013 at 1001 [EST], Susquehanna Steam Electric Station operators observed secondary containment differential pressure was at 0.04 inches water gauge for Zone I (Unit 1 Reactor Building). Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. Zone II (Unit 2 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone I differential pressure was impacted due to equipment malfunction. The inservice reactor building exhaust fan discharge damper developed an air leak at the solenoid operator. Zone 1 Building D/P was restored to within the required band at 1111 [EST] by placing the standby train exhaust fan, which was out of service for maintenance, in operation and verified to be stable. LCO 3.6.4.1 was entered for both units at 1001 [EST] and exited at 1131 [EST]. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The NRC Resident Inspector has been informed. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-27
49587 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-10-30 | 2013-11-27 10:58 | 2013-11-27 | AGREEMENT STATE REPORT - RADIOACTIVE SEED INCORRECTLY PLACED ON PATIENT The following information was received by facsimile: "Reported to NYS DOH [New York State Department of Health] on 11/12/2013. A patient received two seeds for right breast radioactive seed localization when only one was intended. The patient had two marker clips, a cylinder clip marking a benign biopsy site and a coil clip marking a papilloma. It was intended for her to only receive one seed placed at the papilloma site, but the benign site was marked with a 0.252 mCi iodine-125 seed. A second seed (0.251 mCi) was then placed to mark the correct site. The unintended dose from the 0.252 mCi seed in place for 2 days was 0.61 Gy @ 0.5 cm. Root cause analysis is ongoing." Event Report Identification Number: NY-13-06 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-12-05
49586 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-11-27 07:40 | 2013-11-27 08:40 | 2013-11-27 | SERVICE WATER RADIATION MONITOR REMOVED FROM SERVICE "Planned preventative maintenance on service water piping will remove the service water radiation monitor from service. This represents a loss of emergency assessment capability under NUREG-1022, revision 3, specific to RU1.1, RU1.2, RA1.1, and RA1.2. The planned maintenance is expected to last eight hours. "The NRC Resident Inspector was notified prior to removing the service water radiation monitor from service." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-27
49585 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-26 14:00 | 2013-11-26 19:02 | 2013-11-26 | LEAKAGE DISCOVERED ON ELECTROMATIC RELIEF VALVE DURING HYDROSTATIC TESTING "On November 26, 2013, with Unit 2 shutdown for refueling, leakage was identified on the 2-0203-3C Electromatic Relief Valve (ERV) during a Reactor Pressure Vessel (RPV) pressure test. The leak is located on the line connecting the ERV main body to the pilot valve, and is approximately 1 drop per second. Each unit is designed with relief valves which actuate to control reactor coolant system pressure during transient conditions and are located on the main steam lines between the reactor vessel and the first isolation valve within the drywell. The cause of this event is under investigation. "The condition is being reported under 50.72(b)(3)(ii)(A) given the defect was associated with the primary coolant system pressure boundary. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-11-26
49584 | 0 | HARRISON STEEL CASTINGS |  |  |  |  | 2013-11-25 19:00 | 2013-11-26 16:00 | 2013-11-27 | RADIOGRAPHY CAMERA LOCKING MECHANISM FAILURE After the licensee completed an exposure and was retracting the source, the radiographer noticed that he did not hear the click of the posi-lock. The radiographer finished retracting the source using the hand crank. The radiographer then entered the room using a radiac to ensure the source was in the safe position. He found that the spring for the posi-lock had broken. He manually locked the source in the camera and took it out of service. The licensee will send the camera to the manufacturer for repair. There were no overexposures to personnel as a result of this event. * * * UPDATE AT 1043 ON 11/27/2013 FROM DAVE HOLLANDER TO MARK ABRAMOVITZ * * * The projector (camera) is an Amersham 680BE, S/N BE132. Notified the R3DO (Peterson) and FSME Event Resources via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-12-05
49583 | 0 | AMERICAN ELECTRIC POWER |  |  |  |  | 2013-11-26 12:00 | 2013-11-26 14:27 | 2013-11-26 | PROCESS GAUGE SHUTTER CABLE FAILURE The cable used to remotely operate the shutter for a fixed process gauge broke. The gauge is installed in a location that is not readily accessible by personnel. The normal position for the gauge is open. The gauge is currently open and in use. The licensee can manually close the shutter if needed. There were no personnel exposures. The licensee has contacted the manufacturer to repair the cable. The gauge is a Termo MeasureTech Model 5202, Serial Number B2813, containing 200 mCi of Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-12-05
49582 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-09-24 08:00 | 2013-11-26 13:44 | 2013-11-26 | DEFICIENCY IDENTIFIED IN QUALITY ASSURANCE PROGRAM "This is a 10 CFR 50.55(e) initial notification for a significant breakdown in the Quality Assurance (QA) program of Chicago Bridge & Iron (CB&I) Lake Charles facility, a sub-supplier of CB&I. CB&I Lake Charles supplies safety-related structural sub modules for the Virgil C. Summer Units 2 & 3 construction project. "In September 2013, CB&I Lake Charles issued a root cause analysis report for deviations associated with sub-modules being supplied to domestic AP1000 construction projects. An evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10 CFR 50.55(e)(4)(iii) and 10 CFR 50.55(e)(5)(i)." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 50.55(e) |  |  |  | 0 | 2013-11-26
49581 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2013-11-07 | 2013-11-26 12:20 | 2013-11-26 | PART 21 REPORT - IMPROPER DEDICATION OF ACTUATOR PARTS The following information was received via fax: Equipment affected by this information notice: Items subject to this Fisher Information Notice (FIN) were provided to Westinghouse Electric Company, LLC (WEC) via Fisher Order Number 004-X012140579, Items 25, 25A, 25B, and 25C (Westinghouse PO# 4500280610). The valves included Type 657NS2 Size 80 Actuators (Equipment). The equipment is identified by Fisher Serial Numbers 19073487, 19073488, 19073489, and 19073490 (Westinghouse Tag Numbers APP-PXS-PL-V014A, APP-PXS-PL-V014B, APP-PXS-PL-V015A, and APP-PXS-PL-V015B). Purpose: The purpose of this FIN is to alert WEC that as of 07 November 2013, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the performance of the Equipment, including their safety-related function. Fisher is informing WEC of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21. Applicability: This FIN applies only to the subject equipment supplied by Fisher to WEC via the aforementioned order. Discussion: Fisher has determined that the subject valves were provided with actuator parts that had not been properly processed per active valve requirements. Specifically, Fisher provided commercial grade parts instead of commercial grade dedicated items. The parts are identified per Fisher Type III drawing GE40372, find numbers 118, 121, and 122. Action Required: Fisher will support WEC in performing the disassembly and replacement of these parts, at no cost to WEC, on the installed actuators. Arrangements will be made with WEC to retrofit the correctly processed and dedicated parts on the subject serial numbers. In addition, a Corrective Action Request (CAR 1661) has been initiated by Fisher to prevent reoccurrence of this issue. 10 CFR 21 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions or concerns, please contact: George Baitinger Manager, Quality Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Fax: (641) 754-2854 Phone: (641) 754-2026 George.Baitinger@Emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-11-26
49580 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-11-26 04:00 | 2013-11-26 05:08 | 2013-11-26 | DISCHARGE CANAL RADIATION MONITOR REMOVED FROM SERVICE "Planned preventative maintenance on the discharge canal piping will remove the discharge canal radiation monitor from service. This represents a loss of emergency assessment capability under NUREG-1022, revision 3, specific to RU1.1, RU1.2, RA1.1, and RA1.2. The planned maintenance is expected to last 13 hours. "The NRC Senior Resident Inspector was notified [by the licensee] prior to removing the discharge canal radiation monitor from service." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-26
49579 | 0 | ABB INC |  |  |  |  | 2013-11-25 | 2013-11-25 14:52 | 2013-12-18 | PART 21 REPORT - PRIMARY CLOSE LATCH FAILED TO MEET SPECIFICATION IN K-LINE CIRCUIT BREAKERS The following is a summary of a fax received from ABB Inc.: "[ABB Inc. is reporting a] failure to comply with specifications associated with primary close latch, part number 716611K02, used in K-Line 225 to 2000 amp continuous current low voltage electrically operated Model 7 circuit breakers. It does not affect previous models of these same breakers that have not been upgraded to include the interlocking primary and secondary close latches. It does not affect manually operated K-Line breakers or K3000/4000 circuit breakers." * * * UPDATE FROM JAY LAVRINC TO JOHN SHOEMAKER ON 12/18/13 AT 1324 EST * * * The following report was received via facsimile: This is an amended report to identify the affected customers and complete the one outstanding action from the Part 21 Notification of 11/25/2013. Affected customers are: APS, Detroit Edison, Dominion, Duke Energy Progress, Entergy, Exelon, Crystal River and Nextera. Notified R1DO (Dimitriadis), R2DO (Freeman), R3DO (Riemer), R4DO (Lantz), and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-11-25
49578 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-11-22 | 2013-11-25 14:48 | 2013-12-27 | AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK INVOLVED IN ACCIDENT "On November 22, 2013, the Agency [Texas Department of State Health Services] received information from the Odessa, Texas, Emergency Management that an accident involving an industrial radiography truck carrying two radiography cameras had occurred near Andrews, Texas. The Agency contacted the licensee and they reported that the driver had hit a patch of ice on the road, lost control, and the truck turned over. Both of the cameras remained secured inside the transportation box in the truck's darkroom. Another of the licensee's radiographers was following the truck and maintained control of the cameras until the licensee's staff came from Midland to pick them up. There were no exposures to any individual as a result of this event. "On November 25, 2013, an Agency investigator learned from the licensee that the driver had been taken by ambulance to a local hospital's emergency department following the accident. The driver was examined and released after approximately 5 hours. More information will be provided as it obtained in accordance with SA-300." Texas Incident Number: I-9138 * * * UPDATE FROM ARTHUR TUCKER TO JOHN SHOEMAKER ON 12/27/13 AT 0815 CST * * * The following Agreement State Report update was received via email; "The following information was provided to the Agency [Texas Department of State Health Services] by the licensee. It provides additional information regarding the event and stated the cameras did not remain in the transport container throughout the event as previously reported. "On, November 22, 2013, the licensee was transporting two radiography exposure devices from Midland, Texas to La Porte, Texas. The devices were stored in a transport container in one vehicle and a second vehicle was following the transport vehicle. Near Andrews, Texas the transport vehicle hit a patch of ice on the road causing the driver to lose control of the vehicle. The vehicle rolled five times before stopping in the upright position. The darkroom stayed attached to the truck until the last rollover, it then became free from the truck and the exposure devices were dislodged from the transport box. The driver of the second vehicle provided aid to the driver of the transport vehicle until the state police arrived. The driver of the second vehicle then performed an area survey and monitored the exposure devices. He stated dose rates were normal and he did not observe any damage to either exposure device. The exposure devices did not create an exposure risk to any individual. The driver of the transport vehicle was transported to the hospital by ambulance where he was released later that evening. The licensee's Radiation Safety Officer (RSO) contacted the licensee's Midland office and had them send a crew to take possession of the exposure devices. The devices were leak tested and the results were below the limit. The exposure devices were stored at the licensee's Midland location over the Thanksgiving Holiday and later transported to the manufacturer for further inspection. The manufacturer leak tested the devices and the sources and no contamination was detected. The manufacturer performed a thorough inspection of the devices and did not identify any damage to either device. The manufacturer returned the devices to the licensee for continued use. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Whitten) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-12-03
49577 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-11-25 | 2013-11-25 13:53 | 2013-11-25 | AGREEMENT STATE REPORT - MEMBER OF PUBLIC EXPOSURE EXCEEDING LIMITS The following was received from the Commonwealth of Virginia via email: "An individual (non-radiation worker) performing a pipe inspection on a Norfolk Dredging barge received a dose from a Vega America Model SR-2 fixed gauge source while crawling through the pipe. Initial dose estimates to the individual are that he received 146 mrem. Norfolk Dredging sent an e-mail to the Virginia Radioactive Materials Program on Saturday the 23rd and discussions were held on Monday the 25th. Norfolk Dredging is working on an event report to submit, and the RMP will perform an investigation with the licensee. Virginia is providing the event report as the barge is home based in Virginia and is registered as a General License. The barge was operating at a temporary jobsite in New York. The New York State Program and NRC Region 1 was notified of the event." Virginia Report Number: VA-13-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-12-03
49576 | 0 | CB&I LAKE CHARLES |  |  |  |  | 2013-02-08 | 2013-11-24 18:23 | 2013-11-24 | INTERIM PART 21 REPORT REGARDING DEVIATIONS OF SUPPLIED MATERIALS FOR MODULE ASSEMBLY The following is a summary of a fax updating a report initially submitted to the Document Control Desk on February 8, 2013: "CBI Lake Charles (CBI-LC) provided an interim report to the NRC regarding the ongoing 10 CFR Part 21 evaluation that could not be completed within 60-days from discovery of the deviation. This deviation is related to Mechanical Splices delivered to AP1000 Projects, Vogtle Unit 3 and V.C. Summer Unit 2. "CBI-LC executed the test plan and submitted the results to the Design Authority for evaluation. The 'Use-As-Is' disposition by the design authority was contingent upon additional qualification testing performed by the manufacturer. During the review of the testing by the manufacturer, there were some minor administrative errors identified. Therefore, upon the Design Authority approval of these minor error corrections, the evaluation to determine if this deviation is reportable per Part 21.21, could not be completed with the 60-days. Hence, this updated interim report is being provided. CBI Lake Charles expects the Design Authority approval of the test results by January 31, 2014." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-11-24
49575 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2013-11-24 00:01 | 2013-11-24 02:54 | 2013-11-24 | MOMENTARY LOSS OF REACTOR BUILDING VENTILATION "On 11/24/2013 at 00:00:54 seconds [EST], Reactor Building ventilation tripped due to low outside air temperature. At 00:01:42 seconds, Secondary Containment Differential pressure went positive, with a maximum of +0.08 inches WC [water column]. This is a loss of Secondary Containment function. At 00:02:30 seconds, Standby Gas Treatment System was started and Secondary Containment pressure then decreased to <0 inches WC at 00:03:18 seconds. All the above data parameters were taken from the Division 2 Reactor Building Differential pressure recorder. "Secondary Containment pressure is stable with differential pressure negative <-0.30 inches WC. "The loss of Secondary Containment function is reportable under 10CFR 50.72(b)(3)(v)(c) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material." Technical Specification requirement are to maintain secondary containment pressure <-0.125 WC. No actual radiation release occurred during the event. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-24
49574 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2013-11-22 19:20 | 2013-11-22 23:59 | 2013-11-23 | CONTROL ROOM HVAC INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. While the 'A' Train of Control Room HVAC was inoperable and out of service for emergent repairs due to a Freon leak, the 'B' Train of Auxiliary Electric Room HVAC became inoperable due to a failure of the Cooler Condenser Fan. The Main Control Room Envelope consists of the Main Control Room and the Auxiliary Electric Equipment Room. Both the Control Room HVAC and the Auxiliary Electric Equipment Room HVAC Systems are required to be Operable in the current Mode. "This is a loss of safety function for a system that is intended to mitigate the consequences of an accident and is discussed in Chapter 6 of the UFSAR and is Tech Spec required and is Safety Related. Also, the system, structure, or component (SSC) is inoperable in a required mode in the Tech Spec Applicability and there is no redundant equipment in the same system that is operable. "The Required actions of Tech Spec 3.7.5 were entered on 11/22/2013 at 1920 CST when the 'B' train became inoperable. Online Risk remains Green. The station is currently pursuing repairs to both trains." The NRC Resident Inspector has been notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-11-23
49573 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2013-11-21 15:45 | 2013-11-22 15:18 | 2013-11-22 | FITNESS FOR DUTY - BLIND SAMPLE RECOGNITION FAILURE "On November 21, 2013 during an Access Authorization Fitness for Duty (FFD) Baseline Inspection, an NRC Inspector identified laboratory testing of a Blind FFD sample failed to provide anticipated testing results. Laboratory testing results for sample (specimen number 422136066) should have reported the sample as 'Dilute' but the laboratory report results came back as 'Negative.' In addition, the specific gravity of the sample was also outside the expected range. It should have been reported at or near 1.0015 but was reported at 1.0224 instead. The sample was submitted on March 3, 2013. "The results error was not identified when the results were received which caused a violation of 10CFR26. "An investigation with the laboratory has been initiated through the Medical Review Officer for IPEC [Indian Point Energy Center]. "Additionally an investigation with the vendor supplier of the Blind sample will be initiated. "The corrective action for this event is that an extent of condition is being performed to verify that no other Blind errors exist." The licensee notified the NRC Resident Inspector and will be notifying New York State Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2013-11-22
49572 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-11-20 | 2013-11-22 14:40 | 2013-11-22 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following information was received from the State of Texas via email: "On November 22, 2013, the Agency [Texas Department of State Health Services] was notified by the licensee that on November 20, 2013, one of their crews performing radiography work was unable to retract the iridium-192 source into a QSA 880D camera. The radiography crew was performing radiography work on a job that required the use of an extension tube sold by the manufacturer for use with the guide tube. On the fifth of five shots, the source was cranked out of the camera, but when they attempted to retract it, it would not move. The radiographers contacted the licensee's Radiation Safety Officer who responded to the location. The RSO attempted to retract the source and he could not get the source to move. The source was stuck inside the collimator. The RSO dismantled the crank out device and pulled on the drive cable to move the source, but it would not move. The RSO removed the guide tube from its location and placed it on the grating of the platform they were working from. The source was covered with lead to reduce exposures. The barricade was extended and other licensee personnel who were also working at the plant were used to control access to the area. The RSO removed the drive cable housing from the back of the camera and attempted to pull on the cable and retract the source. It did not move. The RSO stated he inspected the locking device and it appeared to be fine. The RSO loosened the clamp that was being used to hold the guide tube extension in place while they were shooting. The source could then be retracted and was returned to the fully shielded position. The RSO believes that over time the extension guide tube walls had weakened and collapsed to a point where the source/drive cable could not pass through it. The RSO stated no one had exceeded any limits. He stated his 0-200 millirem self-reading dosimeter (SRD) had gone off scale, but his assistant's SRD only read 140 millirem. The RSO stated he would send both his and his assistant's dosimetry to their processors for reading. No other individuals received any exposure due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-12-02
49571 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-11-21 16:41 | 2013-11-21 21:41 | 2013-11-21 | LOW CASING COOLING SYSTEM TANK LEVEL POTENTIALLY CAUSES LOSS OF NPSH TO OUTSIDE RECIRCULATION SPRAY PUMPS "The Casing Cooling system at North Anna Power Station (NAPS) Units 1 and 2 provides cold, borated water to the suction of the Outside Recirculation Spray (ORS) pumps to increase net positive suction head (NPSH) following the initiation of a Containment Depressurization Actuation (CDA). As Casing Cooling tank level decreases to the isolation setpoint, it has been determined that vortexing/air entrainment may occur. This air would then enter the suction of the ORS pumps and potentially cause degradation in design flow and/or loss of NPSH. As a result, this constitutes an event or condition that could have prevented fulfillment of a safety function and is reportable per 50.72(b)(3)(v). A prompt operability determination is in progress that should restore the function of the recirculation spray system. "The licensee has notified the NRC Resident Inspector." The licensee will be notifying the Louisa County Administration in the morning. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-11-21
49570 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-11-21 17:37 | 2013-11-21 20:30 | 2013-11-21 | OFFSITE NOTIFICATION TO NJDEP CONCERNING A SMALL SODIUM HYPOCHLORITE SPILL "Today, November 21, 2013, at approximately 1737 EST, the New Jersey Department of Environmental Protection [NJDEP] was notified that an indeterminate amount (less than 1 gallon) of sodium hypochlorite was spilled onto the lands of the State of New Jersey. The spill has been contained and cleaned-up. There was no actual or potential impact on the environment and no impact on the health and safety of the public or onsite personnel. "The spill did not reach the federal reportable quantities limit. "Due to notification of a government agency, this event is being reported under 10CFR50.72 (b)(2)(xi)." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-11-21
49569 | -1 | COLUMBIANA HI TECH, LLC |  |  |  |  | 2013-11-14 | 2013-11-21 16:23 | 2014-01-09 | PART 21 REPORT REGARDING IDENTIFIED DISCREPANCY WITH INDIVIDUAL NDT LEVEL II CERTIFICATION Received the following information was obtained via fax: "Columbiana HI Tech, LLC is performing an evaluation to determine a potentially reportable condition per 10 CFR Part 21 requirements. Description of Noncompliance: A review of NDE certifications revealed discrepant training and work experience records from previous employment provided by a Columbiana HI Tech, LLC employee at the time of certification. This condition was first discovered on 11/14/13. The employee was certified under the Columbiana HI Tech, LLC Qualification & Certification of Nondestructive Examination Personnel Procedure passing all written and practical examinations required for Visual (VT) and Liquid Penetrant (PT) Inspection methods. The discrepant experience and training records from a previous employer were used to help fulfill the training and experience requirements for certification. "Items affected: Columbiana Hi Tech, LLC Licensed components: Package USA/9196/B(U)F-96; certification number 9196 Rev. 26 UX-30 Overpack. A list of units affected will be compiled. "Columbiana HI Tech, LLC CUSTOMER components: A list of components manufactured and inspected during the effected time is being reviewed to allow CUSTOMER Notification. Full disclosure will be made to all effected customers as soon as identified and within the reporting requirements of 10 CFR Part 21." * * * RETRACTION - FROM LARRY WALKER TO GEROND GEORGE AT 1812 EST ON 01/09/2014 * * * "Columbiana Hi Tech, LLC has concluded that the extent of the issue associated with this inspector is limited to his certification and did not negatively impact his competency for performance of Nondestructive Examination. "Columbiana Hi Tech has determined this is not a reportable condition per 10 [CFR] Part 21." Notified R2DO(Hopper), Part 21 Group, and NMSS EO(Silva) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-11-21
49568 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2013-11-20 11:25 | 2013-11-21 14:47 | 2013-11-21 | AGREEMENT STATE REPORT - TROXLER GAUGE INVOLVED IN A FIRE The State of Florida received a call from their licensee regarding a pick-up truck fire with a soil moisture density gauge in the back. On 11/20/13 at approximately 11:25 am EST on I-95 southbound near mile marker 169, a 2002 Ford F150 owned by the licensee caught fire. The exact cause of the fire is unknown. The fire spread so quickly, the licensee was unable to remove the Troxler Model 3440 portable density gauge (S/N: 77-4969) from the truck bed. The licensee notified emergency responders who arrived within 15 minutes and extinguished the fire. The gauge transportation container was damaged in the fire but there was no breach. The licensee RSO responded to the scene to conduct surveys. All surveys of the area were at or near background levels. Surveys of the gauge container and gauge were normal. The gauge itself showed no signs of damage from the fire. The licensee plans on installing the gauge into a spare transportation container to return it to the manufacturer for inspection and repair if necessary. The licensee will instruct employees to avoid driving through high grass and underbrush to avoid a similar incident in the future. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-11-29
49567 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-04-17 | 2013-11-21 14:26 | 2013-11-21 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the State of Texas via email: "On December 2, 2011, the Agency [State of Texas] was notified by a facility owner that the licensee had abandoned what appeared to be Troxler Model 3430 moisture/density gauges in the building. Initial investigation revealed that the license had been revoked by the Agency for nonpayment. The Agency impounded 5 Troxler moisture/density gauges that were at the facility and conducted an on-site investigation. The investigation indicated there was one more gauge that had not been accounted for. The Agency contacted the individual who had been the last Radiation Safety Officer of record. During the investigation he was asked to contact anyone who had worked for the licensee that might have knowledge about the gauge. He responded that he had made contact with several former employees and a former partner and they told him the all of the gauges were in the storage area to their knowledge. The Agency contacted the manufacturer and two gauge service companies in the area. None of them had serviced the gauge recently and they agreed to mark their records to notify the Agency if the gauge came in for servicing. There was no information or evidence that the gauge had been legally sold or transferred. Investigation was closed on 04/17/2012 when gauge was determined lost/missing/stolen. During a record review on 11/14/2013 it was discovered that the event had not been previously reported in accordance with SA-300. The event was reported at that time through the NMED (TX130045). When the file was being processed on 11/21/2013, questions arose as to whether or not an exposure could result to persons in unrestricted areas. The gauges impounded by the Agency were examined and it was discovered that the source rods on the gauges were not locked to prevent the sources from being exposed. Based on that information, it was determined that there was a possibility that an exposure could result to persons in unrestricted areas." Troxler Model number 3430; Serial number 34552; 8 mCi Cs-137,40 mCi Am-241 Texas Incident #: I-8908 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-11-29
49566 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-11-21 02:29 | 2013-11-21 10:38 | 2014-08-28 | DIESEL GENERATOR INOPERABILITY "Following preplanned maintenance on the inoperable 'A' Standby Diesel Generator (SBDG), the operability surveillance (STP-3.8.1-04A Slow Start from Normal Air) was in progress. While securing the 'A' SBDG, the 'B' SBDG control power failure annunciator was received. "The 'B' Standby Diesel Generator was declared inoperable and Technical Specification 3.8.1.B was entered for the 'B' SBDG. Additionally, Technical Specification 3.8.1.D was entered for two Standby Diesel Generators inoperable. Technical Specification 3.8.1.D allows 2 hours to restore 1 SBDG to operable. "At 0343 [CST], the 'A' SBDG was restored to operable and Technical Specification 3.8.1.D was exited. "This condition is reported under 50.72(b)(3)(v)(D), any event or condition at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The NRC Resident Inspector was informed." * * * RETRACTION FROM BOB MURRELL TO DONALD NORWOOD AT 1348 EDT ON 8/28/2014 * * * "The purpose of this notification is to retract a previous report made on 11/21/2013 at 1038 EST (EN 49566). Notification of the event to the NRC was initially made as a result of declaring both trains of the Emergency Diesel Generator (EDG) System inoperable due to receiving the 'B' EDG control power failure annunciator while the 'A' EDG was inoperable for pre-planned maintenance. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the 'B' EDG system was capable of performing its safety function and was fully operable, but degraded during the period that the 'A' EDG was inoperable for pre-planned maintenance. The cause of the annunciator was from an open fuse in the control power circuit that affected the annunciator system logic and did not affect the actual EDG control logic. "This event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Senior Resident Inspector has been notified." Notified R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-11-21
49565 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2103-11-20 22:40 | 2013-11-21 04:23 | 2013-11-21 | SECONDARY CONTAINMENT FAILS DRAWDOWN SURVEILLANCE TESTING "On November 20, 2013 at 2240 [EST], secondary containment drawndown testing surveillance failed to meet acceptance criteria SR 3.6.4.1.5 due to maximum flow rate exceeding the allowable value. "SSES [Susquehanna Steam Electric Station] previously entered SR 3.0.3 at 0900 on 11/15/2013 due to not meeting SR 3.6.4.1.4 and SR 3.6.4.1.5 because of an untested alignment of the 101 bay with ventilation aligned as a no zone during past performances of the drawdown testing surveillance. The surveillance being performed on 11/20/2013 was testing this previously unsurveilled alignment. "Upon failure of the surveillance, secondary containment ventilation was realigned to the previously tested 818 hatch alignment. "Upon restoration of secondary containment ventilation to a known operable alignment, secondary containment LCO 3.6.4.1 was cleared and operability restored. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has placed administrative controls on the 101 bay doors to prevent loss of secondary containment during the investigation to determine the reason for the surveillance test failure. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-21
49564 | 0 | INDUSTRIAL NUCLEAR CO. INC. |  |  |  |  | 2013-11-20 09:30 | 2013-11-20 18:08 | 2013-11-20 | SAFEGUARDS REPORT INVOLVING POTENTIAL LOSS OF SAFEGUARDS INFORMATION The licensee determined that they lost control of Safeguards Information during an internal office relocation. Contact the HOO for additional information.. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | TX | OTH | GEN | 73.71(b)(1) |  |  |  | 1 | 2013-11-20
49562 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-11-20 14:19 | 2013-11-20 16:19 | 2013-11-20 | SECONDARY CONTAINMENT BOUNDARY NOT MAINTAINED "System affected: Secondary Containment Boundary / SLCRS [Supplementary Leak Collection and Release Systems] "Causes: Door in secondary containment boundary found not latched. "Effect of Event on Plant: No impact on the plant as SLCRS was not required for the duration that the door was not functional. "Actions Taken or Planned: Door is now closed and latched. Will repair degraded latch." This condition was identified around 1100 EST on 11/19/13. The NRC Resident Inspector has been notified. State and local authorities were notified by the licensee. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-11-20
49561 | 0 | CITY OF DETROIT |  |  |  |  | 2013-11-19 | 2013-11-20 12:05 | 2013-11-25 | MISSING GENERAL LICENSED MATERIAL The City of Detroit is missing an unknown number of gauges containing Cd-109. The licensee has notified R3 (Kulzer). * * * UPDATE AT 1035 EST ON 11/25/2013 FROM ED KULZER TO MARK ABRAMOVITZ * * * The missing gauges' function was to check for lead in paint. The 13 missing sources were in Niton model 309 detectors with an aggregate activity of 247 mCi of Cd-109. Four of the sources contained 50 mCi and the remaining nine contained a total of 47 mCi. The sources were last known to be in the Herman Kiefer Health Complex, 1151 Taylor Street, Detroit, MI. Notified the R3DO (Hills), ILTAB (Whitney), FSME Event Resources, and Canada. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-11-28
49560 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-11-19 | 2013-11-20 12:07 | 2013-11-20 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was obtained from the State of Texas via email: "On November 20, 2013, the Agency [Texas Department of State Health Services] was notified by the licensee that on November 19, 2013, a source disconnect had occurred at a temporary field site. The licensee stated a crew had performed their first exposure of the day using a 91 curie cobalt - 60 source in a SPEC 300 exposure device. The radiographer attempted to retract the source into the exposure device, but noted the exposure rate on their dose rate meter was still reading the same as when the source was exposed and the camera lock failed to trip. The radiographers contacted the licensee's Radiation Safety Officer who responded to the location. The radiographers were working in a remote area of the facility and the boundaries initially set were adequate to prevent any exposures to other personnel at the facility. The RSO stated the source was located in the collimator. The RSO and a second individual approved for source recovery was able to recover the source. The RSO stated that their inspection of the device found the spring on the source pig tail appeared to have weakened and failed to close the connector in one of three test operations after the source recovery. The radiographers stated they challenged the connection prior to cranking the source out. The source and exposure device were returned to the manufacturer for inspection and repair. No over exposures occurred as a result of the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-11-28
49559 | 0 | SABIC INNOVATIVE PLASTICS |  |  |  |  | 2013-11-20 | 2013-11-20 10:58 | 2013-11-20 | GAUGE SHUTTER STUCK OPEN The licensee reported a shutter stuck in the open position on a gauge used for measuring level on a chemical reactor vessel. The shutter is in its normal operational position and presents no danger to personnel. The malfunctioning device is a Texas Nuclear Model 5195 gauge (serial # B-67) and contains 26 milliCuries of Cesium 137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-11-20
49558 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-11-19 13:41 | 2013-11-19 15:57 | 2013-11-19 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "The Unit 2 High Range Stack Radmonitor, RM-8168 is removed from service for preplanned maintenance. This is reportable as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). RM-8168 was restored to fully functional at 1456 EST." The NRC Resident Inspector has been notified. State and local authorities were notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-19
49557 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-11-19 04:20 | 2013-11-19 08:29 | 2013-11-19 | TECHNICAL SUPPORT CENTER EMERGENCY BACKUP POWER SUPPLY MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will remove the emergency power supply to the TSC from service. The TSC would be rendered non-functional with the loss of normal power. The repair to the power supply is expected to last 1 day. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be expedited to restore the emergency power supply to service. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC emergency power supply has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM TERRY BRANDT TO DONG PARK AT 1653 EDT ON 11/19/13 * * * "The emergency power has been returned to service to the TSC." The licensee has notified the NRC Resident Inspector. Notified R3DO (Hills). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-19
49556 | 0 | CARDINAL ATC |  |  |  |  | 2013-11-18 17:30 | 2013-11-19 06:41 | 2013-11-19 | STOLEN MOISTURE DENSITY GAUGE On 11/18/13, at about 1730 EST, a licensee truck carrying a Troxler model # 3411-B (serial #15760) moisture density gauge was stolen. This gauge has an 8 milliCurie Cs-137 source and a 40 milliCurie Am:Be source. The RSO reported that the gauge was properly secured in its case and properly secured to the vehicle. A report has been filed with the Indianapolis Metropolitan Police Department. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-11-27
49555 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2013-11-14 15:47 | 2013-11-18 18:05 | 2013-11-18 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following was received via facsimile from the Utah Division of Radiation Control: "The Operations Manager of Hales Sand and Gravel reported to the Division of Radiation Control that one of the licensee's gauge operators was at a temporary job site to perform soil moisture density measurements on November 14, 2013. After taking a moisture density measurement, the gauge operator left the gauge sitting on the ground while he walked away to talk to the roller operator. The gauge was left in the backing up path of Hales Sand Gravel's grader (heavy equipment) and was run over. "After everyone was cleared out of the area, the Radiation Safety Officer of Jones & Demille Engineering was contacted to provide a survey instrument. At the time of the incident the radioactive sources were in the safe shielded position. After the gauge was run over, the gauge was broken into two pieces; the source rod was separated from the shielding block but was still in one piece. Upon arrival, the Radiation Safety Officer verified that the radioactive sources were still intact and attached to the source rod. "The Radiation Safety Officer added additional shielding to the source rod to prevent the sources from becoming detached. The Radiation Safety Officer then put the damaged gauge and its pieces into the transportation container. After the gauge was loaded in the truck and removed from the job site, the Radiation Safety Officer performed a survey of the area the accident occurred at to verify that no contamination was present. No contamination was found, and the gauge was returned to its storage area in Elsinore, Utah. "On November 15, 2013, the Division of Radiation Control's inspector arrived at Hales Sand and Gravel's facility at approximately 1230 [MST]. The inspector interviewed personnel involved in the accident and collected statements. The inspector took photographs of the damaged gauge, collected wipe tests, and took surveys of the damaged gauge. The inspector also visited the site of the accident to perform a contamination survey. No readings were distinguishable from background. "Gauge information: Troxler 3430, s/n 31986" Event Report ID Number: UT 130004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2013-11-26
49554 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2013-11-16 12:11 | 2013-11-18 16:24 | 2013-11-18 | CONSOLE KEY LEFT UNATTENDED "At 12:11 pm on 11/16/2013, the console key was found inserted and unattended in the console. Based on the log book, the key had been unattended since 11:00 am 11/16/2013. "The relevant Technical Specification is: 6.1.3 (Staffing): the minimum staffing when the reactor is operating shall be: a licensed reactor operator in the control room. "The control room was locked. There was no unauthorized access while the key was unattended. There was no reactivity manipulation while the key was unattended. We [the licensee] have started a corrective action report. "[The licensee notified NRC] Project Manager Geoff Wertz." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2013-11-18
49553 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-11-18 08:00 | 2013-11-18 15:03 | 2013-11-18 | ULTRASONIC EXAMINATION IDENTIFIED FLAW IN REACTOR VESSEL HEAD PENETRATION "On November 18, 2013, while the Harris Nuclear Plant was shut down for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with lnservice Inspection Program. Ultrasonic examinations identified a flaw in a head penetration nozzle. Bare metal visual inspection of the outer surface of the reactor vessel head revealed no indications of leakage. The unit is in a safe and stable condition and structural integrity of the reactor vessel was maintained. The flaw will be repaired prior to startup from the refueling outage. "The flaw and repair have no impact to the health or safety of the public. "The NRC Senior Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-11-18
49552 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-11-17 14:00 | 2013-11-18 13:51 | 2013-11-18 | REMOTELY OPERATED ISOLATION VALVE FAILED TO CLOSE "At approximately 1400 (CDT on 11/17 /2013) the facility suspended operations due to a tornado warning. Located on the first floor of the Feed Materials Building, it was determined that a remotely operated valve closing mechanism at the #2 fill spot failed to close a UF6 cylinder valve. The cylinder valve was then closed manually by operations personnel. There was no damage, no release, or employee exposure due to this event." "NRC Region II informed: Richard Gibson" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2013-11-18
49551 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-11-18 05:12 | 2013-11-18 12:08 | 2013-11-18 | COMMUNICATIONS LOSS TO NEW YORK STATE WATCH TOWER "James A. FitzPatrick Nuclear Power Plant (JAF) was notified at 0512 EST by the New York State (NYS) Watch Center that the Radiological Emergency Communications System (RECS) and commercial telephones were not available. The unavailability of the communications systems was a result of an unplanned computer server outage affecting the New York State Watch Center. While the RECS line remained operational, it was not available due to the relocation of personnel from the NYS Watch Center to an alternate location. An alternate method of communication was established via cell phone at the time of notification. This condition is reportable as a major loss of emergency offsite communications capability under 10 CFR 50.72(b)(3)(xiii). The NYS Watch Center network and communications systems have been restored and the facility staffed as of 0757 EST. The condition has been entered into the station's corrective action program." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-18
49550 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-11-18 05:12 | 2013-11-18 12:04 | 2013-11-18 | COMMUNICATIONS LOSS TO NEW YORK STATE WATCH TOWER "Nine Mile Point Nuclear Station (NMP1 and NMP2) was notified at 0512 [EST] by New York State (NYS) Watch Center that the Radiological Emergency Communications System (RECS) and commercial telephones were not available. The unavailability of the communications systems was a result of the relocation of personnel from the NYS Watch Center to an alternate location as a result of an unplanned computer server outage affecting the center network and some communications systems. While the RECS line remained operational, it was unavailable due to the relocation. An alternate method of communication was established via cell phone at the time of notification. The cause of the server loss is not known. "This condition is reportable as a major loss of emergency offsite communications capability under 10CFR50.72(b)(3)(xiii). "The NYS Watch Center network and communications systems have been restored and the facility staffed as of 0757 [EST]. The condition has been entered into the station's corrective action program." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-18
49549 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2013-11-14 | 2013-11-18 11:30 | 2013-11-18 | FIRE DAMAGE OF A GENERAL LICENSED DEVICE "On the afternoon of November 15, 2013 at 1530 CST, the Alabama Office of Radiation Control was notified that on November 14, 2013 a coal bed fire occurred at Nichols Aluminum Alabama in Decatur, AL. This fire occurred in the vicinity of a general licensed radioactive material device causing damage to the device. The device was identified as an Accuracy model 7000M, serial number 4084600. The device contained a Sr-90 sealed source model USS-18, source serial number LB-650 with an original activity of 11.1 milliCurie. Initial action taken by the company was to restrict access around the device at a 100 feet radius. A consultant from Phillips Group evaluated the radiation hazard on November 16, 2013 taking radiation measurements and a leak test of the device. Preliminary test indicate that the sealed source capsule remained intact with no leakage. The device shutter could not be completely closed but the device has been secured and presents no hazard to workers. The general licensee plans to contract with the manufacturer to package and dispose of the device. The written report from the general licensee is pending." Alabama Incident #13-52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2013-11-26
49548 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2013-11-18 05:12 | 2013-11-18 10:39 | 2013-11-18 | COMMUNICATIONS LOSS TO NEW YORK STATE WATCH TOWER "R.E. Ginna Nuclear Power Plant was notified at 0512 [EST] by the New York State (NYS) Watch Center that the Radiological Emergency Communications System (RECS) and commercial telephones were not available. The unavailability of the communications systems was a result of an unplanned computer server outage affecting the NYS Watch Center. While the RECS line remained operational, it was not available due to the relocation of personnel from the NYS Watch Center to an alternate location. An alternate method of communication was established via cell phone at the time of notification. "This condition is reportable as a major loss of emergency offsite communications capability under 10 CFR 50.72(b)(3)(xiii). "The NYS Watch Center network and communications systems have been restored and the facility staffed as of 0757 [EST]. The condition has been entered into the station's corrective action program." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-18
49547 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-11-17 17:25 | 2013-11-17 22:37 | 2013-11-17 | SECONDARY CONTAINMENT INTEGRITY MOMENTARILY DECLARED INOPERABLE "Station personnel simultaneously opened the inner and outer air lock doors from the reactor building to the reactor control enclosure (Reactor Building 23 foot elevation North West airlock). Reactor Building secondary containment integrity was declared INOPERABLE per TS 3.5.B.2 due to both containment airlock doors being momentarily open at the same time. Reactor Building D/P (differential pressure) remained less than negative 0.25 inches water column. "Reactor Building secondary containment integrity was declared OPERABLE following verification that at least one airlock door to each access of secondary containment was closed per TS 3.5.B.2. Total LCO time was approximately 10 seconds." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-17
49546 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2013-11-17 12:33 | 2013-11-17 19:27 | 2013-11-17 | ALL CONTROL ROOM ANNUNCIATORS IN ALARM "A station annunciator system malfunction caused all Control Room annunciator indications to be in alarm status. This condition resulted in a loss of normal audible and visual plant condition assessment capabilities and was assessed as being a significant loss of assessment capabilities. Backup assessment capability existed and was dependent upon redundant assets as described in existing station documentation and/or functionality of the Control Room Alarm Typer. "At 1659 EST full annunciator capability was restored following cleaning of a disconnect switch. "The NRC Resident Inspector has been notified." State and local officials will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-17
49545 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-11-17 09:55 | 2013-11-17 16:13 | 2013-11-19 | LOSS OF DRYWELL SAMPLING CAPABILITY "This notification is being made due to a loss of emergency assessment capability. At 0955 (PST) on 11/17/2013, it was discovered that the CMS-SR-13 sample valves would not align to allow monitoring the drywell. The redundant sample rack, CMS-SR-14, is already out of service due to an issue with the sample pump, which is currently awaiting replacement parts. The capability to monitor the drywell for H2 and O2 remotely is non-existent if an emergency situation were to arise because of these two issues. The only method currently available to sample the drywall for H2 and O2 is manually via chemistry procedures. This method would be unavailable in accident conditions because the sample point isolation valves isolate on an accident signal (F or A). Even if the sample points were not isolated, the Chemist would be unable to draw a sample safely during an accident due to radiation levels in the Reactor Building and/or H2 and O2 levels in containment. PPM 13.1.1 Table 6 specifies DW/WW (Drywell/Wetwell) hydrogen and oxygen measurements as a method for determining potential loss of Primary Containment. PPM 13.14.11 does not specify an alternative method for the loss of CMS-SR-13 & 14. Based on this information and discussions with Licensing and Emergency Preparedness, the station has determined this issue is a loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE FROM DAVID HOLICK TO DONALD NORWOOD AT 0159 EST ON 11/19/13 * * * "At 1351 PST on 11/18/13, repairs on CMS-SR-13 were completed, returning the monitor to operable status of being able to sample both the drywell and wetwell for hydrogen and oxygen as required for emergency assessment capability. "The NRC Resident Inspector has been notified." Notified R4DO (PROULX). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-17
49544 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2013-11-17 14:17 | 2013-11-17 15:30 | 2013-11-17 | ALERT DUE TO STORM DAMAGE ON SITE "On 11/17/13, at 1417 CST, an alert was declared at the Paducah Gaseous Diffusion Plant due to an apparent tornado strike/severe weather event. Multiple facilities were damaged with no injuries and no hazardous material released. No damage to the security fence was observed and the protected area remained secured during the event. "This event is reportable under 10 CFR 76.120(a)(4) where an emergency condition has been declared an Alert. "NRC Branch Chief has been notified. PGDP has no NRC Resident Inspector. "PGDP Event Report No. PAD-2013-08." Notified DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE FROM DAVID PETTY TO CHARLES TEAL AT 1746 EST ON 11/17/13 * * * "On 11 /17/13, at 1638 CST, the Paducah Gaseous Diffusion Plant decided to issue press releases describing the Alert issued by the plant that afternoon. The Alert was declared due to an apparent tornado strike/severe weather event on 11/17/13 at 1417 CST. "This event is reportable under Criteria P in Appendix D of USEC procedure CP2-RA-RE 1 030 as any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. "NRC Branch Chief has been notified. PGDP has no resident inspector. "PGDP Event Report No. PAD-2013-08." Notified RA (McCree), NMSS EO (Damon), R2DO (Desai), IRD (Gott), NMSS (Haney), DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE FROM DAVID PETTY TO CHARLES TEAL AT 1910 EST ON 11/17/13 * * * The Alert was terminated at 1806 CST on 11/17/13 after a complete security check of the site perimeter and a compilation of the damages sustained by the site. There were no personnel injuries and no releases (HAZMAT or radiological). Notified RA (McCree), NMSS EO (Damon), R2DO (Desai), IRD (Gott), NMSS (Haney), DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | OTHER UNSPEC REQMNT | [8 empty] | ALERT | 2 | KY | FUE |  | 76.120(a)(4) |  |  |  | 0 | 2013-11-17
49543 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-16 10:19 | 2013-11-16 17:53 | 2013-11-16 | FAILURE OF SECONDARY CONTAINMENT INTERLOCK MECHANISM "At 10:19:02 [CST] on November 16, 2013, indication was received in the Control Room that two Secondary Containment doors, in one access opening, were open simultaneously. The interlock mechanism preventing both doors from operating simultaneously did not operate as expected. A worker was staged in the interlock to operate the doors as an interim action while a modification to prevent additional failures was being developed. The worker reported that while opening the reactor building side door the Turbine Building side door opened several inches. Both doors were immediately closed and the interlock was removed from use. Secondary Containment differential pressure remained within Technical Specification required values during the short time both doors were open. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2. As a result, entry into Technical Specification 3.6.4.1 Condition A was made momentarily due to Secondary Containment being inoperable. The doors were secured at 10:19:07 [CST] and Secondary Containment was declared Operable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of the safety function. "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-16
49542 | 0 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2013-11-14 13:50 | 2013-11-15 13:27 | 2013-11-15 | Y-90 MICROSHPERE DOSE LESS THAN PRESCRIBED "On the afternoon of 11/14/2013, a patient was scheduled for a Y-90 microsphere radioembolization treatment at Indiana University Medical Center under NRC License 13-02752-03. The treatment consisted of two separate doses of Y-90 for which two separate written directives were prepared. Segment 4 of the patient's liver was prescribed a dosage of 27.0 mCi, and the right lobe of the liver was prescribed a dosage of 88.0 mCi. At 13:50 on 11/14/2013, following measurement of the remaining activity after injection of the Y-90 microspheres, it was determined that a dose of 19.5 mCi was delivered to segment 4 (72.2% of the intended dose). Shortly thereafter, at 14:06, a dose of 87.5 mCi of Y-90 was delivered to the right lobe (99.4% of the intended dose). "Both procedures appeared to proceed in accordance with standard operating procedures, and no abnormalities were identified during the procedure by the Interventional Radiology Physician or the Health Physicist supporting the procedure. Following the procedure, personnel and area surveys were performed using an SE International GM meter and no contamination of personnel, the room or equipment was identified. The container holding residual activity from the segment 4 treatment has been set aside for decay and further analysis. "As the activity delivered to segment 4 of the liver meets the criteria in 10 CFR 35.3045(a)(1) and 10 CFR 35.3045(a)(1)(i), a report to the NRC Operations Center shall be made in accordance with 10 CFR 35.3045(c). The attending physician and patient will be contacted in accordance with 10 CFR 35.3045(e)." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2013-11-25
49541 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-11-14 16:00 | 2013-11-14 20:35 | 2013-11-14 | POSTULATED FIRE INDUCED FAILURE OF CENTRIFUGAL CHARGING PUMPS "During analysis of Watts Bar Nuclear (WBN) Unit 2 fire protection features, it was revealed that a potential fire induced failure of centrifugal charging pumps could occur in Unit 1. "Specifically, a potential fire induced failure of both Unit 1 Chemical and Volume Control System centrifugal charging pumps (CCPs) (1-PMP-62-108-A and 1-PMP-62-104-B) could occur due a fire in either auxiliary building room 737.0-A1 (general area for elevation 737.0) or 757.0-A2 (6.9 kV and Shutdown Board Room A). It is postulated that a fire in these rooms could cause a spurious closure of the CCP suction valve (1-LCV-62-133-B) from the volume control tank (VCT) (1-TANK-62-129) and could disable the control circuit which opens the flow from the refueling water storage tank (RWST) suction valve (1-LCV-62-135-A). "The fire safe shutdown analysis (Fire Protection Report, Part VI) currently addresses this occurrence via the performance of a prompt main control room operator action to open the RWST suction path. However, this procedurally directed action may require several minutes to complete and due to the potentially short duration (possibly as short as a few seconds) for CCP survivability without suction flow, the action has now been determined to be unacceptable. As a result, the loss of charging flow could result in a loss of injection to the reactor coolant pump (RCP) seals which could subsequently lead to a RCP seal failure and a small break loss of coolant event. WBN engineering is continuing to validate whether the CCP minimum flow recirculation would protect the pumps with both suction paths (VCT and RWST) isolated and with the reactor at normal operating pressure. "WBN has established compensatory measures to ensure that a fire in affected rooms will not cause a spurious closure of the CCP suctions valves." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2013-11-14
49540 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-11-12 | 2013-11-14 17:49 | 2013-11-14 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL UNACCOUNTED FOR The following was received via email from the Washington Dept. of Health, Office of Radiation Protection: "Tuesday, November 12, 2013, I [State of WA] received a call from the Radiation Safety Officer of the University of Washington. He informed me that his staff was unable to account for 3.3 mCi of C-14 and 7 mCi of H-3, the sum of several vials [unsealed sources used for research], when reconciling the inventory of an AUI [Authorized Investigator] after he died. The AUI had a radioactive materials authorization at the university for well over 20 years. A staff member investigated the problem and interviewed current and previous laboratory staff in an effort to find the documentation of disposition of the missing material. This is believed to be a paperwork/failure to document issue with no actual loss or release. It will be discussed at their next Radiation Safety Committee meeting which the state will attend on 26 November 2013. The licensee will provide us with a full report by then. It is the C-14 which exceeds the reporting activities." State incident number WA-13-056 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-11-22
49539 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-11-14 13:22 | 2013-11-14 16:08 | 2013-11-14 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits has determined the described condition is applicable to the Salem Nuclear Power Plant resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R. The original plant wiring design and associated analysis for ammeters associated with the station batteries are not provided with overcurrent protection features to limit the fault current. "A postulated fire that results in a short to ground concurrent with an opposite polarity short from the same battery could result in excessive current flow (i.e., heating) in the ammeter wiring. This excessive current could result in a secondary fire in another fire area. The secondary fire could adversely affect safe shutdown equipment and cause loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. The areas affected are the Control Room, Relay Rooms and 460 Volt Switchgear Rooms. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for the affected areas of the plant. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-11-14
49538 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-11-14 13:13 | 2013-11-14 16:03 | 2013-11-18 | MANUAL REACTOR TRIP DUE TO INDICATION OF DROPPED CONTROL RODS "On November 14, 2013, at 1313 Eastern Standard Time, Unit 1 was manually tripped from 100% power due to indications of [four] dropped control rods. This manual reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). The cause of the dropped rods is not confirmed at this time, but may be related to maintenance in a Rod Control Power Cabinet ongoing at the time of the event. "The Operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip and all plant systems operated as designed. "The Auxiliary Feedwater (AFW) system [1A and 1B motor-driven pumps] was manually started for steam generator level control following reactor trip. The start of the AFW system is reportable per 10 CFR 50.72 (b)(3)(iv)(A) for a valid system actuation. "Decay heat is being removed via the steam generators [via steam dumps to the main condenser]. This event does not impact public health and safety. "Unit 2 was not affected by this event. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM WARREN MOORE TO DANIEL MILLS ON 11/18/13 AT 0950 EST * * * A subsequent licensee evaluation determined that there were ten dropped control rods. Notified the R1DO (Desai). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-11-14
49537 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-11-08 | 2013-11-14 14:40 | 2013-11-14 | AGREEMENT STATE REPORT - Y-90 THERASHPERE DOSE LESS THAN PRESCRIBED The following report was received from the Washington Department of Health [WA DOH] via e-mail: "The licensee was performing an administration of Nordion TheraSpheres, a procedure performed without incident for over sixty administrations so far, when measurements indicated that an inordinate amount of the material remained in the waste/tubing. The licensee has confirmed the catheter used had an internal diameter [ID] of 0.68mm, which equals and exceeds the manufacturer's specifications of equal or greater than 0.5 mm ID. "1. On Friday, November 8, 2013 at approximately 1040 [PST], the RSO received notification of a possible medical event involving the administration of Y-90 microspheres (TheraSpheres). The Radiation Safety Specialist contacted WA DOH at approximately 1100 on Friday, November 8, 2013 to report a medical event in accordance with requirements in WAC 246-240-651. "2. The routine procedure for Y-90 microsphere administration requires the measurement of the materials used for the administration at a fixed geometry both before and after administration. The ratio of the exposure rate measured (minus background) indicates the percentage of the microspheres remaining in the tubing. This value subtracted from the originally prescribed activity determines the percentage of activity actually administered to the patient. The prescribed dose was 129 Gy to the left lobe, equivalent to an administered activity of 5.0 GBq. The measured activity (via Capintec CRC-15R) was 5.04 GBq which resulted in a pre-administration exposure rate of 5.3 mR/hr. Post-administration, the residual waste exposure rate measurement was 3.8 mR/hr (using the same geometry). The post-administration measurement was taken about 2 hours after the pre-administration measurement. Based on the post administration measurement, it is estimated that at least 73% of the prescribed dose was still present in the waste materials implying that only 27% of the prescribed dose was administered or 1.36 Gbq which would result in a target dose of 35 Gy. "3. Investigation into the root cause indicated that the use of a Surefire Catheter may have been the underlying factor of this medical event. The interventional radiologist (RA) reported that this was the first time he had used the Surefire Catheter in conjunction with a TheraSphere case. This catheter was chosen due to medical need. The interventional radiologist wanted to minimize the amount of auxiliary embolization required for this case and this catheter satisfied that requirement. Prior to administration, contrast was administered to verify the integrity of the infusion system. No issues were noted during the contrast administration. During the administration of the microspheres, the interventional radiologist noted that the feel of the syringe was different from past administrations and that it was more difficult to push the plunger, however it did appear that the infusion was occurring. After completion of the infusion, the interventional radiologist noted that the syringe plunger pushed back. Final measurement of both the patient and the waste materials by medical physics and nuclear medicine indicated that the dose was not properly infused and consequently an underdose had occurred. "4. During the investigation it was noted that this case was the first time the Surefire Catheter was utilized. There were no other changes in the set up. The vendor representative mentioned that he had previously observed issues with the use of this catheter, however there are no documents or other notices issued with regards to catheter usage combinations. Review of the infusion materials did not reveal any physical issues with the setup, though based on the physician's report regarding the feel of the plunger during the infusion, it is possible that there was a kink or other similar issue in either the catheter or infusion system that resulted in incomplete administration of the TheraSphere dose. "5. The interventional radiologist communicated directly with the patient regarding this medical event. Both the interventional radiologist and the radiation oncologist (who is also the physician authorized user for this material) do not anticipate any additional medical issues that would be a result of this incomplete administration. This is based on the history of the patient who had previously received a TheraSphere administration to his right primary lobe vs. the current administration to the left secondary lobe. "6. In order to minimize the possibility of future medical events, the Surefire Catheter will not be used for future procedures. Since there have been no cases during our experience with this procedure prior to this event that have resulted in an underdosing due to equipment malfunction and since the only significant change in equipment set up was the use of the Surefire catheter, it is expected that a return to our previous catheter will insure that underdosing will not occur. "7. In accordance with WAC 246-240-651 a full report regarding this event has been transmitted to WA DOH. " Washington Incident : WA-13-055 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-11-22
49536 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2013-11-14 12:18 | 2013-11-14 14:57 | 2013-11-14 | MANUAL REACTOR TRIP DUE TO LOW LEVEL IN THE 2B STEAM GENERATOR "On November 14, 2013 at 1218 EST, Unit 2 was manually tripped due to a lowering 2B Steam Generator level caused by the spurious closure of 2B Main Feedwater Isolation Valve HCV-09-2A. "All CEAs [Control Element Assemblies] fully inserted into the core. All safety systems responded as expected with the 2B Train Auxiliary Feedwater Actuation System Channel 2 (AFAS 2) actuating on low 2B Steam Generator level. Decay Heat Removal is from Main Feedwater to the 2A Steam Generator and Auxiliary Feedwater to the 2B Steam Generator with Steam Bypass to the Main Condenser. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip and 10CFR 50.72(b)(3)(iv)(A) for the AFAS 2 actuation." The plant is in its normal shutdown electrical lineup. No safeties or relief valves lifted during this event. The NRC Resident Inspector has been notified by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-11-14
49535 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-14 03:00 | 2013-11-14 11:01 | 2013-11-14 | PRIMARY CONTAINMENT ISOLATION VALVE LEAK TEST FAILURE "On November 14, 2013, both the 2-220-58B Feed Water Inboard Check Valve and the 2-220-62B Feed Water Outboard Check Valve failed Local Leak Rate Testing (LLRT) acceptance criteria. These valves are considered primary containment isolation valves and, as such, are required to ensure that an adequate primary containment boundary is maintained. "Technical Specification (TS) 5.5.12, 'Primary Containment Leakage Rate Testing Program,' establishes limits for Primary Containment leakage. Based upon the results of the LLRT, Dresden, Unit 2, may not have met the limits for primary containment leakage during the last operating cycle as specified in TS 5.5.12.c. "Dresden Unit 2 is currently in Mode 5 for a refueling outage and per Dresden TS 3.6.1.1, 'Primary Containment,' Primary Containment is not required in the current mode of operation (i.e., Mode 5). However, in accordance with 10 CFR 50.72(b)(3)(ii)(A), this event is reportable as a condition that resulted in a principal safety barrier being seriously degraded. "The NRC Resident Inspector has been notified [by the licensee]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-11-14
49534 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2013-10-25 | 2013-11-13 11:18 | 2013-11-13 | PART21 - DIODE CR7 WIRING REVERSED ON AUTOMATIC VOLTAGE REGULATOR PANELS The following is a summary of information received via facsimile: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 10/25/2013 after receiving notification from APS-Palo Verde Nuclear Generating Station that diode CR7 on their automatic voltage regulator (AVR) panels had the wiring connections reversed. During installation of the AVR panels, generator output voltage buildup was observed to be longer than expected during fast start testing. The slow voltage buildup was determined to be caused by a lack of generator field flashing. Troubleshooting revealed that the field flash diode CR7 wiring was reversed. "The evaluation was concluded on 11/11/2013, and it was determined that this issue is a reportable defect as defined by 10CFR21. The incorrect wiring of diode CR7 prevents field flashing of the generator. Lack of generator field flashing can result in failure of generator voltage buildup, or excessive voltage buildup time, during starting of the emergency diesel generator (EDG). This condition could therefore have impacted operability of the EDG and prevented it from performing its safety related function. "APS-Palo Verde is the only affected customer. This reversed CR7 wiring condition only applies to the five (5) AVR panels (P/N 072-12200-100-PVNGS) shipped to Palo Verde on ESI sales order 8001720 (4 panels shipped in May 2013 and 1 panel shipped in June 2013)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-11-13
49533 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-11-13 09:24 | 2013-11-13 11:42 | 2013-11-13 | FUEL OIL LEAK TO THE ENVIRONMENT "Approximately 10 gallons of fuel oil was spilled from excavation equipment onto the ground inside the owner controlled area. Notifications will be made to the National Response Center and the Kansas Dept. of Health and Environment. Cleanup by on-site personnel is in progress. No fuel oil made contact with any surface water. "NRC resident inspector has been notified [by the licensee]." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-11-13
49532 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-11-13 | 2013-11-13 10:23 | 2013-11-13 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following Agreement State Report was received via email: "On Thursday, November 7, 2013, Midwest Inspection dba [doing business as] Desert NDT experienced a source disconnect [on a INC Radiography Camera]. The RSO was able to retrieve the source into a shielded source exchange container as authorized to do on the license. No over-exposures are reported at this time, and an investigation is underway by [Colorado] Department employees. A full report will follow in the next 30 days." The camera is an INC radiography camera, Model 32, Serial # 7292. The licensee RSO received 54 mrem while performing a source exchange on the camera. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-11-21
49531 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-11-13 02:26 | 2013-11-13 09:53 | 2014-01-10 | SECONDARY CONTAINMENT ZONE II DIFFERENTIAL PRESSURE LOST DURING RECOVERY FROM VENTILATION DRAWDOWN TEST "On November 13, 2013 at 0226 [EST], Secondary Containment Zone II (Unit 2 Reactor Building) differential pressure was lost during restoration of a ventilation drawdown test. During restoration Unit 2 'A' Train Reactor Building Ventilation fans tripped. The 'B' Train fans were placed in service and secondary containment was restored. Zone I (Unit 1 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone II differential pressure recovered within a few minutes and was verified to be stable. LCO 3.6.4.1 was exited for both units at 0257 [EST]. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. "There have been no further perturbations in differential pressure and secondary containment remains operable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The cause of the Unit 2 "A" Train Reactor Building ventilation fans tripping is still under investigation. The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 1/10/14 AT 1657 EST FROM DOUG LAMARCA TO NESTOR MAKRIS * * * "NUREG-1022, Revision 3 states, ' reports are not required when systems are declared inoperable as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that would have resulted in the system being declared inoperable).' "The event reported in this event notification occurred during a pre-planned evolution for surveillance testing that was done in accordance with an approved procedure and the Susquehanna Technical Specifications. The loss of differential pressure occurred during restoration from the surveillance test and occurred prior to completing the planned evolution and declaring the system OPERABLE. Specifically, the trip of the fans occurred when restoring the Reactor Building normal ventilation after a Zone 1, 2, and 3 isolation (returning back to normal ventilation from the Standby Gas Treatment System). The secondary containment boundary and standby gas treatment system were unaffected. This event occurred as a result of the testing process and would not have occurred during normal operation of the system. There was no discovered condition that would have resulted in the safety function of the system being declared inoperable under normal, non-testing conditions. "Based on the above additional information, PPL is retracting this report. Susquehanna was in a planned evolution and did not discover a condition that could have prevented performing a safety function." The licensee has notified the NRC Resident Inspector. Notified the R1DO (Schmidt). | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-13
49530 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-11-12 | 2013-11-12 16:20 | 2013-11-18 | AGREEMENT STATE REPORT - ACCESS RESTRICTED DUE TO TECHNETIUM-99 SPILL The following information was obtained from the Commonwealth of Massachusetts via email: "On 11/12/13, licensee reported 10 mCi spill of medical Tc-99m (6-hour half-life) liquid during patient administration. Report based on the licensee's need to restrict access to the area of the spill for more than 24 hours. Licensee reported there was no occupational exposure to workers. Spill cleanup action was performed by licensee but enough residual contamination remained for licensee to restrict access to contaminated room until 10 half-lives (approximately three days) of radioactive decay have passed. Licensee will submit written follow-up report within 30 days. "The Agency [Massachusetts Radiation Control Program] considers this matter to be OPEN pending results of ongoing investigation." * * * RETRACTION ON 11/18/13 AT 1055 EST FROM ANTHONY CARPENITO TO DONG PARK * * * "The Agency [Massachusetts Radiation Control Program] agrees with recent USNRC determination that this is not a reportable event, because it meets one but not all three of the requirements contained in 105 CMR 120.142 (B)(1) or 10 CFR 30.50 (b)(1)." Notified R1DO (Bower) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-11-20
49529 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2013-11-12 | 2013-11-12 15:56 | 2013-11-15 | AGREEMENT STATE REPORT - LOST PORTABLE GAUGE The following information was provided by the State of Nevada via email: "The RSO [Radiation Safety Officer] of GeoTek, in Las Vegas, reported the loss of a portable gauge - CPN Model MC1, S/N MD360603270 - containing 10 mCi of Cs-137 and 50 mCi of Am-241/Be. It was lost this morning between 0930 and 1000 [PST] in North Las Vegas, near Charleston and Lambert Blvds. It was not properly secured in the back of the truck and fell out. The user looked for it but could not find it. The RSO is going out to take a look for it. A police report, no. 131112-1703Z, was filed with the Las Vegas Metro at 1115 hrs. The RSO will call the North Las Vegas PD and let [Nevada Division of Radiation Health] know when that is done." Reference number: NV 130021 * * * UPDATE FROM THE STATE OF NEVADA TO HUFFMAN VIA E-MAIL ON 11/15/13 AT 1237 EST * * * "In response to the $500.00 reward offered for the missing gauge, a man came forward today and handed the gauge over to the RSO. Apparently he had found it on the Charleston on-ramp to US-95, which is the route which the technician had taken on the day he had lost the gauge. The gauge is not damaged and appears to be intact. "The RSO used a survey meter and did not get any abnormal readings. He will perform a leak test and then put the gauge back into service. Corrective action will involve additional training to staff to prevent such incidents in the future. An incident report will be sent to the Radiation Control Program [State of Nevada] by the RSO, within 30 days." "A member of staff from the Radiation Control Program visited the licensee and checked the gauge [to confirm] everything was normal. However, the licensee has been advised to send the gauge to the manufacturer (InstroTek), to be completely sure that there was no damage, before being put back into service." Notified R4DO (Farnholtz) and sent e-mail copies to FSME Events Resource and ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2013-11-20
49528 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2013-11-12 00:02 | 2013-11-12 01:23 | 2013-11-12 | MANUAL REACTOR TRIP DUE TO UNISOLABLE LEAK IN DIGITAL ELECTRO-HYDRAULIC SYSTEM "At 0002 EST, Unit 1 Manually tripped the Reactor from 90% power due to an unisolable leak in the Digital Electro-Hydraulic [DEH] System. All CEAs fully inserted into the Reactor Core. All systems responded as expected on the trip. Decay Heat removal currently using Main Feedwater and Steam Bypass Control System. After the trip, DEH pumps were secured to stop the transfer of fluid from the DEH system to the Turbine Building. Investigation ongoing to determine exact location of the leak. This condition is reportable pursuant to 10CFR50.72(b)(2)(iv)(B)." The was no impact on Unit 2. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-11-12
49527 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-11-11 05:20 | 2013-11-11 08:48 | 2013-11-11 | UNIT 1 COMMENCED A TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO RCS LEAKAGE "Oconee Nuclear Station identified a small Reactor Coolant System (RCS) pressure boundary leak on ONS [Oconee Nuclear Station] Unit 1 and initiated a Unit 1 shutdown at 0520 hours [EST] on November 11, 2013 in accordance with procedures and Technical Specifications. Visual inspection confirmed the leak is located on the 1B2 loop High Pressure Injection Line. ONS Unit 1 was operating at full power when the leak was identified and a down power to 20% was commenced at 2141 hours [EST] on November 10, 2013 in order to characterize the leak and leak location. The measured RCS leak rate was 0.13 gpm [gallons per minute] at the time of commencing the down power. "This issue is reportable per 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified. This event poses no threat to the public or station employees." Unit 1 entered TS 3.4.13 Condition B at 0520 EST on 11/11/13. This TS requires Unit 1 be in Mode 3 Hot Standby within 12 hours and Mode 5 Cold Shutdown within 36 hours. The generator is currently offline and the licensee anticipates entering Mode 3 at 1000 EST. Unit 1 entered their Abnormal Operating procedures for leak determination at 0442 EST on 11/09/13. | 13 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2013-11-11
49526 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-11-10 13:51 | 2013-11-10 16:16 | 2013-11-10 | SECONDARY CONTAINMENT INTEGRITY MOMENTARILY DECLARED INOPERABLE "Station personnel simultaneously opened the inner and outer air lock doors from the unit 1 reactor enclosure to the radwaste enclosure. Reactor enclosure secondary containment integrity was declared INOPERABLE per TS 4.6.5.1.1.b.2 due to report of both containment airlock doors on the 217 foot elevation being momentarily open at the same time. Reactor enclosure D/P [differential pressure] remained steady at .35 inches water column. "Reactor enclosure secondary containment integrity was declared OPERABLE following verification that at least one airlock door to each access of secondary containment was closed per U1 TS 4.6.5.1.1.b.2. Total LCO time was approximately 10 seconds." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-10
49525 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-11-09 15:13 | 2013-11-09 16:09 | 2013-11-09 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM Millstone Unit 2 automatically tripped following a turbine trip due to a loss of condenser vacuum. The loss of vacuum was caused by the trip of the "C" circ water pump with the "D" circ water pump out of service. The licensee is still investigating the trip of the "C" circ water pump. The MSIVs are open with steam generators discharging steam to the main condenser. Auxiliary feedwater automatically started as expected following the reactor trip. All rods fully inserted and there were no complications following the reactor trip. All systems functioned as required and the unit is stable in Mode 3. There was no impact on Unit 3. The licensee has notified state and local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-11-09
49524 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2013-11-08 10:45 | 2013-11-08 18:10 | 2013-11-08 | APPARENT DETERIORATION OF PRIMARY AND SECONDARY HEPA FILTERS "On November 8, 2013, at approximately 1045 PST, an Air Balance Technician at AREVA NP's Richland fuel fabrication plant discovered that the primary and secondary HEPA filters servicing the ammonium diuranate (ADU) area showed visible signs of deterioration. The apparent deterioration is being reported in accordance with 10 CFR 70.50(b)(2). "The K-32A HEPA filters were examined by air balance personnel at approximately 1045 PST on November 8, 2013 based on a request to follow-up on some stack monitoring results which indicated some elevated levels (still below required administrative action levels). Air flow was diverted to HEPA filters in a parallel upper housing in order to check the filters in the lower housing. Investigation showed apparent deterioration of both the primary and final HEPA filters. "The processes running at the time served by these HEPAs were the ammonium diuranate process, miscellaneous uranium recovery process, and cylinder wash. Air monitor samples were pulled on the K-32A system. Air monitoring samples showed negligible release levels. A Health and Safety Technician survey of the downstream side of the final HEPA housing of K-32A revealed no surface contamination above 'clean' criteria. "Potential dose to a member of the public and the effect on the environment are essentially negligible. External conditions are not known to have affected the event. "A Corrective Action Report, 2013-8809, was written on November 8, 2013. The cause of the apparent deterioration is under active investigation. Steps to prevent recurrence will be developed as appropriate." The licensee will notify the NRC Regional office and the Washington State government. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2013-11-08
49523 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-10-25 | 2013-11-08 17:30 | 2013-11-08 | ADMINISTRATION OF LESS THAN THE PRESCRIBED DOSE TO A PATIENT The following report was received via e-mail: "10-25-2013 (Friday) HDR [High Dose Rate] treatment to right breast with SAVI 9 Channel HDR unit: 1st channel treated appropriately but only fractional treatments to channel 2-8 of less than 50% of prescribed dose were delivered. Problems with the applicator's curvature caused source delivery problems. The manufacturer (Varian) was contacted but was unable to arrive before the next Monday. "10-28-2013 (Monday) Licensee made another attempt, but again only fractional treatments to channel 2-8 of less than 50% of prescribed dose was delivered. "10-29-2013 (Tuesday) The patient was taken to another Mount Carmel facility (MC West), parameters were recalculated and patient treatment was successfully concluded. The licensee stated they expect that no harm was done to the patient. The licensee stated that they didn't understand that this event was reportable until they were advised by Varian it was an equipment failure so it was a 24 hr. reportable event." Event ID No: OH130015 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2013-11-18
49522 | 0 | FLOWSERVE |  |  |  |  | 2013-09-04 | 2013-11-08 16:26 | 2013-11-08 | PART 21 - MACHINING ERROR IDENTIFIED IN GEARED LIMIT SWITCHES The following is a summary of information received from Flowserve via facsimile: "On September 4, 2013, in-house inspection of Limitorque SMB Geared Limit Switch (GLS) cartridges revealed a machining error in a subcomponent used in the GLS. The deviation was caused by a dimensional error concerning the location of a drilled hole in a drive pinion shaft. This error results in a reduction of gear tooth engagement inside the GLS which could potentially reduce the service life of the GLS causing a loss of function. To date, Limitorque's investigation of this machining error has not shown this deviation to be significant enough to affect the safety related function of the GLS. However, Limitorque has requested all switches certified for nuclear safety related service which were manufactured in the designated time frame be returned for inspection and replacement as needed." The components were sent to Perry Nuclear Generating Station. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-11-08
49521 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-11-08 13:40 | 2013-11-08 15:25 | 2013-11-08 | OFFSITE NOTIFICATION DUE TO ONSITE DEATH OF AN EMPLOYEE "At approximately 1104 CST on November 08, 2013, in the Owner Controlled Area, a station employee fell ill from an apparent personal medical condition. The employee was transported off site and passed away. The death was not related to activities impacting or related to the safety of the public or other on site personnel. Specifically, the individual collapsed and was promptly examined by Duane Arnold Energy Center Emergency Medical Technician(s). An ambulance evacuation was then ordered. The death was not work-related nor the result of an accident. The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. Duane Arnold Energy Center has not observed any heightened public or media concern as a result of the death. Since the death is apparently unrelated to Duane Arnold Energy Center industrial or radiological health and safety, no news release is planned. "The individual's name has not yet been released, pending notification of next-of-kin. "The Iowa Division of Occupational Safety and Health was notified of the death at 1340 CST. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-11-18
49520 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-11-02 | 2013-11-08 13:43 | 2013-11-18 | AGREEMENT STATE REPORT- RECEIVER SURVEY OF LICENSEE-SHIPPED PACKAGE DETECTED SURFACE CONTAMINATION The following was received via email: "On 11/8/13, a licensee shipper informed this Agency [MA Radiation Control Program] that on 11/2/13 the licensee receiver survey of a package containing one patient dose of Fluorine-18 (F-18), indicated removable surface contamination exceeding 49 CFR 173.443 levels. The receiver notified the shipper on 11/2/13. The shipper reviewed the outgoing package survey, as well as routine facility and personnel surveys for 11/2/13, and determined there were no contamination issues. Transports are made via courier vehicles. The shipper retrieved the empty subject package on 11/4/13 during a normal delivery run. F-18 has a half-life of less than two hours. The receiver did use the contained dose for patient administration as intended on 11/2/13. On 11/8/13, this Agency attempted to contact the receiver to confirm specific contamination results obtained by the receiver's package survey. The licensee receiver has not yet responded to this Agency's inquiry so specific results are not yet known at the time of this report. "The Agency considers this matter to be OPEN pending results of ongoing Agency investigation." * * * RETRACTION ON 11/18/13 AT 1310 EST FROM ANTHONY CARPENITO TO DONG PARK * * * "11/14/13 information from the receiver confirmed exclusive use shipment was used. With the new information, the Agency [Massachusetts Radiation Control Program] determined this is not a reportable event because 49 CFR 173.443 contamination limits to be applied should be ten times higher than limits applied previously. The receiver's removable contamination survey results no longer exceed limits." Notified R1DO (Bower) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-11-18
49519 | 0 | E.I. DUPONT |  |  |  |  | 2013-11-05 12:30 | 2013-11-08 11:52 | 2013-11-08 | MISSING NICKEL-63 SOURCE The licensee called to report a missing 15 milliCurie Nickel-63 source. This source is used in an unknown nuclear device. The licensee believes that the device, which was previously removed from a wall was taken to a scrap metal yard. The licensee has searched the scrap yard and is still searching for the source. The licensee is investigating and will update this report when more information is obtained. The following was received via email: "Serial number of 466AN. The plant number for this device is J-128. "Below is a brief sequence of events: "06/04/2013 - J-128 was observed mounted in place and a leak test was performed (A035645). "We [E.I. DuPont] are not sure of the date, but we have evidence that sometime in August maintenance removed the analyzer from the wall to make space for other equipment. There was a clear 'Caution Radioactive Material' label on the front of the unit. "10/30/2013 - J-128 was verified not in place. "10/30/2013 - We have pictures of this device. An extensive plant wide search began. This search then intensified to include all metal dumpsters on site, all operating areas, all scrap metal trailers scheduled to go off site, and then off site locations where metal may have been sent. The local scrapyard with acres of storage piles was searched using heavy equipment. "11/05/2013 - Even with all our efforts to locate the device, we were unable to locate it. On this date our formal investigation began and is ongoing. "11/08/2013 - Called the NRC to report this incident." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-11-18
49518 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-11-07 09:51 | 2013-11-08 09:05 | 2013-11-08 | FITNESS FOR DUTY - CONFIRMED POSITIVE FOR A NON-LICENSED CONTRACT SUPERVISOR A non-licensed, contract, supervisory employee had a confirmed positive during a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2013-11-08
49517 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2013-11-08 04:32 | 2013-11-08 06:01 | 2013-11-08 | SECURITY REPORT INVOLVING INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Actual entry of contraband into the protected area. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 0826 EST ON 11/8/13 FROM EUGENE PALMER TO PETE SNYDER * * * Based on the director of security's review of guidance in Generic Letter 9103 this incident has been reclassified as a 24 hour security logable incident and this report is retracted. Notified R1DO (Noggle). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-11-08
49516 | 0 | PALISADES | 1 |  |  | [1] CE | 2013-11-07 15:52 | 2013-11-07 16:32 | 2013-11-07 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits has determined the described condition to be applicable to the Palisades Nuclear Plant resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. "The original plant wiring design and associated analysis for the Class 1E batteries ampere indications, located in the cable spreading room at Palisades, do not include overcurrent protection features to limit the fault current. In the postulated event, a fire could cause one of the ammeter wires to short to ground. Simultaneously, it is postulated that the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "Interim compensatory measures (i.e., fire tours) have been implemented for affected areas of the plant. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-11-07
49515 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-11-05 08:26 | 2013-11-07 16:05 | 2013-11-07 | FITNESS FOR DUTY - VENDING MACHINE MAINTENANCE CONTRACTOR USED ANOTHER WORKER'S BADGE "On November 7, 2013, at 0826 EST, an investigation determined that a Fitness for Duty (FFD) policy violation as defined in 10 CFR 26.417(b)(1) had occurred in the Chicago Bridge & Iron (CB&I) FFD Program at the South Carolina Electric & Gas (SCE&G) V.C. Summer Units 2 and 3 construction site. "On November 5, 2013, a CB&I contractor vending machine service employee, in the presence of a CB&I contract security officer, used another contractor vending machine service employee's badge to gain access to the construction site after his badge did not allow access due to being inactivated in an effort to facilitate a random FFD test. The contractor vending machine service employee was escorted out of the construction site. "Subsequent investigation uncovered that it was a practice within the contractor vending machine service company to maintain an employee's badge in the vehicle and periodically use it to ensure the badge was not deactivated. "The contractor vending machine service company employee badges have been deactivated pending further investigation. The individuals involved in this event are under 10 CFR 26, Subpart K, and do not perform safety or security related work. This event has been entered in the CB&I and SCE&G Corrective Action Programs for resolution and development of appropriate corrective actions. "SCE&G is providing this notification in accordance with 10 CFR 26.417(b)(1). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FFD PROGRAMMATIC FAILURE |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.417(b)(1) |  |  |  | 0 | 2013-11-07
49514 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-11-07 13:33 | 2013-11-07 15:52 | 2013-11-07 | CONDUIT FLOOD SEAL MISSING "On 11/7/13, it was identified that a missing conduit flood seal between an outside manhole and the West switchgear room compromised the flooding design of both the East and West switchgear rooms. "Compensatory measures were implemented for the flood seal in accordance with the plant's barrier control process. Repair of the seal is in progress. The event is being reported under 10CFR 50.72(b)(3)(v) as internal flooding of both Switchgear Rooms could affect (a.) safe shutdown, (b.) removal of decay heat, (c.) control of release of radioactive material and (d.) mitigating an accident. "The NRC Senior Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2013-11-07
49513 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-10-31 | 2013-11-07 14:40 | 2013-11-07 | ORPHAN SEALED SOURCE RECOVERED AT A SCRAP YARD The following Agreement State Report was received via facsimile: "Notifications: The Southeast Regional (SER) Office was contacted by Coatesville Scrap on October 31, 2013 regarding a radiation alarm on an outbound trailer load. The event is reportable within 24 hours per 10 CFR 20.2201(a)(1)(i). "Event Description: On Thursday, October 31, 2013, a radioactive source was detected when a radiation alarm sounded on an outbound trailer load. The alarm was caused by a small metal object. It was located, placed in a lead pipe, crimped and moved to a remote area of the scrapyard behind a large steel piece of equipment. A SER inspector was sent to the site to determine the isotope and activity. It was identified as cesium-137 and a measurement on the surface of the lead pipe was 320 mR/hr. On Wednesday, November 6th the activity was estimated at approximate 10 mCi. It was determined that three members of the public were involved in locating the source, however one had the longest contact with the source; approximately 2.5 hours on and off. It took site staff some time to find the material via shoveling through the solid material and metal of the load. When found, the radioactive source was carried by a shovel approximately 150 to 200 feet away. An individual then carried the source by hand to an adjoining property and placed it in a lead pipe, which was crimped. This took approximately 10 to 15 minutes. A whole body dose documented from the uncalibrated dosimetry that was being worn by this individual was 364 micro-roentgens (microR). SER staff estimate a possible 10 rad dose to this individual's hand. Hands and feet of all parties were surveyed, with no contamination found. Caution tape was used to create a boundary to help notify other employees to stay away from the area. Meter readings at the caution tape boundary were approximately 60 microR/hr. "CAUSE OF THE EVENT: Loss of control of a Cs-137 sealed source. "ACTIONS: The DEP [Department of Environmental Protection] plans a full investigation of this event. The scrap yard has hired a consultant health physicist to assist with this event and Cs-137 source. The DEP will recommend that the individual who handled the source have their hands photographed and be examined by a physician." Event Report ID No: PA130026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-11-15
49512 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2013-11-07 06:00 | 2013-11-07 13:02 | 2013-11-07 | REACTOR COOLANT SYSTEM COLD LEG DRAIN LINE ULTRASONIC INDICATION "On Thursday, November 7, 2013, while performing planned inspections on a 2 inch reactor coolant system drain line, TMI technicians identified an indication of a flaw on the weld internal diameter of an elbow to pipe weld on the line. This flaw is determined to not meet acceptable criteria and a repair is being developed. This condition is reportable under 10CFR50.72(b)(3)(ii). No actual impact occurred during plant operations. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-11-07
49511 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-11-07 12:00 | 2013-11-07 11:41 | 2013-11-07 | TECHNICAL SUPPORT CENTER TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "Technical Support Center (TSC) out of service due to planned maintenance. This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities during the Unit 2 outage on 11/7/2013 will render TSC out of service for approximately 48 hours. The unit 2 work is on electrical equipment that will impact the power supply to the TSC. "If an emergency is declared requiring TSC activation during this period, the alternate TSC will be used per existing emergency planning procedures. "The NRC Resident Inspector has been notified. This event poses no threat to the public or station employees." | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Defueled | Power Operation | Power Operation | Defueled | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-07
49510 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-11-06 08:00 | 2013-11-06 22:12 | 2013-11-06 | PROHIBITED ITEM FOUND IN THE PROTECTED AREA "On November 6, 2013, at approximately 0800 hours [EST], a 40 oz. beer bottle containing what was believed to be 20 oz. of alcohol (beer) was discovered in the vicinity of the dilution plant trash raking system inside the protected area. The bottle was discovered during a routine tour and the finding was immediately reported to supervision. Based on the location of the bottle, the weathered condition of the bottle, and interviews with maintenance personnel who observed the bottle falling from the trash rake, it is known that the source of the bottle was the intake canal. The bottle was retrieved during automated raking evolutions and fell from the trash rake while the rake was in-transit to the dumpster. This report is submitted pursuant to 10 CFR 26.719 (b)(1) based on the presence of alcohol in the protected area." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2013-11-06
49509 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-11-06 10:28 | 2013-11-06 16:48 | 2013-11-06 | STACK RADIATION MONITORS REMOVED FROM SERVICE FOR PREPLANNED MAINTENANCE "The Millstone Station stack radiation monitor, RM-8169, was removed from service for preplanned maintenance at 1028 [EST] and returned to service at 1513 [EST]. "The Unit 2 high range stack radiation monitor, RM-8168, was removed from service for preplanned maintenance at 1543 [EST] and will be removed from service for approximately 3 days." The licensee has notified the NRC Resident Inspector and applicable state and local authorities. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-06
49508 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2013-11-06 08:30 | 2013-11-06 11:08 | 2013-11-06 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following Agreement State Report was received via facsimile: "The licensee contacted [the NC Radiation Protection] agency at approximately 0930 EST with the following info: A dump truck at a construction site ran over an lnstroTek Model 3500 Xplorer moisture density gauge. The area of the accident was cordoned off and the licensee RSO [was sent to] report back to agency with survey readings and leak test results. The gauge sources contain 11 mCi of Cs-137 and 44 mCi of Am-241/Be. "A survey by the licensee [RSO] showed a maximum reading of 0.5 mrem/hr. The instrument make/model was of the survey meter was not specified. Sources appear to be intact. The gauge and debris were returned to the gauge case (doubles as shipping container- DOT 7A Yellow II). The gauge will be shipped to lnstroTek corporation for repair or disposition." NC State Report Number: ICD 13-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-11-14
49507 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-11-06 00:58 | 2013-11-06 03:26 | 2013-12-02 | R-21 CIRCULATING WATER DISCHARGE RADIATION MONITOR PLANNED OUTAGE "When transferring power supplies to a non-safety related cooling tower bus for planned outage maintenance, R-21, the Circulating Water Discharge Radiation Monitor was removed from service at 0058 [CST] and returned to service at 0111 [CST]. There is no installed backup for R-21 which has an emergency response function to provide indication of gaseous liquid effluent release to the environment. This monitor has no compensatory measure that will allow timely classification of two NUE (Notification of Unusual Event) and Alert classifications when out of service. This resulted in a loss of emergency assessment capability while R-21 was out of service. "There are no radioactive leaks that impact the Circulating Water System. "The licensee notified the NRC Resident Inspector." * * * RETRACTION AT 1155 EST ON 12/2/13 FROM WAYNE EPPEN TO DANIEL MILLS * * * "Based on further reviews of plant drawings and discussion with the Radiation Monitor System Engineer, R-21 was not inoperable when power supplies were transferred to the non-safety related Cooling Tower Bus. While R-21 was logged out of service during the transfer on November 6, 2013, it did not lose power and was not out of service. R-21 did not lose the ability to provide continuous monitoring of discharge canal effluent or monitoring in the event of an unplanned radiological release. Our defense in depth strategies are relied upon to take actions to protect the health and safety of the public. "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Duncan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-06
49506 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2013-11-05 18:00 | 2013-11-05 21:31 | 2013-11-05 | AUTOMATIC REACTOR TRIP DUE TO MOMENTARY LOSS OF 4 KV BUSES AND SAFETY SYSTEM ACTUATION "At 1800 hours EST on 11/05/2013, with the unit in Mode 1 at 19% power, an automatic reactor trip occurred. Operators were transferring loads from the Startup Transformer to the Unit Auxiliary Transformer in accordance with normal operating procedures. When breaker 52/7, Unit Aux to 4KV Bus 1 Breaker, was taken to the close position, indication on the Reactor Turbine Generator Board (RTGB) went from 'Open' to 'No' indication. Breaker 52/12, Incoming Line Startup Transformer No. 2, cycled open and then re-closed. This resulted in a momentary loss of power to 4KV Bus 2 and 4KV Bus 1. The reactor trip signal was based on a loss of 4KV bus voltage to 2 of the 3 required 4KV buses. The cause of the loss of 480V bus E-1 was a result of loss of power to 4KV Bus 2. As a result of the loss of 480V bus E-1, the 'A' Emergency Diesel Generator (EDG) auto started. The required loads sequenced onto the 'A' EDG with the exception of the 'A' Service Water (SW) pump. The cause of the failure of the 'A' SW pump is under investigation. "The one running Main Feedwater Pump ('A' Pump) tripped on the resulting under voltage of 4 kV Bus 1. By design, this condition resulted in an automatic start of Auxiliary Feedwater due to both Main Feed pump breakers being opened. Both 'A' and 'B' Motor-Driven Auxiliary Feedwater (AFW) Pumps started as designed. Steam generator water levels were maintained in the normal operating band. "Currently, the unit is stable in Hot Standby (Mode 3). "This event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B) due to the valid Reactor Protection System Actuation "This event is being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of AFW and EDG auto-start and subsequent starting of required under voltage loads. "At no time during this occurrence was the public or plant staff at risk as a result of this event. "The [NRC ] Resident Inspector has been notified." The reactor trip was uncomplicated and the is plant is stable in mode 3 with decay heat being released to the main condenser. Normal offsite power is available with the exception of the 480V bus E-1 being supplied by the "A" Emergency Diesel Generator. | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-11-05
49505 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-11-05 18:28 | 2013-11-05 19:27 | 2013-11-05 | NOTIFICATION OF UNUSUAL EVENT DUE TO EXPLOSION AND FIRE IN THE TURBINE BUILDING "On 11/5/13 at 1746 [EST], Beaver Valley Unit 1 Generator tripped on 'C' Transformer differential protection. The Unit was at 47%, so an automatic trip of the reactor was not expected. The reactor was tripped manually. Entered E-0 Reactor Trip Response. The Aux Feedwater Turbine Driven Pump automatically started as required and one motor driven pump was manually started. "At 1748, the control room received report of fire in the Turbine building. The deluge system had actuated and extinguished the fire in the Turbine plant mezzanine. Off-site assistance was staged and available. "At 1828, an Unusual Event was declared when fire brigade reports indications that an explosion and fire had occurred in a cable tray in the Unit 1 Turbine Mezzanine. "The [NRC] Resident Inspector was notified of the events that occurred. "At 1836, NRC [Resident Inspector] was notified of the Unusual Event. "Cause of the cable tray explosion and fire is being investigated." The reactor trip was uncomplicated and Unit 1 is stable in mode 3 with decay heat being released to the main condenser. Normal offsite power is available. Unit 2 continues to operate at 100% and there is no impact on the health and safety of the public. * * * UPDATE FROM J. A. DAUGHERTY TO JOHN SHOEMAKER AT 2005 EST ON 11/05/13 * * * At 1959 on 11/5/13, the licensee terminated the Unusual Event. The licensee has notified the NRC Resident Inspector. Notified the R1DO (Noggle), NRR EO (Skeen), IRD (Marshall). Notified the DHS SWO, FEMA, DHS NICC, and Nuclear SSA via e-mail. | 0 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2013-11-05
49504 | 0 | US NAVY |  |  |  |  | 2013-11-05 | 2013-11-05 16:52 | 2013-11-05 | LOST STRONTIUM-90 SOURCE The U.S. Navy reported the loss of an IBIS (In-flight Blade Inspection System) that contained 500 microCuries of Sr-90. The IBIS was attached to an USMC aircraft, when the co-pilot's window fell off and struck the blade resulting in the loss of the system. The incident occurred approximately 10 kilometers northeast of Naval Air Station Jacksonville. The licensee has notified their project manager in Region 1 (Seeley). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-11-05
49503 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-11-05 08:42 | 2013-11-05 15:50 | 2013-11-05 | SECONDARY CONTAINMENT DECLARED INOPERABLE DUE TO FAILURE OF INTERLOCK MECHANISM "At 08:42 [CST] on November 5, 2013, indication was received in the Control Room that two Secondary Containment doors, in one access opening, were opened simultaneously. The interlock mechanism preventing both doors from operating simultaneously did not operate as expected. A worker in the field reported that the Turbine Building side door was opened, and simultaneously the Reactor Building side door opened several inches and then quickly re-closed. This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2. As a result, entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to Secondary Containment being inoperable. The doors were secured at 08:42 and Secondary Containment was declared Operable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." See similar events 49153 and 49379. The licensee is tracking the failure as Incident Report 01581320. | 0 | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-05
49502 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2013-11-05 00:41 | 2013-11-05 05:00 | 2013-11-05 | AUTOMATIC ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM DUE TO MAIN FEED PUMP TRIP "At 0041 hours [EST] on 11/05/2013, while placing the Condensate Polishers into service, a secondary side perturbation occurred, resulting in a loss of the one running Main Feedwater Pump ('A' Pump) on low suction pressure. At the time, the plant was in Mode 2 with Startup Low Power Physics Testing in progress. By design, this condition resulted in an automatic start of Auxiliary Feedwater. Both 'A' and 'B' Motor-Driven Auxiliary Feedwater (AFW) Pumps started as designed. Steam generator water levels were maintained by the Auxiliary Feedwater flow. The 'B' Motor Driven AFW pump was secured following its automatic start to stabilize steam generator water levels and reactor coolant system temperature. Plant conditions including steam generator water levels have been stabilized. At 0250 hours [EST] 'A' Main Feedwater Pump was restarted and at 0252 hours [EST], the 'A' Motor-Driven AFW pump was secured. "At this time, the cause of the secondary side perturbation is being investigated. The plant remains in Mode 2 and Startup Low Power Physics Testing has resumed. "Due to the valid actuation of AFW, this event is being reported as an 8-hour non-emergency per 10CFR50.72(b)(3)(iv)(A). At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-11-05
49501 | -1 | RESEARCH MEDICAL CENTER |  |  |  |  | 2013-11-04 10:00 | 2013-11-04 17:45 | 2013-11-13 | MEDICAL EVENT INVOLVING OVEREXPOSURE TO BLADDER DURING PROSTATE TREATMENT During a prostate cancer treatment, at 1000 hours [CST] on 11/04/13, it was discovered that one I-125 strand with 6 seeds was improperly inserted into the bladder. The patient's prescribed dose was 144 gray to the prostate with a 12% exposure to the bladder. The procedure to the prostate was completed with extra I-125 seeds and the estimated dose to the bladder is 18%. It is believed that shadowing from the urethra, during treatment, was the cause. An attempt to withdraw the seeds from the bladder when the problem was identified was unsuccessful. The patient has been informed and the patient's physician will be informed and will consult with the urologist as soon as possible to determine a method for seed retrieval. * * * UPDATE ON 11/8/13 AT 1150 EST FROM STEPHEN SLACK TO DONG PARK * * * The following was received via email: "The event took place during an implant of I-125 seeds into the prostate of a patient. One strand of six seeds was instead implanted into the bladder. Attempts to remove the strand of seeds at that time were unsuccessful. "Renewed attempts were made to remove the strand this morning and they were successful. The implant was planned for 144 Gy to the prostate over the full decay time of the I-125. This would have resulted in a mean dose to the bladder of 22.34 Gy. If the extra seeds had remained in place, the mean dose to the bladder would have been 39.15 Gy; hence the report of a Medical Event. "By removing the seeds this morning, the mean dose to the prostate has been reduced to 23.09 Gy. This is more than 50 rads to the organ but less than a 50% increase over what the organ would have gotten in the planned treatment." Notified R3DO (Riemer) and FSME Events Resource via email. * * * UPDATE ON 11/13/13 AT 1757 EST FROM STEPHEN SLACK TO NESTOR MAKRIS * * * The following was received via email: The first sentence of the last paragraph in the previous update should have read "By removing the seeds this morning, the mean dose to the bladder has been reduced [to 23.09 Gy]." rather than the mean dose to the prostate. Notified R3DO (Cameron) and FSME Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | OTH | AGR | 35.3045(a)(1) |  |  |  | 0 | 2013-11-12
49500 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2013-11-05 01:00 | 2013-11-04 17:01 | 2013-11-05 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance activity at Cooper Nuclear Station [CNS] will remove the TSC [Technical Support Center] ventilation system from service. The TSC ventilation system will be rendered non-functional during this maintenance period. The maintenance activity on the TSC ventilation is expected to last less than one day. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless uninhabitable due to ambient temperature, radiological, or other conditions. CNS Station procedures provide appropriate monitoring and compensatory measures to ensure habitability of the TSC and, if necessary, instructions for relocation of TSC personnel to alternate TSC facilities, should the need arise. Both of these alternate facilities are equipped with emergency ventilation systems and are currently fully functional. In the event of TSC activation, maintenance will be expedited to restore ventilation to service. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation. "The licensee has notified the NRC Resident Inspector." * * * NOTIFIED BY JEREMY SIMS TO JOHN SHOEMAKER AT 1736 EST ON 11/05/2013 * * * "Cooper Nuclear Station Technical Support Center ventilation system has been restored to service following planned maintenance. The NRC Resident Inspector has been informed." Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-04
49499 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-11-04 07:28 | 2013-11-04 09:15 | 2013-11-06 | PLANNED MAINTENANCE ON THE PARTICULATE, IODINE, AND NOBLE GAS RADIATION MONITOR "On November 4, 2013 at 0728 CST, the Kewaunee Power Station rendered the Auxiliary Building SPING [Particulate, Iodine, and Noble Gas] Radiation Monitor Mid and Hi ranges non-functional for planned maintenance. The Emergency Response Organization (ERO) has been notified of the Auxiliary Building SPING non-functionality. "Work will be performed with high priority on a continuous schedule. The Auxiliary Building SPING is expected to be restored to functional at 1800 CST on November 6, 2013. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify and classify an Emergency Action Level for off-site radiation conditions). The NRC Resident Inspector has been notified." * * * UPDATE FROM GARY AHRENS TO DANIEL MILLS AT 1437 EST ON 11/06/13 * * * The planned maintenance is complete and the Radiation Monitor was returned to service on 11/6/13 at 1010 CST. The licensee has notified the NRC Resident Inspector. Notified R3DO (Duncan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-04
49498 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-11-03 06:00 | 2013-11-03 09:15 | 2013-11-03 | MAIN STEAM LINE RADIATION MONITOR OUT OF SERVICE "At 0600 [EST] on 11/3/2013 main steamline radiation monitor RM4299A failed to zero and is not available. It is undetermined at this time how long the radiation monitor will be out of service. This action is reportable as a loss of assessment capability in accordance with 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector, and state, and local governments. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-11-03
49497 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-11-01 21:47 | 2013-11-02 01:44 | 2013-11-02 | AUTOMATIC REACTOR TRIP DURING SOLID STATE PROTECTION SYSTEM TESTING "At 2147 CDT on 11/1/2013, Unit 2 Reactor tripped during Solid State Protection System Slave Relay Testing. This test utilizes a blocking circuit to verify the operability of the slave relay which trips the Main Turbine and both Main Feedwater pump turbines, on a Hi-Hi Steam Generator level or Safety Injection. No valve actuation is expected to occur. While positioning the Slave Relay switch in a testing lineup, the relay actutated. The Unit 2 Turbine tripped as well as both Main Feedwater Pumps. The Turbine Trip actuated the Reactor Trip since power was above 50%. The trip of both Main Feedwater Pumps started both Motor Driven Auxiliary Feedwater Pumps. The Steam Generator Lo Lo Levels started the Turbine Driven Auxiliary Feed Water Pump. All systems responded as expected. "Currently, Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007B and the Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-11-02
49496 | 0 | KAKIVIC ASSET MANAGEMENT |  |  |  |  | 2013-11-01 17:20 | 2013-11-02 00:56 | 2013-11-02 | CAMERA SOURCE FAILED TO RETURN TO THE LOCKED POSITION An 880D radiography camera source was retracted back to the camera but failed to lock in the stored position because of ice. The supervisor and foreman removed the guide tube and thawed out the camera in the back of the radiography truck. The source was then able to be manually locked in the stored position. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-11-11
49495 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2013-11-01 12:06 | 2013-11-01 17:31 | 2013-11-14 | BOTH TRAINS OF AUXILIARY BUILDING SPECIAL VENTILATION SYSTEM DECLARED INOPERABLE "During Unit 2 refueling outage [currently defueled] preventative maintenance on CV-31117, Loop B Main Steam Isolation Valve (MSIV), an opening in the valve was discovered without direct administrative controls to ensure the opening could be closed within 6 minutes following a Loss of Coolant Accident on Unit 1. Addition of this opening to other openings created a total of greater than 10 square feet of non-closable openings and required declaring the Auxiliary Building Special Ventilation System (ABSVS) boundary inoperable. The inoperable ABSVS boundary caused both trains of ABSVS to be declared inoperable and required entry into Technical Specification (TS) 3.7.12, Condition B. This could have prevented the ability to control the release of radioactive material and is considered a potential loss of safety function per 10CFR50.72(b)(3)(v)(C). "Administrative controls in the ABSVS Boundary were re-established by installing a closure device in the opening on CV-31117 at 1246 CDT. The ABSVS boundary and both trains of ABSVS were declared operable at that time." During the time that the ventilation system was out of service, no evolutions were in progress that could have resulted in an unmonitored release. * * * RETRACTION ON 11/14/13 AT 1648 EST FROM STEPHEN SEILHYMER TO NESTOR MAKRIS * * * "After further evaluation, the non-closable boundary openings for the Auxiliary Building Special Ventilation Zone (ABSVZ) including CV-31117, Loop B Main Steam Isolation Valve (MSIV), at the time of discovery is calculated to be 9.48 square feet. This is below the 10 square feet required in TS 3.7.12, thus both trains of ABSVS were operable and no loss of safety function existed. "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-01
49494 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2013-11-01 09:02 | 2013-11-01 12:09 | 2013-11-01 | AGREEMENT STATE REPORT - LEAKING NI-63 SOURCE "The SC Department of Health and Environmental Control [DHEC] was notified on Friday, November 1, 2013, at 0902 hrs. [EDT], that during routine wipe testing of a Shimadzu GC14A gas chromatograph, an ECD containing 10 milliCuries of Ni-63 was found to have removable contamination exceeding 0.005 microCuries. The chromatograph was being tested in preparation for disposal when wipes of the inside of the chamber indicated contamination. The source was removed and properly bagged to prevent the spread of any further contamination. The chromatograph and source are secured in the Radiation Safety Laboratory awaiting disposal by a licensed vendor. The Radiation Safety Officer stated that wipes of the laboratory where the chromatograph had been located were analyzed and no removal contamination had been detected. "The Radiation Safety Officer was advised by Mark L. Windham [South Carolina DHEC] to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department. Updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2013-11-11
49493 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-10-31 | 2013-11-01 10:57 | 2013-11-01 | AGREEMENT STATE REPORT - RADIOPHARMACY WORKER EXTREMITY OVEREXPOSURE The following report was received from the Kansas Department of Health and Environment via facsimile: "Initial notification of an overexposure to the extremities of a radiopharmacy nuclear medicine technician at St. Francis Health Center, Topeka, KS, was made by the radiation safety officer. "A Landauer report received 10/31/2013 indicated a right hand dosimeter [dose] at 55.85 rem and a left hand dosimeter [dose] at 54.29 rem. Whole body badge [dose] indicated 36 mrem. The tech has been removed from any job duties involving occupational radiation exposure. A more detailed report is being prepared [by the licensee]." Kansas Report Number KS130009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-11-11
49492 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-11-01 03:09 | 2013-11-01 09:51 | 2013-11-01 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE NOT WITHIN LIMITS FOLLOWING TRIP OF EXHAUST FAN "On November 1, 2013 at 0309 EDT, Secondary Containment Zone I (Unit 1 Reactor Building) differential pressure was lost following a routine transfer of Reactor Protection System Power supplies. Upon restoration from the power supply transfer, one of the Reactor Building Exhaust Fans tripped. There were no obvious malfunctions associated with the equipment and fan was able to be restarted. Zone II (Unit 2 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone I differential pressure recovered within a few minutes and was verified to be stable. LCO 3.6.4.1 was entered for both units at 0309 EDT and exited at 0315 EDT. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. "There have been no further perturbations in differential pressure and secondary containment remains operable. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee notified the NRC Resident Inspector. See similar event number #49489. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-11-01
49491 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-10-31 17:22 | 2013-10-31 20:41 | 2013-10-31 | POSTULATED FIRE EVENT COULD RESULT IN A HOT SHORT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "Per review of OE INPO ICES-305419, 'Unfused remote DC ammeter circuit could result in a secondary fire due to multiple fire induced faults' from Davis-Besse and Cooper Condition Report CR CNS-2013-07413; it has been determined that JAF [James A. Fitzpatrick] is potentially susceptible to the same condition. "The condition in the Davis-Besse OE is described as follows: "The wiring design for the ammeters contains a shunt in the current flow from each direct current (DC) battery or charger. Bolted on the shunt bar are two IEEE 383 qualified leads to a current meter in the main control room (MCR). The small difference in voltage between the two taps on the shunt is enough to deflect the current gauge in the MCR when current flows from the battery or charger through the shunt. The ammeter wiring attached to the shunt does not have fuses. It is postulated that a fire could cause one of these ammeter wires to short to ground at the same time the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a ground loop through the unfused ammeter cable. With enough current going through the cable, the potential exists that the cable could self-heat to the point of causing a secondary fire in the electrical tray at some point along the path of the cable (including the Control Room) or possibly heat up to the point of causing damage to adjacent cables that may be required for safe shutdown. "TRM 3.7.M, Fire Barrier Penetrations, is applicable. The functional integrity of the fire barrier penetration seals ensures that fires will be confined or adequately retarded from spreading to adjacent portions of the facility. This design feature minimizes the possibility of a single fire rapidly involving several areas of the facility prior to detection and extinguishment. The fire barrier penetration seals are a passive element in the facility fire protection program and are subject to periodic inspections. The issue identified is with the potential of a fire starting in another location other than the original fire location bypassing fire barriers due to a fire induced electrical short. Per engineering, the areas with the deficient fire barriers are the DC Switchgear Rooms A and B, Cable Spreading Room, Relay Room and Control Room. An active LCO will track the TRM action for the non-functionality of those fire barriers. "This condition is being reported under 10CFR50.72 (b)(3)(ii)(B) as a condition that results in the plant being in an unanalyzed condition which significantly degrades plant safety. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-31
49490 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-31 17:12 | 2013-10-31 19:35 | 2013-10-31 | POSTULATED FIRE EVENT COULD RESULT IN A HOT SHORT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "While performing a review of industry OE [operating experience] concerning unfused ammeter circuits on station batteries, it was discovered that the ammeter circuits for all of the non-1E batteries are of a similar design to that described in the OE. Also, while reviewing additional DC circuits, it was discovered that the control circuit for the Turbine Generator Emergency Lube Oil pump is unfused, protected only by the motor circuit breaker with a trip setting of 350 amps. The concern is that under the fire safe shutdown rules it is postulated that a fire in one fire area can damage these circuits and cause short circuits without protection that would overheat the cables and possibly result in secondary fires in other fire areas where the cables are routed. The secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-31
49489 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-10-31 02:51 | 2013-10-31 05:00 | 2013-10-31 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE NOT WITHIN LIMITS FOLLOWING TRIP OF EXHAUST FAN "On October 31, 2013 at 0251, Secondary Containment Zone I (Unit 1 Reactor Building) differential pressure was lost following a routine transfer of Reactor Protection System Power supplies. Upon restoration from the power supply transfer, one of the Reactor Building Equipment Compartment Exhaust Fans tripped. There were no obvious malfunctions associated with the equipment and fan was able to be restarted. Zone II (Unit 2 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone I differential pressure recovered within a few minutes and was verified to be stable. LCO 3.6.4.1 was entered for both units at 0251 and exited at 0255. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. "There have been no further perturbations in differential pressure and secondary containment remains operable. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-10-31
49488 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-10-29 | 2013-10-30 15:46 | 2013-10-30 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK IN THE OPEN POSITION The following information was obtained from the State of Texas via email: "On October 30, 2013, the Agency [Texas Department of Health] was notified by the licensee that while conducting routine maintenance checks on a Texas Nuclear model 5196 nuclear gauge containing a 20 milliCurie cesium137 source, the shutter was found stuck in the open position. The licensee lubricated the operating shaft and attempted to close and reopen the shutter. While attempting to reopen the shutter, the operating rod for the shutter broke. The licensee determined the gauge is in the open position, which is the normal operating position for the gauge. The licensee has contacted the gauge manufacturer and will either repair or replace the gauge. No individual received any additional exposure as a result of this event. Additional information will be provided as it is received in accordance with Reporting Material Events SA-300." Texas Incident #: I-9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-11-07
49487 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-10-30 15:25 | 2013-10-30 16:44 | 2013-10-30 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSLY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to Millstone Power Station Unit 2 resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to short to the ground plane. Simultaneously, it is postulated that the fire causes another DC wire from the opposite polarity on the same battery to also short to the ground plane. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-30
49486 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2013-10-30 11:17 | 2013-10-30 16:43 | 2013-10-30 | POSTULATED FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to the Cooper Nuclear Station resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire could cause one of the ammeter wires to short to ground. Simultaneously, it is postulated that the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR. 50 Appendix R. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e.., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-30
49485 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2013-10-27 11:25 | 2013-10-30 14:21 | 2013-12-06 | AGREEMENT STATE REPORT - PORTABLE MOISTURE DENSITY GAUGE DAMAGED AT WORKSITE The following report was received from the North Dakota Department of Health via e-mail: "A portable moisture/density gauge possessed by ALLWEST Testing & Engineering, LLC of Hayden, Idaho containing a 10 mCi Cesium-137 sealed source and a 50 mCi Americium-241:Beryllium sealed source was crushed by a piece of heavy equipment (excavator bucket) at a temporary job site located southwest of Dickinson, North Dakota. The portable gauge user had failed to maintain constant surveillance of the gauge. Upon observing the heavy equipment running into the gauge, the user flagged down the heavy equipment operator to halt his activity. The operator lifted the bucket off the gauge and set it to the side. The gauge user instructed the operator to relocate to an area approximately 150 feet from the damaged gauge. Subsequently, he phoned his immediate supervisor and the Radiation Safety Officer (RSO) for guidance. An area at an approximate distance of 150 feet in three directions from the damaged gauge was roped off with 'Caution Radiation' tape. The fourth direction (east) consisted of a large hill of soil not readily accessible. "1:02 PM (MST): The gauge user placed a call to the ND State Radio emergency response number to report the event. "1:08 PM (MST): ND State Radio personnel notified the Stark County Emergency Manager (SCEM) who in turn notified the Southwestern District Health Unit Executive Officer (HUEO). "1:10 pm (MST): The HUEO notified the ND Department of Health Radiation Control Program Manager (RCPM) of the event. The RCPM informed the HUEO the gauge should remain in place until radiation surveys had been performed and the site evaluated by his department. "2:17 pm (MST): The HUEO and the SCEM were present at the event site. They met with the gauge user and the Westcon, Inc. HSE Coordinator for a briefing of the event. The HUEO performed an initial radiation survey using a calibrated SE International, Inc. Model Radiation Alert Inspector survey instrument (SN 35756). The survey was performed beginning at the outer boundary moving inwards toward the damaged gauge. The reading at a distance of 4 feet from the source was 0.063 mR/hr. The background reading was 0.013 mR/hr. The HUEO and SCEM instructed the gauge user to leave the gauge in place and wait for North Dakota Department of Health personnel to be on site the next morning to evaluate the site. Visual assessment of the gauge showed evidence of the two source housings to be physically intact. "October 28, 2013: "6:00 am (MST): As instructed by ALLWEST Testing & Engineering's RSO, the gauge user relocated the damaged gauge and associated fragments to the gauge transport case. The case was secured in the box of his pickup truck. "9:00 am (MST): North Dakota Department of Health (NDDoH) personnel were on site to perform interviews, radiation surveys and evaluation of the site. Radiation surveys were performed by the NDDoH using a calibrated Ludlum Model 19 microR meter (SN 270378) and a Canberra Dineutron neutron meter (SN 18327). The background readings were 12 microR/hr and 0.027 mR/hr respectively. The highest gauge shipping container surface readings were 3.1 mR/hr (gamma) and 0.09 mR/hr (neutron). Surveys of the pathway from the initial impact of the bucket to the gauge's final resting spot revealed background readings. A leak test of the gauge was performed and shipped via overnight express for analysis. The leak test results demonstrated no leakage. The gauge was transported by licensee personnel back to their Idaho office to make arrangements for final disposal. "Throughout the event, the gauge user had not worn personnel dosimetry. Exposure calculations will be performed by the RSO." * * * UPDATE FROM DAVID STRADINGER TO JOHN SHOEMAKER AT 1431 EDT ON 12/6/13 * * * The North Dakota Department of Health has completed their investigation. Several non-compliances were identified during the reactive inspection. A letter of apparent non-compliance was sent to the licensee. Corrective actions will be required to be submitted in response to this letter. The North Dakota Department of Health is recommending the LER (License Event Report) for closure. Notified the R4DO (Vasquez), R1DO (Cook), and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ID | OTH | AGR |  |  |  |  | 0 | 2013-11-07
49484 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2013-10-29 | 2013-10-30 14:36 | 2013-10-30 | ADMINISTRATION OF LESS THAN THE PRESCRIBED DOSE TO A PATIENT The following report was received from the Illinois Emergency Management Agency via e-mail: "On October 29, 2013, the RSO at Loyola University Medical Center (IL-01131-02) called to report a medical event which occurred at their facility the previous day. A treatment dose of 115 Gray (10.5 mCi) of Nordion's Y-90 Theraspheres was prescribed. However, at the completion of the treatment and in accordance with manufacturer's use instructions, the system was evaluated for residual material. Elevated levels were detected within the combination of the catheter, tubing and source delivery vial apparatus. Those elevated levels were determined to correspond to over 2 mCi of Y-90. A detailed evaluation revealed 8.04 mCi had been administered for a total delivered dose of 88 Gray or 76.5% of the intended dose. Most of the remaining 2.5 mCi of Y-90 was adhered within the catheter about 1 inch from the catheter/tubing interface connector despite successfully completing the treatment in less than a minute including 3 successful flushes of the system with 30 cc of sterile solution. No material was detected as remaining in the source vial which was monitored closely during the treatment with a dedicated dosimeter nor were there any observable defects in the catheter or manufacturer supplied tubing where the microspheres had accumulated. "As per regulations, the patient was advised of the situation by the interventional radiologist. Neither the physician authorized user, an oncologist, nor the interventional radiologist believes that there will be any adverse impact to the patient as a result of the lowered dosage. There are no plans to supplement/repeat this treatment to deliver any remaining/additional amount of radiation nor does the licensee have any immediate corrective actions to implement in that the procedure already follows the manufacturer's recommendations. The licensee is aware of the requirement to submit a written report within 15 days." The cause of this event was equipment failure. Illinois Item Number: IL13032 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2013-11-07
49483 | 0 | U.S. AIR FORCE |  |  |  |  | 2013-10-17 08:00 | 2013-10-29 13:50 | 2014-01-30 | LOST GENERAL LICENSE DEVICE CONTAINING A NICKEL 63 SOURCE "On January 20, 2012, leak tests were conducted on all [Air Force] BE's [Bioenvironmental Engineering] APDs [air particulate detectors] with the expectation of disposing them to AFRRAD [Air Force Radioactive Recycling and Disposal]. The APDs were placed in storage at the BE office (Bldg. 3423) awaiting sample results and direction from AFRRAD. At the time, AFRRAD had a backlog in workload and were not receiving GLDs [general license devices]. During a GLD program review on Oct.17, 2013, BE determined that the GLD, a Smith's Detection APD-2000 (ECN: 0300069, SN: 4150) was missing and likely disposed via DRMO [Defense Reutilization and Marketing Office]. A records search commenced immediately. "In April 2013, a SSgt [Staff Sergeant] at 779 AMDS/SGPB began the equipment turn-in process on a GLD, a Smith's Detection APD-2000 (ECN: 0300069, SN: 4150). The GLD was turned over to 779 MDSS/MERC by another SSgt, via AF Form 601 and radiation leak sampling data for the item. Upon receipt of the GLD, MERC then turned it over to 779 MDSS/SGSM. On April 24, 2013, the GLD was removed from the BE Flight's Defense Medical Logistics Standard Support (DMLSS) account, and identified for 'turn-in to DRMO'. "The SSgt [at 779 AMDS/SGPB], contacted the Defense Logistics Agency (DLA) warehouse at Ft. Meade on Oct. 23, 2013 [and] visited them in an effort to retrieve the missing GLD. DLA [Defense Logistics Agency] records management was overhauled shortly after the item was turned in, thus records relating to the GLD from the warehouse were unable to be furnished. Bioenvironmental Engineering's radiation detection equipment, a SAM940 & Victoreen 451P, were used but [the search] was unsuccessful in locating the GLD at the warehouse. DLA warehouse management has been instructed to immediately notify 779 AMDS/SGPB should the GLD be discovered at their location." The licensee considers the device un-retrievable and has contacted NRC R4 (Cook). * * * UPDATE FROM MAJ. DANIEL SHAW TO HOWIE CROUCH AT 1229 EST ON 1/30/14 VIA EMAIL * * * "The missing ADP-2000 reported (Incident report 49483) has been located by the installation RSO at Andrews, AFB, MD. The source was located [approximately 1/20/2014]. The item has been secured and will be turned in for proper disposal as radioactive waste. "Note: No leakage or physical damage to the device was noted. No personnel were exposed as the device contains an embedded Ni-63 source with low energy beta emissions. "Background: The subject device was turned into the Defense Reutilization Management Office (DRMO). DRMO realized that the device contained radioactive material and returned the device to the owning organization. "Device specifications: Model APD-2000, serial no. 4150, 10 mCi, Ni-63." The licensee has notified NRC Region 4. Notified R4DO (O'Keefe) and FSME Events Resource (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-11-06
49482 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-10-29 06:05 | 2013-10-29 13:10 | 2013-10-29 | OFFSITE NOTIFICATION DUE TO EMPLOYEE FATALITY "At approximately 0530 MST on October 29, 2013, an Arizona Public Service Company (APS) employee developed a personal medical condition in the Owner Controlled Area prior to entering the Protected Area at the Palo Verde Nuclear Generation Station (PVNGS). PVNGS Emergency Medical Technicians responded and transported the individual to an offsite emergency trauma center. Upon arrival at the trauma center, medical personnel declared the individual deceased at 0650 [on 10/29/13]. "The fatality was not work related and the individual was outside of the Radiological Controlled Area. No radioactive material or contamination was involved. No news release by APS is planned. Notifications to the Arizona Division of Occupational Safety and Health, and the Maricopa County Sheriff's Office are planned. "The NRC Resident Inspectors have been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Defueled | Power Operation | Power Operation | Defueled | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-29
49481 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2013-10-29 05:56 | 2013-10-29 11:45 | 2013-10-29 | UNPLANNED LOSS OF TEN AREA RADIATION MONITORS IMPACTING EMERGENCY ASSESSMENT CAPABILITY "At 0556 EDT, [on 10/29/13], Nine Mile Point Unit 1 experienced an unplanned loss of ten area radiation monitors due to a loss of the associated power supply. These monitors are located throughout the station. Compensatory local monitoring was established in the affected areas until the area radiation monitors could be restored to service. The cause of the loss of the power supply was determined to be a blown fuse. The fuse was replaced and the power supply was restored at 1040 EDT. All area radiation monitors are restored. Post maintenance testing is in progress. "The condition is reportable as a major loss of emergency assessment capability in accordance with 10CFR50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. "An update will be provided once the area radiation monitors have been restored to functional status." * * * UPDATE FROM RYAN C. HAMILTON TO PETER J. SNYDER AT 1545 EDT ON 10/29/13 * * * "Post maintenance testing is complete and the affected area radiation monitors are declared functional as of 1440 [EDT] on 10/29/13." Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-29
49480 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2013-10-29 05:00 | 2013-10-29 05:01 | 2013-10-30 | MAIN STACK RADIATION MONITORS REMOVED FROM SERVICE "At 0500 [EDT] Tuesday, October 29, the Peach Bottom Atomic Power Station (PBAPS) main stack radiation monitors will be removed from service for planned preventative maintenance activities on the flow elements. This maintenance is scheduled to be worked continuously until completion to minimize out of service time. The planned main stack radiation monitor outage is scheduled to be completed within 13 hours. Periodic gas sampling will be performed in accordance with the offsite dose calculation manual while the monitors are out of service. "The NRC Resident Inspector has been notified. "There are no follow-up written reports required for this event." * * * UPDATE ON 10/30/13 AT 0216 EDT FROM BOB RAUCCI TO DONG PARK * * * "This is an update to notification #49480. The out of service duration has been extended from the original estimated 13 hours due to work scope taking longer than expected with fatigue rule compliance requirements. The radiation monitor maintenance has been completed and the components have been restored to service, however, the post maintenance testing will be delayed until this morning (10/30/13) when the necessary component expert resource is next available. Periodic gas sampling remains in effect in accordance with the Off Site Dose Calculation Manual." The licensee will notify the NRC Resident Inspector. Notified R1DO (Krohn). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-29
49479 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-10-28 11:30 | 2013-10-28 16:03 | 2013-10-28 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State of California submitted the following via email: "At 1130 [PDT] on October 28, 2013, the RSO for AMEC called to report a stolen moisture density [M/D] gauge: Troxler, model 3440, S/N 36036 that contains 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be. "The stolen gauge was last seen on Friday, October 25, 2013 by the authorized user, who secured the M/D gauge in safe mode inside the locked yellow transportation box which was placed inside a locked metal box. The contractor's tools at the site in Mission Valley, CA was also burglarized and a police report was filed. "The [metal] box's lock had been drilled out and the chain attaching it to the building was cut. RHB [Radiation Health Branch] advised the RSO to place a Lost/Found notice in the local paper offering a reward for return of the gauge to AMEC." CA 5010 Number: 102813 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-11-05
49478 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-10-28 12:30 | 2013-10-28 18:02 | 2013-10-28 | POSTULATED EVENT COULD RESULT IN A HOT SHORT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused direct current (DC) ammeter circuits in the control room has determined that the condition described below applies to Fort Calhoun Nuclear Station. This could result in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. "The control room ampere indications for the Class 1E batteries and their chargers do not include over-current protection to limit fault current. "In a postulated event, a fire in the control room could cause one of the ammeter wires to hot-short to the ground plane. Simultaneously, the event could cause another DC wire from the opposite polarity on the same battery to hot-short to the ground plane. This would cause a ground-loop through unprotected ammeter wiring. "Since this circuit is not protected (not fused), this event could result in excessive current flow in the ammeter wiring to the point of causing a secondary fire in the associated raceway system. This could potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-28
49477 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2013-10-23 | 2013-10-28 11:16 | 2013-10-28 | AGREEMENT STATE REPORT - GAUGE DAMAGED IN A FIRE The following report was received from the Illinois Emergency Management Agency, Bureau of Radiation Safety via e-mail: "PDV Midwest Refining (CITGO) in Lemont, IL called on 10/26/13 to report a fixed gauge that was involved in a fire on 10/23/13. The gauge is an Ohmart/Vega gauge containing 37 GBq (1 Ci) of Cs-137. Their consultant had been on site and done a characterization of the area. The housing looked to be intact and radiation surveys at 35 feet from below the housing were 40 microR/hr. A contamination survey of material under the vessel indicated no contamination at this time. No one is able to get into the immediate area because of debris and a perimeter has been established. IEMA/BRS [Illinois Emergency Management Agency, Bureau of Radiation Safety] inspectors have been dispatched to the scene for further evaluation." Item Number: IL13030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2013-11-05
49476 | -1 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-27 17:30 | 2013-10-27 22:29 | 2014-01-30 | AUXILIARY BUILDING GAS TREATMENT SYSTEM INOPERABLE "At 1730 EDT on 10/27/2013, SQN [Sequoyah Nuclear] discovered that Unit 1 containment penetration X-108 had a maintenance flange installed with a service air connection attached. The service air connection was connected to a temporary air compressor supplying air to maintenance loads inside Unit 1 containment. Contrary to the requirements of the breaching permit, personnel were not stationed at the penetration to isolate the service air connection in the event of the air line rupturing inside Unit 1 containment or upon initiation of an auxiliary building isolation signal. Since the Unit 1 containment is open to the auxiliary building as part of outage activities, if the service air line had ruptured, the additional air into the Unit 1 containment could have exceeded the capacity of the Auxiliary Building Gas Treatment System (ABGTS) and potentially have impacted the ability of the ABGTS to perform its design safety function. This resulted in both trains of the ABGTS being declared inoperable requiring Unit 2 to enter the action of LCO 3.0.3. The service air line was isolated immediately and Unit 2 exited the action of LCO 3.0.3 at 1732 EDT. At the time of the event, Unit 1 was defueled and did not require ABGTS to be operable. Unit 1 subsequently entered Mode 6 at 1904 EDT on 10/27/2013 and is currently conducting refueling operations. Unit 2 remains in Mode 1, 100% power and stable. There were no actual operational impacts to either unit." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM BRUCE BUCH TO DANIEL MILLS AT 1428 EST ON 1/30/2014 * * * "Sequoyah Nuclear Plant, Units 1 and 2, are retracting the 8 hour non-emergency notification made on October 27, 2013 at 2229 EDT (EN# 49476). "The notification on October 27, 2013, reported that if the service air line (associated with penetration X-108) had ruptured, the additional air into the Unit 1 containment could have exceeded the capacity of the Auxiliary Building Gas Treatment System (ABGTS) and potentially have impacted both trains of ABGTS from performing its safety function(s). "Subsequent engineering analysis concluded acceptable margin was available. Both trains of ABGTS would have remained operable and capable of performing its design function(s) at all times. The engineering analysis results are captured in the licensee's corrective action program. Based on the new analysis, the condition reported in EN #49476 did not result in a potential uncontrolled radioactive release. This event report is being retracted. "The NRC Resident Inspector has been briefed on the analysis results and informed of this retraction." Notified R2DO (McCoy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-10-27
49475 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2013-10-27 10:55 | 2013-10-27 14:16 | 2013-10-27 | FAILURE OF A STEAM SUPPLY VACUUM BREAKER "During performance of a preventive maintenance check of [Item Relied On For Safety] IROFS 3526 [Uranium Dioxide steam supply system], it was determined to have failed, that is, blocked preventing it to perform its safety function as a vacuum breaker. This vacuum breaker is in a steam line from an unfavorable geometry steam boiler to process service subsystems. This vacuum breaker is designed to prevent backflow from Tank TK-102 when the heat exchanger E-102 leaks internally and the steam supply is off, Accident Sequence 2.13, in E04-NCSA-070 version 11 for the ADU [Ammonium Diuranate] process. This vacuum breaker is also used in Accident Sequence 5.4, E04-NCSA-120 version 16 for the UNH [Uranal Nitrate Hydroxide] reprocessing Integrated Safety Analysis (ISA). This sequence is the transfer of UNH from uranium powder dissolver to the unfavorable geometry steam boiler when the loss of its heat source causes a vacuum in the steam boiler. Additionally this IROFS is used in Accident Sequence 7.5, E04-NCSA-190 version 10 for the UO2 pellet dissolution process. The IROFS prevents UNH to backflow into the unfavorable geometry steam boiler. The UO2 steam boiler was shut down at the time of the finding and remains shutdown. The other IROFS 3527 in these sequences remained available during the time. This was verified when performing the PM. "This determination was completed at 1055 PDT on 10/27/2013. The extent of condition to evaluate other potential uses of this type of vacuum breaker is underway. The safety significance is low as the independent IROFS 3527 was verified to be available and reliable via the testing. The system was shut down and remains shutdown for further evaluation, the failed vacuum breaker has been replaced and verified operable." The licensee will notify Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2013-10-27
49474 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-10-25 14:30 | 2013-10-25 21:21 | 2013-10-25 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED BY EXCAVATOR The following Agreement State Report was received via email: "On October 25, 2013, at approximately 1430 [PDT], Fazel Barmaki, RSO [Radiation Safety Officer] of Fazel Barmaki, RML 7923-37, contacted [California Radiologic Health Branch] RHB Brea concerning their moisture/density gauge, CPN model MC-3, S/N M321106780 (with 10 mCi Cs-137 and 50 mCi Am-241/Be sources) that had been run over by an excavator and damaged while performing measurements at a construction site at 1186 N Ridgeline Rd., Orange, CA. A [California State] ICE RAM-South inspector arrived at the scene to assess the situation and to verify the integrity of the sources. The inspector observed the scene and was able to determine that the Cs-137 source was in the shielded position and the Am-241/Be source was still in the shielded housing. Wipe tests taken at the scene were surveyed and were found to be at background, indicating that the sources were not leaking. The rest of the gauge was inspected and it was observed that the hand and guide tube had broken off from the housing and the electronics were smashed and broken off of the gauge. Despite the damage to the non-radioactive parts, the shielding appeared to be undamaged, and the housing was placed in the transport case. A survey was performed on the transport case while using a Victoreen CHP-450. The highest dose rate on contact with the transport case was 1.8 mR/hr and 0.3 mR/hr at one foot, with a background of 0.01 mR/hr. These dose rates are consistent with a CPN MC-3 moisture density gauge. "The RSO was interviewed by the [California State] inspector who stated that, between taking readings, he was observing the excavator as it was moving while standing near the gauge, making sure to maintain position between the excavator and gauge. While observing the excavator, the excavator made a sudden move toward him and he had to jump out of the way to prevent being run-over and the gauge was run over, causing the damage to the gauge. After checking on the damage, the RSO then immediately contacted RHB to report the incident. "Since the radiation surveys indicated the dose rates were consistent with an intact and operational CPN MC-3 gauge and no leakage was indicated by an inspection of the integrity of the shielding and wipe tests at the scene of the incident, the RSO was allowed to return the gauge to their storage location at [in Escondido, CA.], for storage until the gauge can be sent to a service provider or CPN for repair or replacement. The [State's] investigation will be ongoing to determine if licensee will be cited. This is being reported to the NRC Operations Center as a 24 hour report under 10 CFR 30.5(b)(2) since the gauge cannot be locked in the shielded position (due to the source rod being sheared off from the gauge) despite the fact that the Cs-137 source is in the shielded position since it was in the shielded position at the time of the incident." California Report Number: 102513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-11-04
49473 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-10-24 10:35 | 2013-10-25 15:24 | 2013-10-26 | FAILURE OF RADWASTE BUILDING EFFLUENT RADIATION MONITOR "At 1035 [PDT] on October 24, 2013, during a channel functional test (CFT), the intermediate radiation effluent monitor on the radwaste building failed an as found range check and was declared inoperable. A single range check was found out of tolerance low. The as found values on the remaining five ranges that the instrument spans were within the acceptance criteria. This monitor is one of three methods of declaring a general emergency due to offsite radiation releases originating in the radwaste building. Lower emergency classification levels are supported by a separate radiation monitor that was not impacted. The failure to complete the CFT on the intermediate range monitor with all ranges yielding satisfactory as found values represents a potential major loss of emergency assessment capability. This issue is being conservatively reported under 10 CFR 50.73(b)(3)(xiii). Efforts are underway to restore the monitor and an update will be made when the monitor is returned to service." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM EDAN ENGSTROM TO JOHN SHOEMAKER AT 2044 EDT ON 10/26/13 * * * "The intermediate radiation monitor on the radwaste building has been returned to within tolerance. The radiation monitor has been declared functional at 1558 PDT on 10/26/2013. "The licensee has notified the NRC Resident Inspector." Notified the R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-25
49472 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-10-14 | 2013-10-25 14:04 | 2013-10-25 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATORS The following Agreement State Report was received via facsimile: "Two static eliminators each initially containing 10 mCi, Po-210, were misplaced during the departmental move from one [licensee] facility to another. Each alpha emitting device is identified as a static eliminator manufactured by NRD, LLC of Grand Island, NY, Model No. P.2021.8203, with corresponding Serial No.'s of A2GF745 and A2HD506. The devices were reported missing subsequent to an inventory check. "Calculated device activity with Po-210 half-life = 138 days. "Device Serial No. A2GF745 was shipped by NRD to LTI on June 6, 2008 thus the original activity of 10 mCi is currently calculated to be 0.5 uCi. "Device Serial No. A2HD506 was shipped by NRD to LTI on April 7, 2010 thus the original activity of 10 mCi is currently calculated to be 15 uCi. "The aggregate activity exceeds the threshold of 1.0 uCi (i.e.10 X 0.1 uCi), per CMR 120.297 Appendix C. "The Agency [Commonwealth of Massachusetts] will continue to investigate this matter. "Cause: It is believed that during departmental moves from the Lenox, MA facility to a new location in Pittsfield, MA, that two static eliminators were misplaced." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-11-04
49471 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-10-24 05:53 | 2013-10-24 09:45 | 2014-09-10 | MANUAL REACTOR TRIP FROM FULL POWER DUE TO FEEDWATER SYSTEM OSCILLATIONS "At 0553 EDT on 10/24/2013, Oconee Unit 3 was manually tripped due to oscillations in the feedwater system in anticipation of an automatic reactor trip. At 0549 EDT, Unit 3 began experiencing small feedwater oscillations. The feedwater control system was placed in manual in an attempt to stabilize feedwater flows. Feedwater oscillations continued to grow in magnitude and at 0553 EDT, a manual trip was directed to prevent an automatic reactor trip. "Due to an RPS actuation, this event is being reported as a 4 and 8 hour Non-Emergency per 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.72 (b)(3) "Following the reactor trip, four main steam relief valves failed to reseat. Procedure guidance was utilized to reduce main steam system pressure by approximately 30 psig to reseat the main steam relief valves. All main stream relief valves are now reseated. All other post trip conditions were normal and all other systems performed as expected. Unit 3 is currently in Mode 3 and stable. "Operations have been stabilized on Unit 3. A post-trip investigation is in progress, per site procedures and directives." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BOB MEIXELL TO DONALD NORWOOD AT 1439 ON 9/10/14 * * * "Duke Energy reviewed NRC Event Number 49471 against NUREG 1022, Rev 3, section 3.2.6, "System Actuation" and determined this event should have been reported only per 10 CFR 50.72 (b)(2)(iv)(B), RPS Actuation (while critical). Thus, Duke Energy is revising NRC Event Number 49471 to remove the 8-hour report criteria 10 CFR 50.72 (b)(2)(iv)(A). The NRC Resident Inspector was notified of this revised report. "This update has no effect on safety significance." Notified R2DO (Shaeffer). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-10-24
49470 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2013-10-23 | 2013-10-23 21:18 | 2013-10-23 | AGREEMENT STATE REPORT - DAMAGED SOIL MOISTURE DENSITY GAUGE The following report was received from the Florida Department of Health, Bureau of Radiation Control, via e-mail: "A soil moisture density gauge was damaged by heavy construction equipment. The source was reported to be retracted and not exposed. The electronics panel and housing was reported to be damaged. A Bureau of Radiation Control Inspector is en route. "The incident occurred at a temporary work site in Walnut Hill, Florida. The gauge contained a 10 mCi Cesium 137 source and a 50 mCi Americium241/Beryllium source." The State of Florida Bureau of Radiation Control will update the report as more information is known. Verbal information from the State indicated that the licensee could not verify the integrity of the source because the company does not have access to a radiation detector. Florida Incident Number: FL13-074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-10-31
49469 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2013-10-23 14:05 | 2013-10-23 15:25 | 2013-10-23 | OFFSITE NOTIFICATION OF A FATALITY ONSITE "This is a non-emergency event notification. "On 10/23/2013, a supplemental worker (i.e., a contract individual) suffered an apparent heart attack while servicing portable lighting equipment in a site perimeter parking lot. This parking lot is used by plant workers and is located outside of the Owner Controlled Area. Medical personnel who responded to this location found the worker unresponsive and transported the individual by ambulance to a local hospital for treatment. Following the evaluation by emergency room personnel, the individual was pronounced deceased at 1016 EDT. OSHA was being notified pursuant to the requirements of 29 CFR 1904.39 based on a fatality that could be work related. As such, this ENS report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(xi). There was no radioactive contamination involved in this event. The health and safety of the public was not affected. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-23
49468 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-10-22 18:32 | 2013-10-23 15:02 | 2013-10-23 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been placed on hold. The licensee notified the NRC Resident Inspector. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled | Power Operation | Power Operation | Defueled | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2013-10-23
49467 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-10-23 10:10 | 2013-10-23 13:08 | 2013-10-23 | STACK RADIATION MONITORS OUT OF SERVICE FOR PRE-PLANNED MAINTENANCE Millstone Unit-2 is performing pre-planned maintenance on the power station stack and Unit-2 high range stack radiation monitors. The monitors are expected to be out of service for six hours. Notified the R1DO (Holody). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-23
49466 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-10-23 | 2013-10-23 12:20 | 2013-10-23 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY CAMERA SOURCE TO FULLY RETRACT The following report was received from the Texas Department of State Health Services, Radiation Branch, via e-mail: "On October 23, 2013, the licensee notified the Agency [Texas Department of Health] that one of its radiography crews had been unable to retract an iridium-192 source back into a QSA 880D exposure device at a temporary work site in Baytown, Texas. Following an exposure, the source pigtail would not retract fully into the device. An authorized person, the Radiation Safety Officer (RSO), performed the source retrieval. He received an estimated 600 millirem dose. No member of the public received any exposure as a result of this event. The RSO reported that he had to disconnect the crank handle from the drive cables to pull the source back into the camera. The cause was an equipment failure of the drive cable which was binding. A new set of drive cables was attached to the camera and the source moved in and out freely about 10 times. The drive cables were only 3 weeks old. They will be returned to the manufacturer for inspection. An investigation into this event is ongoing. Information will be provided as it is obtained in accordance with SA-300. "Camera and source information: QSA 880D camera, serial number D4621, source model number 424-9, source serial number 98960B." Texas Incident Number: I-9130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-10-31
49465 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-10-23 06:20 | 2013-10-23 10:20 | 2013-10-23 | REACTOR BUILDING DIFFERENTIAL PRESSURE LESS THAN REQUIRED BY TECHNICAL SPECIFICATIONS "On October 23, 2013 at 0620, Susquehanna Steam Electric Station operators observed secondary containment differential pressure was at negative 0.17 inches water gauge for Zone II (Unit 2 Reactor Building). Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. Zone I (Unit 1 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone II differential pressure was restored to within the required band by manual damper adjustment in about 15 minutes and was verified to be stable. LCO 3.6.4.1 was entered for both units at 0620 and exited at 0635. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-10-23
49464 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-10-22 14:00 | 2013-10-22 19:28 | 2013-10-22 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to Nine Mile Point, Units 1 and 2 resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to short to the ground plane. Simultaneously, it is postulated that the fire causes another DC wire from the opposite polarity on the same battery to also short to the ground plane. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. This condition has been entered into the Nine Mile Point corrective action program as Condition Reports CR-2013-008747 (NMP1) and CR-2013-008749 (NMP2). "This condition is being reported in accordance with 10 CFR 50.72(b)(3(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plants. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-22
49463 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2013-10-22 10:59 | 2013-10-22 16:59 | 2013-10-22 | RANDOM FITNESS FOR DUTY CONFIRMED POSITIVE FOR A NON-LICENSED CONTRACT SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The contractor's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.719 |  |  |  | 0 | 2013-10-22
49462 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2013-10-22 11:29 | 2013-10-22 15:34 | 2013-10-22 | SECONDARY CONTAINMENT PERSONNEL AIR LOCK DOOR INTERLOCK FAILURE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), 'Event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material.' An employee entered a secondary containment interlock and while the door was closing, another employee opened the other secondary containment interlock door thereby having two doors open. The employee immediately secured both doors in the interlock and notified the main control room supervisor. Both doors in the interlock were open for approximately 10 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the main control room, has remained satisfactory and less than -0.25 inches of H20 at all times. Initial investigation determined that a mechanical interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the mechanical interlock." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-10-22
49461 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-22 11:44 | 2013-10-22 13:18 | 2013-10-22 | MANUAL REACTOR TRIP DUE TO DECREASING CONDENSER VACUUM "At 1144 EDT, Vogtle Unit Two was manually tripped in response to lowering Main Condenser vacuum. The Unit 2 Bravo Main Feed Pump was tagged out for scheduled maintenance and the casing was being removed when condenser vacuum started lower due to isolation valve not holding pressure. Main Condenser vacuum lowered to less than procedural limits for continued plant operation. "All systems operated correctly in response to the reactor trip. All control rods fully inserted. AFW was placed in service to control Steam Generator levels. System response allowed for an uncomplicated reactor trip response. Plant is stable in Mode 3 while performing a cause investigation. "The NRC Senior Resident Inspector was notified and at plant site." The plant is in a normal post-trip electrical line-up. Decay heat is being removed via the steam dumps to the Main Condenser. | 0 | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-10-22
49460 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-08-23 07:54 | 2013-10-22 12:43 | 2013-10-22 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID PRIMARY CONTAINMENT ISOLATION VALVE ACTUATION "At 0754 on 8/23/13, a loss of power to the Reactor Protection System (RPS) 'B' occurred due to the unexpected opening of the circuit breaker (RPS-CB-MG2) for the RPS 'B' motor generator due to a failure of the voltage regulator circuit card. The loss of RPS 'B' resulted in a half scram signal, closure of Primary Containment Isolation Valves (PCIVs) from multiple systems and loss of power to main steam line radiation monitors (MS-RIS-610B & MS-RIS-610D). No plant parameters or maintenance activities existed which would cause the opening of RPS-CB-MG2 or actuation of the primary containment isolation; therefore, this is considered to be an invalid actuation of a system listed in 10CFR50.73(a)(2)(iv). "The half scram signal, closure of Primary Containment Isolation Valves (PCIVs) from multiple systems, and loss of power to main steam line radiation monitors were an expected response to the loss of RPS 'B'. "RPS 'B' was repowered from an alternate power supply. The half scram signal was reset, the containment isolation valves were opened and the affected systems were returned to normal operation. The voltage regulator circuit card was replaced and RPS 'B' was returned to its normal power supply. "As indicated in 10CFR50.73(a)(1), in the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv)(A), the licensee may, at its option, provide a telephonic notification to the NRC Operations Center within 60 days of discovery of the event instead of submitting a written LER. This 60-day telephone notification is being made to meet the reporting requirements instead of submitting an LER since the actuation was invalid. "The following additional information is provided as specified in NUREG-1022: "The specific train(s) and system(s) that were actuated: PCIVs in multiple systems EDR-V-19 Drywell Equipment Drain Inboard Isolation Valve EDR-V-20 Drywell Equipment Drain Outboard Isolation Valve FDR-V-3 Drywell Floor Drain Inboard Isolation Valve FDR-V-4 Drywell Floor Drain Outboard Isolation Valve RWCU-V-1 Reactor Water Cleanup Suction Inboard Isolation Valve RWCU-V-4 Reactor Water Cleanup Suction Outboard Isolation Valve RRC-V-19 Reactor Water Sample Inboard Isolation Valve RRC-V-20 Reactor Water Sample Outboard Isolation Valve TIP-V-15 Traversing In-Core Probe Purge Isolation Valve CRD-V-11 Control Rod Drive Scram Discharge Volume Drain Valve "Whether each train actuation was complete or partial: All PCIVs actuations for a loss of RPS 'B' were complete. The reactor half scram for a loss of RPS 'B' was a partial activation. "Whether or not the system started and functioned successfully: All PCIVs functioned successfully." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-10-22
49459 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-10-22 09:30 | 2013-10-22 12:41 | 2013-10-22 | EMPLOYEE EXPERIENCING CHEST PAIN TRANSPORTED FOR OFFSITE MEDICAL TREATMENT "An employee experiencing chest pains reported to the on-site dispensary this morning. The plant nurse administered first aid and then sent the employee to an off-site medical facility. A whole body survey of the employee's plant clothing was performed. The maximum amount of contamination found was present on the employee's right boot, 197,000 dpm/100cm2. Prior to leaving the Restricted Area, the employee's plant clothing was removed, and he was whole body frisked out of the plant. The employee was free of contamination upon release." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-10-22
49458 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2013-10-21 18:00 | 2013-10-21 18:21 | 2013-10-21 | OFFSITE NOTIFICATION DUE TO RELEASE OF PETROLEUM FROM AN UNREGULATED SOURCE "This is a non-emergency event notification. "During planned outage work, H. B. Robinson Steam Electric Plant (HBRSEP), Unit #2 personnel encountered soils with a petroleum odor in an area excavated for inspection of Emergency Diesel Generator fuel oil piping. The inspections were being performed as part of the Buried Piping and Tanks Inspection Program. "Pressure testing of the fuel oil underground piping on 10/14/13 was satisfactorily completed. Additionally, ultrasonic testing (UT) performed on the exposed diesel fuel oil pipes confirmed piping integrity. These fuel oil lines are typically pressure tested on a two year frequency and were previously tested in 2012 with similar results. The release was determined to be historical and transient in nature. "The soil that was removed was replaced with uncontaminated soil. Any future actions will be coordinated with SC DHEC. "HBRSEP, Unit #2 personnel are notifying SC DHEC in accordance with reporting guidance regarding the release of petroleum from an unregulated source. "This event is reportable per 10 CFR 50.72(b)(2)(xi) as described in NUREG-1022, based on an event related to protection of the environment for which a notification to other government agencies has been made. "The health and safety of the public was not affected. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-21
49457 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-19 23:30 | 2013-10-21 15:02 | 2013-10-21 | OFFSITE NOTIFICATION DUE TO SPILL OF WATER CONTAINING LOW-LEVEL TRITIUM CONCENTRATION "A spill of greater than 100 gallons of water, containing a low-level tritium concentration with the potential to reach groundwater has occurred on the Catawba site. The tritium levels in this water were 8,314 picocuries per liter, less than one-half of the US Environmental Protection Agency drinking water standard for tritium of 20,000 picocuries per liter. "While conducting planned Unit 2 maintenance activities, water from the main condenser was being pumped to a site collection pond and overflowed due to exceeding capacity. The source of the spill was stopped. Based upon the on-site spill location and low tritium levels, there is no health or safety risk to the public or employees. "In accordance with the industry voluntary Groundwater Protection Initiative, the NRC Resident Inspector, states, and counties will be notified." | 100 | 19 | 0 | 100 | 19 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-21
49456 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-10-19 23:20 | 2013-10-20 11:07 | 2013-10-20 | LICENSED OPERATOR TESTED POSITIVE FOR ALCOHOL ON A FOR-CAUSE FITNESS FOR DUTY TEST A licensed operator had a confirmed positive for alcohol during a for-cause fitness for duty test. The employee's access to the plant has been placed on hold. The licensee has notified the NRC Resident Inspector. | 90 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2013-10-20
49455 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-10-19 17:05 | 2013-10-19 23:00 | 2013-10-19 | PARTIAL LOSS OF OFFSITE COMMUNICATIONS DUE TO A BLOWN FUSE "On 10/19/2013 at 1705 CDT, Browns Ferry Nuclear Plant (BFN) experienced a partial loss of offsite communications, which included the NRC Emergency Notification System, the Emergency Plan Paging System and normal phone communication to offsite. Main control room indications and assessment capability were not affected. The Nextel cellular phone system and the satellite phones in the control rooms were unaffected. The plant radio system was also unaffected. The Emergency Response Data System is currently out of service due to planned maintenance on the associated offsite power supply. Operation of BFN Unit 1, Unit 2, and Unit 3 was not affected by the event. "The BFN facilities personnel found a blown fuse in one of the temporary Diesel Generators (DGs) supplying the node associated with the outside phone communications. The fuse was replaced and the DG has been in-service with no issues. Normal communications and access have been restored. "The NRC Senior Resident Inspector has been notified. "This event is reportable under 10CFR50.72(b)(3)(xiii), 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability' (e.g., significant portion of control room indication, emergency notification system, or offsite notification system)." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-19
49454 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-10-19 03:31 | 2013-10-19 09:57 | 2013-10-19 | GROUP 1 ISOLATION DUE TO HIGH REACTOR WATER LEVEL "On Saturday, October 19, 2013 at 0331 hours, with the reactor critical at approximately 1% core thermal power and the mode switch in start-up, a high reactor water level condition resulted in a main turbine trip and a valid Group 1 isolation signal. As a result, the Main Steam Isolation Valves (MSIVs) closed. "The plant was in start-up from a forced outage. The initial plant conditions were reactor pressure at approximately 280 psig with a corresponding reactor coolant temperature for that pressure. Currently reactor pressure and water level are being maintained with the MSIVs closed in normal bands. The reactor is being cooled down in preparation for operation in shutdown cooling. Off-site power is supplying station power from the Start-up Transformer (normal power supply for shutdown operations). All plant systems responded as designed. "The cause of the increase in reactor water level is currently under investigation. "This event had no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-10-19
49453 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-19 06:43 | 2013-10-19 09:36 | 2013-10-19 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "VEGP [Vogtle Electric Generating Plant] unit two was at 100% power, normal activities, when the unit two turbine tripped causing an automatic reactor trip. All control rods fully inserted and nothing unusual was noted. Auxiliary feed water and feedwater isolation actuated as expected. The unit is currently stable in Mode 3 at normal operating temperature and pressure. A forced outage response team has been formed to determine the cause of the turbine trip and determine restart criteria and time of restart." During the transient, no relief valves lifted. The electrical grid is stable and supplying plant safety loads. Decay heat is being removed via steam dumps to the condenser. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-10-19
49452 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-10-18 13:28 | 2013-10-18 19:38 | 2013-10-18 | POTENTIAL FOR HIGH ENERGY LINE BREAK ON LETDOWN SYSTEM OUTSIDE CONTAINMENT "A postulated High Energy Line Break (HELB) between the Letdown Heat Exchanger and its containment penetration has been identified in the Fort Calhoun Station calculation FC07885, Rev. 0, Stress Analysis of Small Bore Piping on Isometric CH-4106 High Energy Line Break Assessment. "Based on this, there is a potential for a HELB on the inlet of the Letdown Heat Exchanger that may adversely impact the upstream piping and the outboard containment isolation valve. Assuming a single failure of the inboard isolation, this condition has the potential to degrade a principal safety barrier by bypassing the containment building." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-10-18
49451 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2013-10-18 15:05 | 2013-10-18 15:52 | 2013-10-21 | OFFSITE NOTIFICATION DUE TO ONSITE OIL SPILL "At 1505 EDT on October 18, 2013, Fermi 2 experienced an oil spill to navigable waters, requiring notification of the Nuclear Regulatory Commission, Pollution Emergency Alert System, Detroit Edison Corporate Environmental Management and Resources, and the Primary Public Safety Answering Point. The spill has not left site. "Oil leaked from a fitting on a pump during the performance of fire truck testing. It is estimated that the volume of the overflow was less than four gallons. The overflow entered the on-site quarry. The source of the spill has been terminated. "Media interest is anticipated. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DEREK ETUE TO PETE SNYDER ON 10/21/13 AT 1445 EDT * * * In the first sentence of the second paragraph in the original report above the words 'fire truck' were replaced with 'FLEX pump.' Additionally, "as of 10/18/2013 at 1820 EDT the oil cleanup was completed with no waste generated due to oil dissipation." The licensee also notified the Michigan State Police, Monroe County Sheriff, and the Michigan Department of Environmental Quality. The licensee notified the NRC Resident Inspector. Notified R3DO (Orlikowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-18
49450 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-05-07 | 2013-10-18 15:28 | 2013-10-18 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING THE ADMINISTRATION OF AN UNDER-DOSE TO A PATIENT The following report was received via email: "Event type: Medical Event involving the administration of yttrium-90 (Y-90) Sir-Spheres. "Notifications: On October 17, 2013 the licensee informed the Department's Central Office of the Medical Event. The event is reportable within 24 hours per 10 CFR 35.3045(a)(1)(i). Appropriate reporting to the referring physician and the patient is currently underway. "Event Description: The patient was scheduled to receive two split doses on May 7, 2013. The plan was to treat the left hepatic artery segment 2 and 3 with 11.9 mCi (0.44 GBq) and the left hepatic artery segment 4 with 11.9 mCi (0.44 GBq). The unit doses were assayed separately and were found to be within 10% of the prescribed doses. After the doses were assayed, the exposure rate around the jar was measured and documented. After the procedure was completed, the tubing, V-Vial, and the jar were collected and then measured to calculate the residual activity using the same procedure and geometry used during the pre-dose measurements as per procedure. The post treatment measurements and calculations revealed the following delivered doses. The left hepatic artery segment 2 and 3 branches received 9.2 mCi and the left hepatic artery segment 4 branch received 8.92 mCi. This resulted in under-dosing of 22.48% and 30.03% respectively. "CAUSE OF THE EVENT: Occlusion of SirSpheres in the delivery system. The post treatment measurements were high which indicated that there were some spheres in the tubing or the V-Vial. When the jar was opened, it was found that the three-way stop cock contained some of the activity. "ACTIONS: A new dose work sheet has been built in as a warning to remind the licensee to notify the regulatory agency should the dose variance exceed 20%. "Media attention: None at this time." Pennsylvania Event Report Number - PA130055 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-10-28
49449 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2013-10-18 08:30 | 2013-10-18 14:05 | 2013-10-18 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "At 0830 EDT, Calvert Cliffs Nuclear Power Plant determined that the following was an unanalyzed condition: "As a result of recent industry operating experience (OE 305419) regarding the impact of unfused direct current (DC) ammeter circuits in the Control Room, Calvert Cliffs performed a review of ammeter circuitry. The review determined the described condition to be applicable to Calvert Cliffs resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The wiring design for the ammeters contains a shunt in the current flow from each DC battery or charger. The ammeter wiring attached to the shunt does not contain fuses. "It is postulated that a fire in the Unit 1 Cable Spreading Room could cause one of the ammeter wires to hot short to ground. Concurrently, the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a ground loop through the unfused ammeter cable. The potential exists that the cable could heat-up causing a secondary fire in the Unit 2 Cable Spreading Room. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown per 10 CFR 50 Appendix R. "This condition is reportable as an eight hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-18
49448 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-10-18 12:11 | 2013-10-18 13:47 | 2013-10-18 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF COOLING TO SWITCHGEAR ROOMS "Wolf Creek has commenced a plant shutdown in accordance with Technical Specifications. The A train class 1E electrical equipment air conditioning unit was declared non-functional due to a possible failed oil pressure sensor. This failure could prevent the [AC] unit from performing its required function over its required mission time, as required by Technical Specifications 3.8.4, 3.8.7, and 3.8.9. The following safety related electrical equipment was declared inoperable: 4.16KV bus NB01; 480 volt AC buses NG01 and NG03; 120 volt instrument AC inverters and buses NN11, NN13, NN01 and NN03; 125 VDC chargers and buses NK11, NK13, NK01 and NK03. "Technical Specification 3.0.3 was entered at 1141 CDT on 10/18/2013 from Technical Specification 3.8.7 due to two out of four 120 VAC inverters (NN11 and NN13) being inoperable. Plant shutdown to Mode 5 commenced at 1211 CDT. "All electrical systems listed above remain available but are declared inoperable due to inadequate room cooling capability. "No major equipment is out of service. No switchgear room temperature limits were challenged. "The NRC Resident Inspector has been notified." See event notifications; EN #49339, EN #49126, and EN #49008 for similar events. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-10-18
49447 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-10-09 | 2013-10-18 00:19 | 2013-10-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "On October 17, 2013 ICE-RAM [Inspections Compliance and Enforcement - Radioactive Materials Branch] received a letter dated October 14, 2013, from the RSO at NMG Geotechnical, Inc. (NMG), reporting that, on October 9, 2013, one of their moisture density gauge (CPN MC-1DRP, S/N M60408283, 10 mCi Cs-137, 50 mCi Am:Be-241) was discovered to be lost or stolen at an apartment complex at 1601 W. MacArthur Blvd., Santa Ana, CA, after the gauge operator was on a lunch break. The gauge was placed in the vehicle after using the gauge at the apartment complex just prior to starting lunch. The gauge operator discovered that the gauge and transport box were missing from the rear of the Jeep Cherokee SUV. There were no indications that the vehicle was broke into, making it most likely that the gauge and case were left in the vehicle while it was unlocked and the gauge case was not secured to the frame of the vehicle. The operator contacted the RSO and then filed a report with the Santa Ana Police and notified the Irvine Police afterwards. "On October 17, 2013, an ICE RAM-South inspector contacted the RSO to confirm the information in the letter. The inspector inquired if the operator had searched the complex for the gauge prior to reporting the gauge stolen and the RSO confirmed that they had. The RSO also noted that the operator returned to the complex later to give the apartment management fliers to distribute to residents. The gauge has not been recovered to date. This RSO was informed that they will be cited for loss of control of the gauge and failure to immediately report the loss of the gauge as required. The investigation will continue to determine if any other items of non-compliance are identified." California 5010 Number: 101713 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-11-01
49446 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-10-17 13:00 | 2013-10-17 16:25 | 2013-10-17 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to the Perry Nuclear Power Plant resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1 E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to hot short to the ground plane. Simultaneously, it is postulated that the fire causes another DC wire from the opposite polarity on the same battery to also hot short to the ground plane. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (i.e., heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Resident Inspector." See the following related Event Numbers: 49411, 49419, 49422, and 49444. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-17
49445 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-10-16 10:32 | 2013-10-16 17:08 | 2013-10-16 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "On 10/16/13 at 1032 CDT, the Browns Ferry Nuclear Plant Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable due to an inadvertent isolation that occurred during testing. During performance of surveillance procedure 1-SR-3.3.5.1.2(ATU D), an erroneous signal was induced causing actuation of primary containment isolation system group IV (i.e., HPCI Isolation). Technical Specification 3.5.1, ECCS-Operating, Condition C was entered as a result of the inoperable HPCI system. This constitutes an unplanned HPCI system inoperability and requires an 8-hour NRC notification in accordance with 10 CFR 50.72(b)(3)(v)(D). The erroneous signal was cleared and the HPCI isolation was reset. Upon reset of the isolation signal, the HPCI system was returned to available status. The HPCI system was unavailable for 14 minutes. The HPCI system was returned to operable status at 1503 CDT following successful performance of the surveillance section affecting HPCI isolation logic. "The NRC Resident Inspector has been notified. "Service Request 794050 has been entered into the Licensee's Corrective Action Program to capture this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-10-16
49444 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-10-16 13:15 | 2013-10-16 15:08 | 2013-10-16 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "At 1315 EDT, the VC Summer Nuclear Station determined that the following was an unanalyzed condition: "As a result of recent industry operating experience (OE 305419, EN 49411, EN 49419) regarding the impact of unfused Direct Current (DC) ammeter circuits in the Control Room, VC Summer performed a review of ammeter circuitry. The review determined the described condition to be applicable to VC Summer resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The wiring design for the ammeters contains a shunt in the current flow from each DC battery or charger. The ammeter wiring attached to the shunt does not contain fuses. "It is postulated that a fire could cause one of the ammeter wires to hot short to ground. Concurrently, the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a ground loop through the unfused ammeter cable. The potential exists that the cable could heat-up causing a secondary fire in the ammeter raceway. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown per 10 CFR 50 Appendix R. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-16
49443 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-10-13 | 2013-10-15 13:53 | 2013-10-17 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following report was received from the Colorado Department of Public Health and Environment Radioactive Materials Unit via e-mail: "On Tuesday, October 15, 2013, at approximately 8:30 am MDT (Mountain Daylight Time), the Radiation Safety Officer (RSO) for a portable gauge licensee (Martinez Associates, LLC; Colorado License No. 1076-01, Amendment 09) based in Denver, Colorado notified the Colorado Department of Public Health and Environment (CDPHE) Radioactive Materials Unit that a Troxler moisture density gauge was stolen on Sunday, October 13, 2013 from a private vehicle parked at the private residence of an employee. The private residence was located in Thornton, Colorado. The stolen gauge was last used on Friday, October 11, 2013 and the theft was reported (by the employee) to the RSO and local law enforcement (Thornton, Colorado, Police) on Sunday, October 13, 2013 at approximately 8:30 pm MDT. "The stolen gauge was a Troxler model 3430 (gauge serial number 23358), containing approximately 8 mCi (03/17/1994 assay date) of Cs-137 (source serial #75-5374) and 40 mCi (03/08/1994 assay date) of Am-241:Be (source serial #47-19240). "CDPHE will conduct an investigation and evaluation of the circumstances surrounding the reported theft and intends to issue a press release regarding the incident. Further details and information from the licensee is pending." * * * UPDATE FROM JAMES JARVIS TO CHARLES TEAL ON 10/16/13 AT 0944 EDT * * * "On October 15, 2013, the Radiation Program of the Colorado Department of Public Health and Environment (CDPHE) reported to the NRC Operations Center that a gauge had been stolen from an apartment complex in Thornton, Colorado. The City of Thornton, Colorado Police reported to CDPHE at approximately 10 pm on October 15, 2013 that the gauge had been recovered and that suspects were in custody. The gauge was transported to the City of Thornton Police for further criminal evaluation. The CDPHE will assist the Thornton Police as they evaluate the device." Notified R4DO (Hay), FSME (Henderson), ILTAB (Wray) via email, and FSME Event Resource via email. * * * UPDATE FROM JAMES JARVIS TO CHARLES TEAL ON 10/17/13 AT 1019 EDT * * * "In our email dated 10/16/13 (7:43 am), it was incorrectly reported that the Thornton, Colorado Police Department (PD) had suspects in custody. The Thornton PD had questioned suspects at the time of their notification to our agency, but did not have the individuals in custody nor were any arrests made. All other information is correct to the best of our knowledge and the gauge remains in the custody of the police at this time." Notified R4DO (Azua), ILTAB (Wray) and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-10-23
49442 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-10-14 15:12 | 2013-10-14 22:00 | 2013-10-14 | TRIP OF ONE MAIN FEEDWATER PUMP "On October 14, 2013 at 1512 PDT, Diablo Canyon Power Plant Unit 1 experienced a low control oil pressure on Main Feedwater Pump (MFP) 1-1, which caused MFP 1-1 to trip offline. In response, the turbine control system initiated an automatic ramp from 100 percent to 50 percent turbine load. Operators entered Abnormal Operating Procedure (OP) AP-15, 'Loss of Feedwater Flow.' Procedure OP AP-15 directed operators to manually start both motor-driven Auxiliary Feedwater (AFW) Pumps 1-2 and 1-3, based on existing plant conditions. The manual initiation of an AFW pump in response to actual plant conditions constitutes a valid actuation of a system listed in 10 CFR 50.72(b)(3)(iv)(B). "Unit 1 is stable at 50 percent power. "The NRC Senior Resident Inspector has been informed of this event." | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-10-14
49441 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-10-14 21:21 | 2013-10-14 21:53 | 2013-10-14 | REACTOR SCRAM AND START OF EMERGENCY DIESELS DUE TO PARTIAL LOSS OF OFFSITE POWER "On Monday October 14, 2013 at 2121 hours [EDT], with the reactor critical at 100% core thermal power, the mode switch in RUN, and offsite power 345kV line 342 out of service for scheduled modification, a loss of offsite power occurred due to the loss of the second 345kV line 355. All control rods fully inserted, main steam isolation valves closed on the loss of power to the reactor protection system, emergency diesel generators automatically started supplying power to both 4160V safety buses. Following the scram, reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically per design. A plant cool down is in progress with reactor water level being maintained in the normal post-scram band of +12 inches to +45 inches utilizing the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Preliminary indication from the grid operator was that the line loss was due to a failure of an offsite tower support. This event had no impact on the health and/or safety of the public. The USNRC Senior Resident Inspector has been notified. This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(8)." Pilgrim is currently in Mode 3 and being cooled down to Mode 4. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-10-14
49440 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2013-06-17 | 2013-10-14 16:10 | 2013-10-14 | AGREEMENT STATE REPORT - STUCK PROCESS GAUGE SHUTTERS The following information was received from the Kentucky Radiation Health Branch via facsimile: "Kentucky Radiation Health Branch (RHB) was notified by telephone on 10/2/13 by a representative from a generally licensed facility, Momentive Specialty Chemicals, of the fact that the shutter ON-OFF control mechanisms had been stuck in the open position on two level gauges undergoing routine servicing almost four (4) months previously. The two gauges, Thermo TN Technologies model 7063P each with 100 mCi Cs-137 [sources] (S/N S92BO601 and S94K1101) were being routinely serviced by a licensed manufacturer, VEGA Americas, on June 17, 2013 when the shutters were found to be stuck in the open position. The VEGA service representatives returned to the licensee's two days later (6/19/13) and repaired the sticking shutters so they would operate freely. "The VEGA representatives informed the general licensee's representative that a report to RHB was required but the person responsible for the gauges and for making the report was not notified of the problem until almost four months later. When he did learn of the event and the reporting requirement, he reported the event to RHB by telephone on 10/2/13 and followed up with a written report on 10/11/13. "The reporting criteria is defined in 902 KAR 100:050 Section 3(3)(c)5 and 10 CFR 31.5(c)(5)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2013-10-22
49439 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-10-10 | 2013-10-14 15:16 | 2013-10-14 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following report was received from the Oklahoma Department of Environmental Quality via e-mail: "On Oct. 10 we were informed by the Oklahoma Dept. of Transportation that one of their Troxler Model 3440 gauges (S/N 32291) had been run over at a road construction site on Hwy 412 east of Woodward, OK. The Radiation Safety Officer responded to the site that day, recovered the gauge and transported it back to their facility in Oklahoma City. Department of Environmental Quality staff inspected the gauge the next day. Although the source rod had been completely snapped off, it did not appear that either of the sealed sources had been damaged." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2013-10-22
49438 | 0 | EQ DETROIT |  |  |  |  | 2013-10-14 | 2013-10-14 14:50 | 2013-10-14 | SURFACE CONTAMINATION DISCOVERED ON SEALED SOURCE DURING BIANNUAL WIPE TEST A general license holder reported a leaking Nickel-63 source that is used in an Agilent Electron Capture Detector. The source was wipe tested and discovered to have a surface contamination of 0.011 micro-curies. The Ni-63 source for the detector has a rated source strength of 15 micro-curies. The company sent the source to a contractor for further determination if the source is leaking or can be cleaned and returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-10-22
49437 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-10-14 09:50 | 2013-10-14 12:05 | 2013-10-14 | UNPLANNED MEDICAL TREATMENT OF CONTAMINATED INDIVIDUAL "An employee reported to the on-site dispensary this morning [on 10/14/13,] after a chemical exposure to his face. The plant nurse administered treatment and then sent the employee to an off-site medical facility for further treatment. A whole body survey of the employee's plant clothing was performed; the maximum amount of contamination found was present on the employee's left boot, 32,000 dpm/100cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was whole body frisked out of the plant. The employee was free of contamination upon release." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-10-14
49436 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-10-14 09:50 | 2013-10-14 11:02 | 2013-10-14 | VENTILATION PROCESS FLOW RADIATION MONITOR REMOVED FROM SERVICE FOR PRE-PLANNED TESTING "The supplementary leak collection release system ventilation process flow radiation monitor 3HVR*RE19B has been removed from service for preplanned testing. The system will be returned to service in approximately 6 hours. "Loss of assessment capability due to pre-planned testing affecting a radiation monitor. The ventilation process radiation monitor for supplementary leak collection release system (3HVR*RE19B) out of service is a reportable condition per 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-14
49435 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-10-14 04:02 | 2013-10-14 10:47 | 2013-10-16 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "At approximately 0402 [EDT] on October 14, 2013, planned maintenance activities began on the Technical Support Center (TSC) HVAC. The scope of the maintenance is to inspect and clean the Air Handler Units and Fans that support TSC ventilation. The planned work activity duration is expected to be approximately 43 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. "An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE AT 1418 EDT ON 10/16/13 FROM JOHN CAVES TO HUFFMAN * * * The planned maintenance on the TSC HVAC system has been completed and the TSC returned to service. The licensee has notified the NRC Resident Inspector. R2DO (Ernstes) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-14
49434 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-10-13 16:47 | 2013-10-13 21:55 | 2013-10-16 | ONE MAIN STEAM LINE RADIATION MONITOR OUT OF SERVICE "Loss of assessment capability for steam generator rupture determination associated with the radiation monitor for one of four steam lines. The 3MSS-RE78 is out of service due to the unplanned loss of its power supply. This is a reportable condition in accordance with 10CFR72(b)(3)(xiii). A blown fuse is the suspected cause." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0408 EDT ON 10/16/2013 FROM BARRETT NICHOLS TO MARK ABRAMOVITZ * * * The radiation monitor was returned to service at 0100 EDT on 10/16/2013. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Lilliendahl). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-13
49433 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-10-13 09:46 | 2013-10-13 11:34 | 2013-10-13 | NOTIFICATION OF UNUSUAL EVENT DUE TO CIRCULATING WATER PUMP HOUSE FLOODING "Point Beach declared an Unusual Event based on HU 1.6 Uncontrolled Flooding in the Circulating Water Pump house that has the potential to affect safety related equipment needed for the current operating mode. "The leak was from the North main Zurn Service Water strainer. Operations entered the appropriate abnormal operating procedure and secured and isolated the affected strainer. The leak is now isolated." The licensee notified the NRC Resident Inspector. Notified the DHS SWO, FEMA and DHS NICC and via E-mail the Nuclear SSA. * * * UPDATE FROM ANDREW RADOSEVIC TO CHARLES TEAL AT 1427 EDT ON 10/13/13 * * * The licensee terminated the Unusual Event at 1245 CDT. The licensee notified the NRC Resident Inspector. Notified R3DO (Skokowski), R3RA (Pederson), NRR ET (Uhle), IRD (Morris), NRR EO (Evans), and R3 (Shear). Notified the DHS SWO, FEMA and DHS NICC and via E-mail the Nuclear SSA. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-10-13
49432 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-10-13 04:20 | 2013-10-13 09:11 | 2013-10-13 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE AT ZERO INCHES WATER GAUGE "On October 13, 2013 at 0420 [EDT], Susquehanna Steam Electric Station control room operators received an alarm for a local secondary containment ventilation control panel. Investigation revealed that Zone II (Unit 2 Reactor Building) secondary containment differential pressure was at zero inches water gauge. Tech Spec Secondary Containment Operability requires a negative pressure of at least 0.25 inches water gauge. All fans and dampers appeared to be operating normally and there was no apparent equipment malfunction. Zone I (Unit 1 Reactor Building) and III (Common Refuel Floor Area) ventilation remained in service and stable. "Zone II differential pressure recovered within five minutes and was verified to be stable. LCO 3.6.4.1 was entered for both units at 0420 and exited at 0425. "There have been no further perturbations in differential pressure and secondary containment remains operable. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-10-13
49431 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-10-10 | 2013-10-11 17:38 | 2013-10-11 | AGREEMENT STATE REPORT - POTENTIAL DOSE FROM DECEASED PATIENT WITH PREVIOUSLY ADMINISTERED IODINE-131 The following was received from the State of Colorado via email: "CDPHE [Colorado Department of Public Health and Environment] received telephone notification on 10/11/13 at approximately 2:00 p.m. of a deceased patient who had been administered 150 mCi of I-131 approximately 10-14 hours prior to his death. A male patient, 35 years of age, was administered 150 mCi of I-131 at St. Mary's Hospital and Medical Center on Wednesday October 9, 2013. The RSO at St. Mary's was notified on Thursday that the patient had passed at some point in the night of the 9th. County EMTs as well as staff from the county coroner's office were called to the scene and examined the body prior to the confirmation of death and the transport of the body to the Montrose Memorial Hospital in Montrose, Colorado. "Section 7.22 of the Colorado Regulations require that the licensee shall notify the Department [Colorado Department of Public Health and Environment] by telephone immediately upon discovery that a patient or human research subject containing radioactive material has died, and it is possible that any individual could receive exposures in excess of 4.14 as a result of the deceased's body. "At this time, the licensee has consulted with and performed contamination surveys of all of the members of the public who have come into contact with the deceased and has situated the body in a secluded portion of the morgue with lead aprons to reduce any potential exposure. The preliminary estimates on dose indicate that the highest dose would have been to the driver of the vehicle which was used to move the body and that dose is estimated to be 30 mrem. The pathology staff at the hospital would like to perform an autopsy since the patient was 35 years of age and was not expected to pass based on medical history. "The Department [Colorado Department of Public Health and Environment] will keep communications open as details of the autopsy schedule are finalized and provide guidance on best practices and ALARA techniques for handling of the body. "The licensee will submit a written report with more detail within thirty days. No other details are available at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-10-21
49430 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-10-11 12:30 | 2013-10-11 16:00 | 2013-10-11 | UNPLANNED MEDICAL TREATMENT OF CONTAMINATED INDIVIDUAL "An employee reported to the on-site dispensary this afternoon [on 10/11/13,] with a bump and minor cuts on her head. The plant nurse administered first aid and then sent the employee to an off-site medical facility for further evaluation. A whole body survey of the employee in her plant clothing was performed while in the dispensary; the maximum amount of contamination found was present on the employee's boots, 4,600 dpm/100cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into her personal clothing, and exit monitored from the facility. The employee was free of contamination upon release." The licensee was unable to contact Region II due to the government shutdown. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-10-11
49429 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-10-11 13:17 | 2013-10-11 15:07 | 2013-10-11 | AUTOMATIC TURBINE AND REACTOR TRIP DUE TO STATION SERVICE TRANSFORMER LOCKOUT "At 1317 hours on 10/11/2013, Unit 1 experienced an automatic turbine and reactor trip from 48% power. Unit 1 was in the process of increasing power level following a refueling outage when the 1C Station Service Transformer Lockout Relay actuated as the 'C' Condensate Pump was started. The 1C Station Service Transformer Lockout resulted in the turbine trip which subsequently tripped the reactor. All three station service electrical buses transferred to the Reserve Station Service Transformers. The 1C Station Service Transformer does not have any visible exterior damage. All control rods fully inserted into the core following the reactor trip. The actuation of the Reactor Protection System is reportable per 10CFR50.72(b)(2)(iv)(B). "The Auxiliary Feedwater Pumps actuated as designed following the trip and provided makeup flow to the steam generators. The steam generator levels were returned to normal operating level and the Auxiliary Feedwater Pumps were returned to automatic. The actuation of the Auxiliary Feedwater Pumps is reportable per 10CFR50.72(b)(3)(iv)(A). "Due to low decay heat loads, the Main Steam Trip Valves were closed as the Reactor Coolant Tavg temperature decreased, as directed by the reactor trip response procedure and decay heat is being removed using the atmospheric steam dumps. Decay heat control will be transferred to the main condenser steam dump system. "Unit 1 is stable in Mode 3 at normal Reactor Coolant System temperature and pressure. Unit 2 is operating at 100% power and was not affected by this event." The licensee has notified the NRC Resident Inspector and the local government. | 0 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-10-11
49428 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-10-10 18:45 | 2013-10-10 19:24 | 2013-10-10 | SAFEGUARDS REPORT - ACTUAL INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Discovery of contraband in the Protected Area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2013-10-18
49427 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2013-10-10 09:30 | 2013-10-10 15:38 | 2013-10-10 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING POSSIBLE EQUIPMENT MALFUNCTION The following was received from the Commonwealth of Kentucky via email: "Licensee notified the Radiation Health Branch on October 10, 2013 at 0930 EDT of the possible event. The RSO, reported the following: A vaginal applicator using Cs-137 was found to be dislodged from the patient this morning. The RSO reported that the patient is paralyzed and would not have recognized the specific time that the applicator became dislodged. At this time, (1035 EDT) the RSO has received an email which requested him to provide all required notification information included in 902 KAR 100:072 section 15, has been provided a web link to the regulation, and has been provided with an information form to complete regarding the possible medical event. The RSO indicated he would provide the requested information to the Investigator by return email. The licensee is currently conducting an investigation into this matter to determine dose estimates for the patient and if there was an equipment failure." KY Event Report ID No: KY130004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2013-10-18
49426 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-10 15:19 | 2013-10-10 15:19 | 2013-10-10 | INCOMPLETE BRAZING OF CONTACTS FOR DIESEL GENERATOR CONTROL RELAY "On August 5, 2013, annunciators were received for diesel generator (DG) 2B low lube oil inlet and outlet temperature. Investigation revealed that a control relay in motor control center cubicle 2EMXF F02D was not operating as expected. A work order was generated to replace the relay. While working the work order, a relay contact pad was found resting next to the relay. An inspection of the relay revealed that the contact pad came from the backside of the left movable contact. With the relay coil in the energized state and the contact pad missing, the relay contact would not engage. This prevented the lube oil heaters from energizing. "The failed relay was sent to the Duke Energy Metallurgy Laboratory. It was observed that the gold brazing material was miniscule where the pad should have been attached. The laboratory observed the same brazing issue with the adjacent relay contact pads that were still attached on the failed relay. The material could barely be seen under the pads: it should have protruded out the edges for good brazing. It was determined that the overseas manufacturer of the relays had insufficiently bonded the relay contact pads to the movable contact arms for at least one known batch of relays. "The failed relay is a Cutler-Hammer relay, Model Number 9575H3A000. The failed relay had been installed on July 30, 2013 to replace obsolete relay Model Number 9575H2612A. The replacement relay type was purchased by Duke Energy as a commercial grade item and dedicated for use in safety related applications. The failed relay batch number is 1111AF. Similar relays had been installed in the DG lube oil sump tank heater and the DG jacket water heater applications for DGs 2A and 2B. Duke Energy concluded that for these two installed applications, no substantial safety hazard existed, as DGs 2A and 2B were determined to be operable. (The heaters operate while the DGs are in standby to maintain required lube oil and jacket water temperature. Failure of these heaters to automatically start would be detected by alarms and the DGs could be started to maintain temperature. The heaters do not operate when the DGs are running.) However, because similar affected relays were in inventory, they theoretically could have been utilized in other safety related applications (even though they were not actually utilized in any other safety related applications). The most significant safety related applications where the affected relays could have been utilized were in circuitry associated with safety related ventilation system fans. Had they been utilized in these systems, a failure could have prevented the affected ventilation system fan from starting on an actuation signal. Catawba's evaluation that concluded that this issue could have resulted in a substantial safety hazard was completed on October 7, 2013. However, there was no actual impact to public health or safety. The required company officer notification was made on October 9, 2013. "Catawba is the only Duke Energy site that had the affected relays. In addition, none of the affected relays were sold or transferred to other utilities by Duke Energy. Notifications will he made to the Catawba NRC Resident Inspector and to the required state and local agencies." The licensee will also be notifying North and South Carolina State, York, Gaston, and Mecklenburg Counties. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | SC | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2013-10-10
49425 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-10-10 08:09 | 2013-10-10 14:08 | 2013-10-18 | LOW PRESSURE CORE SPRAY DECLARED INOPERABLE "At 0809 PDT on 10/10/2013, after starting Standby Service Water (SW) pumps, Columbia Generating Station (Columbia) received a flow low alarm for the Low Pressure Containment Spray (LPCS) pump motor cooling water. The flow indicator SW-FIS-19 was reported too low to support pump function. The LPCS system was declared inoperable, and the appropriate Technical Specification action statement was entered. The cause of the low flow alarm has not been determined. This event is reportable under criterion 10 CFR 50.72(b)(3)(v)(D) 'Any Event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (D) Mitigate the consequences of an accident.' "Columbia is continuing to troubleshoot and repair as appropriate to restore the SW flow to the LPCS pump. "The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 10/11/13 AT 1653 EDT FROM MATT HUMMER TO DONG PARK * * * "Subsequent to receipt of the low flow alarm, flushing of the flow indicating switch sensing lines was conducted. It has been determined that the instrument sensing lines are partially blocked providing a flow indication that is slow to respond to actual flow conditions. The flow is currently reading normally. The LPCS pump was declared operable on 10/10/13 at 1447 PDT. The initial notification incorrectly stated 'Low Pressure Containment Spray (LPCS)', the correct description is 'Low Pressure Core Spray (LPCS)'." The licensee has notified the NRC Resident Inspector. Notified R4DO (Hay). * * * RETRACTION FROM DAVID HOLICK TO JOHN SHOEMAKER AT 2030 EDT ON 10/18/13 * * * "Subsequent evaluation of this event found there was no actual low flow condition to the LPCS bearing cooler. A flow scan on the SW outlet line from the LPCS pump bearing cooler was conducted on 10/12/13 which confirmed the actual flow conditions were reading normally. The problem resides in the installed flow indication switch. Since there was no actual low flow condition to the LPCS bearing cooler, the LPCS pump could perform its safety function to mitigate an accident. Therefore, this event notification is being retracted." Notified R4DO (Azua). The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-10-10
49424 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2013-10-10 05:38 | 2013-10-10 07:25 | 2013-10-10 | OFFSITE NOTIFICATION DUE TO SINGLE SIREN ACTIVATION "At 0538 [EDT on 10/10/13], Calvert Cliffs was notified by Calvert Control Center, that a siren in the Calvert County Area was activated. [It was] determined to be siren C-15 on Lloyd Bowen Road. This is 1 of 73 sirens. "Per [procedure] CNG-NL-1.01-1004 this is a verbal report to Calvert Control Center. "This event is reportable as a 4 hour non emergency notification 10CFR50.72(b)(2)(xi) as: any event resulting in notification to other government agencies that has or will be made." Heavy rains in the area are believed to have caused the siren activation. Maintenance personal have been dispatched to repair the siren. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-10
49423 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-10-09 17:30 | 2013-10-09 22:47 | 2013-10-09 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience with respect to fire induced damage to unfused Direct Current (DC) ammeter circuits in the control room has determined that the condition described below is applicable to Wolf Creek Nuclear Generating Station. This condition results in an unanalyzed condition with respect to 10CFR50 Appendix R analysis requirements. The original plant wiring design did not include overcurrent protection features to limit the fault current in these circuits. The wiring design for the ammeters contains a shunt in the current flow from each NK direct current (DC) battery or charger. Two leads run from the shunt to a current meter in the main control room (MCR). These leads are tied to the positive polarity of the NK battery system. The ammeter wiring attached to the shunt is not overcurrent protected. It is postulated that a fire could cause one of these ammeter wires to short to ground at the same time the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a ground loop through the unfused ammeter cable. This event could result in excessive current flow (heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment. Reference Palo Verde plant event #49411. A Breech Authorization with compensatory Control Room hourly fire watch for this issue is in place and will remain in effect until this deficiency is resolved. "This condition has been discussed with the Resident Inspector." Similar Events #49422 and #49419 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-09
49422 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-10-09 15:00 | 2013-10-09 18:23 | 2013-10-09 | POSTULATED FIRE EVENT COULD RESULT IN A HOT SHORT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined that the condition described below to be applicable to Callaway Nuclear Plant resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1E Train B batteries and chargers (including the B Swing charger) control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to hot short to the ground plane; simultaneously, the fire causes another DC wire from the opposite polarity on the same battery to also hot short to the ground plane. This would cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." Similar Events: EN #49411 and EN #49419 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-09
49421 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-10-09 09:30 | 2013-10-09 17:30 | 2013-10-09 | AGREEMENT STATE REPORT - MISSING MOISTURE DENSITY GAUGE The following report was received from the State of Texas via email: "On October 9, 2013 at approximately 1445 CDT, the Agency [Texas Department of State Health Services] received notice by phone that the licensee had lost a Troxler 3430 (sn 28350) moisture/density gauge near the Donna International Bridge near Donna, Texas. The sources contained within are an 8 mCi Cs-137 source (QSA Global X1218 sn 7502362) and a 40 mCi Am-241/Be source (QSA Global AX1 X.1 X.1/2 sn 47-25061). The gauge had been left on a tailgate out of its transport container when the truck left the temporary job site at approximately 0930 CDT. Upon reaching the first light in town approximately 5 miles away, the driver/technician noticed the down tailgate and missing gauge. A search is still underway." Texas Report # I 9123 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-10-17
49420 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-10-08 14:26 | 2013-10-08 16:31 | 2013-10-08 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE The Millstone Power Station Unit 2 Stack Radiation Monitor, RM-8169 is being removed from service for preplanned maintenance. The radiation monitor is estimated to be out of service for approximately 6 hours. This action is reportable as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. State and local authorities were notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-08
49419 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-10-08 12:40 | 2013-10-08 15:42 | 2013-10-08 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to Comanche Peak Nuclear Power Plant resulting in a potentially unanalyzed condition with respect to 10CFR50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1 E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to hot short to the ground plane. Simultaneously, the fire causes another DC wire from the opposite polarity on the same battery to also hot short to the ground plane. This could cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. "This condition is reportable in accordance with 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant." The licensee has notified the NRC Resident Inspector. See related Event #49411. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-08
49418 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-10-07 22:04 | 2013-10-08 00:07 | 2013-10-08 | SERVICE WATER RADIATION MONITOR OUT OF SERVICE "At 2204 EDT on October 7, 2013, Nine Mile Point Unit 2 received DRMS [Digital Radiation Monitor System] low sample flow alarm and sample pump trip for 2SWP*CAB146B. The chemistry department was notified to collect and analyze grab samples per ODCM 3.3.1 as a compensatory measure with the Service Water Radiation Monitor 2SWP*CAB146B out of service. "Attempts to restart 2SWP*CAB146B within 1 hour were unsuccessful. 2SWP*CAB146B remains Non-Functional. Technicians are being called in to restore the monitor to Functional status. "The Service Water Radiation Monitors are necessary for accident assessment and are credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to an out of service monitor is considered a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). This condition does not affect the health or safety of the public or the operation of the facility. Compensatory actions remain in place to sample per the requirements of the ODCM 3.3.1. "The NRC Resident Inspector has been notified." * * * UPDATE ON 10/8/13 AT 1546 EDT FROM JASON SAWYER TO DONG PARK * * * "At 1027 EDT on October 8th, 2013 Nine Mile Point Unit 2 received a DRMS low sample flow alarm and sample pump trip for 2SWP*CAB146A. Service Water Radiation Effluent Monitor SWP*CAB146B remains NONFUNCTIONAL, but in service from the previous shift with required compensatory measures per ODCM 3.3.1 already in place (12 hour grab samples/30 day restoration). "Attempts to restore 2SWP*CAB146A within 1 hour were unsuccessful. As of 1220 EDT on October 8th, 2SWP*CAB146A monitor has been restored to service and is now capable of providing information for emergency assessments, the monitor is in confidence run for restoration to FUNCTIONAL status. "The Service Water Radiation Monitors are necessary for accident assessment and are credited for Emergency Action Level (EAL) classifications. The inability to classify an EAL due to an out of service monitor is considered a loss of assessment capability per 10 CFR 50.72 (b)(3)(xiii). This condition does not affect the health or safety of the public or the operation of the facility because the monitor is currently back in service. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-08
49417 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-10-07 18:04 | 2013-10-07 20:36 | 2013-10-13 | VENT STACK AND AREA RADIATION MONITORS TAKEN OUT OF SERVICE FOR MAINTENANCE "This is a report of a loss of emergency assessment capability as required by 10CFR50.72(b)(3)(xiii). "On October 7, 2013 at 1804 CDT, with Unit 1 in Mode 6 during a refueling outage, power was interrupted to all Unit 1 vent stack radiation monitors and area radiation monitors as part of a pre-planned activity to connect the radiation monitors to an alternate temporary power supply to support deenergizing the normal power source for preventative maintenance. The connection to the alternate supply was completed and power was restored to the vent stack radiation monitors and area radiation monitors at 1833 CDT. While the radiation monitors were without power, pre-planned compensatory measures were implemented where possible to monitor vent stack discharge and to minimize activities that posed a potential for release. "At the completion of the preventive maintenance on the normal power supply, power to the vent stack radiation monitors and area radiation monitor will again be briefly interrupted to reconnect the normal power source to the monitors. The pre-planned compensatory measures will again be utilized during this power interruption. An update to this report will be provided following the restoration of normal power to the radiation monitors. "The NRC Resident Inspector has been informed." * * * UPDATE FROM DARRIN GARD TO JOHN SHOEMAKER AT 0419 EDT ON 10/13/13 * * * "On October 13, 2013 at 0217 CDT, with Unit 1 in defueled mode during a refueling outage, power was interrupted to all Unit 1 vent stack radiation monitors and area radiation monitors as part of a pre-planned activity to transfer the radiation monitors back to their normal power supply. The connection to the normal supply was completed and power was restored to the vent stack radiation monitors and area radiation monitors at 0245 CDT. Pre-planned compensatory measures were implemented where possible to monitor vent stack discharge and to minimize activities that posed a potential for release." Notified R2DO (Widmann) and the licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-07
49416 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2013-10-07 02:19 | 2013-10-07 12:55 | 2013-10-07 | POTENTIAL REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE IDENTIFIED "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 2100 MST on 10/06/13, while performing planned routine visual examinations of the Unit 3 reactor vessel bottom mounted instrumentation (BMI) nozzles, a white residue was identified around the annulus region of BMI penetration number 3. The BMI visual examinations are performed using remote video and photographic equipment to meet the in-service inspection requirements of 10 CFR 50.55a(g)(6)(ii)(E) and ASME Code Case N-722-1. At this time, no other indications of leakage have been identified and inspections of the remaining BMI penetrations are ongoing. "Following review of the photographic images by qualified engineering personnel, at 0219 [MST] on 10/07/13, it was determined, based on past and present photographic evidence, the white residue is most likely dry boric acid resulting from reactor coolant system pressure boundary leakage. An activity to sample and analyze the white residue is being planned and will be performed as soon as possible. This notification is being made for a degraded condition pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(A). "The NRC Resident Inspectors have been informed of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-10-07
49415 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-10-07 10:27 | 2013-10-07 11:44 | 2013-10-07 | PLANNED MAINTENANCE CAUSING LOSS OF METEOROLOGICAL TOWER DATA "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will de-energize the Meteorological Data Tower. No other indications or annunciators will be unavailable during this maintenance to affect the plant's ability to assess or monitor an accident or transient in progress. National Weather Service data is expected to be available throughout the duration of the planned maintenance. A follow up notification will be provided when power to the Meteorological Data Tower has been restored." The NRC Resident Inspector has been notified. * * * UPDATE AT 1718 EDT ON 10/07/13 FROM TERRY BRANDT TO HUFFMAN * * * Maintenance activities on the Meteorological Data Tower is complete and the tower has been returned to service. The licensee has notified the NRC Resident Inspector. R3DO (Skokowski) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-07
49414 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-10-06 11:30 | 2013-10-06 14:26 | 2013-10-06 | MANUAL REACTOR SCRAM DUE TO DEGRADED CONDENSER VACUUM "Today at approximately 1040 [EDT], during a planned reactor power ascension with reactor power at approximately 20% of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 1130 [EDT]. The cause of the degraded vacuum is currently under investigation. "All rods inserted into the core and all systems functioned as expected during the scram. No electromatic (EMRVs) or safety relief valves lifted during the transient. The plant is currently shutdown and parameters are stable. The plant is in its normal shutdown electrical lineup and decay heat is being removed via steam bypass valves to the main condenser. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The licensee has notified the NRC Resident Inspector and will be notifying state authorities. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-10-06
49413 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-10-04 23:24 | 2013-10-05 01:19 | 2013-10-05 | UNEXPECTED CONTAINMENT LINER PENETRATION FOUND "On October 4, 2013, during the Beaver Valley Unit 1 refueling outage, a planned visual examination of the interior containment liner and coatings was being performed. The containment design consists of an interior steel liner that is surrounded by reinforced concrete. An area approximately 0.4 inches by 0.28 inches was discovered that penetrated through the containment steel liner plate. "With the plant currently shut down and in Mode 6 the containment as specified in Technical Specification 3.6.1 is not required to be operable. The cause of this discrepancy is currently being evaluated. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A). "The Site Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-10-05
49412 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-09-27 | 2013-10-04 17:19 | 2013-10-04 | AGREEMENT STATE REPORT - LEAKING ELECTRON CAPTURE DETECTOR SOURCE The following information was received from the Oklahoma Department of Environmental Quality via e-mail: "On Sept. 27, [2013] the [Oklahoma Department of Environmental Quality] was notified by the University of Oklahoma Health Science Center that they had found an Electron Capture Detector with approximately 1 microCi of removable contamination. The unit in question is a Varian 3000 Series (P/N 02-001972-00) S/N A8075 (SSDR #CA-8253-D-80 1-B). Activity was 8 mCi [Ni-63] in Aug. 1990. The unit has been removed from service and is being stored prior to disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2013-10-14
49411 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-10-04 09:46 | 2013-10-04 18:20 | 2013-10-04 | POSTULATED FIRE EVENT COULD RESULT IN A HOT SHORT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of industry operating experience regarding the impact of unfused Direct Current (DC) ammeter circuits in the control room has determined the described condition to be applicable to Palo Verde Nuclear Generating Station resulting in an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated analysis for the Class 1E Train B and D batteries and chargers (including the BD Swing charger) control room ampere indications do not include overcurrent protection features to limit the fault current. "In the postulated event, a fire in the control room could cause one of the ammeter wires to hot short to the ground plane; simultaneously, the fire causes another DC wire from the opposite polarity on the same battery to also hot short to the ground plane. This would cause a ground loop through the unprotected ammeter wiring. This event could result in excessive current flow (heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10CFR50 Appendix R. "The train B and D DC circuits were reviewed first since they are part of alternate safe shutdown capability for the control room fire event. An extent of condition review is ongoing for the A and C train DC circuits and other similar circuit designs that could potentially cause a secondary fire. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Compensatory measures (fire watches) have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-04
49410 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2013-10-04 11:17 | 2013-10-04 17:13 | 2013-10-04 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received from the South Carolina Department of Health and Environmental Control via e-mail: "The SC Department of Health and Environmental Control was notified on Friday, October 4, 2013, at 1117 hrs (EDT), that a CPN Model MC-1-DR had been damaged at 1110 hrs [EDT] on October 4, 2013. [The] RSO, stated that the gauge had been run over by a bulldozer during a density test. [The South Carolina] Duty Officer responded to the scene and arrived at 1223 hrs [EDT]. The source rod was extended and the gauge had sustained considerable damage. The inspector placed a small lead pig over the exposed source rod and placed the source rod and the damaged components in the transport container. The inspector surveyed all parts and was unable to verify that the Am-241:Be source was still contained with the gauge. A thorough survey of the area was made and the area under the damaged gauge was dug up but the inspector was unable to verify that the Am-241:Be source was with the damaged gauge. The inspector traveled to the permanent storage location of the licensee to ensure that the gauge was properly secured. [The licensee] was advised to contact the gauge manufacturer for further instruction regarding disposal and to keep all personnel away from the gauge. "[The licensee's RSO] was advised by [the South Carolina inspector] to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department. Updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2013-10-14
49409 | 0 | UNIV OF WISCONSIN |  |  |  | 1000 KW TRIGA (CONVERSION) | 2013-10-04 10:01 | 2013-10-04 16:34 | 2013-10-04 | TECHNICAL SPECIFICATION VIOLATION DUE TO OPERATOR LEAVING CONTROL ROOM "Technical Specification 6.7.2(1)(c) Special Report Violation of Technical Specification 6.1.3(1)(a) "The following special report is being made in accordance with the requirements of Technical Specification (TS) 6.7.2(1)(c) which states in part: There shall be a report not later than the following day by telephone or similar conveyance to the NRC Headquarters Operation Center of any reportable occurrence as defined in TS 1.3. TS 1.3 defines an observed inadequacy in the implementation of administrative or procedural controls, such that the inadequacy caused the existence of a condition which results in a violation of technical specifications as a reportable occurrence. "Specifically, on Friday October 4, 2013, while performing a training session, an operator left the control room while the console key remained in the console key switch and the switch was in the ON position. This is in direct violation of the staffing requirements defined in TS 6.1.3(1)(a) which states a licensed reactor operator must be in the control room when the reactor is not secured. The reactor was not secured by the fact that the console key switch was not in the OFF position and the key remained in the console key switch. However, all control elements were fully inserted, a normal reactor SCRAM condition was present, the reactor was shut down, no work was in progress involving core fuel, core structure, control elements or drives and no experiments were being moved. This condition remained for a period of 67 seconds until the reactor operator returned to the control room. The reactor operator subsequently secured the reactor and notified the Reactor Supervisor. A review of security records confirms the control room remained locked and unoccupied during the entire duration. "A follow-up written report to the NRC describing the circumstance of the event including an analysis of the cause of the occurrence, corrective actions and measures to prevent or reduce the probability of the recurrence shall be made no later than 14 days from today, October 4, 2013." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 3 | WI | NPR | [5 empty] | 0 | 2013-10-04
49408 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2013-10-03 14:00 | 2013-10-04 11:25 | 2013-10-04 | AGREEMENT STATE REPORT - FAILED RETRACTION MECHANISM ON FIXED GAUGE DEVICE The following Agreement State Report was received via facsimile: "Event Description: The South Carolina Department of Health and Environmental Control was notified by the licensee at 2:00 p.m. [EDT] on October 3, 2013, that a source on a gauging device would not retract into the holder as designed. This licensee also stated, 'steam is leaking from the top of the right hand side source holder where the pulley is. The source tube is welded to the vessel. At the present time the cable is stuck, so the source will not retract into the holder. "The [South Carolina] Department [of Health and Environmental Control] responded to this event and found that an Ohmart Model SHLM-C-2 fixed gauging device containing two 200 mCi Cs-137 sources (s/n 2667/2668) had incurred a failure of the shutter/retraction mechanism. There was no evidence of steam being released from the gauge housing but water was dripping very slowly from the top of the gauge housing. Surveys indicated background readings of 0.03 mR/hr as the source has now been locked in place in the vessel. "The area is roped off to prevent unauthorized access. Vega Americas, Inc. is scheduled to perform repair of the shutter/retraction mechanism on October 8, 2013. Notifications and updates will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2013-10-14
49407 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2013-10-03 20:45 | 2013-10-04 02:12 | 2013-11-07 | UNIT 2 HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE DUE TO DRAIN LINE LEAK "On October 3, 2013, at 2045 [CDT] hours, a defect (pinhole through-wall leak) was identified on the drain line for the LS 2-2365, HPCI TURBINE INLET DRAIN POT LEVEL SWITCH. The defect was identified during investigation of leakage near LS 2-2365. The LS 2-2365, HPCI TURBINE INLET DRAIN POT LEVEL SWITCH, is provided to detect a failure of the HPCI steam trap during standby line-up. The location of the defect, is in Class 2 Safety related piping. HPCI is a single train safety system and this notification is being made in accordance with 10CFR50.72(b)(3)(v)(D). The instrument isolations for LS 2-2365 have been close and the leak has been isolated." There is no increase to plant risk and RCIC (Reactor Core Isolation Cooling) is available. The licensee will inform the NRC Resident Inspector. * * * RETRACTION ON 11/7/13 AT 1412 EST FROM JEFFERY JACOBSON TO DONG PARK * * * "The purpose of this notification is to retract the ENS report made on October 4, 2013, at 0212 EDT (ENS Report # 49407). "Upon further investigation the pinhole through-wall leak discovered in the Unit 2 HPCI room was in a weld at a 'Tee' downstream of the Unit 2 HPCI turbine inlet drain pot level switch (LS 2-2365) on drain line 2-2386B-1-B. The defect was characterized as a 1/16-inch rounded hole due to gas porosity (with no evidence of cracking). "A subsequent evaluation performed by Quad Cities Station considering the defect size, location, and characterization confirmed the Unit 2 High Pressure Coolant Injection (HPCI) system would have performed its safety function when required. Based on this subsequent evaluation, ENS Report # 49407 is being retracted. "Note: On October 3, 2013, at 1155 CDT the Unit 2 HPCI drain line leak was isolated and HPCI was declared operable." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-10-04
49406 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-10-03 15:35 | 2013-10-03 21:10 | 2013-10-03 | INADEQUATE SHIFT STAFFING TO SUPPORT IMPLEMENTATION OF SAFE SHUTDOWN INSTRUCTIONS "The Browns Ferry Nuclear Plant (BFN) minimum Operations shift staffing was evaluated for response to a fire in the Control Bay that ultimately leads to entry into Appendix R Safe Shutdown Instructions (SSIs). The result of this evaluation revealed that the minimum Operations shift staffing does not provide sufficient staffing to support SSI required staffing levels. In the event of an Appendix R fire, one BFN unit would be without a Senior Reactor Operator to direct the implementation of the time critical manual actions specified in the SSI procedures. "On October 3, 2013, this condition was determined to be an 8 hour non-emergency report in accordance with 10 CFR 50.72(b)(3)(ii)(B) since sufficient shift staffing levels to implement the SSI procedures in the event of an Appendix R fire were not provided. "Compensatory measures have been implemented to ensure sufficient shift staffing is provided to implement Appendix R SSIs. "The event was entered into the licensee corrective action program as Service Request number 788812. "The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-10-03
49405 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2013-10-01 | 2013-10-03 15:46 | 2013-10-03 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following report was received from the Wisconsin Radiation Protection Section via e-mail: "On October 1, 2013 the licensee identified a tritium exit sign as missing and reported it to the state of Wisconsin on October 2, 2013. Last inventoried during 2009, the sign was not recorded on an inventory conducted on September 17, 2013. The missing sign is a double-sided Isolite exit sign model 2040-07R-20BA SN: 227163. According to the SSD sheet, this device contains up to 25 Curies of tritium. The licensee stated it might have gone missing after a lighting retrofit project in 2010." Wisconsin Report ID: WI130020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2013-10-11
49404 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-10-03 06:43 | 2013-10-03 09:20 | 2013-10-03 | AUTOMATIC REACTOR SCRAM DURING STARTUP "At 0643 EDT [on 10/03/13], during reactor startup, with the reactor critical and power in the intermediate range, an automatic reactor scram occurred due to an invalid (noise) intermediate range monitor (IRM) scram signal processed on both RPS trip systems. All control rods fully inserted and plant response was as expected. This notification is in accordance with 10CFR50.72(b)(2)(iv)(B). The reactor is currently subcritical." When the reactor scram occurred, reactor power was below the Point of Adding Heat and had minimal effect on the plant. Normal offsite power is being maintained. Decay heat is being maintained via normal shutdown cooling. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-10-03
49403 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-10-02 17:15 | 2013-10-02 18:31 | 2013-12-26 | AGREEMENT STATE REPORT - LEAKING CESIUM-137 CALIBRATION SOURCE The Massachusetts Radiation Control Program provided the following report via facsimile: "[The Massachusetts Radiation Control Program] Agency received a call from the licensee [stating] that a Cs-137 dose calibrator sealed source was leaking. This sealed source [has been] stored for a long time. [The] licensee performed a leak test today on the sealed source before the sealed source was going to be used. The leak test results indicated that [the source] was leaking and the activity reported was 0.3 microCuries of activity, which is above the regulatory reporting limit of 0.005 microCuries. "The licensee provided the following information about the sealed source: original activity: 251 microCuries; Manufacture Date: 9/01/2011; and Source lD # 743-16-17. The leaking sealed source was never used and it was returned to storage for disposal. There was no personnel contamination or area contamination from this leaking source. "The licensee will file a report to the Agency within 5 days of this leak test." * * * UPDATE ON 11/04/13 AT 1128 EST FROM MASSACHUSETTS RADIATION CONTROL PROGRAM * * * The Massachusetts Radiation Control Program provided the following information via e-mail: A Licensee letter to Agency [Massachusetts Radiation Control Program] dated 10/7/13 contained updated source manufacture date and original activity information and confirmed contact made with manufacturer to arrange for return shipment of source for eventual disposal. On 11/4/13, upon Agency inquiry, the licensee stated that arrangements for return of source to manufacturer were progressing. The original source strength was revised to 241 microCuries as of 9/01/03. The revised leak test results were 0.357 microCuries of activity. The Agency considers this matter to still be OPEN pending confirmed return of source to manufacturer. The R1DO (Noggle) notified. A copy of this update was provided to FSME Events Resource via e-mail. * * * UPDATE AT 1159 EST ON 12/26/2013 FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * The Massachusetts Radiation Control Program provided the following information via e-mail: "Source returned to manufacturer 12/12/13. The Agency [Massachusetts Radiation Control Program] considers this matter CLOSED. "Additional Information: Model# RV-137; Manufacture Date 9/01/01; Original Activity 0.000251 Ci." Notified the R1DO (Dwyer) and FSME Events (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-10-10
49402 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2013-09-23 | 2013-10-02 14:02 | 2013-10-02 | AGREEMENT STATE REPORT - RADIOPHARMACEUTICAL WORKER RECEIVED >50 REM TO BOTH HANDS The following information was received from the State of Georgia via email: "An authorized user exceeded the annual extremity limit for both the left and right finger. Landauer sent an immediate report (report date 9/23/2013) to the corporate office of Cardinal informing them of the over exposure. At the current moment, Cardinal does not know the time frame at which this took place, but should know in a week and a half when Landauer will send their monthly report. "The immediate report issued by Landauer reported the following doses: Employee One, who resigned on August 13, 2013, received 57,554 mrem for the left finger and 52,681 mrem for their right finger. Employee Two received 22,016 mrem - left finger and 39,861 mrem - right finger. Employee Three received 43,140 mrem - left finger and 16,647 mrem - right finger. "Cardinal will be investigating the incident to determine the root cause. They will be looking a systemic issues at the facility." Georgia Incident Number: 72258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2013-10-10
49401 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-07-12 | 2013-10-02 09:52 | 2013-10-02 | AGREEMENT STATE REPORT - LOST IODINE 125 SEALED SOURCE SEED The following information was received from the New York State Department of Health (NYS DOH) via facsimile: "The source was a seed source for Breast Localization Procedures. The medical procedure occurred on July 12, 2013. A tissue specimen was removed from a patient. The localization seed was identified and removed from the specimen post-surgery. The seed was not returned to the Nuclear Medicine Department per institute policy, which initiated a facility search for the missing RAM [radioactive material]. Immediate actions included conducting extensive facility area surveys for several weeks. The source was declared officially lost on August 29, 2013. The root cause involved a failure to follow the facility policy. The seed was allowed to become lost, after it had been properly identified. Corrective actions involve an incident review with the pertinent staff and an in-service refresher training for all staff. The facility has been informed by NYS DOH that this event should have been reported immediately on July 12, 2013." Manufacturer, Best Medical International, Inc., Model No. 2301 I-125, Activity, 140 microCuries. New York State Report ID No. NY-13-05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-10-10
49400 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2013-10-01 11:31 | 2013-10-01 14:11 | 2013-10-01 | INADVERTENT ACTUATION OF EMERGENCY WARNING SIRENS "Exelon Generation has successfully tested the new emergency warning sirens installed in the 10-mile radius surrounding Peach Bottom Atomic Power Station. With approval from the Federal Emergency Management Agency (FEMA), Exelon Generation began transitioning to the new sirens on 10/1/13. At 11:31 am EDT, during the transition, a vendor technician inadvertently actuated the York County emergency warning sirens. The Sirens went through a full sounding of three minutes and then stopped alarming. The alarming sirens were not due to any condition at Peach Bottom. Exelon and York County have investigated the issue and found that the system worked properly. The cause of the inadvertent actuation was that a test signal was not given sufficient time to clear prior to putting the system in service after testing. "The NRC Resident Inspector has been informed." The licensee will issue a press release. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-10-01
49399 | 0 | NANTICOKE MEMORIAL HOSPITAL |  |  |  |  | 2013-06-28 | 2013-10-01 11:52 | 2013-10-01 | TWO GERMANIUM-68 CALIBRATION SOURCE RODS LOST DURING SHIPPING On June 28, 2013, the licensee shipped two boxes to Eckert & Ziegler Isotope Products, Inc., located in Burbank, CA. One box contained a cylinder phantom and the other box contained two source rods, serial numbers D689 and D690, containing 1.35 mCi Ge-68 each. On July 8, the licensee received confirmation from the shipper that the boxes arrived and were signed for at their destination. In September, the licensee followed up with the manufacturer who informed them that they had received the cylinder phantom but the box containing the source rods was empty. The shipper confirmed that the boxes were not identified as damaged at the time of delivery. The licensee searched their lab and shipping areas and could not find the sources. The manufacturer's RSO said that the incident is still under investigation but that they could not locate the sources. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-10-09
49398 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-09-30 22:57 | 2013-10-01 01:05 | 2013-10-02 | OFF-SITE EMERGENCY OPERATIONS FACILITY DECLARED INOPERABLE DUE TO AIR IN-LEAKAGE "At 2257 CDT on September 30, 2013 the Callaway Plant Emergency Off-Site Facility (EOF) was declared nonfunctional due to air in-leakage outside acceptance criteria while ventilation is in filtration mode. "Efforts are underway to restore the air in-leakage within acceptance criteria at the EOF. "If EOF activation is necessary during the period of EOF non-functionality, the Recovery Manager will evaluate the suitability of the facility for the specific conditions of the event. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the unavailability of an emergency response facility. "The NRC Senior Resident Inspector has been notified." * * * UPDATE FROM RICHARD HUGHEY TO JOHN SHOEMAKER AT 0248 EDT ON 10/02/13 * * * "Repairs were made to the EOF ventilation system and all required post-maintenance testing has been completed satisfactorily. The EOF has been restored to a functional status." The licensee will notify the NRC Resident Inspector. Notified R4DO (Gepford). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-10-01
49397 | 0 | SHAW AREVA MOX SERVICES, LLC |  |  |  |  | 2013-08-07 | 2013-09-30 16:21 | 2013-09-30 | NONCONFORMING WELDS RESULTING IN CRACKS IN HVAC FILTER HOUSING REPAIR WELDS Summary of information received via fax: The Shaw AREVA Mixed Oxide Fuel Fabrication Facility found nonconforming welds that resulted in cracks in HVAC filter housings supplied to MOX Services by Flanders. The filter housings are credited for the confinement of radioactive material. There is a possibility for additional material stresses to be placed on the subject filter housings which could cause the propagation and increase in size of the cracks. Because the cracks identified in the non-conformance report could propagate to an indeterminate size, the ability of the portions of the HDE system upstream of these filter housings to maintain the confinement boundary and perform its safety function cannot be determined. MOX Services will ensure repairs are performed by either the vendor, MOX Services, or a third party. These repairs will be performed in support of the construction schedule. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-09-30
49396 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2013-08-15 | 2013-09-30 15:37 | 2013-09-30 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION OF Y-90 The following information was received from the City of New York via email: "Incident: Due to the technical difficulties, physician could not deliver the full prescribed dose of Y-90. "Radiation Dose evaluation: As per physician's medical judgment, the dose given to the patient was adequate for the treatment of this volume and tumors within the region. "Health effects: Patient will be followed up to determine if an appropriate therapeutic result is achieved. "Corrective Actions: Administered radiological agent was Y-90 SIRTex. RSO and administering physician have come to the conclusion to wait until the vial and related accessories reach background [radiation levels] in order to investigate this matter. It is unknown whether this was a human error or manufacturer defect. "As per facility's report, as a precautionary measure, derma bond will be applied to the v-vial before administration of the dose in order to prevent any possibility of leakage." The prescribed dose of Y-90 was 30 mCi; the delivered dose was 19.26 mCi. NYC Incident Report Identification Number: 75-2885-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-10-08
49395 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-09-30 14:22 | 2013-09-30 15:35 | 2013-09-30 | TRANSPORT OF POTENTIALLY CONTAMINATED INJURED WORKER "At approximately 1422 EDT on 9/30/2013, a craft contractor worker was transported to an off-site medical facility due a work-related injury. The injured individual was in a radiologically controlled area when the injury occurred. The injured was partially surveyed by a Health Physics technician in their anti-contamination clothing prior to leaving the site and no radioactive contamination was detected. The injured individual was then transported by ambulance accompanied by a Health Physics technician to the local hospital for medical treatment. "Follow up surveys determined that no contamination was detected on the individual or materials transported. All materials are being recovered and returned to the site. "This notification is being made under the 10CFR50.72(b)(3)(xii) reporting requirements, since a complete survey of the injured individual was unable to be made and he was considered to be potentially contaminated prior to being transported off-site." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2013-09-30
49394 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-09-27 21:15 | 2013-09-30 12:52 | 2013-09-30 | TRITIATED WATER LEAK FROM TEMPORARY PIPING ON PLANT SITE "Harris Nuclear Plant is following the guidance in NEI 07-07 and has initiated this Event Notification as a result of our voluntary communication to state agencies in accordance with the Groundwater Protection Initiative. "On Sept. 27, 2013, at 9:15 pm EDT, plant personnel identified a leak from a temporary transfer pipe on plant property, well within the site boundary. The pipe carries secondary plant and water treatment building waste water for chemical processing. The leak is conservatively estimated to be 240 gallons of water containing a low level of tritium (3,954 picocuries per liter) leaked into the surrounding soil. The EPA drinking water standard is 20,000 picocuries per liter. The leak was stopped and the piping replaced. "The health and safety of the public and employees on site are not affected by this event based on the leak location and low tritium level." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-09-30
49393 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2013-09-28 12:30 | 2013-09-30 10:30 | 2013-09-30 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RUN OVER BY DUMP TRUCK The following information was obtained from the State of Florida via facsimile: "On Sept 28, 2013, at approximately 12:30 pm (EDT), the Florida Department of Radiation Control, received a call from the licensee, City of Palm Coast Utilities, concerning a Troxler soil moisture density gauge that had been run over by a dump truck. The licensee's RSO (Radiation Safety Officer) made the initial call from the scene where the gauge was left under truck to it keep out of the rain. However, the driver drove off and ran over the gauge. The licensee technicians had no survey meter on scene and the licensee's ARSO [Assistant Radiation Safety Officer] was on his way to assess the area with a survey meter. The Florida Department of Radiation Control verified with the licensee's RSO that the source was in the shielded condition and this was later verified by the ARSO with a survey meter. The plastic case and digital gauge face was damaged. The gauge will be retained by the licensee and later sent to Troxler for repair and leak test. Corrective action consists of training personnel and procedure changes as necessary. The Florida Department of Radiation Control has assigned the event to the Orange Park Inspection Office and Materials Office for further investigation. This office will take no further action on this incident. "The gauge is a Troxler Model 3430 Soil Moisture Density Gauge, Serial # 20850, with Am-241 40 mCi and Cs-137 8 mCi sources." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-10-08
49392 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-09-30 02:38 | 2013-09-30 09:26 | 2013-09-30 | MANUAL START OF MOTOR DRIVEN AUXILIARY FEEDWATER PUMP "At 0238 [EDT] hours on September 30, 2013, during a planned shutdown of Beaver Valley Unit 1 for a refueling outage, the 'B' Motor Driven Auxiliary Feedwater (AFW) pump was manually started in Mode 3 due to lowering levels in the steam generators. The steam generator levels were restored to normal following the start of the AFW pump. The lowering [steam generator] levels were a result of a component failure in a normal non-safety related make up system. The manual start for the AFW pump is being reported as a system actuation per 10 CFR 50 72(b)(3)(iv). The plant is currently in Mode 5. "The NRC Resident Inspector has been notified." A condensate pump recirculation valve failing open was the component failure in the normal non-safety related make up system. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-09-30
49391 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-09-28 12:13 | 2013-09-28 19:25 | 2013-10-01 | DIGITAL RADIATION MONITOR LOW SAMPLE FLOW ALARM RECEIVED "At 1213 EDT on September 28, 2013 Nine Mile Point Unit 2 received [Digital Radiation Monitor System] DRMS low sample flow alarm and monitor status of sample pump off for 2SWP*RE146A. The chemistry department was notified to collect and analyze grab samples per [Offsite Dose Calculation Manual] ODCM 3.3.1 as a compensatory measure with the service water radiation monitor 2SWP*CAB146A out of service. 2SWP*RE146A was restarted at 1517 EDT and declared functional. "At 1548 EDT on September 28, 2013 Nine Mile Point Unit 2 received DRMS low sample flow alarm and monitor status of sample pump off for 2SWP*RE146B. Chemistry was again notified to collect and analyze grab samples per ODCM 3.3.1 as a compensatory measure with the service water radiation monitor 2SWP*CAB146B out of service. "The service water radiation monitors are necessary for accident assessment and are credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to an out of service monitor is considered a loss of assessment capability per CFR 50.72(b)(3)(xiii). This condition does not affect the health or safety of the public or the operation of the facility. Compensatory actions remain in place to sample per the requirements of the ODCM. "The NRC Resident Inspector has been notified." * * * UPDATE FROM CARL JONES TO CHARLES TEAL AT 0122 EDT ON 9/29/13 * * * "The Service Water radiation monitors have been restored to service and declared functional. 2SWP*CAB146B restored after maintenance Saturday, 09/28/13 at 2243 EDT. 2SWP*CAB146A was removed from service for maintenance at 2243 EDT on 09/28/13, restored to service and declared functional Saturday, 09/28/13 at 2337 EDT." The NRC Resident Inspector will be notified. Notified R1DO (Welling). * * * UPDATE FROM CARL CRAWFORD TO CHARLES TEAL AT 1040 EDT ON 09/29/13 * * * Update to notification: "Received subsequent DRMS low sample flow alarm and sample pump trip at 0619 on 9/29/13 for Service Water Radiation monitor 2SWP*CAB146B. The sample pump was returned to service and subsequently tripped again. The monitor has been declared non-functional and Compensatory Actions are being taken per ODCM. Maintenance is engaged for resolution. Investigation includes potential impact from Service Water Mollusk Biocide Treatment which concluded 9/26/13." The licensee informed the NRC Resident Inspector. Notified R1DO (Welling). * * * UPDATE ON 10/1/13 AT 2109 EDT FROM JASON SAWYER TO HOWIE CROUCH * * * "The Service Water Radiation monitor 2SWP*CAB146B was removed from service for inspection. The cause of the radiation monitor tripping is attributed to the scale that is forming on the flow switch sensing element. Flow switch element on 2SWP*CAB146B has been cleaned and radiation monitor has been placed back in service. The monitor was placed in service on 9/29/13 at 1200 and has been functioning properly since then. As of 2100, 2SWP*CAB146B has been declared functional and ODCM 3.3.1 actions have been exited." The licensee will notify the NRC Resident Inspector. Notified R1DO (Joustra). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-28
49390 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-27 13:30 | 2013-09-27 17:42 | 2013-09-27 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO RADIATION MONITORS OUT OF SERVICE "On 9/27/13, Monticello Nuclear Generating Plant personnel identified that when the Service Water Radiation Monitor or the Discharge Canal Radiation Monitors are removed from service for planned maintenance activities, a loss of emergency assessment capability may occur. The adequacy of compensatory measures for when these radiation monitors are removed from service is under evaluation. "The Service Water Radiation Monitor is taken out of service weekly for flushing. This last occurred at 0221 [CDT] on 9/26/13. The Discharge Canal Radiation Monitors are taken out of service approximately once a year for cleaning. The last time these monitors were removed from service was at 1250 [CDT] on 9/18/13. "In accordance with 10CFR50.72(b)(3)(3)(xiii) these past occurrences are being reported as a loss of emergency assessment capability. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-27
49389 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-09-27 12:45 | 2013-09-27 13:35 | 2013-10-29 | CALCULATION ERROR RESULTED IN UNANALYZED CONDITION FOR APPENDIX R EVENT "On July 18, 2012, TVA identified that a calculation error resulted in the inability to establish Essential Raw Cooling Water (ERCW) supply to the Component Cooling System (CCS) heat exchanger within the required time to ensure cooling is available to Reactor Coolant System (RCS) seal injection water during an Appendix R event. TVA promptly established fire watches as a compensatory measure to prevent initiation of fires in the areas of concern. Subsequently, abnormal operating instructions were revised to take action to ensure that adequate time is available to establish ERCW cooling to CCS, and ensure cooling to [Reactor Coolant Pump] RCP seal injection water. "The calculation error was identified on July 18, 2012, however, it was not recognized at the time that an unanalyzed condition existed that was reportable under 10 CFR 50.72(b)(3)(ii)(B). This report documents that the condition that existed until fire watches were established is reportable under 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified of this condition." * * * RETRACTION FROM BRIAN MCILNAY TO DONALD NORWOOD AT 1021 EDT ON 10/29/2013 * * * "Watts Bar Nuclear Plant Unit 1 is retracting this 8 hour non-emergency notification made on September 27, 2013, at 1335 EDT (EN #49389). The notification on September 27, 2013, reported a calculation error which resulted in the inability to establish Essential Raw Cooling Water (ERCW) to supply the Component Cooing System (CCS) heat exchanger within the required time to ensure cooling is available to Reactor Coolant System (RCS) seal injection water during an Appendix R event. "Subsequent analysis of actual plant data concluded that TVA could have established cooling to RCS seal injection during the subject Appendix R event, and achieved and maintained fire safe shutdown. Therefore, this event was not reportable under 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." R2DO (Bartley) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-27
49388 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-27 08:20 | 2013-09-27 09:33 | 2013-09-27 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "On 9/27/13, Monticello Nuclear Generating Plant's Technical Support Center power supply will be isolated to perform a planned maintenance activity. The maintenance activity may require implementation of compensatory measures to maintain TSC functionality during the activity. The compensatory measures include having the Emergency Director report to the Control Room and co-locating the remaining TSC staff at the EOF should an event be declared requiring ERO activation. The ERO has previously successfully demonstrated the ability to implement these compensatory measures. The maintenance activity is scheduled to be completed with the TSC returned to full functionality by the end of the dayshift on 9/27/13. The Site Emergency Response Organization has been notified of the maintenance activity. "The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 9/27/13 AT 1916 EDT FROM MARK IHLENFELDT TO DONG PARK * * * "On 9/27/13, Monticello Nuclear Generating Plant's Technical Support Center power supply was isolated to perform a planned maintenance activity. The maintenance activity required implementation of compensatory measures to maintain TSC functional during the activity. Maintenance activity is completed and TSC is fully functional and returned to service. Site Emergency Response Organization has been notified. The licensee has notified the NRC Resident Inspector." Notified R3DO (Dickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-27
49387 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-09-26 12:20 | 2013-09-26 20:12 | 2013-09-26 | FITNESS FOR DUTY PROGRAM MEMBER IN VIOLATION OF POLICY A Fitness For Duty (FFD) program member was in violation of the Northern States Power Company - Minnesota Nuclear FFD policy. The program member's access has been suspended pending assessment and management review. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2013-09-26
49386 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-09-25 15:30 | 2013-09-25 21:20 | 2013-09-25 | ENVIRONMENTAL IMPACT DURING SERVICE WATER MOLLUSK BIOCIDE TREATMENT "During Service Water mollusk biocide treatment, divers in Lake Ontario found approximately 20 Goby fish dead near the intake structure. Nine Mile Point Unit 2 Operating License Appendix B, Environmental Protection Plan, paragraph 4.1 requires a 24-hour notification of any occurrence of an unusual or important event that indicates or could result in significant environmental impact causally related [to] plant operations. This fish kill may have been caused by the chemical injection line being dislodged above the intake structure. Chemical injection was secured when the mispositioned line was discovered. The New York State DEC [Department of Environmental Conservation] was notified in a related report of the unexpected injection site of the chemical. "The NRC Resident inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2013-09-25
49385 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-20 | 2013-09-25 12:30 | 2016-04-27 | AGREEMENT STATE REPORT - MISSING MOISTURE DENSITY GAUGE The following report was received from the State of Texas via email: "On September 25, 2013, the Agency [Texas Department of State Health Services] was notified by a licensee that one of its Humboldt Model 5001EZ moisture/density gauges was missing and presumed stolen from its facility. The gauge (SN: 3561) contains one 10 millicurie cesium-137 source and one 40 millicurie americium-241/beryllium source. The gauge could not be located on Friday, September 20, 2013, and the licensee began a search and investigation. On Monday, September 23, 2013, it made the determination that it was missing/presumed stolen. The gauge had been secured inside a locked storage area inside the facility with the licensee's other gauges. No other gauges were missing. The licensee notified local law enforcement and a gauge sales/service company in Houston. The Agency will notify the Texas Pawnbrokers Association. An investigation into this event is ongoing. Further information will be provided as it is obtained in accordance with SA-300. "[The] Houston Police Department [was notified by the licensee on 09/23/2013]." Texas Report # I 9118 * * * UPDATE AT 1540 EDT ON 4/27/2016 FROM ARTHUR TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On April 26, 2016, the Agency was notified by the licensee they had recovered the gauge reported stolen on September 23, 2013. The licensee reported they were contacted by the Houston, Texas Police Department (HPD) and informed that HPD was in possession of their missing gauge. The HPD stated they had recovered the gauge from a vacant property and they had been storing it in their impound building for about one year while they searched for the owner. The licensee will leak test, calibrate, and inspect the gauge prior to returning it to service." Notified the R4DO (Groom), ILTAB (Rockhill via e-mail), Mexico (via e-mail), and NMSS Events Resource (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-10-03
49384 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-09-25 10:06 | 2013-09-25 11:54 | 2013-09-25 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "The Millstone Power Station Unit 2 High Range Stack Radiation Monitor, RM-8168 is being removed from service for preplanned maintenance. The radiation monitor is estimated to be out of service for approximately 6 hours. This action is reportable as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. State and local authorities were notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-25
49383 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-09-25 03:04 | 2013-09-25 11:08 | 2013-11-02 | LOSS OF NORMAL TSC POWER DUE TO TRANSFORMER ISOLATION "At 0304 (CDT), on Sept 25, 2013, the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) normal power supply was lost when the T4 '36KV-12.5KV DAEC SITE TRANSFORMER' was lost. Automatic power transfer occurred to maintain power to the TSC from the TSC Emergency Diesel Generator (EDG) which automatically started. Prior to the loss of normal power, the TSC Emergency Diesel Generator maintenance functional testing had been completed and was in standby readiness, awaiting post maintenance testing to be completed on the auto start circuit. The TSC Emergency Diesel Generator responded normally to the loss of power and energized TSC loads. The TSC remained functional throughout the incident. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency assessment capability. An update will be provided once the normal power supply has been restored." The NRC Resident Inspector has been notified. * * * UPDATE FROM STEVE SPEIRS TO HOWIE CROUCH AT 1844 EDT ON 11/2/13 * * * The TSC normal power supply was returned to service at 1830 EDT on 11/2/13. The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Daley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-25
49382 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-09-24 15:30 | 2013-09-24 23:21 | 2013-09-24 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE DUE TO AN UNQUALIFIED ELECTRICAL SPLICE "On 9/24/13 at 1530 CDT, the Browns Ferry Nuclear Plant Unit 2 High Pressure Coolant Injection (HPCI) System was declared inoperable due to inoperability of the minimum flow valve (2-MVOP-073-0030). Engineering identified during review of EQ [Environment Qualification] WO [Work Order] # 113598388 that the motor leads for 2-MVOP-073-0030 were taped instead of terminated with a Raychem splice. The valve actuator is an EQ component and requires termination of the motor leads to the incoming power cable by Raychem splice or a Marathon 300 terminal block. Engineering evaluation was requested and operability of 2-MVOP-073-0030 could not be supported due to the tape being unanalyzed for harsh environmental conditions. The HPCI Minimum Flow valve has a required OPEN safety function to prevent overheating the HPCI pump and a CLOSED safety function to provide containment isolation. Technical Specification 3.5.1, Emergency Core Cooling System-Operating, Condition C was entered for HPCI system inoperability. In addition, the actions of Technical Specification 3.6.1.3, Primary Containment Isolation Valves, were entered due to the inoperability of the primary containment isolation function of the HPCI Minimum Flow valve. "This incident is reportable as an 8-hour ENS notification under 10 CFR 50.72 (b)(3)(v)(D) as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. It also requires a 60 day written report in accordance with 10 CFR 50.73(a)(2)(vii). "The NRC Resident Inspector has been notified. "SR number associated with this report: 784462" The licensee is in a 14-day LCO action statement to return HPCI to operable under TS 3.5.1. The LCO for TS 3.6.1.3 was satisfied. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-09-24
49381 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-08-22 | 2013-09-24 15:53 | 2013-09-24 | AGREEMENT STATE REPORT - MISSING BRACHYTHERAPY SEED The following was received by the Commonwealth of Massachusetts via fax: "On 8/22/2013, Brigham and Women's Hospital (BWH) was involved in a discrepancy in the contents of a shipment of I-125 brachytherapy seeds. The shipment was labeled to contain 71 seeds (as ordered), plus 4 seeds to be used for QC purposes. Upon opening, in preparation for administration, a count of the sources revealed only 70 of the 71 expected therapy seeds. "Immediate recount and subsequent survey & investigation of the area, packaging and container showed no indication of the presence of the 71st seed. There was also no evidence of contamination detected. "BWH does not believe the 71st seed was delivered. "Meanwhile, the supplier, Bard Brachytherapy, Inc.'s (BBI) investigation indicates that the 71st seed was shipped to BWH. "The expected 71st seed was a Bard Brachytherapy, Inc., model 125I containing 0.561 mCi (with an apparent activity of 0.330 mCi), with a reference date of 8/17/2013." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-10-02
49380 | 0 | CARROLL COUNTY MEMORIAL HOSPITAL |  |  |  |  | 2013-09-24 | 2013-09-24 13:35 | 2013-09-24 | PACKAGE WITH EXTERNAL CONTAMINATION The licensee's RSO (Radiation Safety Officer) reported that a package received from the pharmaceutical supplier was contaminated externally. Swipes from the outside of the package had counts of 91,500 cpm (counts per minute) with a background count reading of 588 cpm. Swipes from inside the package had counts of 1008 cpm. There were no indications of contamination to personnel or the surrounding area. The pharmaceutical supplier was contacted and has verified the driver was not contaminated. They will also check the delivery vehicle. The package, containing Iodine-131 (18 mCi) and Technetium-99m (6 mCi) sources, has been placed in a secure location pending further investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2013-10-02
49379 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-09-23 16:55 | 2013-09-23 22:13 | 2013-09-23 | BOTH SECONDARY CONTAINMENT ACCESS DOORS OPENED SIMULTANEOUSLY "At 16:55:59 [CDT] on September 23, 2013, indication was received in the Control Room that two Secondary Containment doors, in one access opening, were opened simultaneously. The interlock mechanism preventing both doors from operating simultaneously did not operate as expected. This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2. As a result, entry into Technical Specifications 3.6.4.1 condition A was made due to Secondary Containment being inoperable. The doors were secured at 16:56:04 and Secondary Containment was declared operable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-09-23
49378 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-09-23 13:40 | 2013-09-23 18:37 | 2013-09-23 | UNANALYZED CONDITION - EPOXY FLOOR COATINGS DO NOT MEET DESIGN BASIS REQUIREMENTS IN TWO ROOMS "At 1340 CDT, on 09/23/2013, as part of a vendor analysis for the high energy line break reconstitution project, it was determined that Room 81 and 82 epoxy floor coatings do not meet the design basis requirements for a high energy line break barrier. This is an unanalyzed condition based on 10 CFR 50.72(b)(3) as loss of the floor coating could affect multiple redundant trains of safety-related equipment during a design basis event. The plant is currently in a cold shutdown condition." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-23
49377 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-09-23 09:36 | 2013-09-23 10:25 | 2013-09-23 | LOSS OF ASSESSMENT CAPABILITY DUE TO PREPLANNED MAINTENANCE AFFECTING RADIATION MONITORS "Ventilation process radiation monitors for the Turbine Building Stack Discharge (monitors HVR*RE10A and HVR*RE10B) will be out of service for preplanned maintenance. This is reportable in accordance with 10 CFR 50.72(b)(3)(xiii)." The licensee stated that this condition is being reported based on the inability to sufficiently identify and classify an Emergency Action Level for radiation releases that utilize input from the affected monitors while they are out of service. The licensee will notify state and local authorities. The licensee will also notify the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-23
49376 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-09-22 20:36 | 2013-09-22 23:48 | 2013-09-23 | TRANSPORT OF POTENTIALLY CONTAMINATED WORKER OFFSITE "On 09/22/2013 at 1940 CDT, Prairie Island Nuclear Generating Plant (PINGP) requested an offsite ambulance via the 911 system for medical assistance for an individual in the radiologically controlled area. The person was treated as potentially contaminated because a complete survey to confirm the absence of contamination was not completed prior to transport of the individual. An ambulance arrived on site at 1956 CDT and departed the site at 2036 CDT to the Red Wing Minnesota Hospital. PINGP radiation protection personnel accompanied the individual to the hospital. A survey at the hospital determined that the individual was not contaminated. "This is considered a transport of a potentially contaminated individual requiring an 8 hour ENS Notification per 10CFR50.72(b)(3)(xii). "The Prairie Island Indian Community was notified of the transport of an individual by ambulance. "This is considered a notification of another government agency and an event that may have potential interest to the media requiring a 4 hour ENS Notification per 10CFR50.72(b)(2)(xi). "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2013-09-23
49375 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-09-21 15:31 | 2013-09-21 19:07 | 2013-09-21 | LOSS OF COMMERCIAL AND ENS COMMUNICATIONS DUE TO AN AREA PHONE OUTAGE "At 1531 CDT, Byron Station was contacted via NARS [Nuclear Accident Reporting System] phone line by the Illinois Emergency Management Agency (IEMA) that an issue exists for the phone systems in the Byron area. Byron subsequently contacted lEMA via the NARS phone and was able to communicate with lEMA. At 1536 CDT, the ENS phone was verified to not be functioning and at 1541 CDT NRC Headquarters was contacted via Byron Main Control Room cell phone to report the failure of the ENS and commercial phones. The Byron Station Main Control Room cell phone is functioning normally. The loss of ENS and commercial phone capability is reportable under 10CFR50.72(b)(3)(xiii). The cause of the loss of phone capability is not known but is under investigation and an update will be provided upon restoration." ERDS has been verified as operable and the licensee is transmitting data. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-21
49374 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2013-09-20 16:00 | 2013-09-20 19:45 | 2013-09-20 | POTENTIAL DESIGN BASIS FLOODING ISSUES RELATED TO BATTERY ROOM WALL PENETRATIONS AND CABLE VAULT FLOOR DRAINS "On 9/20/2013 at 1600 EDT, R.E. Ginna Nuclear Power Plant determined that there was a potential for flooding of both battery rooms during a design basis flood due to unqualified wall penetration material and partially blocked cable vault floor drains. Testing of underground cable vault drain lines failed to demonstrate that they could pass the required flow due to debris accumulation. The penetrations are below grade and approximately five feet above the bottom of the vault floor. During a design basis flood, water could flow through the holes in the vault manhole covers and fill up the vaults to the level of the penetrations. Since the penetration barriers do not appear to be qualified for flooding, leakage into Battery Room B could be expected. Battery Room A and Battery Room B have a normally closed emergency fire door between them that allows water to pass under the door into Battery Room A where a sump pump exists. It is not currently known if the sump pump capacity would have been able to mitigate flooding of both battery rooms. The discovery of this condition is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B). "The 125VDC system is currently Operable. Current weather forecasts do not predict the conditions necessary for flooding. Additionally, compensatory measures have been implemented to provide barriers to water entry into the vault manholes until corrective actions are implemented. "The NRC Resident Inspector has been notified of this condition" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-20
49373 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-09-20 09:17 | 2013-09-20 18:00 | 2013-09-20 | SAFE SHUTDOWN ANALYSIS REVEALS NONCOMPLIANCE FOR A FIRE OUTSIDE DIESEL ROOM "During the performance of a focused area self assessment (FASA) for the Clinton Power Station Fire Protection Program, the FASA team identified a noncompliance with the Safe Shutdown Analysis for a fire outside the Diesel Generator (DG) rooms (i.e., Fire Zone CB-1e, CB-1f, CB-2 and CB-4). The CO2 panels for each DG train are all located in the same area outside the DG engine bay rooms (i.e., 737' Control Building) and a fire in this area could cause fire damage to all three CO2 panels and/or wiring such that a trip (short) could be initiated to all three DG Ventilation (VD) fans. Loss of the VD fans (1VD01CA, B and C) results in loss of cooling in the DG rooms and ultimately loss of the diesels. This constitutes an Unanalyzed Condition that Significantly Affects Plant Safety. "Compensatory measures are in-place that will allow these VD trips to be overridden and the VD fans to be restarted from the Main Control Room. "The NRC Resident Inspector has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-20
49372 | 0 | ABB, INC. |  |  |  |  | 2013-07-23 | 2013-09-20 16:35 | 2013-09-20 | ABB SOLID STATE CIRCUIT SHIELD AND POWER SHIELD RELAYS SHIPPED WITH INCORRECT CERTIFICATES OF CONFORMANCE The following information was obtained from ABB, Inc. via facsimile: "This notification is submitted in accordance with 10 CFR 21.21(d)(3)(ii). Solid State Circuit Shield Relays (27, 40, 47, 60, 81, 25V, 27/59, 27D, 27H, 27N, 46D, 46Q, 47H, 50H, 59G, 87M) and Power Shield (K-Line) Relays containing CMOS technology Integrated Circuits (IC's) have been shipped with Certificates of Conformance (CoC's) that incorrectly state that they are qualified to 100,000 rads. "On July 23, 2013, ABB discovered that the above radiation tolerance value had been incorrectly communicated to customers due to a reference to an incorrect document. ABB failed to update the reference document following the Part 21 notification dated July 28, 1994. ABB's investigation showed that this issue dates back to the beginning of production of solid state relays in the Coral Springs facility in 2009 when the CoC format changed to include this information. As such, the CoC's that ABB provided incorrectly identified the radiation tolerance as 100,000 rads rather than 1,000 rads. "All qualification documents and future CoC's will be reviewed to ensure proper record of radiation tolerance is maintained. This review is to be completed by Dec 31, 2013 "ABB will notify the affected customers for the listed relays that they should review their applications which require total radiation tolerance greater than 1,000 rads to determine the effects of a possible device malfunctioning on the system. "ABB does not have the capability to perform an evaluation to determine if a defect exists, and therefore in accordance with 10 CFR 21.21(b), we are making this notification simultaneously to our customers so they may evaluate this issue, pursuant to 10 CFR 21(a). "Any customers finding that [ABB's] qualification level is insufficient will be advised to contact [ABB's] customer support line at 1-800-222-1946 or 1-954-752-6700 for discussion of remedial action. "This information was provided by: Dennis Batovsky Managing Director ABB, Inc. 4300 Coral Ridge Drive Coral Springs, FL 33065" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-09-20
49371 | -1 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-09-09 17:00 | 2013-09-20 14:40 | 2013-10-31 | UNANALYZED LEAKAGE OF CONTAINMENT SYSTEM ISOLATION VALVE CONTROLLED LEAKAGE DEVICES "On September 9, 2013, during the A1R17 Braidwood Station Unit 1 refueling outage, the as-found leakage of the controlled leakage devices (1RH01SA and 1RH01SB) for the safety injection (SI) system ECCS sump containment isolation valves (1SI8811A and 1SI8811B) were determined to not be 'leak tight' as described in the UFSAR. Since there was only minor leakage from the isolation valves or the associated residual heat (RH) system piping (1-2 drops/month from 1SI8811A and no leakage from 1SI8811B), there was no actual impact on offsite dose or long-term ECCS operation. However, further evaluation has concluded that there was a potential to exceed the assumed leakage limits of the Alternate Source Term (AST) calculation. "The RH system is classified as a closed system outside containment meaning the system is designed to accommodate a single active failure (i.e., the failure of the 1SI8811B valve to close) and still maintain an adequate isolation barrier to release recirculation water outside containment. The encapsulation device is intended to capture and limit leakage from a potential leak in the 1SI8811A/B or piping. The controlled leakage device is built to the same standards as the remainder of the RH system recirculation water outside containment. The design function is to limit potential offsite dose due to leakage of recirculation water outside containment. This is not a specified safety function and there are no Technical Specification requirements for these devices. The encapsulation devices do not perform a containment function and are not a principle safety barrier. As there was only minor ECCS system leakage at the time of discovery, there was no impact on past offsite dose or long-term ECCS operation. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B) since the as-found leakage of the controlled leakage devices could have allowed RH leakage to exceed the calculated limits for ECCS systems outside containment. "The NRC Resident Inspector has been informed." * * * RETRACTION FROM RANDY RAHRIG TO HOWIE CROUCH AT 1556 EDT ON 10/31/13 * * * "Retraction of ENS 49371 dated 9/09/2013: "The purpose of this report is to retract ENS report #49371 (September 9, 2013). This report was made during Braidwood's refueling outage (A1R17) for the as-found leakage on the controlled leakage devices (1RH01SA and 1RH01SB) for the safety injection (SI) system ECCS sump containment isolation valves (1SI8811A and 1SI8811B) that were determined not to be 'leak tight' as described in the UFSAR. When the ENS notification was made on 9/9/2013, the station determined that there was a potential to exceed the assumed leakage limits of the alternate source term (AST) calculation. The ENS notification was made under 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "At 1500 CDT on Thursday, October 17, 2013, the Braidwood Generating Station concluded that the prior ENS notification could be retracted based on the completion of Revision 2 of calculation BRW-13-0135-M, '1/2RH01SA/B Leak Rate Conversion and Test Pressure Determination'. "The as-found pressure test results for the 1RH01SA and 1RH01SB valve containment assemblies would not have resulted in a total ECCS leakage outside containment in excess of that assumed in the AST dose calculation BRW-04-0038-M, 'Re-Analysis of Loss of Coolant Accident (LOCA) Using Alternate Source Terms (AST)'. "The as-found valve containment assembly (VCA) pressure test results did not result in an unanalyzed condition that significantly degrades plant safety. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Daley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-20
49370 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2013-09-20 | 2013-09-20 12:54 | 2013-09-20 | PART 21 ISSUE ON ROSEMOUNT MODEL 710DU TRIP UNITS The following is a summary of the information received from Rosemount Nuclear Instruments, Inc. (RNII) via facsimile: In August 2013, Rosemount conducted normal, transient and accident radiation testing on a sample of Model 710DU Trip Units (master and slave) to verify radiation performance of some commercial grade semiconductor components. The results indicated that post-exposure radiation performance may not meet the criteria established in their previously published Qualification Report D8200037. This affects all transmitters shipped from RNII since June 1983. Per RNII's Model 710 Trip/Calibration System Discontinuance Letter dated September 14, 2011, RNII stopped accepting purchase orders as of December 31, 2012. At this time RNII is no longer accepting orders and no corrective actions are being taken. These transmitters were purchased by: Carolina Power and Light/Duke Energy, Commonwealth Edison Co., Constellation Energy Group, Inc., DTE Energy Services, Inc., Energy Northwest, Entergy Nuclear, LLC, Exelon Generation Co., LLC, Gavial, General Physics Corp., GE Nuclear Energy, Georgia Power Co./Southern Nuclear Operating Co., Harlo Corp., Knolls Atomic Power Lab, Long Island Lighting Co., Mercury Co. of Norwood, Inc., Mississippi Power & Light Co., Nebraska Public Power District, NextEra Energy/FPL Energy, Northern States Power/XCEL Energy, Inc., NuTherm International, Inc., PPL Susquehanna, LLC, Progress Energy Carolinas, LLC/Duke Energy, PSEG Nuclear, LLC, Public Service Electric & Gas, Singer Co., Tennessee Valley Authority, Texas Municipal Power Agency, United Controls and Westinghouse Electric Corporation. Name and address of the individual providing the information: Mr. Marc D. Bumgarner Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-09-20
49369 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2013-09-20 14:00 | 2013-09-20 13:28 | 2013-09-20 | PRESS RELEASE NOTIFICATION "A press release is being made today by the FirstEnergy Nuclear Operating Company regarding routine inspections of the Davis-Besse Nuclear Power Station's concrete shield building. "These routine inspections of the Davis-Besse Nuclear Power Station's concrete shield building conducted to date have confirmed that the building continues to maintain its structural integrity and ability to safely perform its functions." The NRC Resident Inspector has been informed. * * * UPDATE FROM GERALD WOLF TO CHARLES TEAL AT 1623 EDT ON 9/20/13 * * * "The press release originally provided to the NRC was revised prior to release to the public to update the inspections completed to date." The NRC Resident Inspector has been informed. Notified R3DO (Riemer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-09-20
49368 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-09-20 08:00 | 2013-09-20 12:18 | 2013-09-20 | SUPERVISOR TESTED POSITIVE FOR ALCOHOL ON A FOR CAUSE TEST A facility supervisor tested positive for alcohol on a for-cause fitness for duty test. The supervisor's access to the facility has been restricted. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2013-09-30
49367 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2013-09-18 | 2013-09-20 12:17 | 2013-09-20 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following was received by the State of Illinois via email: "On September 18, 2013, Equistar Chemical's Radiation Safety Officer contacted the Agency [Illinois Emergency Management Agency] to report that a shutter on a fixed gauge could not be closed at their Morris, Illinois facility. The shutter on the fixed level gauge, manufactured by Vega America, could not be closed during a routine shutter check. The gauge is located on a vessel that is not routinely accessible to personnel due to temperatures on their hot particle line. The gauge normally operates in the constant 'open' position. It remains in its normal operational configuration at this time. This situation does not pose an immediate threat to health or safety unless an emergency shutdown condition were necessary requiring access to the vessel. At the time of discovery, a consultant was on-site performing the shutter checks and he immediately performed a dose rate survey of the device with no unusual measurements noted. This device was last checked and found to be operational in June 2013. The manufacturer was contacted to arrange service of the device on-site. "The next day, the Radiation Safety Officer reported that following several additional attempts, they had been able to close the shutter. Per the manufacturer, the gauge shutter and handle shaft were sprayed with a light penetrating oil and after some time spent partially rotating the shutter, it will now rotate 90 degrees and allow the licensee to close the gauge if necessary. Arrangements were made with the manufacturer's field engineering group to have a shutter repair kit sent to the site within the next week when a field technician can perform the necessary repairs. The licensee believes that since all of the symptoms were very similar to previous device issues at the facility in the same area of the plant, water and resulting corrosion are inside of the gauge housing which is binding the shutter." Illinois NMED Number: IL13029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2013-09-30
49366 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-05-09 | 2013-09-20 11:58 | 2013-09-20 | MEDICAL EVENT INVOLVING DOSE TO THE WRONG ORGAN The following information was obtained from the State of Ohio via email: "At 1000 [EDT] on Sept 20, 2013 the Cleveland Clinic Foundation (CCF) RSO called the Ohio Department of Health (ODH) Bureau of Radiation Protection to report the determination of a medical event based on the back calculations from a symptomatic patient that had received a Y-90 microsphere treatment on May 9, 2013. The patient received a treatment of Y-90 SIR-Spheres to both the left and right lobes of the liver. "The vessel to the stomach area was coiled to prevent shunting. At the time of the treatment, the patient complained of some abdominal pain. The post-treatment scan was inconclusive regarding the shunting to the stomach area. The AU [authorized user] and interventional radiologist concluded that a shunt was unlikely. "The patient continued to complain of stomach pain and returned to the CCF on Sept 5, 2013 for an endoscopy. The endoscopy revealed ulcers in the potentially affected areas. "After additional review of the post-treatment scan by the licensee, it was not abundantly apparent, but possible, that shunting did occur. Based on the assumption that shunting did occur, the licensee determined that the gastric antrum, an unintended treatment area, received a dose of 62 Gy. "The ODH Bureau of Radiation will be conducting an onsite investigation. "This incident was assigned ODH incident report number 2013-011." NMED Item Number: OH130014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2013-09-30
49365 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-09-20 06:45 | 2013-09-20 08:22 | 2013-09-21 | AUXILIARY BUILDING SPECIAL PARTICULATE IODINE NOBLE GAS (SPING) MAINTENANCE "On September 20th, 2013 at approximately 0645CDT, the Kewaunee Power Station rendered the Auxiliary Building Special Particulate Iodine Noble Gas 'SPING' both Mid and High Range [radiation monitors] non-functional for maintenance on the Mid range. The Emergency Response Organization (ERO) team has been notified of the Auxiliary Building SPING non-functionality due to the maintenance. "The SPING is expected to be out of service for approximately 7 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify and classify an Emergency Action Level for offsite radiation conditions). "The NRC Resident Inspector has been notified." * * * UPDATE FROM DANIEL BACKUS TO CHARLES TEAL AT 1453 EDT ON 9/20/13 * * * The maintenance required the replacement of the Geiger Muller (GM) detector. The GM detector requires a 12-hour burn in time. The detector is expected to be returned to service at approximately 1900 CDT on 9/21/13. The NRC Resident Inspector has been informed. Notified R3DO (Riemer). * * * UPDATE FROM DAVE IRLBECK TO CHARLES TEAL AT 2121 EDT ON 9/21/13 * * * At 2019 CDT on 9/21/13 the SPING system has been returned to service. The licensee will notify the NRC Resident Inspector. Notified R3DO (Riemer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-20
49364 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-09-19 22:30 | 2013-09-20 05:42 | 2013-09-20 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT ACTIVATION OF AN EMERGENCY SIREN "On 9/19/13 at approximately 2230 EDT, Emergency Siren 602 inadvertently actuated. Berrien County Dispatch was notified by local residents at 2237 EDT. The cause of the actuation is under investigation but believed to be due to rain water intrusion. The siren was subsequently disconnected by a station technician to prevent further erroneous actuation. The siren remains out of service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ). There are a total of 70 sirens. "This notification is being made under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report. The Operations Shift Manager was notified of the actuation on 9/20/13 at 0340 EDT. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-09-20
49363 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-19 17:50 | 2013-09-19 23:56 | 2013-10-28 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO STEAM LEAK "On 9/19/2013, during the performance of the High Pressure Coolant Injection (HPCI) quarterly pump and valve surveillance, a steam leak was discovered. HPCI had previously been declared inoperable due to planned maintenance. As a result of the steam leak, HPCI remains inoperable. "Action taken: 14 days Required Action TS 3.5.1.J.2 remains in effect and corrective actions are in progress. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM RANDY SAND TO PETE SNYDER AT 1546 EDT ON 10/28/13 * * * "The licensee performed an evaluation that determined the minor steam leak from the High Pressure Coolant Injection (HPCI) turbine reported on 9/20/2013 was not significant enough to prevent HPCI from mitigating the consequences of an accident or mitigating a Station Blackout (SBO) event. "The licensee performed an engineering evaluation of the HPCI system, the HPCI pump/turbine and the HPCI room environmental conditions assuming conservative leakage conditions existed. The results of this evaluation confirmed that the HPCI system would have been able to perform its design function assuming conservative leakage conditions existed throughout limiting events. The HPCI pump/turbine would not have failed during any accident or SBO event, and sufficient motive (steam) force was available for the HPCI system to perform its design functions. There would have been no unacceptable impact on the HPCI pump/turbine oil system due to the steam leak. The HPCI room environment would not have exceeded allowable limits. For events where AC power is available, the analysis took advantage of the HPCI room cooler that is powered from an essential power source and supplied from a safety related service water system. This cooler was available during the period of the steam leak. The evaluation of room conditions for SBO conditions did not include use of the HPCI room cooler and also showed room conditions would have remained within acceptable values. There would not have been a buildup of fluid sufficient to cause a flood in the HPCI room. "Therefore, based on the results of the formal engineering evaluation, the HPCI system was capable of performing its safety function and therefore, this event may be retracted." The licensee will notify the NRC Resident Inspector. Notified R3DO (Daley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-09-20
49362 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2013-09-19 14:37 | 2013-09-19 20:31 | 2013-09-19 | SECONDARY CONTAINMENT INOPERABLE DUE TO AN UNATTENDED OPEN DOOR "Security personnel reported to the Main Control Room that at time 1437 CDT, an alarm indicated that a secondary containment door was open beyond the normal delay time allowed for entry and exit. Security personnel responded and found the door open and unattended with the dogs extended meaning that the door was unable to be closed. Security personnel secured the door at time 1441 CDT. No deficiencies were found with the door. The fact that the door was open and unattended beyond the time allowed for normal entry and exit violates Technical Specification 3.6.4.1, 'Secondary Containment- Operating,' because surveillance requirement SR 3.6.4.1.3 was not met. This surveillance requires that doors be closed except during normal entry and exit. "In summary, an SSC was inoperable in a required mode as a result of a personnel error and no redundant equipment in the same system was operable. Thus, the condition is reportable under 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-09-19
49361 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-09-19 12:20 | 2013-09-19 17:13 | 2013-09-19 | NO DOCUMENTED PLAN IN PLACE TO RECEIVE ADDITIONAL FUEL OIL DURING MAXIMUM PROBABLE FLOOD CONDITION "On September 19, 2013, a potential unanalyzed condition was identified. The current licensing basis requires a 14 day supply of fuel oil. Preliminary calculations show that there is sufficient tank volume for the duration of design basis maximum probable flood condition. However, during maximum flood condition there is currently no documented plan in place to receive additional fuel oil to maintain Unit 1 and Unit 2 Emergency Diesel Generators operable and running to supply emergency power to essential loads for the duration of the effects of a design basis maximum probable flood condition. These effects, such as flooded roads, may exceed 14 days. This is not an immediate safety concern because additional fuel oil can be added to the fuel oil storage tanks for imminent flood conditions. "The NRC Resident has been notified." | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-19
49360 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2013-06-25 | 2013-09-19 14:56 | 2013-09-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the State of Nebraska via facsimile: "B & J Partnership purchased two Isolite model SLX60 exit signs with 6.2 curies of H3 in each sign on December 8, 2011. On September 19, 2013 the Department [Nebraska Department of Health and Human Services] was notified that the General Licensee did not know where the exit signs were after an extensive search." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2013-09-27
49359 | 0 | DUKE ENERGY |  |  |  |  | 2013-09-18 16:45 | 2013-09-19 14:32 | 2013-09-19 | APPARENT FALSE NEGATIVE INDICATED ON A BLIND PERFORMANCE TEST "Per 10 CFR 26.719 section (c)(3), Duke Energy is making this notification of an apparent false negative error that has occurred on a blind performance test sample submitted to the Health and Human Services (HHS)-certified laboratory used for drug testing. On September 18, 2013, Duke Energy was notified that a drug sample that was part of a blind performance test package provided by El Solhy and submitted to LabCorp tested negative. Duke Energy will investigate the issue and report to the NRC as required by part 26.719(c)(1). El Solhy and LabCorp are contracted by Duke Energy as required by NRC regulations to provide fitness for duty services. Duke Energy has notified the NRC Branch Chief for the Fitness for Duty program [Paul Harris], which advised that Duke needs to notify the NRC Headquarters Operations Center." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 1 | NC | OTH | GEN | 26.719 |  |  |  | 0 | 2013-09-19
49358 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-07-23 | 2013-09-19 13:17 | 2013-09-19 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM GROUP 3 ACTUATION "This notification is being made in accordance with 10CFR50.73 (a)(2)(iv)(A) to provide information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment valves in more than one system. "On 7/23/2013, and again on 7/24/2013, with the reactor at 100% power, an invalid PCIS Group 3 actuation occurred from a momentary spike of the 'B' Reactor Building ventilation radiation monitor which reached the instrument's high radiation trip set point. A radiation protection technician was dispatched and radiation levels in the vicinity of the 'B' radiation monitor were verified to be normal and below the alarm set points. The radiation monitor was verified to be indicating normal expected radiation levels. Subsequent visual inspection and functional checks of the radiation monitors were completed satisfactory and the instrument channel was returned to service. "At the recommendation from the vendor, the detectors were replaced in both of the Reactor Building ventilation monitors as well as the Refuel Floor radiation monitors. "On 8/19/2013, 9/12/2013, and 9/13/2013, with the reactor at 100% power, invalid PCIS Group 3 actuations occurred from a momentary spike of the 'A' Refuel Floor radiation monitor which reached the instrument's high radiation trip set point. A radiation protection technician was dispatched to the refuel floor and dose rates in the vicinity of the 'A' radiation monitor detector were verified to be normal and below the alarm set points. The radiation monitor was verified to be indicating normal expected radiation levels. Subsequent visual inspection and functional checks of the radiation monitors were completed satisfactory and the instrument channel was returned to service. "Both trains of Standby Gas Treatment System started as designed and Reactor Building ventilation isolated as a result of the invalid PCIS actuation. "The PCIS functioned successfully providing a complete Group 3 isolation. The PCIS Group 3 isolation involves the following systems: Drywell and Suppression Chamber air and vent: V16-19-6A, 6B, 7, 7A, 7B, 8, 9, 10, 23 Containment Makeup: V-16-20-20, 22A, 22B Containment Air Sampling: VG-23, 26, V109-76A, 76B Containment Air compressor suction: V72-38A, 38B Containment Air Dilution: VG-9A, 9B, 22A, 22B, NG-11A, 11B, 12A, 12B, 13A, 13B "Since no actual high radiation condition existed which required the PCIS Group 3 isolation, and the actuation was not in response to actual plant conditions satisfying the requirements for isolation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." "In accordance with 10CFR50.73(a)(1) a telephone notification is being made instead of submitting a written Licensee Event Report. The licensee has notified the NRC resident inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-09-19
49357 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-09-19 04:50 | 2013-09-19 09:58 | 2013-09-25 | TECHNICAL SUPPORT CENTER EMERGENCY DIESEL GENERATOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will remove the emergency power supply to the TSC from service. The TSC would be rendered non-functional with the loss of emergency power. The repair to the power supply is expected to last 2 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be expedited to restore the emergency power supply to service. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC emergency power supply has been restored to normal operation. "NRC Resident Inspector has been notified." * * * UPDATE FROM TIM ERGER TO HOWIE CROUCH AT 1325 EDT ON 9/22/13 * * * The TSC EDG remains unavailable due to emergent work. The licensee has notified the NRC Resident Inspector. Notified R3DO (Riemer). * * * UPDATE FROM MIKE STROPE TO DANIEL MILLS AT 1237 EDT ON 9/25/13 * * * The TSC EDG has returned to functional status. The licensee notified the NRC Resident Inspector. Notified R3DO (Dickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-19
49356 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-18 22:29 | 2013-09-19 03:10 | 2013-09-20 | BOTH SECONDARY CONTAINMENT ACCESS DOORS BRIEFLY OPENED SIMULTANEOUSLY "While performing the secondary containment airlock door interlock surveillance, the interlock to the main plenum room did not prevent the opening of both doors to the plenum room airlock (DOOR-85 and DOOR-86). The plenum room airlock doors were immediately closed. The time both doors were opened is estimated to be approximately one (1) second. "When both doors open, Technical Specification surveillance requirement SR 3.6.4.1.3 was not met and secondary containment was declared inoperable. Secondary containment was declared operable after independently verifying at least one secondary containment access door was closed. "There were no radiological releases associated with this event. The NRC Resident Inspector has been notified." * * * UPDATE FROM KIM HOFFMAN TO HOWIE CROUCH AT 1753 EDT ON 9/20/13 * * * "This update provides additional information on the initial notification of the event. On 9/18/13, while testing secondary containment airlock doors, the interlocks did not prevent opening of both doors simultaneously. With the outer door to the main plenum room open, the inner door was able to be opened. At this point, Technical Specification SR 3.6.4.1.3 was not met and secondary containment was inoperable. The inner door was closed immediately. While in this condition, the inner door was then opened, and the interlock did not prevent the opening of the outer door. The outer door was closed immediately. "Secondary containment was declared operable after verifying at least one of the airlock doors was closed. "There were no radiological releases associated with this event. The NRC Resident Inspector has been notified. " Notified R3DO (Reimer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-09-19
49355 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-09-18 12:59 | 2013-09-18 18:48 | 2013-10-31 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE DUE TO STEAM LEAK "On 9/18/13, during performance of the High Pressure Coolant Injection (HPCI) pump operability surveillance, a minor steam leak was discovered on the governor valve inspection cover flange. Due to the leak, HPCI was declared inoperable. "Actions taken: A 14-day LCO per TS 3.5.E.2 has been entered and corrective actions are in progress." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM BENJAMIN EGNEW TO HOWIE CROUCH AT 1341 EDT ON 10/31/13 * * * "After further evaluation, the gasket leak at the flange was determined to have no impact on the operability of the HPCI system, and therefore the HPCI system was able to perform all safety functions with the identified condition. The immediate determination, made on September 18, 2013, that the HPCI system was inoperable was revised based on the results of an analysis of the HPCI room heat up rate. The heat up rate was modeled using a calculated steam leak rate based on actual measurements of the damaged gasket after removal from the HPCI turbine flange. The time to heat up was based on the first set point at which isolation due to a temperature increase would occur. It was determined that the existing gap in the gasket represented approximately one-tenth of the approximate size of a steam leak that would be expected to result in an isolation, therefore the existing flange leak had no impact on operability of the HPCI system or its ability to mitigate the consequences of an accident. "The licensee has notified the NRC site Resident Inspector." Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-09-18
49354 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-09-18 | 2013-09-18 16:28 | 2013-09-18 | AGREEMENT STATE REPORT - UNDERDOSE TO PATIENT'S LIVER The Commonwealth of Massachusetts submitted the following information via email: "A dose that likely differs from the prescribed dose by more than 50 rem to an organ, the liver, and the total dose delivered differs from the prescribed dose by 20% or more. "The licensee's radiation safety officer reported to the Agency [Massachusetts Radiation Control Program] on 9/18/2013 that on same date licensee administered yttrium-90 SIR-Spheres to patient's left lobe of liver for treatment of metastatic disease; that 16.8 millicuries of yttrium-90 was prescribed; and that 12.06 millicuries was administered resulting in an under dose of 28.1 percent. "The licensee discovered the event upon measurement of waste material including dose vial as part of normal quality assurance. "The licensee's radiation safety officer reported that the authorized user and the referring physician have been notified and it is unknown at time of the report whether the referring physician has elected to notify the patient. "The licensee's radiation safety officer reported that medical staff does not believe that this error will adversely affect the patient treatment outcome. "The licensee will submit a written report within 15 days in accordance with the [Massachusetts] requirements of 105 CMR 120.594(A)(4) to include why event occurred and actions to prevent recurrence. "Root cause and corrective action are not known at this time and the Agency continues to investigate. "System Name: Brachytherapy Product; Manufacturer: Sirtex Wilmington LLC" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-09-26
49353 | -1 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-09-18 05:10 | 2013-09-18 11:15 | 2013-09-27 | BOROSCOPIC INSPECTION OF REACTOR VESSEL HEAD DETERMINED EVIDENCE OF BOUNDARY LEAKAGE "Boroscopic inspection of the reactor head assembly during refuel outage A1R17 has determined that white powder residue observed at reactor head penetrations 41, 49, 61, 65, and 73 is evidence of past Reactor Coolant System pressure boundary leakage at one or more of these locations. This determination was made today at 0510 [CDT] after completion of boroscopic inspections and consultation with the reactor head vendor. These reactor head penetrations are control rod drive mechanism (CRDM) penetrations. The location of the identified leakage is suspected to be the omega seal welded threaded connection on one or more of these CRDM penetrations. Further inspections must be performed to confirm the exact leakage location. This condition will be repaired before U-1 returns to mode 4." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 9/27/13 AT 1529 EDT FROM MATTHEW HENSON TO DONG PARK * * * "The purpose of this report is to retract ENS report #49353 (September 18, 2013). This report was made after boroscopic inspection of the Unit 1 reactor head assembly during refueling outage A1R17 determined that white powder residue observed at five Reactor Pressure Vessel (RPV) head penetrations was evidence of past Reactor Coolant System (RCS) pressure boundary leakage at one or more of these locations. "At 1400 CDT on Wednesday, September 25, 2013, the Braidwood Nuclear Power Station (BNPS) concluded that the prior ENS notification could be retracted because the Plant Operations Review Committee had concluded that the white powder residue observed at five Unit 1 RPV head penetrations was not evidence of past RCS pressure boundary leakage. A detailed examination plan was implemented, which included a disassembly of the Digital Rod Position Indication (DRPI) and Control Rod Drive Mechanism (CRDM) coils for all five penetrations and a detailed visual examination using remote video equipments. The visual examinations used remote video equipments to inspect the lower and intermediate canopy seal weld areas for the five CRDMs. In addition, an examination of the upper canopy seal weld areas and a bare-metal inspection of the Reactor Pressure Vessel Head did not identify any evidence of boric acid leakage. Based on these inspections and a review of available photos from previous outages, BNPS concluded that the white residues were from incomplete cleaning in prior outages. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Dickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-09-18
49352 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-09-14 01:30 | 2013-09-17 11:42 | 2013-09-17 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE WITH POTENTIAL EXPOSURE FROM AN UNSHIELDED SOURCE ROD An operator did not maintain direct control of a Troxler Model 3440 Gauge and it was run over by a roller at a work site in Portland, Oregon. This resulted in severe damage to the gauge and the source rod being separated from the device. The licensee's CRSO (Corporate Radiation Safety Officer) responded to the work site to check for elevated radiation levels and determined that the sources were still intact. Personnel shielded the rod and transported the gauge and the rod back to the licensee's facility. The damaged gauge has been placed in a locked storage room at the licensee's corporate office with warnings attached to the door to prevent entry. The dose received by the CRSO was 4.36 mrem. The licensee will provide refresher training and review and revise procedures as necessary. The licensee will ship the gauge back to Troxler Laboratories in the near future. The gauge is a Troxler Model 3440, Serial # 37190, with 9.0 mCi Cs-137 and 44.0 mCi Am-241/Be sources. State Event Report # OR 13-0037. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-09-25
49351 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-09-16 14:55 | 2013-09-16 21:11 | 2013-09-16 | DEGRADED CONDITION CAUSED BY RHR RELIEF VALVE LEAKAGE "At 1455 EDT, [on 91/16/13], [Susquehanna] Engineering determined the leakage from the 2B RHR Pump Suction Relief valve caused the Engineered Safety Feature (ESF) Leakage to exceed the 2.5 gpm which was provided to the NRC during the implementation of the Alternate Source Term (AST) submittal. The calculated leakage rate was 7.5 gpm. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii). "Unit 2 is currently in Mode 4 (cold shutdown) for a maintenance outage." This leaking RHR pump suction relief valve, previously identified in EN #49344, is being evaluated and repaired. The licensee has notified the NRC Resident Inspector and the state. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-09-16
49350 | 0 | KALISPELL REGIONAL MEDICAL CENTER |  |  |  |  | 2013-09-11 14:00 | 2013-09-16 16:50 | 2013-09-16 | LOST BRACHYTHERAPY MEDICAL SOURCE The licensee reported that a brachytherapy source/seed was lost after completion of a medical procedure. After the seed was removed from the patient, the device was improperly placed in the rack for sterilization and cleaning and it is believed the seed was lost as part of this cleaning process. Normally, the device would have been placed in a surgical bowl and moved to a flash chamber for seed recovery. The seed was a Best Double Walled I-125 seed with a 204 microcurie source, model #2301. There was no harm to the patient or exposures to other personnel. The licensee is continuing their investigation and will provide additional information when it becomes available. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-09-24
49349 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-09-16 15:00 | 2013-09-16 16:57 | 2013-09-16 | VENT STACK MONITOR MAINTENANCE "System(s) Affected: RM-8169 Vent Stack Radiation Monitor "Actuations & Their Initiation Signals: None "Causes (If known): Pre-Planned Maintenance "Effect of Event on Plant: Loss of assessment capability "Actions Taken or Planned: Compensatory samples - restore RM-8169 to service ASAP. "Additional Information: None" The licensee notified the NRC Resident Inspector, the State of Connecticut and local Waterford Dispatch. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-16
49348 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-13 | 2013-09-16 13:58 | 2013-09-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILS TO RETRACT "On September 16, 2013, the licensee notified the Agency [Texas Department of Health] that on September 13, 2013, one of its radiography crews had been unable to retract a Iridium-192 source back into a SPEC 150 exposure device at a temporary work site in Tilden, Texas. Following the first exposure of the morning, the source pigtail would not retract fully into the device. An authorized person performed the source retrieval. This individual received 20 millirem and the individual that assisted him received 10 millirem. No member of the public received any exposure as a result of this event. "The licensee's radiation safety officer inspected the inside of the source guide tube using a tube scope and found that the coil in the source guide tube was pushed out into the inside of the tube where the connector fitting was crimped onto the guide tube. The connector had just been replaced by a local service company. An investigation into this event is ongoing. Information will be provided as it is obtained in accordance with SA-300." Texas State Report # I-9114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-09-24
49347 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-12 | 2013-09-16 13:58 | 2013-09-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILS TO RETRACT "On September 16, 2013, the Agency [Texas Department of Health] received notification from the licensee that on September 12, 2013, one of its radiography crews working at a temporary work site in Tilden, Texas, had been unable to retract an Iridium-192 source back into its SPEC 150 exposure device. After several attempts, the connector on the end of the cable came off which allowed the cable to come all the way through the device and left the source inside the guide tube. "Source retrieval was performed by authorized person who received 120 millirem, an assistant who received 55 millirem, the radiographer trainer who also assisted received 100 millirem (including the day's work) and the radiographer trainee who received 32 millirem (including the day's work). "The licensee will have the crank assembly, cable, and connector evaluated. No member of the public received any radiation exposure as a result of this event. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas State Report # I-9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-09-24
49346 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-16 | 2013-09-16 13:49 | 2013-09-16 | AGREEMENT STATE REPORT - RONAN FIXED GAUGE WITH STUCK SHUTTER The State of Texas submitted the following information via email: "On September 16, 2013, the Agency [Texas Department of State Health Services] received notice that one of the licensee's fixed gauges had a stuck shutter. This [stuck shutter] had been discovered during the morning shutter check that morning. The licensee is in contact with the manufacturer for repair. The gauge is a Ronan SA-1 and contains a Cesium-137 20 mCi source, with serial # M3824. The licensee is compiling a written report and is acquiring authorization to operate while awaiting repairs. Additional information will be provided as it is received in accordance with SA-300." Texas State Report # I 9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-09-24
49345 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-09-16 07:00 | 2013-09-16 11:53 | 2013-09-16 | OFF-SITE NOTIFICATION TO SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL (SCDHEC) "At approximately 0700 [EDT] on 9/16/13, site personnel discovered a sewer lift station, in the owner controlled area, overflowing. The overflow entered a nearby storm drain that discharges into Outfall 13. The estimated release volume is between 500-1000 gallons. The release has been stopped. At 1045 an initial notification was made to SCDHEC. A pump failure is suspected to be the cause of the back-up and subsequent overflow. Repair and clean-up is in process. "The NRC Residents have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-09-16
49344 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-09-15 11:23 | 2013-09-15 11:52 | 2013-09-15 | UNUSUAL EVENT DECLARED AT SUSQUEHANNA UNIT 2 DUE TO FLOODING IN A RHR PUMP ROOM "At 1123 EDT, [on 9/15/13], Susquehanna Unit 2 received a Division 2 RHR [Residual Heat Removal] room Flooded alarm. Plant operators reported 3 inches of water in the room with water coming from the 2B RHR pump suction relief valve. The Suppression Pool Isolation valve was closed to isolate the leaking relief valve from the Suppression Pool. This action stopped Suppression Pool level from lowering. The Leak is isolated at this time. Further water is being added to the room as the system piping is being drained. The cause of the relief valve lifting is unknown at this time and is under investigation. At the time of the event, Division 2 RHR system had been declared inoperable for unrelated equipment issues." At 1222 EDT, the licensee confirmed that leakage from the 2B RHR pump suction relief valve had stopped. Susquehanna Unit 2 remains stable and there was no impact on Susquehanna Unit 1. The licensee notified the NRC Resident Inspector, State, and Local authorities. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only). * * * UPDATE FROM MARTIN LICHTNER TO JOHN SHOEMAKER AT 1641 EDT ON 9/15/13 * * * "U2 SSES [Susquehanna Steam Electric Station] has exited the Unusual Event for Division 2 RHR room flooded as of 1552 EDT. The leak has been isolated, water removed from the room and Division 1 RHR is operating in shutdown cooling proceeding to Mode 4 (Cold Shutdown)." "A press release for this event was authorized at 1613 and issued at 1628 [on 9/15/13]." The licensee has notified the NRC Resident Inspector. Notified R1DO (Cahill), NRR (Dorman), IRD (Gott), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2013-09-15
49343 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-09-14 02:00 | 2013-09-14 05:47 | 2013-09-14 | LIQUID PENETRATION EXAMINATION RESULTS IN INDICATION ON REACTOR VESSEL HEAD PENETRATION "On September 14, 2013, during the A1R17 Braidwood Station Unit 1 refueling outage, an inservice Liquid Penetration examination was performed on the previously repaired Penetration 69. This repair was performed during A1R16. The PT [Penetrant Testing] examination revealed 22 recordable indication and 5 non-relevant indications. Rounded indications that exceed 3/16" are rejectable. All 22 indications are rounded and 13 of these indications exceed the 3/16" criteria. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as found indication did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-09-14
49342 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-09-14 03:30 | 2013-09-14 05:15 | 2013-09-14 | MANUAL REACTOR SCRAM DUE TO FEEDWATER TRANSIENT DURING SHUTDOWN "At approximately 0330 hours on September 14, 2013, Susquehanna Steam Electric Station Unit 2 reactor was manually scrammed while transitioning the 'A' reactor feed pump from flow control mode to discharge pressure mode. Reactor water level rose to +54 inches causing a trip of reactor feedpumps. Subsequently the mode switch was taken to shutdown to manually scram the Unit 2 reactor. "All control rods inserted. Reactor water level lowered to approximately +18 inches. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. No containment isolations occurred. All safety systems operated as expected. RCIC system was manually initiated for level control until a reactor feedpump was recovered, then RCIC was manually shutdown. The cause of the feedwater flow transient and trip of the reactor feedwater pumps is under investigation. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a 4 hour report, and 10CFR50.72(b)(3)(iv)(A) for an 8 hour report. Decay heat is being removed via the turbine bypass valve to the condenser. Offsite power remains stable, and there was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. The Pennsylvania Emergency Management Agency will be notified, and the licensee will be making a press release. | 0 | 0 | 0 | 0 | 14 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-09-14
49341 | -1 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2013-09-13 10:45 | 2013-09-13 10:55 | 2013-09-27 | ITEM RELIED ON FOR SAFETY MAY NOT BE RELIABLE "At about 1045 EDT on 9/13/13, it was discovered that the feed tube level sensor on a press operation is not fail safe upon loss of signal. The sensor is a sole IROFS [Item Relied On For Safety] for a particular sequence. Criticality controls remained in place. Affected equipment has been shut down. No unsafe condition exists. Feed tube level sensor is in place for the sequence to limit mass. At no time was the mass limit exceeded. We are reporting under Part 70, Appendix A, (a)(4) which states that credited IROFS must remain available and reliable. We cannot evaluate reliability in the time required for a 1 hour report. In addition, the affected equipment has been secured. An investigation is underway to determine corrective actions and extent of condition." The license will notify NRC Region 2. * * * RETRACTION FROM SCOTT MURRAY TO DANIEL MILLS ON 9/27/2013 AT 1003 EDT * * * "On 9/13/13, GNF-A conservatively made a 1 hour event notification (EN 49341) due to a discovery that a feed tube level sensor is not fail safe upon loss of signal. After further review, it has been determined that the control remained available, reliable and continued to meet performance requirements. As a result, the event notification is retracted." The licensee has notified NRC Region 2. Notified R2DO (Sykes), NMSS EO (Rubenstone), and IRD (Grant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2013-09-13
49340 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-08-13 | 2013-09-12 20:17 | 2013-09-12 | AGREEMENT STATE - SCRAP METAL SHIPMENT CONTAINING RADIOACTIVE MATERIAL The following information was received via facsimile: "On August 13, 2013, the Colorado State Department Public Health and Environment received a phone call from Western Metals Recycling indicating a need for a special permit to return a shipment of scrap metal flagged as containing radioactive materials by portal monitor alarms. The shipment originated at Baker Hughes of Brighton, Colorado (CO RML#678-01). The DOT Special Permit (#CO-CO-13-01) was issued on August 13, 2013, with a reading of 0.04 mrem/hr on the outside of the shipment. "On August 15, 2013, the rolloff was returned to Baker Hughes, where they determined a number of valves and seats from a fluid end of a well fracking site contained the contamination. The Baker Hughes staff tracked the parts back to a site worked in conjunction with ProTechnics (CO RML#545-01) with radioactive tracer material. ProTechnics was contacted and offered to take possession of the material. Baker Hughes reported valves with readings ranging from 0.02 mrem/hr to 1 mrem/hr on contact. "On August 19, 2013, the Colorado State Department Public Health and Environment's Health Physicists visited the Brighton location of Baker Hughes, where the material was being held, to meet with staff from both Baker Hughes and ProTechnics. The material was identified as Ir-192, using an Identifinder 2 detector, with a dose rate of 0.2 mrem/hr on contact with one of the valves. It was decided ProTechnics would take possession of all parts contaminated with radioactive material in order to decontaminate and store the waste for decay. An amendment or provisional license was necessary for either Western Metals Recycling or Baker Hughes. "On August 26, 2013, the Colorado State Department Public Health and Environment received the survey reports from the Thompsen well site for the dates of concern. The survey reports showed no contamination was detected "On August 30, 2013, the Colorado State Department Public Health and Environment received a full report from Protechnics indicating approximately 0.026 mCi of Ir-192 was recovered from the contaminated equipment and will be held for decay at their Fruita facilities. "A Notice of Violation will be issued in response to this event." Colorado State Incident Report I13-09. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-09-20
49339 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-09-11 17:31 | 2013-09-11 20:37 | 2013-09-12 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF COOLING TO SWITCHGEAR ROOMS "Wolf Creek has commenced a plant shutdown in accordance with Technical Specifications. The A Train Class 1E Electrical Equipment Air Conditioning unit was declared non-functional due to a possible failed compressor cylinder, as indicated by increased vibration. This failure could prevent the unit from performing its required function over its required mission time, as required by Technical Specifications 3.8.4, 3.8.7, and 3.8.9. The following safety related electrical equipment was declared inoperable: 4.16KV Bus NB01; 480 Volt AC buses NG01 and NG03; 120 Volt Instrument AC inverters and buses NN11, NN13, NN01 and NN03; 125 VDC chargers and buses NK11, NK13, NN01 and NN03. "Technical Specification 3.0.3 was entered at 1645 CDT on 9/11/2013 from Technical Specification 3.8.7 due to two out of four 120 VAC inverters (NN11 and NN13) being inoperable. Plant shutdown to Mode 5 commenced at 1731 CDT. The unit is currently at approximately 50% power. "All electrical systems listed above remain available but are declared inoperable due to inadequate room cooling capability. "No major equipment is out of service. "The NRC Resident Inspector has been notified." No switchgear room temperature limits were challenged. See EN #49008 (May 6, 2013) and EN #49126 (June 17, 2013) for similar events. * * * UPDATE ON 9/12/13 AT 0215 EDT FROM MARCY BLOW TO HUFFMAN * * * "At 00:36 CDT 9/12/13, Wolf Creek had an Auxiliary Feedwater Actuation during a plant shutdown in accordance with Technical Specifications. The plant was in Mode 3, all control rods inserted, with reactor trip breakers closed when low steam generator levels prompted a manual reactor trip. A Valid Auxiliary Feed Actuation signal was received due to low steam generator levels. All Auxiliary Feedwater pumps started and operated as expected." The licensee has informed the NRC Resident Inspector. R4DO (Hay) notified. | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-09-11
49338 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-09-11 | 2013-09-11 17:24 | 2013-09-12 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following information was received via facsimile: "A Troxler model 3411 gauge was stolen from the licensee's truck while at a temporary jobsite. The authorized user placed the gauge in the back of the truck and stepped away to perform other work. When he returned, he found the gauge was gone. He contacted his RSO. The Dinwiddie Sheriff's office was notified and a report filed. The licensee searched the near area but did not find the gauge. "A press release is being issued by VDH [Virginia Department of Health] utilizing the Richmond and Petersburg area media outlets." Virginia Report Number: VA-13-08 * * * UPDATE FROM MIKE WELLING TO JOHN SHOEMAKER AT 1605 EDT ON 9/12/13 * * * "On September 12, 2013, a member of the public returned the gauge to a local business who then contacted the local authorities. The [Virginia] RMP (Radiation Materials Program) was notified and a staff member was dispatched to ascertain the gauge condition. A survey was performed and all readings were found to be within expected dose rates. A wipe test of the gauge was performed and no contamination was found. The licensee was notified and arrived on scene. The gauge was returned to the licensee and an observation was made of the gauge being blocked and braced and secured with cables in the vehicle. An investigation is being performed by RMP." Notified R1DO (Cahill), FSME Events Resource (via email), and ILTAB (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-09-19
49337 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2013-08-02 | 2013-09-10 13:36 | 2013-09-10 | PART 21 REPORT - IMPROPER DEDICATION OF ACTUATOR PARTS Fisher issued an information notice (FIN 2013-03) to alert Palo Verde Nuclear Generating Station of an issue associated with two valve assemblies supplied to PVNGS by Fisher. Fisher determined that the valves were provided with actuator parts that were not properly processed per active valve requirements specified in the purchase order. Specifically, Fisher provided commercial grade parts instead of commercial grade dedicated items. Arrangements have been made with PVNGS to retrofit the correctly processed parts on the subject valves. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-09-10
49336 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-09-10 08:52 | 2013-09-10 15:57 | 2013-09-10 | FITNESS FOR DUTY - CONFIRMED POSITIVE FFD TEST A non-licensed, contract, supervisory employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2013-09-10
49335 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-09 14:00 | 2013-09-09 22:39 | 2013-10-04 | HIGH ENERGY LINE BREAK BARRIER IMPROPERLY OBSTRUCTED "At 1400 [CDT] on September 9, 2013, plant personnel found HELB barrier HATCH-1/TB blocked. The hatch is diamond plate steel located on the turbine floor. Pallets, a fan and a gantry were positioned on top of the hatch possibly preventing pressure relief during a HELB event. This issue is being reported as an unanalyzed condition per 10CFR50.72(b)(3)(ii)(B). All items were removed from the hatch by 1800 on September 9, 2013." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM JEREMY TANNER TO JOHN SHOEMAKER AT 1118 EDT ON 10/04/13 * * * "The licensee reviewed the design basis calculations and analyses for HELB events in the area where Hatch-1/TB is located. The review determined that it is acceptable to block or hold Hatch-1/TB down and that the painted markings on the hatch are overly restrictive. "In looking at HELB calculation of record, feed water break at the feed water pumps, there is no flow path modeled between the HELB volumes. Therefore, if Hatch-1/TB is blocked, the physical flow path is in accordance with the Gothic model of the HELB volume. Further, the analyses also indicated that no credit is taken for the hatch to relieve as no HELBs are postulated in the room under the hatch. Finally, Hatch 1/TB structural integrity was verified assuming a HELB occurred with the hatch blocked as described in notification 49335 (pallets, fan and gantry) the barrier would function as designed. "Licensee initiated a Work Request to remove any markings on Hatch-l/TB that indicate do not block or hold down." The licensee will notify the NRC Resident Inspector. The Region 3 Duty Officer (Valos) was notified. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-09
49334 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-09-09 13:00 | 2013-09-09 16:05 | 2013-09-19 | PLANNED PARTIAL LOSS OF COMMUNICATIONS CAPABILITY IN TECHNICAL SUPPORT CENTER "This is a non-emergency eight hour notification for a planned loss of communications capability at the DCPP Technical Support Center (TSC). This event is reportable in accordance with 10CFR50.72(b)(3)(xiii) because planned maintenance affects the functionality of some TSC communications systems. "Planned maintenance activities on the TSC communications systems begins 09/09/13. The work includes removing phones and normal business use computers from service to support a minor remodel which includes the installation of new furniture and painting in the TSC command room. The communications equipment scope of work is confined to the TSC command room only and there is no expected loss of capability in the engineering, administrative or radiological rooms within the TSC. There is no expected loss of plant display systems (SPDS, ERDS, or ERFDS) in the TSC during this planned maintenance. The work is scheduled to complete by 09/26/2013. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. A select group of TSC ERO personnel have been pre-designated to respond to their backup TSC location in accordance with applicable site procedures. If a complete relocation of the TSC becomes necessary, the Site Emergency Coordinator will relocate the remaining TSC staff to a backup location in accordance with applicable site procedures. The Emergency Response Organization teams have been notified of the planned maintenance and the possible need to relocate during an emergency. "The NRC Resident Inspector has been notified. This planned maintenance poses no threat to the public or station employees." * * * UPDATE FROM ADAM PECK TO HOWIE CROUCH AT 1704 EDT ON 9/19/13 * * * "The planned maintenance on the TSC communications systems is complete. DCPP restored the emergency response communications capability at 1400 PDT on September 19, 2013." The licensee has notified the NRC Resident Inspector. Notified R4DO (Deese). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-09
49333 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2013-09-07 | 2013-09-09 14:08 | 2013-09-09 | AGREEMENT STATE REPORT - RADIOPHARMACEUTICAL PACKAGE HAD EXTERNAL CONTAMINATION The following information was obtained from the State of Illinois via email: "Saturday morning a call was received by the Illinois Emergency Management Agency [IEMA] from the RSO at Loyola University Medical Center reporting exterior contamination on one of two packages received from their radiopharmacy, Cardinal Health, that same morning. Staff at Loyola confirmed the presence of contamination with a second wipe which measured less than 15,000 dpm. The contaminant was verified as Tc-99m by Loyola staff. The package involved contained 6 doses of Tc-99m to be used for imaging that morning. Smears taken of the interior of the package and on each shielded syringe showed no removable contamination present. Smears on the exterior of the black nylon shipping package showed contamination only on the bottom of the package and on no other surfaces. The maximum measured dose rate from the empty package near the surface of the contaminated package was less than 500 microRem/h. The second package which had arrived at the same time as the first showed no contamination or unexpected radiation levels. "The pharmacist at Cardinal Health was subsequently contacted by the Agency [IEMA] that same morning. The responsible pharmacist confirmed he'd been notified by the RSO of Loyola University Medical Center immediately at the time of discovery of the event. The pharmacy's courier vehicle made one other delivery to an area hospital before reaching Loyola and then proceeded to a third hospital. Both other facilities were contacted by Cardinal and told to be on the lookout for potential exterior contamination should cross contamination be involved. The pharmacist indicated that neither facility reported any noted contamination. The pharmacist noted that the couriers for all packages from their facility in Glendale Heights are Cardinal employees using Cardinal vehicles. Once the vehicle returned to Glendale Heights, surveys of the vehicle were completed and no removable contamination or elevated levels were detected. During the interim, a survey of the radiopharmacy was also conducted with no contamination found in the package preparation areas. "Based on this information and past inspection results of both facilities, it appears this event is an isolated instance where incomplete/inadequate surveys were conducted to evaluate the potential hazard present and assure that packages offered for transport are free of contamination in excess of the limits." Illinois Item Number: IL13026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2013-09-17
49332 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-09-09 04:07 | 2013-09-09 07:11 | 2013-09-15 | MAINTENANCE ON TECHNICAL SUPPORT CENTER / OPERATIONS SUPPORT CENTER VENTILATION "Scheduled maintenance of the Technical Support Center (TSC) / Operations Support Center (OSC) HVAC system for maintenance on the Air Handler (AMA-AH-S1) recirculation fan, outside air duct heater, and thermostat will start at approximately 0400 hours PDT on 09/09/13 and will last approximately 40 hours (estimated time from equipment tag out back to OPERABLE). During this time the TSC and OSC will not be available for use to support emergency response activities. Established compensatory measures direct Emergency Response Organization (ERO) members normally responding to either of these facilities to respond to alternate locations. No other emergency response facilities are impacted by the scheduled TSC / OSC Facilities HVAC maintenance work. "This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The resident inspector has been notified. A follow up notification will be made when HVAC maintenance to the TSC / OSC Facilities has been completed and operability of these EP Facilities has been restored." * * * UPDATE FROM VERLE KESZLER TO PETE SNYDER AT 0823 EDT ON 9/15/13 * * * "Scheduled maintenance of the Technical Support Center (TSC) / Operations Support Center (OSC) HVAC system is completed. The HVAC system has been returned to service and declared functional at 05:05 PDT on 9/15/13. "The licensee has notified the NRC Resident Inspector." Notified R4DO (Hay). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-09
49331 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-06 | 2013-09-06 14:29 | 2013-09-06 | AGREEMENT STATE REPORT - DOSE DELIVERED TO WRONG SITE The following information was received from the State of Minnesota via email: "The planned/prescribed dose that was to be delivered to a patient's tumor volume was 400cGy (4Gy) on this fraction. Due to medical event, [approximately] 0cGy (0Gy) was delivered to the tumor volume during HDR treatment fraction #2 of 6. The prescribed fraction dose of 400cGy (4Gy) was unintentionally delivered 5.4cm superiorly to the tumor volume in the patient's small bowel/external bladder wall region. "The HDR remote afterloader at Abbott-Northwestern being used/in use during this patient's treatment is a Nucletron/Elekta V2 mHDR, serial number 31823; mHDR Ir-192 source #D36E-6829. The Ir-192 source activity at time of above medical event was 6.407 Ci. "Abbott-Northwestern Radiation Oncology is actively investigating the cause of the above medical event, corrective action(s) to implement to prevent such an event from happening in the future, and any medical follow-up/expected implications to the patient from the above medical event. These items will be detailed in Abbott-Northwestern's full written report to be submitted within 15 days of discovery. "MDH [Minnesota Department of Health] will submit more information as it becomes available." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2013-09-16
49330 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-07-19 | 2013-09-06 14:51 | 2013-09-06 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE OF A RADIOGRAPHER "Dosimetry badge result were reported to the licensee around July 19, 2013 with an individual's badge having received a total annual occupational dose exposure exceeding 7,437 mrem. 2013 badge history results showed exposures for the following months: January - 538 mrem, February - 410 mrem, March - 287 mrem, April 367 mrem, May 2,412 - mrem, and June - 3,423 mrem." LA Event Report ID No. LA130003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-09-16
49329 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-01-28 | 2013-09-06 15:11 | 2013-09-06 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE OF A RADIOGRAPHER "Individual badge received 3.491 REM through September 2012. His exposure for October wear period was 0.565 REM, which gave him a total of 4.056 REM through October 2012. On 01/02/2013, November badge results came back 1.040 REM. On 01/10/2013, the December badge results came back with 0.043 REM. Making the annual exposure for the individual 5.139 REM for 2012." LA Event Report ID No. LA130002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-09-16
49328 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-09-06 06:07 | 2013-09-06 14:47 | 2013-09-06 | RADIATION MONITORING SAMPLE RACK DECLARED NON-FUNCTIONAL "At 0607 hours PDT on September 6, 2013, the Radwaste Building process radiation monitoring sample rack was declared non-functional due to a loss of power to the sample rack. The cause of the loss of power is under investigation. "At 0945 hours PDT, auxiliary sampling equipment was installed to collect samples from the associated effluent release pathway. "To compensate for the loss of assessment capability while the Radwaste Building process radiation monitoring sample rack is non-functional, field team survey results will be used if required. "This event is being reported as a loss of emergency assessment capability in accordance with 10CFR50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM QUOC VO TO VINCE KLCO ON 9/6/13 AT 2251 EDT * * * "Repairs have been completed and the Radwaste Building process radiation monitoring sample rack has been returned to service and declared functional at 1631 hours PDT. "The licensee has notified the NRC Resident Inspector." Notified the R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-06
49327 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-09-05 22:44 | 2013-09-06 05:10 | 2013-09-06 | TURBINE BUILDING STACK RADIATION MONITOR OUT OF SERVICE "At 2244 PDT on September 5, 2013, the Turbine Building Stack Radiation Monitor - Low Range detector, and the Turbine Building Stack Radiation Monitor - Intermediate Range detector were declared non-functional due to a failure of the sample rack supply fan. "At 0156 hours PDT on September 6, 2013, a temporary sample cart was installed to return the Turbine Building Stack Radiation Monitor - Low Range detector, and the Turbine Building Stack Radiation Monitor - Intermediate Range detector to service. "To compensate for the loss of assessment capability while the Turbine Building Stack Radiation Monitoring equipment was nonfunctional, a field team survey would have been used if required. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-06
49326 | 0 | WATERFORD | 3 |  |  | [3] CE | 2013-09-05 16:00 | 2013-09-06 00:27 | 2013-09-06 | LOSS OF AUXILIARY COMPONENT COOLING WATER SYSTEMS "This is a non-emergency notification from Waterford 3. Conditions were discovered which appear to require immediate NRC notification per 10CFR50.72(b)(3)(ii)(B) due to both trains of Auxiliary Component Cooling Water [CCW] being inoperable several times since 7/27/2012. A deficiency was identified with Auxiliary Component Cooling Water valve ACCW-126A, which is a part of the ultimate heat sink system, associated with the inability to adequately close this valve manually, locally, in order to preserve Wet Cooling Tower A inventory during an accident. System operability requirements came into question and resulted in Operations declaring the system inoperable on 9/4/2013 at 1509 CDT, and entering Technical Specification (TS) LCO 3.7.3 and associated cascading TS. As part of the review for NRC reporting requirements associated with the inoperable CCW Train A, historical information was discovered that indicated the redundant train of CCW, Train B, was declared inoperable several times, while ACCW-126A was presumably in the degraded or inoperable condition, since ACCW-126A had last been rebuilt on 7/27/2012. This condition requires immediate reporting to NRC under 10CFR50.72(b)(3)(ii)(B), an unanalyzed condition that significantly degrades plant safety. The condition was corrected and the system declared operable on 9/5/2013 at 1231 CDT, exiting the CCW TS LCO and associated cascading TS. "Prior to the condition with ACCW-126A being corrected, a snubber pin (FWSR-60) was found missing on 9/5/2013 at 1228 CDT that could have adversely affected the ability to feed Steam Generator #2 with Emergency Feedwater. Less than 4 hours later, the pin was replaced, which restored the path to operable at 1609 CDT on 9/5/2013. "The plant remained stable at 100% during this time. Plant risk index was 10.0 green." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-06
49325 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2013-07-22 10:00 | 2013-09-05 18:50 | 2013-09-05 | AGREEMENT STATE REPORT - BRACHYTHERAPY SEED LOST On July 22, 2013, it was discovered that one I-125 0.5 mCi prostate implant seed from a procedure that took place on July 10, 2013, was unaccounted for. Cartridges are assumed to be preloaded with 100 seeds with delivery documentation attesting to the count. Fluoroscopic x-rays confirmed that seventy two (72) I-125 seeds were implanted in a patient following brachytherapy prostate seed implantation using a Nucletron seed Selectron implantation system on July 10, 2013. During the initial seed calibration process one (1) seed was disposed into a sterile pig. The implant went smoothly except at one point where due to patient movement three (3) seeds were ejected into a sterile pig. On July 22, 2013, the medical physicist unloading the seeds from the cartridge found 23 seeds which was 1 less than expected. Surrounding hallways, rooms, and the implant robotic equipment along with the equipment storage area and sterilization areas were surveyed but no additional seeds were discovered. No foul play is suspected and no unusual levels of radiation have been detected from the operating room or radiation oncology staff. As a corrective action the licensee will x-ray incoming seed cartridges to take a physical count of the seeds prior to the procedure. Immediately following the implant procedures seed cartridges will be removed from the delivery system and a second x-ray image will be acquired to perform another physical inventory. Images will be retained for record keeping. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-09-13
49324 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-09-05 08:31 | 2013-09-05 17:31 | 2013-10-31 | POTENTIAL LOW PRESSURE SAFETY INJECTION PUMP RUN OUT CONDITION "Current design basis calculations indicate the Low Pressure Safety Injection (LPSI) pumps could potentially operate in a run-out condition under certain worst case design basis conditions. The LPSI pumps could operate in a run-out condition beyond the analyzed time by 20 minutes. Current design basis calculation assumes LPSI Pump would be shutdown by [the] RAS [Recirculation Actuation Signal] in less than one hour, however due to past changes to Containment Spray Pump Start Logic, the time was lengthened to 80 minutes which is beyond the one hour analyzed. This represents a reportable unanalyzed condition." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM LUKE JENSEN TO HOWIE CROUCH AT 1722 EDT ON 10/31/13 * * * "Fort Calhoun completed additional analysis which verified that the LPSI pumps will not go into run-out as previously reported. Therefore Fort Calhoun is withdrawing the event notification." The licensee will notify the NRC Resident Inspector. Notified R4DO (Drake). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-05
49323 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-09-05 13:14 | 2013-09-05 14:51 | 2013-09-05 | FAILURE TO ALIGN CONTROL ELEMENT ASSEMBLY DURING TESTING "CCNPP [Calvert Cliffs Nuclear Power Plant] U2 CEA [Control Element Assembly] #27 fully inserted (CEA dropped) into the core during testing per STP 0-029-2. Technical Specification 3.1.4, Action B was entered and required the CEA to be realigned within 2 hours. With this action not met Technical Specification 3.1.4, Action C required the Unit be reduced to < 70% rated thermal power (achieved at 1308 [EDT]) and the CEA to be realigned within 2 hours. "With the CEA being unable to be realigned, Technical Specification 3.1.4.F was entered at 1314 [EDT] which requires the Unit to be placed in Mode 3 within 6 hours. "A plant shutdown has been initiated in accordance with this Technical Specification. Therefore, this is reportable under 10 CFR 50.72(b)(2)(i), 'Plant Shutdown Required by Technical Specifications.'" The licensee will notify the NRC Resident Inspector. | 0 | 45 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-09-05
49322 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-09-04 | 2013-09-05 13:50 | 2013-09-05 | AGREEMENT STATE REPORT - DAMAGED GUIDE TUBE PREVENTS SOURCE RETRACTION IN A RADIOGRAPHY CAMERA The State of Texas submitted the following information via email: "On September 5, 2013, the Agency [Texas Department of Health] was notified by the licensee that on September 4, 2013, a radiography crew was unable to retract an iridium - 192 source into a QSDA 880 D exposure device. The failure was caused when the camera fell from a pipe it was set on and hit the ground crimping the guide tube at the outlet nozzle of the camera to a point where the source could not pass through the tube at the crimp. "The radiographers isolated the area, and contacted their Radiation Safety Officer (RSO). The RSO went to the location to recover the source. The RSO stated that he had to cut both the guide tube and the drive cable so that the guide tube connection to the camera could be broken and the connector removed. The cable was then threaded through the camera and the cable pulled by hand to return the source to the fully shielded and locked position. The camera was returned to the licensee's facility for further inspection. "No one involved in the event received an exposure that exceeded any regulatory limit. No member of the general public was exposed to any radiation due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-09-13
49321 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2013-09-04 16:15 | 2013-09-05 12:30 | 2013-09-05 | CONFIRMED POSITIVE FITNESS-FOR-DUTY TEST A licensed employee had a confirmed positive during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2013-09-05
49320 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-08-05 | 2013-09-04 15:07 | 2013-09-04 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY SOURCE TO RETRACT The following report was received from the Kansas Bureau of Environmental Health via facsimile: "During radiography operations on the night of 5 Aug 2013, two employees, a radiographer and an assistant radiographer of Coder Welding & X-ray Service were finishing an 8 hour shift (which is 2nd shift for Alstom), when the source and crank assembly would not operate correctly. At that time, they could only determine that the source had not fully retracted into the camera correctly. After several additional attempts, they concluded a malfunction of unknown causes prevented the source from retracting to a full and locked condition. Following Coder Operating and Emergency protocol, the first action was to secure and maintain a 2mr/hr boundary. A complete survey of the area determined that the original roped and placarded boundaries were still correct and valid. Next the RSO was contacted as well as the assistant RSO. The RSO advised the radiographer to secure and maintain the 2mr/hr boundary and asked if any personnel or workers had been exposed to radiation levels in excess of those in Kansas Radiation Protection Regulations, Part 4 and following, and they stated no. They were advised that the RSO would be on site in 90 minutes to oversee the incident and resolve the situation. While waiting for the RSO to arrive, the two Coder employees decided to extend the roped boundaries an additional 75 feet in addition to the existing roped area and inform Alstom management of the situation. Since this was the end of 2nd shift for Alstom workers, and no Alstom workers were in the area at the time, there was no disruption of production or evacuation needed. Any Alstom employees on site were advised not to enter plant area as a precaution. At no time were Coder or Alstom employees at risk or in danger of overexposure. "The RSO arrived on site at approximately 12:15 p.m. and made a radiation survey of the area and boundaries. The RSO found correct actions had been taken and 2mr/hr boundaries were maintained. In fact, 1mr/hr was the highest reading. The RSO then walked up to the crank-out reel and found the radiation level to be 5mr/hr. He concluded that the source was in fact in the tungsten collimator (4.3 hvl [half value integers]) secured on the pipe weld where it was during earlier radiographic operations. Several attempts to return the source to its shielded and locked condition failed, so plans were made to allow for closer inspection of the cables and source tube. At this point, the assistant RSO was contacted and advised to bring additional drive cables and source tube in the event they could be needed. While the radiographer and assistant radiographer maintained security over the boundaries and source, the RSO and several Alstom management, who had arrived on site, went outside to look for suitable shielding that could be brought in. Two one inch plates were chosen for use. The plates were tack welded together and moved to an area where overhead cranes could be used to move into position. This was accomplished by using the remote controls of the crane system so no person would have to be in a high radiation environment. With help from Alstom personnel, the steel plates were directed into place by the RSO next to the source camera, providing additional shielding. It was then possible for the RSO to walk up to the source camera with a survey level of 32mr/hr. It was then possible to inspect the drive cables and look at the source tube for possible causes of the return failure. A small depression was noted some 6 to 7 feet from the camera and cable attachment. Using a hacksaw, pliers, and other tools, the outer cable shielding was removed and the RSO returned to the cable crank, and was able to retract the source into the camera in the full and locked position. During the entire operation the RSO received a whole body dose of 35 mr. "Due to the time and distance for the RSO, late arrival of the assistant RSO arrival on site, and the caution taken to resolve the situation, some 3-1/2 hours elapsed from the start to the end. The help and materials provided by Alstom management aided in the safe and satisfactory conclusion of this incident. At this time, it is unknown what might have caused the depression in drive cables or why it suddenly caused a failure to retract situation." Kansas Report Number: KS130006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-09-12
49319 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-09-04 04:05 | 2013-09-04 04:13 | 2013-09-04 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10CFR50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed on 09/04/13 to the Technical Support Center (TSC) HVAC. The work includes performance of planned outside air intake valve electrical repair. The planned work activity duration is approximately 12 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The NRC Resident Inspector has been notified. This event poses no threat to the public or station employees." | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-09-04
49318 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-09-03 06:46 | 2013-09-03 14:10 | 2013-09-03 | SECONDARY CONTAINMENT ACCESS AIR LOCK DOORS OPENED SIMULTANEOUSLY RESULTING IN MOMENTARY DEGRADATION "During planned maintenance activities, station personnel simultaneously opened the inner and outer airlock doors from unit 2 reactor enclosure to the U2 reactor enclosure HVAC room, resulting in a lowering of reactor enclosure delta pressure to below the tech spec minimum required value. The airlock doors were closed within approximately 5 seconds and reactor enclosure delta pressure recovered to greater than the tech spec minimum required value within approximately 20 seconds. "Unit 2 secondary containment was declared inoperable for the time that reactor enclosure delta pressure was below the tech spec minimum required value, and was declared operable when reactor enclosure delta pressure recovered to greater than the tech spec minimum required value. Total Limiting Condition of Operation time was approximately 20 seconds." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-09-03
49317 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2013-09-02 19:26 | 2013-09-02 22:53 | 2013-09-03 | UNUSUAL EVENT DECLARED DUE TO FIRE IN THE TURBINE BUILDING "An Event Classification of Unusual Event (HU2.1) was declared at 1926 [MST] for the Palo Verde Nuclear Generating Station. At 1912, smoke was detected by a security officer by the 'A' train Main Feed pump. An Auxiliary Nuclear Operator investigated and identified a fire on lagging, with one foot flames behind the main standard 'A' train Main Feed pump. The fire team responded to the fire and is currently on scene. Fire was declared out at 1957. "No reactor protection system (RPS) or engineered safety feature (ESF) actuations occurred and none were required. The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences, and this event did not adversely affect the safe operation of the plant or health and safety of the public. The 'A' Main Feed pump high vibration alarm was received, but the continued operation of the main feed pump is currently not in jeopardy." While removing lagging, during the recovery process, the licensee had 2 reflash events. The flame was extinguished and the licensee continues to remove the oil soaked lagging for the 'A' Main Feed pump. The licensee has notified the NRC Resident Inspector, State, and Local Authorities. The Tonopah Fire Department was contacted and did respond to the site. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only). * * * UPDATE FROM WAYNE TIMOTHY TO JOHN SHOEMAKER AT 0352 EDT ON 9/3/13 * * * "PVNGS Unit 2 Terminated the Unusual Event HU2.1 on 9/3/13 at 0029 MST. The fire no longer constitutes a hazard to plant or personnel. 'A' Main Feed Pump is running and Unit 2 is operating at 100% power. The fire was extinguished at 1957 MST (per fire team advisor) and was declared extinguished by the incident commander at 2055 MST. A small oil vapor leak was identified coming from the high pressure bearing seal. Vapor extraction differential pressure was increased to eliminate the oil vapor leak. At 2134 MST, received a report of two reflash events while the Fire Department was removing additional lagging with no sustained flame or fire. All the affected lagging has been removed and the fire emergency was terminated at 2345 MST on 9/2/13." The licensee updated event times to reflect MST. The licensee has notified the NRC Resident Inspector, State, and Local Authorities. Notified R4DO (Hagar), NRR (Galloway), IRD (Marshall), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (email only). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-09-03
49316 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-09-01 16:10 | 2013-09-01 23:34 | 2013-10-13 | RECIRC PUMP RUNBACK AND POWER REDUCTION "On September 1, 2013 at 1610 CST, Monticello Nuclear Generating Plant (MNGP) experienced a runback of 'A' Recirc pump from 87% speed to 82% speed. Operators took action to lock 'A' Recirc pump scoop tube. This runback resulted in a power reduction from 100% to 98% RTP [Rated Thermal Power]. Should a LOCA [Loss of Coolant Accident] occur with the resultant mismatch between total jet pump flows of the two loops greater than required limits, the core flow coastdown and resultant core response may not be bounded by the LOCA analyses. It has been determined that this is an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(B). "At 2123 CST on September 1, 2013, MNGP completed adjusting recirc flow speed on 'A' and 'B' Recirc pumps to match jet pump loop flows to within the required limits and is no longer in an unanalyzed condition. Both 'A' and 'B' Recirc scoop tubes remain locked pending investigation." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 10/11/13 AT 1253 EDT FROM MARK HOESCHEN TO DONG PARK * * * "This is a retraction for ENS 49316: The licensee reviewed the MNGP design basis analysis to determine if the event was bounded. The licensee determined that the Loss of Coolant Accident (LOCA) provides a bounding analysis for this event. "The limiting LOCA event for the MNGP as analyzed in accordance with 10CFR50 Appendix K conditions is based upon single failure of the Low Pressure Coolant Injection (LPCI) injection valve, effectively making LPCI inoperable for the event. The large break Design Basis Accident (DBA) with LPCI injection valve failure (which is analytically equivalent to the condition of both LPCI subsystems being inoperable) is the event analyzed for the current Licensing Basis Peak Cladding Temperature (PCT). This analysis bounds the event as a recirculation pump flow mismatch event is less limiting than the LOCA with LPCI injection valve failure analysis. "Therefore, this recirculating loop flow mismatched event is less limiting than a previously analyzed event and ENS 49316 may be retracted as an unanalyzed event." The licensee has notified the NRC Resident Inspector. Notified R3DO (Skokowski). | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-09-01
49315 | -1 | ACUREN INSPECTION INC |  |  |  |  | 2013-09-01 15:00 | 2013-09-01 17:55 | 2013-09-04 | POTENTIAL OVEREXPOSURE OF RADIOGRAPHER The RSO for the licensee called to report a potential overexposure of a radiographer. This event occurred while the radiographer was checking welds at a refinery in Wyoming. While moving the camera to another location, the radiographer's dosimeter alarmed. It is suspected that the camera's source was not fully retracted into the safe position. The source was subsequently retracted back into the fully shielded position. The RSO calculates an estimated dose to the radiographer of 5 rem. The licensee will send the radiographer's dosimetry for expedited reading as soon as possible. The licensee will update this report with additional details as they become available. * * * RETRACTION FROM GAYLE STATON TO HUFFMAN AT 1436 EDT ON 9/04/13 * * * The RSO has received the radiographer's dosimetry badge readings. The radiographer was still wearing his August dosimetry when the event occurred. His badge readings was 328 mrem for the entire month of August including the exposure from this event. Since there was no significant exposure from the event, the licensee has retracted this event notification. The licensee has notified NRC (Thompson) in Region 4. R4DO (Gaddy) notified and a copy of this report was sent to FSME Event Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2013-09-09
49314 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-08-29 11:00 | 2013-08-29 18:35 | 2013-08-29 | FAILURE TO ADDRESS ALL THE EFFECTS OF EXTERNAL FLOODING SCENARIOS "On August 28, 2013, Monticello Nuclear Generating Plant (MNGP) was notified of the NRC's final significance determination for a finding involving the failure to maintain a procedure addressing all of the effects of an external flooding scenario on the plant. Specifically, MNGP failed to maintain flood Procedure A.6, 'Acts of Nature,' such that it could support the timely implementation of flood protection activities within the 12 day timeframe credited in the design basis as stated in the updated safety analysis report. "The finding is not a current safety concern. On February 15, 2013, actions were completed to reduce the flood mitigation plan timeline to less than 12 days by developing an alternate plan for flood protection features, pre-staging equipment and materials, improving the quality of the A.6 procedure, and preplanning work orders necessary to carry out Procedure A.6 actions. "The NRC Resident Inspector has been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-08-29
49313 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-08-29 08:44 | 2013-08-29 11:33 | 2013-08-29 | LOSS OF ASSESSMENT CAPABILITY DUE TO RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE Millstone Unit 2 removed their plant high range stack radiation monitor RM-8168 from service for pre-planned maintenance. This represents a reportable loss of assessment capability under 10CFR50.72(b)(3)(xiii). The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-29
49312 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-08-27 21:52 | 2013-08-28 05:16 | 2013-10-13 | RECIRC PUMP RUNBACK AND POWER REDUCTION "On August 27, 2013 at 2152 CDT, Monticello Nuclear Generating Plant (MNGP) experienced a runback of [the] 'B' Recirc pump from 87% speed to 71% speed. Operators took action to lock [the] 'B Recirc pump scoop tube. This runback resulted in a power reduction from 100% to 94% RTP [Rated Thermal Power]. With the resultant mismatch between total jet pump flows of the two loops greater than required limits, should a LOCA [Loss of Coolant Accident] occur, the core flow coastdown and resultant core response may not be bounded by the LOCA analyses. It has been determined that this is an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(8). "At 0121 CST on August 28, 2013, MNGP completed reducing power to 88% using 'A' Recirc pump to match total jet pump flows and [the plant] is no longer in an unanalyzed condition. The 'B' Recirc scoop tube remains locked pending investigation." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 10/11/13 AT 1253 EDT FROM MARK HOESCHEN TO DONG PARK * * * "This is a retraction for ENS 49312: The licensee reviewed the MNGP design basis analysis to determine if the event was bounded. The licensee determined that the Loss of Coolant Accident (LOCA) provides a bounding analysis for this event. "The limiting LOCA event for the MNGP as analyzed in accordance with 10CFR50 Appendix K conditions is based upon single failure of the Low Pressure Coolant Injection (LPCI) injection valve, effectively making LPCI inoperable for the event. The large break Design Basis Accident (DBA) with LPCI injection valve failure (which is analytically equivalent to the condition of both LPCI subsystems being inoperable) is the event analyzed for the current Licensing Basis Peak Cladding Temperature (PCT). This analysis bounds the event as a recirculation pump flow mismatch event is less limiting than the LOCA with LPCI injection valve failure analysis. "Therefore, this recirculating loop flow mismatched event is less limiting than a previously analyzed event and ENS 49312 may be retracted as an unanalyzed event." The licensee has notified the NRC Resident Inspector. Notified R3DO (Skokowski). | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-08-28
49311 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-08-28 01:48 | 2013-08-28 03:20 | 2013-08-28 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. Planned maintenance activities are being performed on 08/28/13 in the Technical Support Center (TSC) HVAC. "The work includes performance of planned outside air intake valve electrical troubleshooting. The planned work activity duration is approximately 16 hours. "If an emergency is declared requiring TSC activation during period, the TSC will be staffed and activated using existing emergency planning procedure unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The NRC Resident Inspector has been notified. "The event poses no threat to the public or station employees." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-28
49310 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-08-22 | 2013-08-27 18:00 | 2013-08-27 | AGREEMENT STATE REPORT - THERAPY DOSE APPLIED TO WRONG LOCATION The following report was received via e-mail from the Louisiana Department of Environmental Quality: "On 08/27/2013, the RSO for Tulane University Hospital called to notify the Department that their facility had a Medical Event involving [exposure to unintended tissue greater than] 50 Rem. The event was discovered on 08/27/2013 when an application was not able to be applied to the intended tissue. The HDR source had 'dog legged' into the bowel area when it was intended to apply the radiation dose to the cervical area. The films were pulled for the application on 08/22/2013 and revealed that the application had 'dog legged' also. The cervical tissue did not receive the initial intended dose. "The HDR [High Dose Rate Brachytherapy Afterloader] unit was a Nucletron Micro-Selectron, loaded with [an] Ir-192 [source]. The therapy dose was 8.4 Gray [840 rads] given in fractions. The patient is to receive the entire corrected therapy dose prescribed. "This is believed to be (under investigation) a positioning problem and not an equipment malfunction. "The patient's physician has been notified. However, the patient was heavily sedated and has not been notified. "Updates will be made when additional information is available." Louisiana Report ID: LA-130001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-09-04
49309 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2013-08-24 | 2013-08-27 16:27 | 2013-12-06 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE INVOLVED IN FIRE AT WELL SITE The following information was received via facsimile: "A fire started at a well site near Williston, ND on Saturday, August 24, 2013. At the time of the event, fracking activities were being performed utilizing a Thermo Fisher Scientific model 5190 nuclear density gauge containing a Cs-137 source attached to a blender. Personnel evacuation was immediately performed and notification was made to the local fire department. Local fire department personnel arrived on-site and established control of the scene. The fire was extinguished later that night. Local fire department personnel restricted access to the site until Sunday morning. At that time, licensee personnel on-site were allowed to approach the gauge from a safe distance working their way towards the gauge while continually monitoring a radiation survey instrument (Ludlum Model 3). As the observed readings were higher than expected, it was believed the lead shielding had melted inside the steel casing and shifted to the lower area within the casing. The steel casing remained intact. After the initial assessment, licensee personnel maintained continual surveillance while site security personnel prohibited access within the public dose boundary set by the licensee. The licensee dispatched their Radiation Compliance Coordinator for further evaluation. "The licensee's Radiation Compliance Coordinator arrived in Williston late Sunday night. Early Monday morning he arrived on site to perform more complete radiation surveys and leak testing of the involved gauge. The highest radiation levels noted around the gauge were 2.6 R/hr at the surface and 20 mR/hr at 1 meter. Wipe tests were collected and sent to Applied Health Physics of Bethel, PA for analysis. The results of the first two wipe samples demonstrated no evidence of contamination. "The licensee contacted the manufacturer regarding disposal of the damaged gauge. The manufacturer, not willing to accept receipt of the gauge, suggested the licensee contact a waste broker for final disposal. The licensee subsequently contacted Applied Health Physics (AHP). AHP plans to cut out the gauge and package it in a lead lined 55 gallon steel drum for transport, and ship the container for final disposal. AHP is scheduled to perform this activity on Thursday, August 29, 2013. "Licensee and site security personnel will continue to maintain surveillance and control of the site until the disposal personnel arrive." * * * UPDATE FROM DAVID STRADINGER TO PETE SNYDER AT 1756 EDT ON 9/5/13 * * * AHP removed the gauge and packaged it for transport. Notified R4DO (Gaddy) and FSME EVENTS RESOURCE (e-mail). * * * UPDATE FROM DAVID STRADINGER TO JOHN SHOEMAKER AT 1431 EDT ON 12/6/13 * * * The North Dakota Department of Health has completed their investigation and recommending the LER (License Event Report) for closure. Notified the R4DO (Vasquez), R1DO (Cook), and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2013-09-04
49308 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2013-08-26 23:05 | 2013-08-27 04:10 | 2013-09-05 | POST ACCIDENT MONITORING INSTRUMENTATION POWER SUPPLIES POTENTIALLY DEGRADED "At 2305 on 26AUG13 the Shift Manager Declared PC-ES-1A and PC-ES-1B inoperable due to a Part 21 Notification that called the operability of the equipment into question. PAM [Post Accident Monitoring] Instrumentation LCO 3.3.3.1.A and 3.3.3.1.C were entered for Functions 1 (Reactor Pressure), 3 (Containment Level), and 7 (Containment Pressure). Both divisions are potentially affected. LCO 3.3.3.1.C represents a 7 Day shutdown LCO. "CR-CNS-2013-6096 identified a Part 21 issue associated with Foxboro Power Supply PC-ES-1A and PC-ES-1B. The Part 21 issue identifies a potential failure mechanism in which the adhesive backing on aluminum tie-wrap base used in the power supply fails and the base becomes detached from the power supply case. The nylon tie-wrap affixed to these bases becomes brittle with age and fails releasing the aluminum base to fall into the power supply where it has the potential to short out electrical equipment and fail the power supply. The equipment affected is: PC-LRPR-1A, PC-LRPR-1B, NBI-PR-2A, and NBI-PR-2B. These power supplies affect both Control Room Reg. Guide 1.97 Cat A instruments and associated PMIS/SPDS points. This instrumentation is utilized for emergency plan actions (EALs) and EOP 3A actions in addition to monitoring the previously mentioned functions. The loss of this instrumentation represents a significant loss of emergency response capability. The affected instruments are for indication only and perform no active safety functions. All of the referenced instrumentation is currently functioning as required. "This condition has been entered into the CNS Corrective Action Program. "A 60 day Licensee Event Report is not required for this event." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DAVID MADSEN TO VINCE KLCO ON 9/5/13 AT 1854 EDT * * * "This notification is being made to retract Event Notification EN 49308 that was reported on August 26, 2013. This EN identified Cooper Nuclear Station had equipment potentially affected by a Part 21 issue in which a potential failure mechanism of adhesive on aluminum ty-wrap bases used in two power supplies fails and the base becomes detached from the power supply case. The nylon ty-wraps affixed to these bases become brittle with age and fails, releasing the aluminum base to fall into the power supply with the potential to short out electrical equipment. These power supplies affected Post Accident Monitoring equipment that is used to monitor for Emergency Plan Actions (EALs) and EOP 3A actions. This equipment provides no active safety function and is used for indication only. The equipment affected included PC-ES-1A and PC-ES-1B and they provided divisional power to Post Accident Monitoring equipment for Reactor Pressure, Containment Level and Containment Pressure. "Ten of the eleven aluminum cable tie holders were found to still be in place during the inspection of PC-ES-1A under WO 4972878. The one cable tie holder that was found to not be adhered was initially attached when the power supply was opened. Based on physical inspection of the removed cable ties and the installed wiring, and ten of the eleven cable tie holders being adhered upon inspection of the power supply it is concluded that this power supply remained qualified to perform its function under all design conditions in its as found configuration. The failure mechanism identified in the Part 21 required two failures. The inspection performed on PC-ES-1A only revealed the failure of one cable tie mount and not the widespread failures reported in the Part 21. Additionally, the cable ties removed from PC-ES-1A remained flexible and would not have failed during a seismic event based on engineering judgment. As such, PC-ES-1A remained capable of performing its design function. By engineering judgment PC-ES-1B also remained capable of performing its function. Therefore, there was no actual or potential major loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. Notified the R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-27
49307 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-08-25 18:18 | 2013-08-26 01:05 | 2013-08-26 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "Reactor Building (Secondary Containment) pressure increased to above the Technical Specification Surveillance requirement of 0,25 inches vacuum water gauge. This event is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. The Reactor Building differential pressure controller was placed in manual operation and Secondary Containment pressure was restored to normal (greater than 0.25 inches vacuum water gauge) returning Secondary Containment to operable status. Secondary Containment pressure was outside the allowable Technical Specification requirement for 4 minutes. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-08-26
49306 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-08-24 16:14 | 2013-08-25 00:46 | 2013-08-29 | MALFUNCTION OF STACK RADIATION MONITOR SUPPORTING EQUIPMENT "At 1614 hours PDT on August, 24, 2013 the Reactor Building Stack Radiation Monitor - High Range and Reactor Building Stack Radiation Monitor - Intermediate Range detectors were declared non-functional due to a loss of supporting equipment. Corrective actions are being pursued to restore the affected monitors to functional status. "To compensate for the loss of assessment capability due to the non-functioning Radiation Monitoring Equipment, an additional Health Physics (HP) Technician trained to acquire offsite dose assessment information on offsite releases is available. The additional personnel are pre-staged in support of the Radiation Monitoring System outage and will be mobilized in accordance with guidance in the compensatory measure instructions. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). A follow up notification will be made when the Equipment has been returned to service. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM MATT HUMMER TO VINCE KLCO ON 8/29/13 AT 1739 EDT * * * "Repairs have been completed and both the Intermediate and High Range Reactor Building Stack Radiation Monitors have been returned to service. "The licensee has notified the NRC Resident Inspector." Notified the R4DO (Hagar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-25
49305 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2013-05-10 | 2013-08-23 14:05 | 2013-08-23 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO FAMILY MEMBER A family member may have received an exposure of 5,925 mrem while providing home care for the patient undergoing I-131 therapy administered on March 22, 2013. The patient was hospitalized from March 22 to March 29, 2013 and then discharged with at-home precautions. During the patient's hospitalization visitors including family members were provided radiation badges to monitor exposure. The badges were subsequently processed by Landauer on May 5, 2013 which identified that a family member received 5,925 mrem effective dose equivalent during this period of hospitalization. The subject badge was reread on May 6, 2013 which confirmed the initial reading. The Children's Hospital was notified on May 10, 2013 of the results. A survey of the patient's room found little contamination. Children's Hospital conducted an extensive investigation but could not definitively identify the cause for the high exposure level. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-09-02
49304 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-08-22 13:00 | 2013-08-23 11:39 | 2013-08-23 | ALCOHOL FOUND IN THE RESTRICTED AREA "The following significant FFD policy violations and programmatic failures must be reported to the NRC Ops Center within 24 hours by telephone after the licensee or other entity discover the violation. "(1) The use, sale, distribution possession or presence of illegal drugs, or the consumption or presence of alcohol within a protected area. "Ours [licensee] is a conservative decision to notify due to the fact that the contraband was found in the restricted area and NOT in the protected area. "On 8/22/13 at approximately 1300 hours, an employee conducting demolition work on the 542 level of the Auxiliary Building discovered an old dust covered pint glass bottle of Jim Beam Bourbon Whiskey containing approximately 1 inch of brown liquid which, when opened, smelled of alcohol. The bottle was located in bus trays 12 to 15 feet above the floor. The employees retrieved the bottle and handed it to an individual on the ground. Radiation Protection [RP] personnel bagged the bottled due to it being in a contaminated area. The bottle was surveyed by RP and released to Security. The bottle was removed to the FFD Office and the liquid was disposed of in the toilet. The glass bottle was then disposed of offsite." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2013-08-23
49303 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  |  | 2013-08-23 | 2013-08-23 13:01 | 2013-08-23 | PART-21 NOTIFICATION - AP-1000 TIME RESPONSE FOR THE SAFETY ANALYSIS CANNOT BE DIRECTLY MEASURED The following information was received via fax: "Several technical specifications were identified in a Corrective Action Report (CAR) as having a time response surveillance requirement that cannot be directly measured due to logic pathways where overlap with another protective function occurs. Westinghouse is now determining what other reactor trip and engineered safeguards actuation system protective functions have a credited time response in the Safety Analysis for the AP1000 plant and therefore should be assigned a time response surveillance requirement in the Technical Specifications. The evaluation will address the safety implication of the items identified in the CAR as well as confirm that all other protective functions where a time response was credited in the safety analysis have a measurable surveillance requirement in the Techni.cal Specifications. "The safety significance evaluation for the AP1000 plant is still in process and a determination of the potential to create a substantial safety hazard is not yet complete." Affected licensees: Summer Units 2 and 3 Vogtle Units 3 and 4 Levy Units 1 and 2 Harris Units 2 and 3 Lee Units 1 and 2 Turkey Points Units 6 and 7 Bellefonte Units 3 and 4 Point of contact: James Gresham 412-720-0754 Westinghouse letter: LTR-NRC-13-62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-08-23
49302 | 0 | BALDOR ELECTRIC CO. |  |  |  |  | 2013-08-23 | 2013-08-23 12:35 | 2013-08-23 | PART-21 NOTIFICATION - MOTORS MAY HAVE A POINT FOR FOREIGN MATERIAL ENTRY The following information was received via fax: "This is a reportable 10CFR21 notification because some 1E motors in frame sizes 360, 400, and 440 may have been shipped by Baldor Electric, which contain an entry point for blast media to enter the motor during post shipment paint treatment preparations. During a recent inspection of a returned motor, some foreign materials were discovered inside the motor which appeared to consist of two types of blast media. One type of blast media found is used during the manufacturing process to clean the rotor end ring area before applying an end ring coating. This media is non-conductive and is typically cleaned away as part of the treatment process. The presence of blast media is a key inspection point at rotor final inspection. In mid 2008 this type of blast media was eliminated from Baldor processes and substituted with C02 blast media. "The other blast media found inside the motor is not used during the motor manufacturing process at Baldor. It was a metallic bead media and used during a paint preparation process after leaving Baldor. The entry point of this material was found to be through a small window in the frame casting that normally is closed with weld after the stator is assembled into the frame. In this instance, one of the stator weld notches was aligned with one (of the two) small windows in the frame casting. This allowed the blast media to enter and travel along the OD [outside diameter] of the stator core weld notch and into the motor. "Engineering and Quality reviewed all nuclear orders to verify the frame sizes that may have used the weld slot construction. The frames were determined to be 360, 400, and 440 during the time frame when the welds may not have been verified. The date range was established as 2002 thru 2013. "The motors identified as possibly having this non-conformance should be inspected for the following: a. The frame weld windows on identified 360,400 or 440 frame motors show no weld. and b. The stator core weld notch is visible in at least one (of the two) frame weld windows." If both issues exist, then remediation is recommended. Customers who have received these motors: Areva, Inc. David Brown Union Pumps Co. Duke Energy Corp. Enertech First Energy First Energy Service Co. Flowserve Pump Division - Spain Georgia Power Howden North America Inc. Limitorque Spencer Turbine Co. Taiwan Power Company Westinghouse Electric Company Point of Contact: James Thigpen, 678-947-7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-08-23
49301 | 0 | MIRION TECHNOLOGIES CONAX NUCLEAR |  |  |  |  | 2013-08-23 | 2013-08-23 12:54 | 2014-02-05 | PART-21 NOTIFICATION - UNQUALIFIED MATERIAL USED IN ELECTRICAL PENETRATION ASSEMBLIES The following information was received via fax: "Material supplied to MTCN [Mirion Technologies (Conax Nuclear)] by approved sub-suppliers audited to NCA-3800 by MTCN was considered to be ASME [American Society of Mechanical Engineers] qualified source material for Section II and Section III requirements. During triennial survey of MTCN by the ASME for renewal of our N Type Certificates of Authorization, it was identified by the ASME survey team that material supplied by two (2) MTCN approved sub-suppliers should be considered unqualified source material. At that time, MTCN's Quality Program did not include the use of unqualified source material. "Testing of the coupons for materials used with the basic components supplied to the operating plants is expected to be completed within the next 30 days." The potentially defective components are electrical penetration headerplates, mounting weldment rings and weld neck flanges for mounting the electrical penetration assemblies. The affected facilities are: Oconee, Ginna, Crystal River, Point Beach, Monticello, Cook, and Turkey Point. Point of contact: John MacDonald 716-681-1973 * * * UPDATE FROM JOHN MACDONALD TO HOWIE CROUCH ON 9/23/13 AT 1747 EDT * * * MTCN has determined the material supplied to U.S. plants does not impact the material safety or performance of the EPAs (Electrical Penetration Assemblies) delivered. Chemical and mechanical re-verification test results to date indicate there have been no test failures compared to the ASME SA-240 material requirements. Notified R1DO (Welling), R2DO (Seymour), R3DO (Riemer), and NRR Part 21 Group (email only). * * * UPDATE FROM JOHN MACDONALD TO HOWIE CROUCH (VIA EMAIL) ON 2/5/14 AT 1627 EDT * * * MTCN has determined that chemical and mechanical tests indicate that the materials used in the EPAs delivered met ASME requirements and does not impact safety or performance of the delivered devices. Due to the evaluation results, the vendor submitted this update to provide final closure of this Part 21 issue. Notified R1DO (Lilliendahl), R2DO (Masters), R3DO (Orlikowski) and the Part 21 group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-08-23
49300 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-08-22 16:26 | 2013-08-22 17:08 | 2013-08-22 | UNIT 1 COMMENCED A TS REQUIRED SHUTDOWN DUE TO UNIDENTIFIED RCS LEAKAGE > 1 GPM "Salem Unit 1 has initiated a unit shutdown in accordance with TS (Technical Specification) Action Statement 3.4.6.2(b) for unidentified leakage greater than 1 gpm [gallon per minute] (Entered on 8/22/13 at 1029 EDT). TS 3.4.6.2 Action Statement (b) requires a reduction of leakage rate to within limits within 4 hrs. or be in at least Hot Standby within the following 6 hours. Initial investigation has indicated that the leakage source is from packing on Pressurizer Spray Valve 1PS1 located in the RCS [Reactor Coolant System] Pressurizer shroud area inside Containment. Unidentified leakage is currently indicating 4 gpm. NRC Resident [Inspector] has been notified. Manual isolation is in progress. "Additionally, TS Action Statement 3.6.1.4 Primary Containment Internal Pressure was entered at 1510 [EDT] for exceeding 0.3 psig. Action requires restoration of containment pressure to within specification in 1 hour or be in hot standby within the next 6 hours. Containment pressure was restored to less than 0.3 psig at 1647 [EDT] and TS 3.6.1.4 was exited. Peak containment pressure reached [was] 0.33 psig. "Location of leak: Unit 1 RCS (containment), Pressurizer, 1PS1 Pressurizer Spray Valve Packing "Time & date leak started: 1019 [EDT] on 08/22/2013 "Leak rate: 4 gpm, T/S leak limits: 1 gpm "Last known coolant activity: Primary (DEI [Dose Equivalent Iodine]-microCuries/cc) 5.973E-5 microCuries/cc "Secondary (gbg [Gross Beta Gamma]-microcuries/cc) < LLD [Lower Limit of Detectability] "Was this leak a sudden or long-term development? Sudden" The licensee is reducing power at 30%/hour and anticipates entering Mode 3 in approximately 3 hours. The 1PS1 Pressurizer Spray Valve was replaced and the air operator rebuilt during the last refueling outage in April/May of 2013. The licensee informed the State of New Jersey and will 9inform the Lower Alloways Creek [LAC] Township. | 81 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-08-22
49299 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-08-22 14:50 | 2013-08-22 16:09 | 2013-08-22 | OFFSITE NOTIFICATION OF A FATALITY AT MILLSTONE UNIT 3 "On August 22, 2013, a contract worker was discovered unresponsive at Millstone Power Station in the plant's condensate polishing facility. The worker was transported offsite to a local hospital. At 1450 [EDT], the Millstone Power Station Unit 3 Shift Manager was informed the individual had been pronounced dead at the hospital. "The cause of the fatality is under investigation. The injury does not appear to be related to industrial work activities. The person was not contaminated. Local law enforcement and other government agencies have been notified. "OSHA is being notified of the event under the requirements of 29 CFR 1904. "No press release is planned. This event is reportable pursuant to 10 CFR50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The woman was found at the bottom of a staircase at 1258 EDT. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-08-22
49298 | 0 | PALISADES | 1 |  |  | [1] CE | 2013-08-22 10:48 | 2013-08-22 15:05 | 2013-08-22 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee informed the NRC Resident Inspector and will inform stakeholders at their scheduled meeting. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2013-08-22
49297 | -1 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-08-21 13:45 | 2013-08-22 14:33 | 2013-09-05 | AGREEMENT STATE REPORT - PATIENT GIVEN DOSE PRESCRIBED FOR ANOTHER PATIENT The following was received from the State of Oregon via facsimile: "The inpatient was having an Adenosine Myoview stress test. The Nuclear Medicine Technologist took the dose that was already in the dose calibrator (place there earlier by another Nuclear Medicine Technologist). It measured about the same activity as 99m-Tc Myoview would measure in the dose calibrator. The Nuclear Medicine Technologist gave the patient 37.4 millicuries of 99m-Tc DTPA (lung ventilation dose) instead of 30 millicuries of 99m-Tc Myoview. The route of administration for 99m-Tc DTPA is inhalation and the route of administration for 99m-Tc Myoview is intravenous. The 99m-Tc DTPA was intended for a different patient. The patient was informed of the mistake and the stress test will be repeated tomorrow (8/22/13). The ordering physician was also notified of the event. There were no adverse effects to the patient, just delayed the study. "This will be reported at the next Radiation Safety Committee Meeting along with any actions that will be taken to prevent this in the future." Oregon Event Number: 13-0031 * * * RETRACTION ON 9/4/13 AT 1310 EDT FROM RICK WENDT TO DONG PARK * * * "This item is ready for closure. Incident closed. Not a reportable event." Notified R4DO (Gaddy). * * * UPDATE ON 9/5/13 AT 1306 EDT FROM RICK WENDT TO PETE SNYDER * * * The event was not reportable due to the fact that the total organ dose was less than 50 REM. Notified R4DO (Gaddy). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-08-30
49296 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-08-22 07:55 | 2013-08-22 11:39 | 2013-08-22 | REACTOR PROTECTION ACTUATION (SCRAM) "On Thursday, August 22, 2013 at 0755 hours [EDT], with the reactor critical at approximately 98% core thermal power, and the mode switch in RUN, a manual reactor scram was inserted due to lowering reactor water level. The cause of the lowering reactor water level was due to the trip of all three Feedwater Pumps. The cause of the Feedwater Pump trip event is currently under investigation. "Following the reactor scram, all control rods were verified to be fully inserted. All 4kV busses transferred to the Startup Transformer as designed. Following the scram the reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically as per design. "Reactor water level lowered to -46 inches initiating Primary Containment Isolation System Group I - Main Steam Isolation Valves (MSIVs); Emergency Core Cooling Systems (ECCS) actuated which included automatic start and injection of the High Pressure Coolant Injection (HPCI) System and the Reactor Core Isolation Cooling (RCIC) System and an automatic start of the Emergency Diesel Generators as designed. Reactor water level was promptly restored to normal level. "Currently a cooldown is in progress with reactor pressure is being maintained by the HPCI System operating in the pressure control mode and reactor water level is being maintained by the RCIC System. Reactor Water Clean-up System and normal reactor building ventilation have been restored. Off-site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The USNRC Senior Resident Inspector has been notified. This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(A) and (B)." The plant is transferring from decay heat removal to the torus to decay heat removal to the main condenser. Reactor pressure is 371 psig. Initial indications are that a main feedwater power supply breaker tripped. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2013-08-22
49295 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-08-21 21:00 | 2013-08-22 01:28 | 2013-08-22 | INADVERTENT SIREN ACTUATION "Point Beach was notified via our EP [emergency plan] manager that emergency plan siren K 5 actuated inadvertently at 2100 [CDT] on 8/21/13, during severe weather. Initial notification of this occurrence was made by Kewaunee County Emergency Management to the Kewaunee Nuclear Plant EP manager. The Kewaunee EP manager in turn notified the Point Beach EP manager. The siren stopped sounding at 2125 on 8/21/13, and was removed from service to prevent additional inadvertent actuations before it is repaired. The loss of coverage for siren K-5, which is the only Point Beach siren out of service at this time, is 1.9%, which is below the 50% loss of coverage requiring additional notifications." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-08-22
49294 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-08-21 21:00 | 2013-08-22 01:11 | 2013-08-22 | INADVERTENT SIREN ACTUATION "On 08/21/2013, the Kewaunee Power Station was notified by Kewaunee County Emergency Management of the inadvertent actuation of siren K-005 at 2100 [CDT]. At the time of the actuation, there was severe weather in the area. The siren stopped actuating at 2125. Kewaunee Power Station requested maintenance crews remove power from the siren to prevent additional actuation until repairs can be made. The resulting loss of siren coverage is 4%. Siren K-005 is a shared siren with Point Beach Nuclear Power Plant. Point Beach control room has been notified." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-08-22
49293 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-08-21 20:00 | 2013-08-21 22:20 | 2013-08-21 | UNANALYZED CONDITION FOR EMERGENCY DIESEL GENERATOR FUEL OIL PUMPS TRAIN SEPARATION "On August 21, 2013 at 2000 CDT, it was determined following receipt and review of an NRC position document, that the design of the Monticello Nuclear Generating Plant diesel fuel oil supply system is not consistent with current and historical licensing and design basis documents. This condition affects fuel oil supply from the diesel fuel oil storage tank to both emergency diesel generators and is being reported pursuant to 10CFR50.72(b)(3)(ii) as an unanalyzed condition that could significantly degrade plant safety. "Actions are in progress to address the unanalyzed condition. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-08-21
49292 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2013-08-20 11:15 | 2013-08-20 17:56 | 2013-08-22 | 24 HOUR REPORT RELATED TO CRITICALITY CONTROL BULLETIN 91-01 "The Hematite Decommissioning Project (HDP) is excavating burial pits containing enriched uranium. HDP has established criticality safety controls to ensure the safe handling of the buried waste as it is excavated. These controls involve redundant surveys and visual inspections at the time of excavation. These controls failed to identify an item upon excavation that was 400,000 ncpm [net counts per minute] on contact and had dimensions of 6 inches or greater. Instead, the item was identified and placed in criticality safety controls (collared drum) after it had reached the Waste Holding Area. "The item appeared to be a crushed container, estimated at 10 gal. in original size, and had contents primarily consisting of gloves and plastic. After the contents were removed, the empty container was confirmed to have only contamination that was below the threshold of criticality safety controls. The detailed assay of the contents was 22 g of U-235, which does require criticality safety controls. "Work in the burial pit areas was stopped pending retraining of those workers on the requirements and criticality safety controls regarding survey and visual inspection during excavation. Excavated burial pit area waste that has not reached the Waste Holding Area will be resurveyed and inspected prior to proceeding to the Waste Holding Area." The licensee notified NRC R3 (Tapp). * * * UPDATE FROM KEVIN DAVIS TO PETE SNYDER ON 8/22/13 AT 1054 EDT * * * "[HDP's] controls failed to identify and control an item upon excavation that was 100,000 ncpm on contact had dimension 6 inches or greater. Instead, the item was identified to require and be placed in criticality safety controls (collared drum) after it had been counted at the Material Assay Area. "The item appeared to be the mangled remnant of a container. There were no contents, but there was soil-like material adhering to the surfaces. The soil-like material was separated from the remnant for detailed assay. Detailed assay identified the remnant contained 3 g of U-235 and the soil like material contained 21 g of U-235, which requires criticality safety controls. "Work in the burial pit areas was stopped pending retraining of those workers on the requirements and criticality safety controls regarding survey and visual inspection during excavation, and pending development of additional engineered measures. In addition, shipment of railcars has been suspended pending additional evaluation. "Excavated burial pit area waste that has not reached the Waste Holding Area will be resurveyed and inspected prior to proceeding to the Waste Holding Area." The licensee notified the NRC R3. Notified R3DO (Kozak) and NMSS (Hsia). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0 | 2013-08-20
49291 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-08-19 14:24 | 2013-08-20 11:49 | 2013-08-20 | NON-LICENSED CONTRACT SUPERVISOR HAD A CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed contract supervisor had a confirmed positive fitness for duty test. Plant access for the individual has been terminated. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2013-08-20
49290 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-08-19 10:13 | 2013-08-19 17:23 | 2013-08-22 | INCREASING BACKGROUND NOISE IN STACK RADIATION MONITOR RENDERS IT NON-FUNCTIONAL "At 1013 hours PDT on August 19, 2013 the Reactor Building Stack Radiation Monitor High Range Detector was declared nonfunctional due to increasing background noise. The Reactor Building Stack Radiation Monitor Intermediate Range Detector remains functional and shows no increase in effluent radioactivity. "To compensate for the loss of assessment capability due to the nonfunctioning radiation monitoring equipment, an additional Health Physics (HP) Technician trained to acquire offsite dose assessment information on offsite releases will be available. The additional personnel will be pre-staged in support of the Radiation Monitoring System outage and will be mobilized in accordance with guidance in the compensatory measure instructions. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). A follow-up notification will be made when the equipment has been returned to service. "The licensee will notify the NRC Resident Inspector." * * * UPDATE FROM MICHAEL STODICK TO PETE SNYDER AT 2028 EDT ON 8/19/13 * * * "Initial investigation into the cause of the malfunction of the Reactor Building Stack Radiation Monitor High Range Detector revealed that the condition also affected the Reactor Building Stack Radiation Monitor Intermediate Range Detector. Therefore, this monitor has also been declared non-functional as of 1633 hours PDT on August 19, 2013. Compensatory measures remain in effect to provide emergency response capability for assessing and monitoring actual or potential offsite consequences of a radiological release through this pathway. Corrective actions are being pursued to restore the affected monitors to functional status." The licensee notified the NRC Resident Inspector. Notified R4DO (Werner). * * * UPDATE FROM MOT HEDGES TO HOWIE CROUCH AT 1236 EDT ON 8/21/13 * * * "The cause of the increased background noise for the Reactor Building Stack Radiation Monitor-High Range was due to failing cooling components for the instrumentation, resulting in increased electronic background noise in the instrumentation. There has been no change in the radiation levels at the plant. "The NRC Resident Inspector has been notified." Notified R4DO (Werner). * * * UPDATE FROM MOT HEDGES TO MARK ABRAMOVITZ ON 8/22/2013 AT 1630 EDT * * * "Repairs have been completed and both the Intermediate and High Range Reactor Building Stack Radiation Monitors have been returned to service. The licensee has notified the NRC Resident Inspector." Notified the R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-19
49289 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-08-19 09:00 | 2013-08-19 08:46 | 2013-10-15 | LOSS OF EMERGENCY PREPAREDNESS CAPABILITIES DUE TO UNIT 1 PPC REPLACEMENT "The Unit 1 DC Cook Nuclear Plant (CNP) Plant Process Computer (PPC) will be removed from service on Monday, August 19, 2013 at 0900 EDT to support planned replacement. The Unit 1 PPC, including the Emergency Response Data System (ERDS), will be unavailable to the NRC Operations Center. Planned replacement also affects the Safety Parameter Display System (SPDS), the Real Time Data Repository (RDR), and PPC data to Emergency Response Facilities at CNP. Safety system annunciators and indications in the control room remain available. "The scheduled replacement, returning of equipment to service and post maintenance testing is expected to be completed by 2000 EDT on Saturday, September 7, 2013. "Compensatory measures exist within the DC Cook emergency response procedures to provide plant data via the Emergency Notification System to the NRC Operations Center until the ERDS can be returned to service. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system)." * * * UPDATE AT 1228 EDT ON 10/15/13 FROM BOWMAN TO HUFFMAN * * * The Unit 1 DC Cook Nuclear Plant (CNP) Plant Process Computer (PPC) was restored to service on Tuesday, October 1, 2013 at 1649 EDT following the planned replacement of the PPC. The Unit 1 PPC is fully functional, including the Emergency Response Data System (ERDS), which is available to the NRC Operations Center. This also restores the Safety Parameter Display System (SPDS), the Real Time Data Repository (RDR), and PPC data to Emergency Response Facilities at CNP. The licensee has notified the NRC Resident Inspector. R3DO (Duncan) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-19
49288 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-06-09 20:16 | 2013-08-16 13:50 | 2013-08-16 | PART 21 - AUXILIARY FEEDWATER LEVEL CONTROL VALVE STEM/PLUG ASSEMBLY OUT OF TOLERANCE "On June 9, 2013, Auxiliary Feedwater Level Control Valve [AFW LCV] 1-LCV-3-156-A, failed its closed-to-open stroke time during quarterly surveillance testing. This level control valve is a basic component which regulates auxiliary feedwater (AFW) flow to Steam Generator 2. The valve failed to open during two attempts. Local observation during testing indicated that the valve 'popped' off the seat, and then traveled smoothly to its full open position on the third and fourth attempt. The failure was determined to be a Maintenance Rule Functional Failure and a CC1 Functional Failure. There were no previous indication(s) of this failure mode during the previous quarterly stroke time testing. The valve internals were replaced on October 7, 2009, during a refueling outage. "TVA installed a new trim kit which included the cage, lower seat ring, and stem/plug assembly. The valve was returned to service on June 12, 2013, following successful post modification testing. A Kepner-Tregoe (K-T) problem analysis revealed the direct cause was binding due to the stem/plug assembly being out of tolerance. Upon inspection, the Total Indicated Run-out (TIR) of the stem/plug assembly removed from the affected valve was determined to be 0.022 inches. The valve was manufactured by Dresser Masoneilan with a TIR specification of less than or equal to 0.005 inches. The valve model and stem/plug assembly part numbers are: "Valve: Masoneilan Model 37-20721, 4 inch Control Valve "Stem: 012160204-215-J000 "Plug: 011501710-1H6U "Inspection of the five unused spare stem/plug assemblies in storage had a TIR that ranged from 0.006 to 0.022 inches, which is outside vendor specifications. Because the stem/plug assembly removed from the affected AFW LCV and five of the unused stem/plug assemblies were found to be out-of-tolerance, a condition exists and is being reported in accordance with 10CFR50 Part 21.21(d). "Similar LCVs in the AFW systems were tested and are OPERABLE with no known defects. "A detailed report using NRC Form 366, Licensee Event Report, will be submitted to the NRC by 09/15/13 in accordance with 10CFR50 Part 21.21(d)(3)(ii)." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2013-08-16
49287 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-08-15 18:24 | 2013-08-16 02:36 | 2013-08-16 | LOSS OF STARTUP POWER RESULTS IN VALID STARTS OF ALL THREE EMERGENCY DIESEL GENERATORS "At 1824 PDT on August 15, 2013, Unit 1 experienced a loss of startup power due to a failure of Startup Transformer 1-1 load tap changer. This loss caused a valid auto-start signal to all three emergency diesel generators and they all started successfully. At 1921, all EDGs were shutdown and returned to standby per plant procedures." As a result of the loss of startup power, power was also lost to site service buildings. ERDS was lost but compensatory measures are in place to transmit required data via the ENS line if required. The plant is in a 72-hr. shutdown LCO action statement under T.S. 3.8.1 for the loss of one of three qualified circuits. The two other qualified circuits (vital power via auxiliary transformers and the EDGs) remain operable. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-08-16
49286 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-08-15 09:15 | 2013-08-15 17:53 | 2013-08-15 | DIESEL GENERATOR DECLARED INOPERABLE DUE TO DAMPER FAILING TO OPEN "During a run of the Division 3 Diesel Generator room ventilation fan to perform thermograph, it was identified that the damper (1VD01YC) that provides the flow path from the outside area into the ventilation room would not open when the fan was started. This renders the Division 3 Diesel Generator inoperable. High Pressure Core Spray was declared inoperable at 1420 hours [CDT], but remains available. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "The cause of the damper failing to open has not yet been determined. Troubleshooting is in progress to determine the cause and actions required to restore operability. The Division 1 and Division 2 Diesel Generators are operable." The licensee is in a 14-day shutdown TS LCO. The licensee has notified the NRC Resident Inspector. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-08-15
49285 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-08-15 16:10 | 2013-08-15 16:47 | 2013-08-15 | A HOT SHORT IN THE RHR SHUTDOWN COOLING CONTROL CABLE COULD RESULT IN AN INTER-SYSTEM LOCA "A condition was identified that resulted from an inter-cable circuit analysis as part of the safe shutdown analysis that identified a vulnerability associated with two Unit 2 valves with controls in Fire Area 2203. Specifically, during the postulated fire scenario, an inter-cable hot short could occur on the control cables for the RHR shutdown cooling suction valve 2E11-F008 valve and cause the valve to open in the event of a postulated fire in Fire Area 2203F which is in the vicinity of the Unit 2 remote shutdown panel. In addition, a spurious opening of RHR shutdown cooling suction valve 2E11-F009 valve could occur due to a hot short on the control cables. The fire is postulated while in Mode 1 which could cause both valves to open during power operation. This postulated event would expose the low pressure RHR-shutdown cooling suction line to normal operating pressures which would result in an inter-system LOCA. "Immediate actions were taken to de-energize the valves in the 'closed' position which removed the vulnerability. When this condition was first discovered, the consequences of this postulated condition were evaluated and there was reasonable assurance that the condition did not represent an unanalyzed condition that significantly degrades/degraded plant safety. A review of the FSAR, design documents and regulatory requirements was performed to document the foundational logic for the engineering judgment to support the original conclusion that there was reasonable assurance that the inter-system LOCA did not represent an unanalyzed condition that significantly degraded plant safety and that this would not result in a loss of a safety function. Based on information learned in this review there was not sufficient information to make a conclusive determination. Since a conclusive determination cannot be made at this time and since there is some doubt regarding whether or not the report is needed, this report is being made in accordance with 10CFR50.72(b)(3)(ii)." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-08-15
49284 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-02-06 | 2013-08-15 15:46 | 2013-08-15 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The following information was received by email: "Oregon Radiation Protection Services was notified by email on 2/20/13 at 11:28 a.m. [PDT], by Curtis Kreil, RSO, a representative of Carestream Health, Inc., of one tritium exit sign discovered missing during a 6-month radioactive material inventory check on 2/6/13. The sign was last inventoried on 8/1/12. A site-wide email alert was issued regarding the missing sign. "Exit sign details are: Manufacturer: SRB Technologies Model: Betalux E Serial Numbers: 258030 Radioactive material: H-3 Activity: Nominal 20 Ci (on 10/2/02), currently 11.2 Ci (2/20/13) "Engineers and technicians are currently aware of the location of the [remaining] exit signs and monitor their presence. The licensee added discussion information into their Radiation Safety Training document regarding the exit signs and awareness of their location to assist in timely reporting of any future issues as a corrective action." Oregon Incident: OR-13-0011 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-08-23
49283 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2013-08-07 | 2013-08-15 14:45 | 2013-08-15 | AGREEMENT STATE REPORT - VENTILATION PERFUSION LUNG SCAN ADMINISTERED INSTEAD OF CT LUNG SCAN The following event report was received from the State of Florida via facsimile: "Received notification of a medical event on 15 Aug 2013 at 10:30 am [EDT] from Bayfront Medical Center, license number 4374-1. Date of procedure was 7 Aug 2013. A patient was prescribed a CT lung scan by the physician. Technologist entered, by mistake, Ventilation Perfusion Lung Scan into the computer (9 mCi's of Xenon-133). Patient's physician was notified, patient was on a ventilator and was not able to communicate. [This incident was] assigned to the Tampa Office for investigation. No further action will be taken on this incident." Florida Incident Number: FL13-056 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-08-23
49282 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2011-11-03 | 2013-08-15 14:05 | 2013-08-15 | AGREEMENT STATE REPORT- DELIVERED PATIENT DOSE DIFFERENT THAN PRESCRIBED The following information was received by email: "Based on protocol, a dose of 120 Gy (1.79 GBq) was prescribed. Upon completion of the treatment, survey of the Nalgene waste container measured higher than expected. Ensuing calculations resulted in dose delivered to be 85 Gy (1.24 GBq); greater than 20% variation from prescribed dose. All drapes, towels, etc were surveyed with no evidence of radioactivity present, therefore assuring no contamination present. Contents of the waste container were measured separately to locate the source of residual activity. The readings indicated minimal activity in the Y -90 vial; readings of the patient delivery microcatheter were indicative of residual microspheres. The treatment protocol was followed with no variations of procedure. As is typical, 3 saline flushes were made of the catheter including several vigorous flushes to dislodge any microspheres as recommended by Nordion, the product manufacturer. No high pressure was detected at any point during infusion which would trigger the pressure valve and deliver saline in the overflow vial. There was no build up of particles in the hub of the delivery catheters as inspected throughout the procedure. Measurements over the length of the catheter revealed greatest activity in the proximal portion of the catheter with little-to-no activity in the tip. Nordion has been contacted. In the future, survey of the catheter prior to disconnecting it for disposal may help detect the build-up of particles." Oregon Incident: 11-0037 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-08-23
49281 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-08-15 11:14 | 2013-08-15 12:07 | 2013-08-15 | SAFEGUARDS EVENT - ACCESS ALLOWED PRIOR TO DISCOVERY OF UNDISCLOSED ADVERSE INFORMATION Discovered undisclosed, adverse information on an employee in training that would have resulted in denial of access if known at the time of hire. The individual's access has been suspended. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-08-15
49280 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-08-14 08:40 | 2013-08-14 12:41 | 2013-08-14 | OFFSITE NOTIFICATION DUE TO A LOW LEVEL TRITIUM SPILL "This is a non-emergency notification. "During a routine plant inspection, plant personnel discovered a leak from a pipe on plant property on Tuesday, August 13, [2013]. An isolation valve, 3WN-38, leaked causing approximately 9,900 gallons of water containing low levels of tritium (5,780 picocuries per liter) to leak onto the surrounding soil. The valve was secured and the leak stopped. Based upon the leak location and low tritium levels, there is no health or safety risk to the public or to employees on the site. There is no impact to public health and safety due to this condition. Due to NPDES requirements at 0840 EDT on August 14, a report of this condition was made to the state of [North Carolina]. The state has evaluated the event and classified the event as a spill-non-sewage (no environmental impact). "The NRC Resident Inspector has been notified." * * * UPDATE FROM JUSTIN KELLY TO JOHN SHOEMAKER AT 1644 EDT ON 8/14/13 * * * "Additional voluntary notifications have been made to state agencies in accordance with the Groundwater Protection Initiative following the guidance of NEI 07-07." The licensee has notified the NRC Resident Inspector. Notified R2DO (Musser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-08-14
49279 | -1 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2013-08-13 22:30 | 2013-08-14 12:32 | 2013-09-06 | VALVE FAILED TO CLOSE AS REQUIRED ON LOW TEMPERATURE INTERLOCK "At 2230 [PDT] on 8/13/2013, AREVA Richland Dry Conversion Operations notified AREVA Safety personnel that a low temperature interlock on one of the uranium hexafluoride (UF6) headers activated and that the valve, HV1-1054, did not close as required, and therefore the process has been shut down pending investigation. The system remains down and will remain down pending thorough investigation and appropriate corrective actions. "The low temperature interlock is not an IROFS [Item Relied on for Safety]. However, further investigation this morning determined the valve, HV1-1054, impacted the function of four IROFS, which would not have performed as required. Of these four, two were found to be used in accident sequences that only credited one additional IROFS for nuclear criticality accident sequences. In each of the cases accidental nuclear criticality remained highly unlikely due to the robustness of the remaining IROFS and the low occurrence frequency of the initiating event. "Operating with only one IROFS to protect against accidental nuclear criticality is reported within one hour of discovery under 10CFR70 Appendix A criterion (a)(5). AREVA determined that this criterion had been met at approximately 0900 [PDT, on 8/14/2013]. It is estimated that this particular process line had operated for less than 100 hours in this condition." The licensee has notified NRC Region II. * * * UPDATE AT 1526 EDT ON 9/6/13 FROM CALVIN MANNING TO PETE SNYDER * * * "Based on the following discussion, AREVA formally withdraws the notification made in NRC event report 49279 with this update. "After careful review of this plant condition, the apparent causes and the extent of condition, AREVA NP has concluded that the plant condition that precipitated the initial notification did not meet the criteria for reporting to the NRC under 10CFR70 Appendix A. This conclusion is based primarily on the fact that closure of valve HV1-1054 (for UF6 isolation) was not required to meet the safety function specified by the IROFS credited to prevent the accident sequences related to this plant condition. Specifically, the temperature triggers for IROFS 1005, 1006, and 1018 each activate both the UF6 Isolation and the Reaction Gas Shutoff interlocks. The UF6 isolation interlock causes valve HVx-1054 to close. However, UF6 isolation was not required to meet the safety function specified for IROFS 1005, 1006, and 1018. "AREVA was compliant with the performance requirements of 10CFR70.61 at all times during the condition reported to the NRC on 8/14/2013. "A more detailed write-up of this conclusion was previously provided to NRC Region II and additional information will be provided to them later today [9/6/13]." Notified R2DO (Ernstes) and NMSS (Guttmann). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2013-08-14
49278 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-08-13 | 2013-08-13 21:56 | 2013-08-13 | AGREEMENT STATE REPORT - CONTAMINATION LIMITS ON PACKAGE EXCEEDED The following Agreement State report was received via email. "[The California Department of Public Health / Radiation Health Branch was notified that Stanford University received a package containing Radium 223 from Cardinal Health in Denver, Colorado and the package indicated removable contamination of 400 DPM of technetium 99 on the package. The following information was provided: "The caller stated, that a package was received at the Nuclear Medicine Department and the package had a reading of 400 DPM which exceeds the Dept. of Transportation limits. Caller stated the package has been isolated and secured in the appropriate area and the carrier notified. Caller stated that the package will be at normal readings tomorrow. "Cardinal Health, in Denver, was notified and will investigate this issue. RHB California will report additional information." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-08-21
49277 | 0 | R&M ENGINEERING - KETCHIKAN |  |  |  |  | 2013-08-12 08:15 | 2013-08-13 20:03 | 2013-08-13 | TROXLER 3450 MOISTURE DENSITY GAUGE DAMAGED DURING ROAD CONSTRUCTION The licensee reports that a Troxler 3450 moisture density gauge was damaged at a construction site on Prince Wales Island, Alaska. The gauge had been left at the side of a road and was run over by a pickup truck. The operating handle and source rod were bent, however the gauge sources were in the safe position. The gauge was surveyed by the licensee and there is no indication of leakage or personnel exposure. The licensee has stored the gauge in a secure location until the gauge can be returned to the manufacturer for repair. The Troxler 3450 gauge is serial #540 and contains a 8 mCi Cs-137 and a 40 mCi Am-241/Be source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-08-21
49276 | 0 | PALISADES | 1 |  |  | [1] CE | 2013-08-13 11:02 | 2013-08-13 16:11 | 2013-08-13 | BOTH CONTROL ROOM VENTILATION FILTRATION TRAINS DECLARED INOPERABLE "At approximately 1102 [EDT], August 13, 2013, both control room ventilation filtration trains were declared inoperable in accordance with Technical Specification 3.7.10, Condition B, due to a control room boundary door not being fully closed. The door was unable to be closed for approximately nine minutes due to an apparent mis-operation of the door operating mechanism. The door's locking bolts fully extended causing interference between the door and door frame. The door was restored to operable status at approximately 1111 [EDT], August 13, 2013. "Technical Specification 3.7.10 allows control room boundary doors to be opened intermittently, under administrative control for preplanned activities, provided the doors can be rapidly restored to the design condition. Previous evaluations of the door not being fully closed for a limited time concluded no loss of safety function had existed. "This condition had no impact on the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-08-13
49275 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-08-13 16:00 | 2013-08-13 14:46 | 2013-08-13 | PLANNED MAINTENANCE ON TECHNICAL SUPPORT CENTER VENTILATION SYSTEM POWER SUPPLY "This ENS [event notification] is being issued in advance of planned corrective maintenance on a TSC [Technical Support Center] HVAC [Heating Ventilation Air Conditioning] power supply. "On 8/13/2013 at 1600 [EDT], the Technical Support Center ventilation system will be removed from service to perform corrective maintenance on an electrical panel that supplies power to the system. The emergency ventilation system will not be available and cannot be restored within the time period required to staff and activate the Emergency Response Organization (ERO). The work is scheduled to complete on 8/13/2013 at 1800 [EDT]. "If an emergency is declared and the TSC activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological or other conditions. The Station Emergency Director would assess habitability in accordance with station procedures. TSC relocation of personnel would be directed as required until such time that the TSC ventilation system is returned to service. "An update will be sent upon TSC HVAC restoration." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MARK ARNOSKY TO JOHN SHOEMAKER AT 2255 EDT ON 8/13/13 * * * At 2030 EDT on 8/13/13, the TSC emergency ventilation system has been restored to normal. The licensee notified the NRC Resident Inspector. Notified R1DO (Powell). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-13
49274 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-08-02 02:30 | 2013-08-13 14:22 | 2013-08-13 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the State of Oregon via email: "A Troxler portable moisture density gauge was stolen out of the back of a worker's truck around 2:30 AM [PDT] on August 2nd, 2013. The gauge was recovered by the Sherwood police within the hour and returned to worker. The gauge handle and case remained locked. The only locks breached were the locks securing the device in the back of the truck. The licensee was just informed of the theft and reported it to Oregon RPS [Radiation Protection Services] at 10:00 AM on August 13th, 2013. The licensee will conduct further investigation and develop corrective actions. This information will be reported to Oregon RPS within 30 days. "Device: Troxler 3430 SN: 38580 Sources: 9 mCi Cs-137 and 44 mCi Am-241/Be" Oregon Incident #: 13-0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-08-21
49273 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2013-03-25 | 2013-08-13 09:34 | 2013-08-13 | AGREEMENT STATE REPORT - SHUTTER STUCK ON FIXED PROCESS GAUGE The following event report was received from the State of Maine Radiation Control Program via e-mail: "Rumford Paper Company reported that the shutter on a fixed nuclear gauge (Ohmart model SH-F1-A45, serial #13520085) was stuck in the open position on 3/25/2013. The gauge contained a 370 MBq (10 mCi) Cs-137 source (model A-2100, serial #3133CM). Restrictions were put into place so no personnel could enter the vessel until repairs could be completed. The manufacturer was contacted and performed the necessary repairs and the shutter now operates properly." Maine Report Number: ME130002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2013-08-21
49272 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-08-13 02:25 | 2013-08-13 07:41 | 2013-08-15 | TECHNICAL SUPPORT CENTER VENTILATION FAILURE "A condition is being reported per Technical Requirements Manual 13.13.1 emergency response facilities action B.2. The functionality of the Technical Support Center (TSC) has been lost due to a failure to start of the TSC HVAC unit. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with high priority. The NRC Resident Inspector has been notified." * * * UPDATE FROM NAVEEN KOTEEL TO HOWIE CROUCH AT 0744 EDT ON 8/15/13 * * * The Technical Support Center HVAC system was returned to service at 1100 EDT on August 14, 2013. The licensee has notified the NRC Resident Inspector. Notified R2DO (Musser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-13
49270 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-08-12 15:50 | 2013-08-12 20:56 | 2013-08-16 | TECHNICAL SUPPORT CENTER (TSC) VENTILATION OUT OF SERVICE DUE TO DISCOVERED CONDITION "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. There is no impact to public health and safety due to this condition. "On August 12, 2013 at 1550 [EDT], during routine testing of the HVAC [Heating Ventilation Air Conditioning] system, the TSC Emergency filtration Fan, MUF-1, was observed to have high vibration levels. Maintenance is working to determine the cause of the high vibrations and to make necessary repairs. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. If the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions, the Site Emergency Coordinator - TSC will relocate the TSC staff to an alternate TSC in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the condition and the possible need to respond to or relocate to an alternate TSC during an emergency. "An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE ON 8/16/13 AT 2126 EDT FROM TIM ENGLISH TO DONG PARK * * * "Technical Support Center (TSC) ventilation has been returned to service on August 16, 2013 at 2100 [EDT] following bearing replacement on TSC Emergency Make-up Fan, MUF-1. Post maintenance testing has been completed and the emergency response facility is functional." The licensee has notified the NRC Resident Inspector. Notified R2DO (Musser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-12
49269 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2013-08-07 | 2013-08-12 17:11 | 2013-08-20 | AGREEMENT STATE - PATIENT RECEIVED 20% LOWER THAN I-131 PRESCRIBED DOSE The following Georgia Agreement State report was received via email. "Event Description: Patient was scheduled for an I-131 prescribed dose of 100-150mCi for the treatment of Thyroid Carcinoma. The patient instead was administered a dose that deviated 20% lower than the prescribed dose. This incident was reported to the [Georgia] State per Rule 391-3-17.05(115)(a)1.(i): 'A dose that differs from the prescribed dose by more than 0.05 Sv (5 rem) effective dose equivalent, 0.5 Sv (50 rem) to an organ or tissue, or 0.5 Sv (50 rem) shallow dose equivalent to the skin; and either (i) The total dose delivered differs from the prescribed dose by 20 percent or more.'" The State will provide the corrective action information when provided by the licensee. GA State Report ID: CTS 71850 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM TRAVIS CARTOSKI TO HOWIE CROUCH VIA EMAIL ON 8/20/13 AT 1240 EDT * * * "A sodium iodine I-131 thyroid ablation treatment was ordered as a NaI I-131 whole body scan resulting in a patient receiving a diagnostic dose of 5 mCi of NaI (I-131) instead of the therapeutic dose of 50 mCi of NaI (I-131). "Both the referring physician and the patient were also informed of the misadministration of the 5 mCi I-131 dose for the whole body scan on August 7, 2013 in light of the confirmed order for an I-131 thyroid ablation. The order verification process was reviewed with all involved staff members and an extensive review of the process was begun. "Nuclear Medicine, like all diagnostic services, requires verification of the order for services. This verification must be in the form of a written order or an electronic authenticated order. On August 1, 2013 Piedmont Hospital Atlanta implemented EPIC, a new electronic medical record (EMR). The orders verification process changed a bit, because Piedmont Physician Groups could place an order within the EPIC environment (EPIC Physicians) and have them electronically authenticated, with e-signature and a time stamp. Physicians not in the EPIC environment (non-EPIC Physicians) could still schedule services through scheduling by providing a written order. Once scheduling had received a written order, the ancillary orders process would produce an order that looked just like the order produced by an EPIC physician, but the chart would have a paper clip to signify that it was a non-EPIC Physician order. "During the first week of the EPIC implementation, many of the orders that were transcribed by the scheduling services department did not have the attachment of the original written order. This information came to light during the first few days of go-live but not all end users were informed on the issue. In this particular case, the patient's order was requested by a non-EPIC physician, as an I-131 whole body scan. The order was transcribed by scheduling , and as of August 7, 2013, the original order was not scanned into the chart. The order in the chart appeared to be an EPIC Physician order. Based on the information known at the time, the order for an I-131 whole body scan was verified and the patient was dosed and instructed to return on Friday August 9, 2013 for imaging. "On August 8, 2013, a copy of the original order was scanned into the patient's record. The order contained more detailed information concerning the reason for the referral to nuclear medicine. This information would prove to be vital in determining the actual course of treatment requested by the referring physician. "On Friday August 9, 2013, the patient returned for the whole body scan, but due to a downed system at the hospital the patient was referred to the Piedmont West Imaging Center to complete their test. While preparing the report template in PACs (Name removed), noticed that the patients chart had a paper clip icon but the documentation that she had received from the hospital Nuclear Medicine department only had an EPIC Physician order. (Name removed) opened the original scanned order for an I-131 whole body scan and discovered that within the comments section of the note that the Authorized User was referring the patient for an I-131 thyroid ablation. The office was contacted, and the order for an I-131 thyroid ablation was confirmed. (Name Removed), contacted the RSO to inform him of the events leading up to this misadministration. "The actions taken to prevent a future reoccurrence of a similar event include: -Training on the orders verification process in EPIC for all Nuclear Medicine staff members -Defining the difference between an EPIC Physician order and a non-EPIC Physician order -All non-EPIC Physician orders must have an attached copy of the original order or a call must be placed to the provider's office requesting a copy of the order if the patient does not have an original copy." Notified R1DO (Schmidt) and FSME (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2013-08-20
49268 | 0 | NYC OFFICE OF RADIOLOGICAL HEALTH |  |  |  |  | 2013-01-31 12:38 | 2013-08-12 15:05 | 2013-08-12 | AGREEMENT STATE - EQUIPMENT FAILURE RESULTED IN NO PRESCRIBED DOSE DELIVERED TO PATIENT The following report was received from New York City via email. "Summary: Zero percent of prescribed dose delivered due to patient catheter occlusion. "Details of the incident: On January 31, 2013 a male patient, 83 years of age, was scheduled to receive Theraspheres treatment in Interventional Radiology. "The patient has a history of hepatitis C and hepatocellular carcinoma (HCC) with multiple HCC tumors in the liver, progressive in spite of previous chemoembolization and radiofrequency ablation therapy, was referred by oncology for Yttrium-90 microspheres therapy. At the time of a nuclear medicine consultation of December 21, 2012, it was determined that the patient is a candidate for Yttrium-90 (Y90) Therasphere therapy, the preferred radioembolization agent (device) for HCC. A lung shunt fraction of 3.3% (predetermined), and a desired dosimetry of 120 Gray, the Y90 Therasphere activity of 3.83 GBq was ordered for the patient. "Interventional Radiology Physicians placed a 0.021 inch microcatheter, inside of a Sarah 5 Fr. Radial catheter, via the left radial artery, into the right hepatic artery, into the same position as during the January 11, 2013 diagnostic study. When the catheter was in place, a Y90 Therasphere administration kit was brought into position for dose delivery. The administration kit was prepared by the Authorized User according to standard operating procedure, using a manufacturer's checklist. The delivery line was connected to the angiocatheter in the patient's arm. Just prior to that, the catheter was first flushed with IV contrast to ensure position, followed by flushing with normal saline, and then connected to the Therasphere kit infusion line. "The infusion was started at 12:18 PM [EST] by Interventional Radiology Physician and the Authorized User, according to standard protocol, with sufficient pressure applied to result in periodic drops of saline dripping into the pressure relief bottle. At the end of the first 20cc bolus of saline, the reading on the radiation meter outside of the container failed to drop to 0.0 as usual. This was an indication that most of the radioactivity was still present in the vial. There were 10 more attempts to infuse the activity. In spite of additional attempts, only some of the Theraspheres moved forward into the catheter. The infusion attempt was terminated at 12:38 PM. At that point, the catheter was disconnected, taking care not to spill any contents inside. Towels were positioned under the catheter opening, a syringe was connected directly to the catheter, and an attempt was made to flush the catheter, but it was not possible, as it was blocked. "At this point the catheter was withdrawn from the patient, and was placed together with the connecting line, dose vial and infusion kit container into a plastic bag for containment. The Interventional Radiology Physicians and the Authorized User underwent the standard survey procedure for removal contamination, the outer gloves were surveyed. Indicating some activity. The gloves were removed and placed into the administration box. The booties were removed and the principles stepped away after testing negative for contamination. The absorbent lining, which was wet from the infusion saline over-flow and box platform supporting the infusion kit, was also placed into a plastic bag. The floor absorbent mat was rolled up and also placed in a plastic bag, and replaced with a new floor mat to allow patient transfer onto a stretcher. The patient sterile covering was also rolled up and placed in a plastic bag. Both the Nuclear Pharmacist and the Nuclear Medicine Technologist were surveyed and found free of contamination. Once the plastic bags with the infusion materials were removed from the immediate area and the patient taken for imaging in nuclear medicine, the procedure room (Number 1) was surveyed by the Radiation Safety Office staff and was declared free of removable contamination and cleared for routine clinical use. "The patient underwent a whole body scan in Nuclear Medicine, but was found to have no radioactivity in his body. A survey of all the plastic bags with the materials involved in the procedure, revealed that all the activity was contained in one bag (containing the catheter, administration set and dose vial), independently documenting that the patient received no Y90 activity. "Corrective action taken by the facility: Facility is working with the manufacturer to determine the cause of the incident. Corrective action will not be developed until the manufacturer determines what was the cause of the failure to deliver the prescribed dose. "How was it discovered: The physician discovered the event when the reading on the radiation dosimeter outside of the delivery system failed to drop to 0.0 mR/hr as usual. "Causes/Contributing Factors: Equipment malfunction. "Equipment used: NORDION TheraSphere Administration Accessory Kit Part #: K125914-001 -RADOS Model: RAD 60R Personal Dosimeter -Fluke Victoreen Ion Chamber Model: 451B-RYR-SS -0.021" Microcatheter and a Sarah 5 Fr. Radial Catheter "RSO's review summarization: The Radiation Safety Office was notified on January 31, 2013 at 12:40 PM that an incident had just occurred in the Interventional Radiology suite which may have resulted in contamination. The RSO staff immediately responded to the location and was informed of the details of the event by the Authorized User. The Authorized User had already collected all of the equipment associated with the Y-90 infusion kit in a large plastic bag which was on a cart. The RSO survey of this cart indicated that the entire dose activity was still within the infusion kit and associated delivery tubing. Thorough survey of the patient, floor, table, hands and feet of staff (who had remained in the room waiting for RSO arrival) did not find any contamination. The whole body scan of the patient confirmed that no radioactive material was injected into the patient. The RSO immediately informed the local regulatory authority by phone followed by a written report of the incident. The Authorized User contacted the manufacturer of the radiopharmaceutical and infusion kit and requested an engineer to come to the medical center to determine the cause of the incident. The referring physician also was informed. On February 6, 2013 an inspector from the local regulatory authority visited the medical center and reviewed the incident. At the conclusion of this meeting the inspector collected all the documentation including the Standard Operating Procedure and training materials to investigate further to see if this incident was a Medical Event since 0% of the prescribed dose had been administered. The inspector also requested that a date be scheduled where they could witness kit preparation as well as an actual patient procedure. The engineer from the manufacturer was in contact with the Authorized User and agreed to come to the medical center to examine the used equipment associated with the Y -90 infusion kit to reveal the cause of the incident." The patient and referring physician have been notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-08-20
49267 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-08-12 13:35 | 2013-08-12 14:56 | 2013-08-12 | LOSS OF ACCIDENT ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE ON THE PLANT STACK RADIATION MONITOR The licensee will be removing the station stack radiation monitor, RM-8169, from service for planned maintenance. This constitutes a loss of assessment capability under 10CFR50.72(b)(3)(xiii). The licensee notified the State of Connecticut, the city of Waterford and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-12
49266 | 0 | NYC OFFICE OF RADIOLOGICAL HEALTH |  |  |  |  | 2012-09-20 | 2013-08-12 13:54 | 2013-08-12 | AGREEMENT STATE - PATIENT BEING TREATED WITH Y-90 THERASPHERES RECEIVED ONLY 9.5% OF A TOTAL DOSE The following report was received from New York City via email. "Summary: Patient being treated with Y-90 Theraspheres received only 9.5% of a total dose of Y-90. The rest remained in the tubing. "Details of the incident: A patient [at the NYC Mount Sinai Medical Center] was being treated with Y-90 Theraspheres. The target organ was the liver. Due to the need to access the liver via the radial artery in the arm, the angiocatheter was too short to connect to the delivery apparatus directly, thus requiring an extension tubing. The entire contents of the dose vial was emptied and flushed 4 times. It was discovered by the radiochemist [after the patient's treatment] that only 9.5% of the total dose was delivered. The rest remained in the extension tubing. [The prescribed dose was 120 Gy and the delivered dose was 11.4 Gy]. "Corrective action taken by the facility: More time will be taken to reposition the patient proximal to the delivery system. Also, the use of extension tubing will be avoided if possible. Policy and procedures will be updated to include when the use of extension tubing is allowed. "Causes/Contributing Factors: Inadequate policy and procedures. "RSO's review summarization: The failure to administer the correct dose to the patient was due to the addition of extension tubing. Because of the additional 40cm of IV tubing, which was used to bridge the distance between the Y-90 delivery system and the radial catheter, the intended dose remained lodged inside the extension. The additional flush used was not enough to push the dose through to the target." The dose deviation was greater than 50%, and no additional patient testing or extended hospital stay was required. The patient and referring physician have been notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-08-20
49265 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2013-08-12 08:59 | 2013-08-12 09:23 | 2013-08-20 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "This condition does not affect the health and safely of the public or the operation of the facility. "At 0859 EDT on August 12, 2013, pre-planned maintenance commenced which affects the Technical Support Center (TSC) ventilation. The scope of the maintenance is to replace the TSC ventilation charcoal filters and sampling canisters. This maintenance is currently scheduled to be completed by August 20, 2013. "TSC emergency functionality during a radiation release event requires TSC ventilation be maintained. The actual TSC ventilation emergency function for iodine removal will be lost for the duration of the pre-planned maintenance. If an emergency should occur and a radioactive release occurs, the ventilation system will not provide iodine removal capability. "If an emergency is declared and the TSC facility activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological or other conditions. If relocation of the TSC staff becomes necessary, the staff will be directed to relocate to the alternate TSC location. The alternate TSC has been verified to have electrical power and communication capability. The Technical Support Center Directors have been notified. "This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been notified." * * * UPDATE FROM KEN CROW TO PETE SNYDER AT 1749 EDT ON 8/20/13 * * * The TSC ventilation has been returned to service as of 1742 EDT on 8/20/13. Notified R1DO (Schmidt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-12
49264 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-07-02 | 2013-08-11 23:26 | 2013-08-11 | AGREEMENT STATE REPORT - SEVEN STOLEN TRITIUM EXITS SIGNS The following information was obtained from the State of California via email: The California Department of Public Health received the following information from the licensee: "Please be advised that during a survey of the location seven missing exit signs were discovered in the exit corridors. "Having been stolen prior to site survey we are unable to provide the specific manufacturer or serial number of the stolen units. A police report was filed (case: 13705804) within the jurisdiction of San Diego with the San Diego Police Department. The state of California has also been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-08-19
49263 | -1 | SUSQUEHANNA |  |  |  | ISFSI | 2013-08-10 04:30 | 2013-08-10 10:58 | 2013-10-03 | DEGRADED NEUTRON SHIELDING FOR A SPENT FUEL CASK "PPL Susquehanna, LLC became aware of a reduction in the effectiveness of a spent fuel confinement system at 0430 [EDT] on Saturday August 10, 2013. One of the safety barriers in a spent fuel cask is the water filled volume of the cask which provides neutron shielding. This volume is normally filled with approximately 670 gal of demineralized water. It has been determined that the neutron shielding volume was not completely filled. The cask neutron shield volume is currently being filled. The loaded spent fuel canister is currently located in the reactor building on the refuel floor and has been located there for the duration of the event. Investigation is currently in progress concerning personnel radiation exposure. The lack of neutron shielding represents a significant reduction in the effectiveness of a spent fuel storage cask confinement system which is an 8 hour reportable condition under 10CFR72.75(c)(2). This also represents a dry fuel storage safety system that was disabled or failed to function which is a 24 hour reportable condition under 10CFR72.75(d)(1)." The cask was a TransNuclear NUHOMS-61BTH. Personnel on the refuel floor were equipped with neutron dosimetry. The licensee notified the NRC Resident Inspector and will notify the Commonwealth of Pennsylvania. * * * RETRACTION AT 1609 EDT ON 10/3/2013 FROM DOUG LAMARCA TO MARK ABRAMOVITZ * * * "At the time the original ENS notification was made, PPL Susquehanna, LLC had determined that a significant reduction in the effectiveness of a spent fuel storage confinement system had occurred, and that spent fuel equipment important to safety was disabled or failed to function as designed. This conclusion was reached because a loaded dry fuel storage transfer cask's neutron water shield was found partially drained down. "Subsequent to this event, an investigation concluded that the identified condition is not reportable in accordance with 10 CFR 72.75(c)(2) or 10 CFR 72.75(d)(1). Transnuclear's Final Safety Analysis Report (FSAR), Chapter K.7 defines the 61BT dry fuel storage 'confinement system' as those components which make up the dry shielded cask (DSC) and not the transfer cask. Therefore, the transfer cask neutron shield is not part of the confinement system and the reporting requirements of 10 CFR 72.75(c)(2) do not apply. In addition, Transnuclear FSAR drawing number NUH-03-8002-SAR, Rev. 8, Sheet 1 'General License NUHOMSr ISFSI Onsite Transfer Cask Inner & Outer Shell Assembly' defines the neutron shield components as 'not important to safety.' Therefore, the TC neutron shield is not part of the dry fuel storage safety system and the reporting requirements of 10 CFR 72.75(d)(1) do not apply.'" No personnel exposures exceeded regulatory limits. The licensee notified the NRC Resident Inspector and will notify the state. Notified the R1DO (Joustra). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SPENT FUEL, HLW OR RX-REL GTCC RED. EFECT | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [8 empty] | NON EMERGENCY | 1 | PA | ISF |  | 72.75(c )(2) | 72.75(d)(1) |  |  | 0 | 2013-08-10
49262 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2013-08-10 07:11 | 2013-08-10 10:38 | 2013-08-10 | OFFSITE NOTIFICATION DUE TO INADVERTENT SINGLE EMERGENCY SIREN ACTIVATION "Calvert Cliffs was notified at 0711 [EDT] by Calvert Control Center that a siren in the Calvert County Area was activated. [It was] determined to be Siren C15 on Lloyd Bowen Road. "Per CNG-NL-1.01-1004 this is a verbal report to Calvert Control Center. "This event is reportable as a 4-hour non-emergency notification [under] 10CFR50.72(b)(2)(xi) as 'Any event resulting in notification to other government agencies that has or will be made.'" The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-08-10
49261 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-08-09 20:28 | 2013-08-10 01:21 | 2013-09-10 | INOPERABLE CONTROL ROOM ENVELOPE "In 2010, Control Room Envelope testing was conducted to satisfy SR 3.7.10.5 (this surveillance testing is required each 6 years). At that time, as a prerequisite, the surveillance procedure contained a step to add water to two floor drain loop seals that penetrated the Control Room Envelope; this practice was determined to be unacceptable preconditioning. Because the 2010 surveillance test was the first performance of this surveillance, the unacceptable preconditioning resulted in the following: a never-performed surveillance, failure to meet the associated surveillance requirement, and an inoperable Control Room Envelope. At 2028 CDT the station entered LCO 3.7.10, Condition B. "The station has taken action to periodically add water to the loop seals; this practice validates the loop seals will remain full of water. This action ensures, through Engineering judgment, that the loop seals will perform their function and the Control Room Envelope will provide adequate protection to the plant operators. "The NRC Resident Inspector was notified." The floor drains are located inside the control room envelope near the control room chillers. Prior to this report, filling the loop seal was performed sporadically. The loop seal is now filled daily. * * * UPDATE FROM STEVEN SKOYEN TO PETE SNYDER AT 2019 EDT ON 9/10/13 * * * "On 9/10/13, the Tracer Gas Test of Control Room failed to meet its acceptance criteria for the surveillance test. The failure was due to three (3) doors with minor seal leaks and/or test uncertainty. The station is evaluating door repairs and test uncertainty. "The actions for the test failure to offset the consequences of the inoperable Control Room Envelope have been modified to protect the operators with the use of SCBA's and Potassium Iodine (KI) in the event of a DBA. "The NRC Resident Inspector was notified." The R3DO (Lipa) was notified. | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-08-10
49260 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-08-09 21:19 | 2013-08-09 22:27 | 2013-08-09 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL The loss of a non-vital 480v bus resulted in a feedwater transient that caused steam generator water level to lower below the automatic reactor trip setpoint. The reactor trip and plant response was uncomplicated with all rods being inserted into the core. The auxiliary feedwater system automatically actuated and is currently being to used to feed the steam generators. Decay heat is being removed via the steam dumps to the condenser. No relief valves or safeties lifted during the transient. The plant is currently stable in Mode 3 at normal operating pressure and temperature and is in its normal shutdown electrical lineup. There was no impact on Unit 2 which is currently operating at 100% power. The licensee has notified state and local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-08-09
49259 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-08-09 10:00 | 2013-08-09 17:01 | 2013-08-09 | RADIATION MONITOR OUT OF SERVICE "During the performance of SP [Surveillance Procedure] 1027.2A, NMC Radiation Monitor Train A Calibration, Radiation Monitor R-21, Circulating Water Discharge Radiation Detector failed the source test point three times and was removed from service. "R-21 has an emergency response function to provide indication of gaseous or liquid effluent release to the environment. This monitor has no compensatory measure that will allow timely classification of two NUE [Notification of Unusual Event] and Alert classifications when out of service. "This is a priority 1 activity to repair the monitor. The repair activity is continuous and is in progress. "There are not radioactive leaks that impact the Circulating Water System. "The NRC Resident Inspector was notified." | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-09
49258 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-08-09 13:00 | 2013-08-09 16:20 | 2013-08-09 | STORAGE RACKS DETERMINED TO BE IN AN UNANALYZED CONDITION EVENT DESCRIPTION: "At B&W's NOG-L [Nuclear Operations Group - Lynchburg] facilities, scrap and waste material is generated during fuel bearing operations. Certain streams are collected in favorable volume less than or equal to 2.5 liter containers and eventually transferred to the Drum Count Area for U-235 assay. Because the U-235 content of such containers is not known until they have been assayed, they are referred to as 'unknowns' and are subject to a bulk weight limit. These containers are limited to a maximum of 7,000 grams net weight (approximately 15 pounds). The unknowns are stored on designated less than or equal to 2.5 liter container storage racks. "The construction of the storage racks controls the spacing between storage locations and the distance from the floor. The racks' materials of construction are credited as a fixed neutron poison. Some of the unknown racks are fitted with an additional poison plate which allows the rack-to-rack spacing to be reduced. "On August 9, 2013, at approximately 1:00 p.m., a contract Nuclear Criticality Safety (NCS) engineer working with B&W's NCS staff identified a safety concern. While working to consolidate information in several Safety Analysis Reports, it was determined that the poisoned less than or equal to 2.5 liter storage racks fitted with a horizontal poison plate were improperly analyzed. EVALUATION OF THE EVENT: "The NCS evaluation of the poisoned less than or equal to 2.5 liter storage racks fitted with a horizontal poison plate was completed in October of 2000. The analysis was based on an evaluation of a poisoned transport cart completed earlier the same year. However, a review by the B&W NCS staff indicated the conclusions of this earlier analysis were not properly applied to the analysis of the poisoned less than or equal to 2.5 liter storage racks fitted with a horizontal poison plate. The racks were improperly analyzed. "The requirement of 10 CFR 70.61 (d) states in part: '...the risk of nuclear criticality accidents must be limited by assuring that under normal and credible abnormal conditions, all nuclear processes are subcritical, including use of an approved margin of subcriticality for safety.' "Further evaluation of the poisoned less than or equal to 2.5 liter storage racks fitted with a horizontal poison plate indicated that under optimal moderation the keff exceeds the safety limit of 0.95 in NRC License SNM-42. Therefore the performance requirement of 10 CFR 70.61 (d) was not maintained. NOTIFICATION REQUIREMENTS: "B&W is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1) - 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61.' "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. A portion of the storage locations in the poisoned less than or equal to 2.5 liter storage racks fitted with a horizontal poison plate were removed from service. This action was taken to restore compliance with the performance requirements of 10 CFR 70.61. STATUS OF CORRECTIVE ACTIONS: "An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2013-08-19
49257 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2013-08-08 14:30 | 2013-08-09 14:29 | 2013-08-12 | TECHNICAL SPECIFICATION VIOLATION DURING CORE RELOAD While the reactor was shut down for planned maintenance, the licensee was performing a core reload in accordance with procedure. This procedure requires control rods elements to be withdrawn to get a count rate. As expected, the reactor became critical at some point. It was noted on 8/8/13 that this criticality was a violation of Technical Specification (TS) 3.1.3 which prohibits operating the reactor with any grid position empty. This procedure has been used multiple times in the past. A core reload is performed approximately every 4 years. The licensee plans on either modifying their procedure or TS to prevent this in the future. * * * UPDATE FROM SEAN O'KELLY TO HOWIE CROUCH AT 1624 EDT ON 8/12/13 * * * Further investigation determined that two other technical specifications were violated during the core reload experiment being conducted. Technical specification 3.3.1(1) requires reactor water level to be no more than 25" below the overflow standpipe during critical operations. This TS was violated because the experiment was being conducted with the water level at refueling level which is lower than 25" below the standpipe and the reactor became critical, as expected. Technical specification 3.9.2.1 prohibits critical operation until all fuel elements handled are locked into their grid positions. By the very nature of the experiment, this TS was violated. The licensee will be notifying their NRC Project Manager. Notified NRR (Yin, Adams, Isaacs). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | MD | NPR | [5 empty] | 0 | 2013-08-09
49256 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-08-09 11:00 | 2013-08-09 14:49 | 2013-08-09 | SAFEGUARDS REPORT - SECURITY OFFICER FAILED TO MEET PREEMPTION AUTHORITY REQUIREMENTS A licensee Security Officer failed to meet preemption authority requirements specified under EA-13-092, an order designating an interim class of NRC-licensed facility. Required actions were taken upon discovery of adverse information. See similar EN #49248. The licensee has notified R1 (Cherubini) and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-08-09
49255 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-08-08 23:00 | 2013-08-09 10:40 | 2013-08-09 | AGREEMENT STATE REPORT - FIRE DAMAGES A TROXLER MOISTURE DENSITY GAUGE The following report was received via fax: "An employee of GET [Geotechnical Environmental Testing] went home with a Troxler 3430 portable gauge in the bed of his work truck. The employee mishandled charcoal embers after cooking dinner on a grill, which caused the bed of the truck to start on fire. A neighbor noticed the fire and called 911 . When the fire trucks arrived, the employee discovered it was his truck on fire and talked with the VA Beach fire personnel. He stated that a portable gauge containing radioactive material was in the bed of the truck. The VA Beach hazmat team was contacted and arrived on scene. The fire was extinguished and surveys were performed by the hazmat team indicating 1 mR/hr, a normal. reading for a secured gauge. The GET employee began to contact management regarding the situation. The VA Beach GET RSO was on vacation so the North Carolina GET RSO responded and also performed surveys when he arrived. Survey readings indicated the sources were in their shielded position. The RSO was able to package the damaged gauge into another transportation case and return it to the VA Beach office. GET has contacted Troxler and has sent a swab for leak test analysis. The gauge will be returned to Troxler after verification of the sources not leaking. There is no threat to public health or safety from this event. The Virginia RMP [Radiological Materials Program] will be performing an investigation and inspection. "Media attention: Yes, two local news stations ran a story this morning on the incident." VA Report ID: VA-13-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-08-19
49254 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-02-09 | 2013-08-09 10:26 | 2013-08-09 | AGREEMENT STATE REPORT - SHUTTER PROBLEM ON A GAMMA GAUGE The following report was received via e-mail from the State of Arkansas Radiation Control Program: "During an on-site inspection on August 8, 2013, the licensee stated that a VEGA Americas Corporation model A-2102 gamma gauge shutter was vibrating shut. The source rotor and top plate was replaced on February 9, 2011. The gauge is serial number 6757GK and contains 10 mCi of Cesium-137. "The licensee indicated the gauge was locked out and unused until it was repaired. "In accordance with RH-1502.f.2. (10 CFR 30.50(b)(2)) the stuck shutter should have been reported to the State of Arkansas within 24 hours. "The State of Arkansas is awaiting a written report from the licensee. " Arkansas Report: ARK-2013-005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2013-08-19
49253 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-08-08 19:53 | 2013-08-09 08:21 | 2013-08-09 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM A contractor supervisor tested positive for alcohol on a follow-up fitness for duty screening. The individual's construction site access was revoked. The Unit 2/3 Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2013-08-09
49252 | 0 | WATERFORD | 3 |  |  | [3] CE | 2013-08-05 14:30 | 2013-08-08 19:52 | 2013-08-08 | AN OFF-DUTY LICENSED OPERATOR WAS ARRESTED FOR DRIVING UNDER THE INFLUENCE A off-duty licensed operator was arrested while driving a vehicle under the influence of alcohol. This was determined to violate the Waterford Fitness for Duty program. The individual has been administratively removed from performing licensed duties pending investigation. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2013-08-08
49251 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-07-15 | 2013-08-08 16:06 | 2013-08-08 | AGREEMENT STATE REPORT - EXTREMITY DOSE EXCEEDS LIMIT The following information was obtained from the State of New York via facsimile: "On 08/07/2013, the licensee called to report an overexposure of an individual as measured with an extremity monitoring device (ring badge). The licensee had been notified by the processor on the morning of 08/07/13 in regard to the 242 rem shallow extremity dose. The monitoring period for the ring badge is one week, and the whole body monitors are exchanged on a monthly basis. The affected individual is a male production technologist whose duties include cyclotron operations. The RSO and consulting health physicist are investigating and NYS DOH [New York State Department of Health] will perform an onsite review. The licensee has reassigned the technologist to non-radiological duties, sent the individual's whole body badge via overnight service for an emergency read and has requested the badge vendor to perform any additional analysis of the ring badge that may provide additional information. This event summary will be updated after the results of the licensee's and DOH's investigations are available." New York Event Number: NY-13-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-08-16
49250 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-08-05 10:00 | 2013-08-08 11:09 | 2013-08-08 | AGREEMENT STATE REPORT - ELEVATED AIRBORNE URANIUM LEVELS DUE TO EQUIPMENT MALFUNCTION The following report was received from the State of Tennessee Division of Radiological Health via e-mail: "Tennessee's Division of Radiological Health was notified on Wednesday August 7, 2013 by the RSO from Aerojet Ordnance Tennessee, regarding the failure of a primary ventilation system. On August 5, 2013 at 10:00 AM, an employee at the Deflash Station observed smoke outside the operation booth while grinding burrs off radiography camera castings. A supervisor was notified and investigation showed the ventilation system was working, but the belt connecting the pump and fan was broken. Operations were suspended and personnel evacuated. "The belt was replaced on the pumps and the ventilation system was up and operational by 10:30 AM. Event resulted in elevated airborne uranium concentrations. All personnel in the building submitted urinalysis. Workers at the Deflash station were wearing respiratory protection during time of event as part of standard procedures. Area air samplers along with environmental air samplers were pulled and analyzed; initial results identified no concerns of elevated concentrations. "The State will follow-up and keep NRC informed of the status of our investigation." Tennessee Report Number:TN-13-134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-08-16
49249 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-08-08 03:05 | 2013-08-08 03:15 | 2013-08-10 | ALERT DECLARED DUE TO A SWITCHGEAR EXPLOSION THAT SUPPLIES SAFE SHUTDOWN EQUIPMENT The licensee reported that there was an explosion in a non-safety related electrical bus (Bus 1E2). The bus is designated as a safe shut down bus. The licensee has classified this event as an Alert based on an EAL entry condition of "an explosion of sufficient force to damage permanent structures or equipment within the Protected Area." The licensee is still investigating what loads come off this bus but no safety-related loads have been identified at this time. The plant is currently stable at 92% power. Power was reduced due to the loss of moisture separator reheaters on the secondary side as a result of this event. There is no ongoing fire as a result of the bus explosion. No personnel were injured. No damage to other equipment has been identified at this time. The licensee has notified state and local authorities and the NRC Resident Inspector. Notified DHS SWO, DOE, FEMA, HHS, DHS NICC, USDA, EPA, FDA and NuclearSSA via email. NRC PAO (Brenner) notified. * * * UPDATE AT 0404 EDT ON 8/8/13 FROM TYLER HALYE TO MARK ABRAMOVITZ * * * "Auxiliary bus 1E2 (safe shutdown equipment bus) is de-energized due to the explosion. The Alert was declared due to the explosion affecting safe shutdown equipment." The licensee also noted that the event was initially classified as an Unusual Event at 0234 EDT and then upgraded to an Alert classification at 0305 EDT when the bus was determined to supply safe shutdown equipment. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0453 EDT ON 8/8/13 FROM TYLER HALYE TO MARK ABRAMOVITZ * * * No offsite assistance was requested during this event. The licensee verified that there was no fire. It was noted that the licensee is in Technical Specification Action Statement 3.8.1.1 for the "B" Emergency Diesel Generator being out of service. The EDG is out of service due to loss of power to the "C" and "D" air compressors. The licensee was uncertain if the loss of these air compressors was related to the event. The licensee has notified the NRC Resident Inspector. R2DO (Shaeffer) and NRR EO (Hiland) notified. * * * UPDATE AT 0546 EDT ON 8/8/13 FROM SHANNON JONES TO MARK ABRAMOVITZ * * * The licensee terminated the Alert declaration at 0533 EDT based upon no fire at Bus 1E2 and verification that Bus 1E2 is de-energized and disconnected from all electrical systems. The licensee remains at 92% power. The only noted safety related equipment that was impacted is the "1B" Emergency Diesel Generator which has been declared inoperable due to loss of power to associated air compressors "1C-SB" and "1D-SB." The licensee has notified the NRC Resident Inspector. R2DO (Shaeffer), NRR EO (Hiland) and IRD MOC (Morris) notified. Notified DHS SWO, DOE, FEMA, HHS, DHS NICC, USDA, EPA, FDA and NuclearSSA via email. NRC PAO (Brenner) notified. * * * UPDATE FROM TIM ENGLISH TO HOWIE CROUCH AT 1347 EDT ON 8/10/13 * * * "It has been determined that operability of the 1B Emergency Diesel Generator (EDG) was not affected by the damage to 480 volt auxiliary bus 1E2. The 1C and 1D starting air compressors for 1B EDG did not lose power and thus the 1B EDG was operable. "The NRC Resident Inspector has been notified." Notified R2DO (Shaeffer). | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-08-08
49248 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-08-06 15:45 | 2013-08-07 16:08 | 2013-08-07 | SAFEGUARDS REPORT - ONE SECURITY OFFICER FAILED TO MEET PREEMPTION AUTHORITY REQUIREMENTS A licensee Security Officer failed to meet preemption authority requirements specified under EA-13-092, an order designating an interim class of NRC-licensed facility. Required actions were taken upon discovery of adverse information. The licensee has notified RI (Dimitriadis, Cherubini) and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-08-07
49247 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-08-07 01:00 | 2013-08-07 09:05 | 2013-08-07 | LOSS OF POWER TO EMERGENCY SIRENS DUE TO SEVERE WEATHER "On August 7, 2013, at 0345 [CDT], Kewaunee Power Station was notified that a loss of alert sirens impacting greater than 50% of the Emergency Planning Zone population are non-functional due to a loss of power. The sirens are used to provide a public prompt notification. The sirens lost are those that Point Beach Nuclear Power Plant takes primary responsibility. Power was lost to them during a severe thunderstorm and the expected out of service time is unknown at this time. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." See related EN #49246 * * * UPDATE FROM SCOTT CIESLEWICZ TO PETE SNYDER AT 1652 EDT ON 8/7/13 * * * Most emergency sirens have been returned to service such that the lost coverage is now only 24%. The licensee notified the NRC Resident Inspector. Notified R3DO (Lara). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-07
49246 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-08-07 01:00 | 2013-08-07 09:01 | 2013-08-07 | LOSS OF POWER TO EMERGENCY SIRENS AND POWER TO EMERGENCY OPERATIONS FACILITY DUE TO SEVERE WEATHER "At approximately 0100 (CDT) on 7 August, 2013, severe thunderstorms and high winds in the area resulted in a loss of power to the Point Beach Nuclear Plant (PBNP) Emergency Operations Facility (EOF) and to Alert and Notification System (ANS) sirens. Loss of ANS sirens resulted in a loss of greater than 50% of the Emergency Planning Zone (EPZ) population coverage [14 out of 22 lost]. Note: PBNP has installed a new siren system that is currently in operational acceptance testing and remained fully functional on backup battery power. "During the loss of power to the EOF, station personnel verified that power remained available to the Alternate Emergency Operations Facility (AEOF). At approximately 0545 CDT, station personnel verified that power to the EOF was restored. Efforts are ongoing to restore power to sirens." The licensee has notified State and local authorities and the NRC Resident Inspector. See related EN #49247. * * * UPDATE FROM JERRY STRHARSKY TO HOWIE CROUCH AT 1654 EDT ON 8/7/13 * * * At 1525 CDT on 8/7/13, the licensee returned 9 of 14 emergency sirens to service which brings the percentage of population covered by the sirens below the reporting threshold. The licensee has notified the NRC Resident Inspector. Notified R3DO (Lara). | 85 | 67 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-07
49245 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-08-06 12:15 | 2013-08-06 13:13 | 2013-10-03 | PROGRAMMATIC ERROR ASSOCIATED WITH SITE ACCESS The licensee identified an error in a safeguard program that resulted in actual entry to the site before completing all required training. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector and the State of Pennsylvania. * * * UPDATE AT 1609 EDT ON 10/3/2013 FROM DOUG LAMARCA TO MARK ABRAMOVITZ * * * The licensee clarified the number of personnel involved in the event. The licensee will notify the NRC Resident Inspector and the state. Notified the R1DO (Joustra) and 73.71 Group (via e-mail). | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-08-06
49244 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-08-05 | 2013-08-06 12:21 | 2013-08-06 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE The State of Texas submitted the following information via email: "On August 6, 2013, the Agency [Texas Department of Health] was notified by the licensee that on August 5, 2013, one of its radiography crews at a temporary work site near Tilden, Texas had a source disconnect on a QSA model 880D camera which contained an iridium-192 source. Authorized persons performed the source retrieval. "The radiography two man crew pocket dosimeter readings were 188 and 22 millirem. Their dosimetry badges are being sent for processing. The two man retrieval team pocket dosimeters read 21 and 24 millirem. No member of the public received an exposure. "The licensee is investigating the cause of the disconnect. All equipment is being sent for evaluation. Further information will be provided as it is obtained per SA-300." TX Incident # I-9103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-08-14
49243 | -1 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-08-01 | 2013-08-06 11:04 | 2013-10-01 | AGREEMENT STATE REPORT - EXTERNAL RADIATION LEVELS ON SHIPMENT EXCEEDED 2MR/HR LIMIT FOR UNMONITORED EXPOSURES The following information was received from the Commonwealth of Virginia via facsimile: "On Thursday, August 1st, a shipment was being received by B&W from QSA Global, Inc. During the receipt survey, readings indicated 5.4 mrem/hr in the cab of the truck. The sources were received and leak tests were performed indicating no leakage. B&W contacted the Virginia Radioactive Materials Program (RMP) who then contacted the Massachusetts RMP. "B&W also reported the event to the NRC Operations Center on August 1st. A discussion to retract the event as this shipment occurred under the Virginia license was held on Friday 8/2 but the final determination was not made until Monday 8/5 to retract the NRC report. A decision was agreed upon for the Virginia RMP to report the event to the NRC Ops Center. "The Massachusetts RMP contacted QSA Global, Inc. A preliminary investigation indicates that a QSA Global, Inc. employee did not perform the proper survey before the sources were shipped. "The [contract carrier] consultant was contacted and made aware of this event. The [contract carrier] has begun an investigation into the event. "There was no adverse effect to public health and safety from this event. "Media attention: Yes" VA Event Report ID Number: VA-13-04 * * * RETRACTION FROM MIKE WELLING (VIA EMAIL) TO HOWIE CROUCH AT 1513 EDT ON 10/1/13 * * * The following retraction was submitted by the Commonwealth of Virginia via email: "On August 1st, a shipment from QSA Global using [a common carrier] was received at Babcock & Wilcox. During the receipt, a survey indicated readings >2 mrem/hr in the cab. An investigation was performed by the Massachusetts Radioactive Materials Program, during which they spoke with QSA and [the carrier]. Based upon this investigation, it has been determined that the shipment was not an exclusive shipment and all DOT regulations were met. "This event is being retracted based upon the investigation results." Notified R1DO (Joustra), NMSS EO (Bjorkman), Fuels Group (via email) and FSME Events Resource (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-08-14
49242 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-08-05 | 2013-08-06 11:04 | 2013-08-06 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following information was received from the Commonwealth of Virginia via facsimile: "On August 5, 2013, an Authorized User (AU) was conducting density testing for asphalt placement for a parking lot using a CPN MC-1-DR. The AU had just performed a density test and set the gauge on the adjacent asphalt approximately 5 feet from the joint for the hot asphalt. The AU stepped to the joint to tell the asphalt roller operator that density values were low. As the AU stepped back, he heard a tandem axle truck backing up. As he stepped to pick up the gauge, he realized the rear tandem axle tire was about to strike the gauge. By the time he pulled the gauge handle, the rear tire rolled over the gauge. He pulled the gauge away from between the rear tandem axle tire and the center axle tire. He then set the gauge down. A survey of the damage gauge was performed by the RSO and the sources were verified to be in their shielded position. The gauge was returned to the shop for shipment to CPN. There was no adverse effect to public health and safety from this event." VA Event Report ID Number: VA-13-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-08-14
49241 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-08-06 07:22 | 2013-08-06 08:48 | 2013-08-06 | UNUSUAL EVENT DECLARED DUE TO HIGH WINDS "Fort Calhoun Station entered a notification of unusual event due to high wind speeds at the site of 90.2 mph during a severe thunderstorm. IC [Initiating Condition] HU1 EAL2. Wind speeds have reduced to 25 mph sustained." The licensee has offsite power available and is in progress of conducting plant walkdowns. The thunderstorm has passed and sustained winds are 25 mph. The licensee has notified the NRC Resident Inspector, the State, and local governments. * * * UPDATE FROM MATT AMIELAK TO VINCE KLCO ON 8/6/13 AT 0928 EDT * * * "At 0828 CDT Fort Calhoun Station terminated from the notification of unusual event. There was no damage to plant equipment or structures from the storm. " Sustained winds are 15 mph. The licensee has notified the NRC Resident Inspector, the State, and local governments. Notified R4DO (Vasquez), NRR EO (Chernoff), IRD MOC (Kozal), DHS SWO, FEMA and DHS NICC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-08-06
49240 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-08-05 09:43 | 2013-08-06 07:30 | 2013-08-06 | INITIATION OF MATERIAL CONTROL AND ACCOUNTABILITY ALARM RESOLUTION PROCEDURE "10CFR74.57(f)(2) requires notification within 24 hours that a Material Control & Accountability (MC&A) alarm resolution procedure has been initiated. In the Oxide Dissolution Area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure has been initiated, this notification is being made. Security and MC&A investigations are underway along with actions to resolve the alarm per the criteria in the NFS Fundamental Nuclear Material Control Plan (FNMCP). There is no indication that a material loss has occurred. "There were no actual or potential safety consequences to workers, the public, or the environment. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM RANDY SHACKELFORD TO JOHN SHOEMAKER AT 1512 EDT ON 8/6/13 * * * The abrupt alarm has been reconciled. The licensee has notified the NRC Resident Inspector. Notified R2DO (King), NMSS EO (Smith), and FUEL OUO GROUP via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 1 | 2013-08-06
49239 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-08-05 14:56 | 2013-08-05 21:38 | 2013-08-05 | BOTH OFFSITE POWER SOURCES INOPERABLE DURING UNDERVOLTAGE TESTING "Both Limerick 4 KV offsite sources were inoperable and Technical Specification 3.0.3 was entered for Unit 2 from 1456 to 1512 [EDT] during D23 4KV Undervoltage testing. During the undervoltage test, the affected diesel and one offsite source (101 Bus) are inoperable. During the test, the alternate offsite source (201 Bus) UV relay was tested and found to be inoperable, resulting in the need to declare the second offsite source (201 Bus) inoperable. "When notified of the failure, action was taken to restore the 101 Bus offsite source to operable and exit the 3.0.3 condition [at] (1512 EDT). The 201 Bus Relay was successfully calibrated and tested to subsequently restore the 201 Bus to operability [at] (1543 EDT)." Testing of the 201 bus UV relay is directed per procedure while the 101 bus is powered from the diesel generator. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-08-05
49238 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2013-08-05 09:50 | 2013-08-05 15:52 | 2013-08-05 | AGREEMENT STATE REPORT - SHUTTER STUCK ON A PROCESS GAUGE The State of Nebraska submitted the following information via email: "The licensee uses fixed industrial gauges for measuring levels in fly ash hoppers at the station's precipitator building. The industrial fixed gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in April, 1984, and at the time contained 50 millicuries per source. The sources were manufactured and installed by Kay Ray Inc. The gauge that experienced the event was Kay Ray Gauge, Housing Model #7080 and housing serial number 16784H. The source capsule manufacture was Amersham model no. CDC 800 and K-R Ref. Number serial number 15095 V. "In accordance with their license conditions two of the station's chemists were securing the Unit #5's precipitator sources in preparation for an inspection of the precipitator. The 'external' source closure mechanism for Unit #5 precipitator's 5FA-3E & 4E hoppers did not operate as designed and the shutter did not close when the handle on the floor was operated. "The radiation sources, which are part of a hopper level sensor, are mounted between two fly ash hoppers 20 feet off the floor. The source closure mechanisms are connected to a handle located at the floor level by a flexible cable. These closure cables are secured to the structures so that when the handles are operated the control cables slide inside a sheath. On the 5FA-3E & 4E source, the shutter closure cable became loose up at the source which allowed the whole cable to slide back and forth when the handle was operated to try and close the shutter. This type of failure has been seen in the past and is easily fixed by tightening the screw which secures the end of the cable to the structure. This required a scaffold to be built up to the source level. A contractor came on site at 12:30 pm [CDT] on 8/5/2013 and erected a scaffold so repairs could be made." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2013-08-13
49237 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2013-08-01 | 2013-08-05 13:14 | 2013-08-05 | AGREEMENT STATE REPORT - WRONG FRACTIONAL DOSE ADMINISTERED TO PATIENT The licensee reported the administration of a 700 cGy fractional dose instead of the 500 cGy prescribed fractional dose to a patient during GYN treatment on 8/1/13. The 700 cGy fraction was prepared for another patient. The isotope involved was Ir-192. The fraction was the second of a three fraction total dose of 1500 cGy. The final fraction will be adjusted so that the total dose to the patient is 1500 cGy. The prescribing physician had been informed. The patient will be informed of the adjustment prior to administration of the final fraction on 8/8/13. There are no anticipated adverse consequences to the patient. The cause is under investigation and the licensee is still discussing potential corrective actions. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2013-08-13
49236 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-08-05 10:45 | 2013-08-05 11:18 | 2013-08-05 | HIGH RANGE STACK RADIATION MONITOR OUT OF SERVICE FOR MAINTENANCE: "The Millstone Unit 2 high range stack radiation monitor is out for pre-planned maintenance. This is reportable in accordance with 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector, State, and local governments. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-08-05
49235 | 0 | COVANTA INDIANAPOLIS, INC. |  |  |  |  | 2013-08-02 | 2013-08-05 08:49 | 2013-08-05 | STUCK SHUTTER ON A LEVEL DETECTOR One source holders for a Ronan Engineering, model GS-400, level detector had the shutter door seized in the open position which is the normal operating position. The licensee was unable to free up the shutter at their facility and has contacted the manufacturer (Ronan) for assistance. The source is secure and not leaking. The radiation levels are normal around the device. There is no possibility of exposure to individuals due to the active beam not being accessible. Manufacturer: Ronan Engineering Model: GS-400 Activity: 100mCi Isotope: CS-137 S/N: 5134C0 * * * UPDATE FROM BRIAN FOSTER TO PETE SNYDER AT 1601 EDT ON 8/5/13 * * * As of 1600 EDT on 8/5/13 the shutter door has been freed and now cycles normally. No further action is needed and Ronan's Engineering service has been canceled. Notified R3DO (Lara) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-08-13
49234 | 0 | AMEC ENVIRONMENTAL & INFRASTRUCTURE |  |  |  |  | 2013-08-03 | 2013-08-03 14:36 | 2013-08-26 | INTERIM REPORT REGARDING LABORATORY TEST DATA FOR SAFETY CLASS C CONCRETE AND GROUT An interim report was made, as required per 10CFR21.21 (a)(2), of a deviation identified by AMEC Environment & Infrastructure, Inc. The CTLGroup, a supplier of AMEC, did not initially provide all the traceable calibration information required for all the chemicals used in performance of procured tests in regard to laboratory test data of screening tests for constituents related to Safety Class C concrete and grout. An evaluation is underway, but could not be completed within 60 days of discovery. AMEC anticipates that the evaluation will be completed within two weeks of this correspondence, August 17, 2013. Affected plants; Vogtle Units 3 & 4 Safety Class C Concrete and Grout and VC Summer Units 2 & 3 Safety Class C Concrete and Grout. Name and address of the individual or individuals informing the Commission. Donald B. Chandler AMEC Environment & Infrastructure, Inc. 4021 Stirrup Creek Drive, Suite 100 Durham, NC 27703 Phone # 919-381-9908 * * * UPDATE ON 8/26/13 AT 1323 EDT FROM CHANDLER TO HUFFMAN * * * The following update was received from the licensee via facsimile: "The purpose of this letter is to follow up on the Interim Report of the Evaluation of a Deviation Pursuant to 10 CFR 21.21(a)(2) provided to the Commission on August 3, 2013. The August 3rd report informed the Commission of a deviation identified by AMEC Environment & Infrastructure, Inc. (AMEC) where an evaluation was underway, but could not be completed within 60 days of discovery. The evaluation was completed by AMEC on August 8, 2013 and it was determined that the nonconformance did not represent a defect." Notified R2DO (Haag) and sent copy to the Part 21 e-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-08-03
49233 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2013-08-02 09:32 | 2013-08-03 10:25 | 2013-08-03 | CONTAMINATION FOUND IN PROCESS BUILDING "While Health Physics (HP) technicians were checking radiological control wrapping in the Uncomplicated Handling (UH) waste storage area on the ground floor of the C-337 Process Building, contamination was discovered on the floor around some valve subassemblies. A Contamination Area (CA) was set up to establish contamination boundaries. Due to the contamination spread, access requirements for the area will be increased for more than 24 hours. Decontamination efforts are underway but will not be completed within 24 hours from the time that radiological controls were increased. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(1)(i) 'An unplanned contamination event that: requires access to the contaminated area, by workers or the public, to be restricted for more than 24 hours by imposing additional radiological controls or by prohibiting entry into the area'. "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-13-1667: PGDP Event Report No. PAD-2013-06." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2013-08-03
49232 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-08-03 05:20 | 2013-08-03 06:50 | 2013-08-03 | ALERT DECLARED DUE TO AN INADVERTENT CO2 FIRE PROTECTION SYSTEM DISCHARGE "[On August 3, 2013, at 0520 CDT], Farley Unit 1 declared an ALERT emergency based on [EAL] HA3, 'Release of Toxic, Asphyxiant, or Flammable Gas'. This was due to a tagout of the CO2 Fire Protection System, which resulted in an unexpected discharge of CO2 on the Unit 1 Radiation Side of the Auxiliary Building. The 100 foot elevation level on Unit 1 had an oxygen concentration below the required amount. CO2 has been isolated at the source tank in order to terminated the leak. No personnel have been affected. There is no radiation release in progress. ERDS has been activated." The licensee is assembling a team to enter the affected area and verify oxygen levels are within allowable limits in order to terminate the ALERT emergency. The licensee has notified the NRC Resident Inspector and the State and local organizations. Notified DHS SWO, DOE, FEMA, HHS, DHS NICC, USDA, EPA, FDA and NuclearSSA via email. * * * UPDATE FROM JONATHAN MCCORY TO STEVE SANDIN AT 1215 EDT ON 08/03/13 * * * Farley Unit 1 terminated from the ALERT at 1110 CDT on 8/3/13. Oxygen levels are acceptable in all areas of the plant. The CO2 tank has been isolated and is stable at 68%. Plant conditions are stable and improving and all necessary compensatory measures are in place. The licensee has notified the NRC Resident Inspector and applicable state and local authorities. Notified R2DO (King), NRR EO (Hiland), IRD (Kozal), and PAO (Couret), DHS SWO, DOE, FEMA, HHS, DHS NICC, USDA, EPA, FDA and NuclearSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-08-03
49231 | -1 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-08-01 09:00 | 2013-08-01 12:00 | 2013-08-05 | EXTERNAL RADIATION LEVELS ON SHIPMENT EXCEEDED 2MR/HR LIMIT FOR UNMONITORED EXPOSURES "The conditions for reporting under the requirements of 10 CFR 20.1906(d) have been met. QWI 14.1.10, Classification & Notification Criteria for Unusual Incidents Radiation Protection section - for shipments, bases reporting requirements on receipt of a shipment with radiation or contamination levels in excess of 10 CFR 20.1906(d). This requirement was exceeded and an NRC report is required. The truck cab sleeping area (normally occupied space) dose rate of 5.4 mrem/hr is greater than the allowable limit of 2.0 mrem/hr. The carrier drivers (2) state that they do not have dosimetry. "Immediate actions that have been taken: - The area was secured. - Confirmatory measurements were taken. - Digital photographs have been taken. - The shipper has been notified. - A review of the associated regulations was performed. - The carrier has been notified. - The truck has been unloaded and released." The shipment contained Am241/Be sources sent from QSA Global in Burlington, MA for use in refurbishing sources, typically well-logging. The estimated departure time/date was 0800 EDT on 07/31/13 with estimated arrival time/date of 0800 EDT on 08/01/13. The driver team consisted of two (2) individuals during the 24-hour transit time. The shipment was off-loaded and secured following the receipt rad survey. The licensee notified the shipper, the carrier, the Commonwealth of Virginia and informed the NRC Resident Inspector. * * * RETRACTION FROM TONY ENGLAND TO PETE SNYDER AT 1702 EDT ON 8/5/13 * * * "This event has been reported to the Commonwealth of Virginia under Event Number VA-13-04. The material involved in this event is regulated under Commonwealth of Virginia License." Notified R2DO (King), R1DO (Trapp), FSME Event Resource (email), and FUELS OUO (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2013-08-07
49230 | 0 | ABB INC. |  |  |  |  | 2013-07-31 | 2013-07-31 17:45 | 2015-04-08 | PART 21 REPORT - DEVIATION OF HK CIRCUIT BREAKER CLOSE LATCH SPRING ABB identified a deviation with close latch springs provided since 1/20/2010 used in medium voltage HK circuit breakers. These close latch springs are used on new legacy HK circuit breakers, replaced during HK circuit breaker refurbishment activities, and provided in HK refurbishment kits and as component items. The ABB part number for the close latch spring is: 162374A00. The nature of the deviation is a reduced spring force. There is a potential for an aged HK circuit breaker with hardening grease and this reduced spring force not to close. The following is a list of affected customers: Detroit Edison Fermi 2 Dominion VA DTE Duke Catawba Duke Energy - Seneca Duke Energy - Cataw Duke Huntersville Duke McGuire Duke Oconee Entergy River Bend Exelon Limerick Exelon Nuclear Exelon Peach Bottom Exelon Point Beach First Energy Beaver Valley Georgia Power Plant Vogtle Nextera Point Beach Nextera Seabrook Prairie Island Nuclear Progress Energy Brunswick Progress Energy Crystal River PSEG Alloway Creek Southern Cal Edison STP Nuclear TVA Sequoyah. * * * UPDATE AT 1715 EDT ON 04/08/15 FROM DAVID C. BROWN TO S. SANDIN * * * The following information is excerpted from a fax/email submitted by ABB, Inc.: "This letter amends the previous 10CFR Part 21 Notification of 31 July 2013 to encompass a wider time period during which the close latch spring (P/N: 162374A00) was sold for use in medium voltage HK circuit breakers. The initial time period of concern reported was January 2010 to July 2013. Revision 7 to the print was issued in January 2010 and it was determined during the initial investigation that this was the start of the deviation because the free angle was incorrectly shown. Our [ABB, Inc.] corrective actions in 2013 corrected this mistake. "In February 2015, a licensee notified us [ABB, Inc.] of springs from 2007 that have the same improper free angle. The order of springs received just prior to it had the proper free angle. We [ABB, Inc.] have narrowed the start time of this issue to the lone batch of springs purchased in 2007 as they were received shortly before the order identified by the licensee was released." Notified R1DO (Ferdas), R2DO (Heisserer), R3DO (Skokowski), R4DO (Azua) and NRR Part 21 via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-07-31
49229 | 0 | VETERANS HEALTH ADMINISTRATION |  |  |  |  | 2013-07-31 08:15 | 2013-07-31 16:03 | 2013-07-31 | PACKAGE RECEIVED EXCEEDING EXTERNAL RADIATION LIMITS "Per 10 CFR 20.1906(d)(2), the Veterans Health Administration (VHA) reported receipt of a package of radioactive material with external radiation levels exceeding NRC reporting limits (as referenced in 10 CFR 71.47). "The package was received today (July 31, 2013) around 0815 PDT by the VA Southern Nevada Healthcare System, North Las Vegas, Nevada. This medical center holds permit number 27-00593-01 under the VHA master materials license. "The package was surveyed by the VA facility nuclear medicine technologist with a pressurized ionization chamber. Readings were 160 mR/hr on the top surface of the shipping container and 32 mR/hr at 1 meter away from the top of the container (i.e., Transport Index = 32, which exceeded the NRC reporting limit of 10). Removable radioactivity tests of the external package surfaces were within regulatory limits. "The shipping container lacked proper shielding on the top and bottom. The package contained 2 lead pigs each containing F-18 (half-life 110 minutes). One source was assayed at 0929 PDT on 7/31/2013 at 350 mCi. The other source was calibrated for 12 mCi at 1100 PDT. "The VA facility Nuclear Medicine Technologist immediately notified, by telephone, Cardinal Health in Las Vegas, NV, who was the package shipper and final delivery carrier, regarding the high readings from the package. The vendor contact person acknowledged that the incorrect shipping box was used and the source should have been shipped later in the day. "As corrective actions, the VA facility technologist isolated the package in the VA medical center hot lab, and additional lead shielding was placed on the top of the package. "VHA has also notified NRC Region III (Null) by telephone of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | NV | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2013-08-08
49228 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-07-31 05:10 | 2013-07-31 11:40 | 2013-07-31 | EMERGENCY RESPONSE FACILITY PREPLANNED MAINTENANCE "This condition does not affect the health and safety of the public or the operation of the facility. At 0510 [EDT] on July 31, 2013, preplanned maintenance commenced which affects the Technical Support Center (TSC) ventilation and radiation monitoring systems. The scope of the maintenance is to inspect and perform functional checks on various TSC ventilation system fans and the outside air intake radiation monitor. This maintenance is scheduled to be performed and completed within approximately 20 hours. "TSC functionality requires all occupied areas of the TSC be maintained between 60.8 degrees F and 82.4 degrees F. Actual TSC temperatures have been verified to be less than 78 degrees F. If an emergency should occur, the ventilation system will be restored, but potentially not within the time required for activation of the TSC. If the facility were activated with full staff, temperatures could rise above the 82.4 degree F limit. Consideration will be given to relocating the TSC to the alternate emergency facility in accordance with PEP-240. The alternate TSC has been verified to have electrical power, ventilation, and communication capability. The Technical Support Center - Site Emergency Coordinator has been notified. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1620 EDT ON 07/31/13 FROM RICHARD DAVIS TO S. SANDIN * * * Preplanned maintenance was completed at 1540 EDT on 7/31/13. The licensee informed the NRC Resident Inspector. Notified R2DO (King). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-31
49227 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2013-07-29 16:45 | 2013-07-30 18:21 | 2013-07-30 | RADIOGRAPHY SOURCE RETRACTION FAILURE DUE TO DAMAGED GUIDE TUBE The following information was received via facsimile: "A report was received concerning a stuck source that occurred while performing radiography at approximately 1645 EDT on July 29, 2013. A test stand fell approximately 10 feet and crushed the source guide tube preventing retraction of the source back to the shielded position. Four employees lead shielded the source, cut into the guide tube, and repaired the metal braiding underneath the plastic coating. This allowed the source to be returned and locked back into the shielded position. The incident was referred to the Orlando inspection office for further investigation." Florida Incident Number: FL13-053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-08-07
49226 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-07-29 | 2013-07-30 17:45 | 2013-07-30 | RADIOGRAPHY SOURCE RETRACTION FAILURE The following information was received via E-mail: "On July 30, 2013, the Agency [Texas Department of State Health Services] received a call from the RSO of Fugro Consultants, Inc. regarding a source retraction failure on July 29, 2013. The licensee had a temporary industrial radiography site in Houston, Texas. The IR-192 source was in an INC IR-100, serial number 7231. The source was unable to be retracted due to a malfunction with the safety latch plate engaging before the source was retracted. The RSO received a call about the problem at 2000 CDT that evening and travelled to the site. The source was retrieved according to the conditions of the license. The RSO determined that no overexposures resulted to the crew, nor were there exposures to the public, resulting from the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9100. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-08-07
49225 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-07-30 14:32 | 2013-07-30 17:32 | 2013-07-30 | REACTOR SCRAM DUE TO TURBINE GENERATOR TRIP "Actuation of Reactor Protection System with reactor critical. Reactor Scram occurred at 1432 CDT on 7/30/2013 from 100% Power. The cause of the scram appears to be a Turbine Generator trip. "05-S-01-EP-2, 'Reactor Pressure Vessel Control,' 05-1-02-I-1, 'Reactor Scram Off Normal Event Procedure,' and 05-1-02-I-2, 'Turbine and Generator Trip Off Normal Event Procedure,' were entered to mitigate the transient. "No Loss of Off-site Power occurred. No Emergency Core Cooling System or Diesel Generator initiation occurred. Reactor Core Isolation Cooling initiated and injected. The lowest reactor water level reached was -36 inches wide range (RCIC initiation set point is -41.6 inches wide range). "Main Steam Isolation Valves remained open and no Safety Relief Valves actuated. Currently, Main Turbine Bypass valves are controlling reactor pressure to the Main Condenser and Condensate and Feedwater is controlling reactor water level in the normal band and removing decay heat. There are no challenges to Primary or Secondary Containment. "The NRC Senior Resident Inspector was notified." * * * UPDATE FROM CHRIS ROBINSON TO PETE SNYDER AT 1841 EDT ON 7/30/13 * * * The first out recorder indicated that RPS actuation signal was due to high reactor pressure as a result of the turbine control valves going shut. Notified R4DO (Farnholtz). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-07-30
49224 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-07-29 | 2013-07-30 10:49 | 2013-07-30 | AGREEMENT STATE REPORT - LOST AND SUBSEQUENTLY RECOVERED WELL LOGGING SOURCE The following report was received from the State of Colorado via fax: "The Colorado Department of Public Health and Environment received notification on the evening of 7/29/13 from ThruBit LLC, Colorado License Number 1179-01, that a 1.78 Ci Cs-137 well logging source fell out of a logging tool at a well site in Colorado and was not recovered until the following morning. "Details are as follows: On Sunday 7/28, the well-logging crew finished operations at the well site and removed the logging tool from the well around noon. Apparently, the Cs-137 source fell out of the logging tool while it was being returned to the logging truck. Seventeen hours later, the logging crew discovered the source was missing and returned to the well-site and retrieved the source, which was found on the ground. ThruBit's RSO and Department inspectors are on their way to the well-site to conduct an investigation and assess potential exposures. "No other details are available at this time." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-08-07
49223 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-07-30 06:35 | 2013-07-30 08:40 | 2013-07-30 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR PRE-PLANNED MAINTENANCE "On July 30th, 2013 at 0635 CDT, the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. The ventilation system is expected to be out of service for approximately 5 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DANIEL BACKUS TO DONALD NORWOOD AT 1550 EDT ON 7/30/2013 * * * Maintenance was completed and the TSC was returned to service at 1430 CDT. The licensee notified the NRC Resident Inspector. Notified R3DO (Orth). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-30
49222 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-07-29 10:42 | 2013-07-29 17:19 | 2013-07-29 | FIRE RELATED UNANALYZED CONDITION THAT COULD IMPACT CREDITED SAFE SHUTDOWN ANALYSIS "This is a non-emergency notification. In preparation for converting from 10 CFR 50, Appendix R, to NFPA (National Fire Protection Association) 805, a review of the Brunswick Steam Electric Plant (BSEP) Safe Shutdown Analysis identified conditions that may not ensure required equipment remains available under certain postulated fire scenarios. The analysis determined that the effects of a postulated fire in specific fire areas could prevent critical systems or components from performing their intended functions, potentially resulting in the inability to achieve and maintain safe shutdown. Alternate safe shutdown procedures currently credited with bringing about operator actions to mitigate a postulated fire have been found not to contain needed actions. "Affected fire areas are RB1-N, RB1-S, RB2-N, RB2-S, DG-07, and DG-08E. A fire in one of these areas could potentially adversely affect Emergency Diesel Generators (EDGs) 2, 3, and 4 along with EDG Building ventilation system components that could fail vital auxiliaries (HVAC) to the affected switchgear rooms. "This is reportable as an unanalyzed condition that significantly degrades plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). Most required fire watches were already in place as a result of a previous similar event reported in Brunswick ENS Report 47341 and Brunswick LER 1-2011-002. Two additional actions have been taken to establish fire watches in areas containing electrical busses E6 and E7. "This condition has been entered into the Corrective Action Program (i.e., CR 619341). "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-07-29
49221 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-07-29 10:00 | 2013-07-29 13:31 | 2013-07-29 | FITNESS FOR DUTY - CONFIRMED POSITIVE FFD TEST A non-licensed, supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been restricted. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2013-07-29
49220 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-07-28 10:18 | 2013-07-28 13:43 | 2013-07-29 | MANUAL REACTOR TRIP FOLLOWING SECONDARY PLANT TRANSIENT "On July 28, 2013, at 1018 EDT, DC Cook Unit 2 Reactor was manually tripped due to lowering steam generator level caused by an automatic trip of the west main feed pump. The west main feed pump tripped on low suction pressure resulting from a secondary plant transient. The cause of the secondary transient is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an (8) hour report. "The DC Cook Sr. Resident NRC Inspector has been notified. "The electrical grid is stable and Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post trip review. No radioactive release is in progress as a result of this event." There was no affect on Unit 1. * * * UPDATE FROM DEAN BRUCK TO DONALD NORWOOD AT 1753 EDT ON 7/29/13 * * * "Additional information received determined the Turbine Driven Auxiliary Feedwater Pump discharge valve to Steam Generator #2 did not position, as required, following the reactor trip. The affected discharge valve opened as expected during pump start. The valve closed instead of throttling to the intermediate position upon subsequent high flow demand. Feedwater flow to Steam Generator #2 was maintained by the East Motor Driven Auxiliary Feedwater Pump. "The NRC Resident Inspector has been notified of this update." Notified R3DO (Orth). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-07-28
49219 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-07-26 23:49 | 2013-07-27 01:14 | 2013-07-27 | UNUSUAL EVENT DECLARED DUE TO A FIRE IN THE TURBINE BUILDING LASTING GREATER THAN 15 MINUTES On July 26, 2013, at 2349 CDT, the Callaway nuclear power plant declared an Unusual Event due to a fire not extinguished within 15 minutes of control room notification, EAL HU 2.1. The fire was located in the turbine building near the main generator. Concurrent with the fire, the reactor tripped due to a turbine trip. All control rods fully inserted and all reactor coolant pumps (RCPs) tripped. The fire has been extinguished and the licensee is in progress of restoring RCPs. The licensee notified the NRC Resident Inspector, State Emergency Management Agency and Local Authorities. Notified DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/27/13 AT 0201 EDT FROM MARK COVEY TO BILL HUFFMAN * * * The licensee terminated the Unusual Event at 0101 CDT. Decay heat is being removed via aux feed water from the steam generators to the condenser. Visual inspection determined the location of the fire to be in the phase B generator bus duct. Notified R4DO (Allen), NRR EO (Monninger), IRD (Marshall), DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/27/13 AT 0430 EDT FROM MARK COVEY TO DONG PARK * * * The licensee made notifications under 10CFR50.72(b)(2)(iv)(B) [RPS Actuation], 10CFR50.72(b)(2)(xi) [Offsite Notification] and 10CFR50.72(b)(3)(iv)(A) [ESF Actuation - AFW]. The licensee will be making a press release and notifying the NRC Resident Inspector. Notified R4DO (Allen). * * * UPDATE ON 7/27/13 AT 0826 EDT FROM MARK COVEY TO BILL HUFFMAN * * * Upon further review, the licensee believes that the initially reported EAL for the UE notification, HU 2.1, was not applicable. Although indications of a fire were present for greater than 15 minutes, the criteria at Callaway apply to a fire within 50 feet of safety related equipment. There was no safety related equipment within 50 feet of where the fire occurred. The proper EAL classification should have been HU 3.1 due to release of potentially toxic gas or asphyxiant or flammable gas that could impact plant operation. This EAL is applicable due to the heavy smoke release from burning electrical insulation and melted bus and ductwork which prevented access to the turbine building area where the fire took place. The licensee will notify the NRC Resident Inspector of this update. Notified R4DO (Allen). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | MO | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2013-07-27
49218 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-07-26 17:06 | 2013-07-26 18:59 | 2013-07-26 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM A vulnerability was discovered in a safeguard system that could allow access to a controlled access area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. | 48 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-07-26
49217 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2013-07-26 | 2013-07-26 13:15 | 2013-07-26 | POTENTIAL EXISTENCE OF DEFECTS IN SHIELD PASSIVE THERMAL SHUTDOWN SEAL SYSTEM "The defect being reported concerns an identified inconsistency between the intended design functionality of the SHIELD passive thermal shutdown seal (SDS) and that observed during post-service testing. "The purpose of the SDS is to reduce current reactor coolant system inventory losses to very small leakage rates for a plant that results in the loss of all reactor coolant pump (RCP) seal cooling. The SDS is a thermally actuated, passive device integral to the RCP Number 1 seal insert and is positioned between the Number 1 seal and the Number 1 seal leak-off line to provide a near leak-tight seal once activated. "There are two delivered components associated with this report: 1. the SDS hardware, and 2. the Probability Risk Assessment (PRA) SDS model and the assigned SDS reliability. The hardware component is the SHIELD passive thermal shutdown seal. The associated PRA SDS model and assigned reliability basic component is WCAP-17100-P-A, Supplement 1, Rev. 0, 'PRA Model for the Westinghouse Shut Down Seal Supplemental Information for All Domestic Reactor Coolant Pump Models' (dated December 2012). "The SDS has only been delivered and installed in the following plants: Beaver Valley Unit 2, Callaway, D.C. Cook Unit 1, Farley Units 1 and 2, and Wolf Creek. "Westinghouse has concluded that the hardware itself will not adversely impact safe plant operation. "Westinghouse has completed a root cause analysis (RCA) and an independent third party review of this RCA is expected to be completed by August 2013. In parallel, SDS design improvements are being considered and may be completed during the third quarter of 2013. Additionally, and if necessary, Westinghouse will revise WCAP-17100 and its Supplements, as needed, to reflect any new information that is developed. "Affected customers have been informed via their respective Customer Project Managers of the post-service test failure." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-07-26
49216 | 0 | IDAHO TRANSPORTATION DEPARTMENT |  |  |  |  | 2013-07-18 09:00 | 2013-07-26 10:30 | 2013-07-26 | MISSING TROXLER MOISTURE DENSITY GAUGE The Radiation Safety Officer (RSO) at the Idaho Transportation Department discovered a Troxler 3440 moisture density gauge missing when it was believed to be in lock-up and a wipe test was to be performed on July 18, 2013. The Idaho Transportation Department searched all the projects and alerted everyone in the district that the gauge was missing. After a week, the gauge could not be located. Gauge Information: Troxler Model 3440, Serial # 26155 Sources: Americium-241/Beryllium, 40 millicuries; Cesium-137, 8 millicuries * * * UPDATE FROM DIANNA HOFFECKER TO VINCE KLCO ON 7/26/13 AT 1307 EDT * * * The gauge has been found and is in the possession of the licensee. Notified R4DO (Allen), FSME Events Resource, ILTAB and Canada.. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-08-05
49215 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-07-25 11:35 | 2013-07-25 16:58 | 2013-07-25 | MALFUNCTIONING NOAA TONE ALERT RADIO SYSTEM "On Thursday, July 25, 2013, at 1135 EDT, Hatch Nuclear Plant [HNP] experienced of a loss of the National Weather Service (NWS) Tone Alert Weather Radio System and was unable to contact the NWS Jacksonville, Florida Office. Site emergency procedures define a loss of Tone Alert Radio for greater than 15 minutes as a significant loss of emergency communications. Plant Hatch EP contacted NOAA and was told they had lost phone service and were attempting to restore it. "The NWS Tone Alert Weather Radio is utilized as the Prompt Notification System (PMS) for HNP. The loss impacts the ability to notify the Emergency Planning Zone (EPZ) population for the HNP. This failure meets NRC 8-hour reporting criteria 10 CFR 50.72(b)(3)(xiii). The State of Georgia Department of Homeland Security/Georgia Emergency Management Agency (GEMA) 24 hour warning point and the '911' dispatch centers of Appling, Jeff Davis, Tattnall and Toombs Counties were notified so compensatory measures would be available should the Prompt Notification System be needed. This consists of utilizing route alerting and the 'Code Red' system which is a reverse 911 feature available from the county 911 center. "As of the time of this report, the NOAA [system] has not been returned to service nor does the Jacksonville Office have a cause for the loss or a projected RTS [return to service] time." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT BRITT TO PETE SNYDER AT 2005 EDT ON 7/25/13 * * * As of 1910 EDT on 7/25/13, the tone alert radio systems have been returned to service and are fully operational. The licensee notified the NRC Resident Inspector. Notified R2DO (Hopper). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-25
49214 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2013-07-24 14:19 | 2013-07-24 17:46 | 2013-07-24 | AUTOMATIC REACTOR TRIP FROM FULL POWER "At 1419 EDT on 7/24/2013, the reactor tripped due to a reactor protection system (RPS) actuation signal from a turbine trip, which was caused by a generator trip. All control rods inserted on the trip and reactor coolant system (RCS) pressure is currently 2235 psig and stable with RCS temperature stable at 547 degrees F. Decay heat is being removed by steam dumps [to the main condenser] and auxiliary feedwater which auto started as expected. "The cause of the generator trip is under investigation. The plant will remain in Mode 3 until the cause of the trip is determined. "The plant notified the NRC Resident Inspector." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-07-24
49213 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-07-23 13:45 | 2013-07-24 12:21 | 2013-07-24 | PROGRAMMATIC FAILURE TO TEST PERSONNEL RETURNING TO THE SITE "On July 23, 2013 at 1345 [EDT], the Fitness-for-Duty Snapshot Self-Assessment team identified an anomaly with the Employee Plant Access Control Tracking (EMPACT) program used to randomly select V.C. Summer employees for daily fitness for duty (FFD) screenings. More specifically, when an employee terminates employment at the station, Access Control personnel select 'Exclude from Random' feature in the EMPACT program to remove their name from the program code that randomly selects current employees for daily FFD screenings. When a former employee returns to the station for re-employment, Access Control personnel select 'New Request' within the EMPACT program. The 'New Request' feature is supposed to automatically deselect the 'Exclude from Random' feature, which adds the employee back to the randomly selected population. This feature of the EMPACT program was determined not to be functional. "In accordance with 10 CFR 26.719(b)(4), this program flaw constitutes: 'Any programmatic .... discovered vulnerability of the FFD program that may permit the undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program.' "This event has been entered into the station's corrective action program under CR-13-03066. The issue is limited to 53 employees (2.9% of the randomly selected population) that have returned to V.C. Summer for employment in the previous six years. Immediate corrective actions consist of contacting the program vendor, conducting an Access Control Program standdown, and contacting the 53 employees to report for fitness-for-duty screening. "The NRC Resident Inspector has been notified. "Other utilities known to use the EMPACT software have been contacted." This issue does not affect units 2 or 3 since they use a different system. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FFD PROGRAMMATIC FAILURE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.417(b)(1) |  |  |  | 0 | 2013-07-24
49212 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-07-20 | 2013-07-24 10:16 | 2013-07-24 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE INTO RADIOGRAPHY CAMERA The following information was obtained from the State of Texas via E-mail: "On July 23, 2013, the Agency [Texas Department of State Health Services] was notified by the licensee that on July 20, 2013, a radiography crew was unable to retract an Iridium - 192 source into a QSDA 880 D exposure device. The failure was caused by a spool that had fallen on the guide tube, crimping the tube so that the source could not pass through the tube at the crimp. The radiographers isolated the area, placed bags of concrete over the source to reduce area dose rates, and contacted their Radiation Safety Officer (RSO). The RSO drove to the location and reach the site about six hour later. The RSO was able to remove the crimp enough to allow the source to pass through the crimp and lock back in the exposure device. The camera was returned to the licensee's facility for further inspection. No one involved in the event received an exposure that exceeded any regulatory limit. No member of the general public was exposed to any radiation due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-08-01
49211 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-06-14 18:06 | 2013-07-24 07:55 | 2013-07-24 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO A RADIATION MONITOR SPIKE "This notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment valves in more than one system. "On 6/14/2013, and again on 7/11/2013, with the reactor at 100% power, an invalid PCIS Group 3 actuation occurred from a momentary spike of the 'A' Refuel Floor radiation monitor which reached the instrument's high radiation trip setpoint. A radiation protection technician was dispatched to the refuel floor and dose rates in the vicinity of the 'A' radiation monitor detector were verified to be normal and below the alarm setpoints. The radiation monitor was verified to be indicating normal expected radiation levels. Subsequent visual inspection and functional checks of the radiation monitors were completed satisfactory and the instrument channel was returned to service. The cause of the spurious spikes is attributed to an unknown source of electrical noise. The issue with spurious spiking has been entered into the station's corrective action program. "Both trains of Standby Gas Treatment System started as designed and Reactor Building ventilation isolated. The train actuation was complete. "The PCIS functioned successfully providing a complete Group 3 isolation. The PCIS Group 3 isolation involves the following systems. "Drywell and Suppression Chamber air and vent: V16-19-6A, 6B, 7, 7A, 7B, 8, 9, 10, 23 "Containment Makeup: V-16-20-20, 22A, 22B "Containment Air Sampling: VG-23, 26, V109-76A, 76B "Containment Air compressor suction: V72-38A, 38B "Containment Air Dilution: VG-9A, 9B, 22A, 22B, NG-11A, 11B, 12A, 12B, 13A, 13B "In accordance with 10CFR50.73(a)(1) a telephone notification is being made instead of submitting a written Licensee Event Report." The licensee has notified the NRC Resident Inspector and will notify the State and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-07-24
49210 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-07-22 11:45 | 2013-07-22 23:14 | 2013-07-22 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2013-07-22
49209 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-07-22 09:55 | 2013-07-22 09:55 | 2013-07-22 | POTENTIAL PROGRAMMATIC BREAKDOWN OF THE QUALITY ASSURANCE PROGRAM "As a result of an extent of condition review for potential programmatic breakdown issues in response to an apparent violation 05000391/2013611-02 related to TVA's Commercial Grade Dedication Program. TVA has identified a previous Problem Evaluation Reports (PERS) that constitute significant breakdown in a portion of the Quality Assurance program. This review was initiated upon discovery of a misinterpretation of 10 CFR 50.55(e) where it was thought that to be reportable a 'significant breakdown in a portion of the Quality Assurance program' had to be associated with a confirmed substantial safety hazard. "The subject of the previous PER is as follows; "On May 31, 2011, TVA identified a number of revised Drawing Revision Authorizations (DRAs) that had not been incorporated into work orders to ensure field work required by the DRA revision was implemented in the field. This condition was documented as PER 378571. TVA has concluded that a significant breakdown in a portion of the Quality Assurance program had occurred that could have produced a defect in a basic component. However, TVA has subsequently determined that no safety significance can be attributed to this condition. This issue has been resolved and PER 378571 was closed on February 19, 2013. "These items are being reported in accordance with 10 CFR 50.55(e) as significant breakdown in a portion of the Quality Assurance program." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 50.55(e) |  |  |  | 0 | 2013-07-22
49208 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-07-20 04:38 | 2013-07-20 12:56 | 2013-07-20 | HPCI SYSTEM DECLARED INOPERABLE "During performance of 1-SR-3.3.5.1.3(D), 'High Pressure Coolant Injection System Condensate Header Low Level Switch Calibration and Functional Test,' the High Pressure Coolant Injection (HPCI) system was declared inoperable due to exceeding the allotted 1 hour time frame for instrument inoperability of 1-LS-073-0056A and 1-LS-073-0056B [low condensate storage tank (CST) level HPCI suction transfer switches]. The HPCI system was declared inoperable in accordance with technical specification (TS) 3.3.5.1 Condition D.1. Condition D of TS 3.3.5.1 is required to be entered during performance of this surveillance. The surveillance disables the automatic CST to Torus suction path transfer function of the HPCI system by booting relay contacts in order to perform a functional test of referenced switches. The 1 hour completion time of TS 3.3.5.1 required by action D.1 was exceeded due to issues with associated test equipment. This constitutes an unplanned HPCI system inoperability and requires an 8 hour NRC notification per 10CFR50.72(b)(3)(v)(D). HPCI remained available for automatic and manual injection during this time period. "The HPCI system was declared inoperable at 0438 CDT on 7/20/13 and operability (CST to Torus suction transfer function) was restored at 0454 CDT on 7/20/13. "The NRC resident inspector has been notified." The level switches (suction transfer switches) had been taken out-of-service for calibration and testing at 0338 CDT on 7/20/13. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-07-20
49207 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-07-19 | 2013-07-19 21:08 | 2013-07-19 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following information was received via E-mail: "On July 19, 2013, the Agency was notified by a licensee that a TFS model 5221 nuclear gauge containing two, 300 millicurie Cesium 137 sources failed to function as designed when attempting installation of the device on a process vessel. "When the source was inserted into the vessel, the chain connecting one of the sources to the nuclear gauge broke allowing the source to travel to the bottom of the insertion tube. This is the normal operating position for the source. A radiation survey was conducted by the licensee indicating radiation levels to the general public were normal. The manufacturer has been contacted and is responding. It is anticipated that an attempt will be made by TFS to retrieve the source from inside of the vessel between July 20, 2013 and July 22, 2013 and then proceed to immediately repair the device. "There is no additional risk of radiation exposure to members of the general public as a result of this failure. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-07-29
49206 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2010-11-30 23:59 | 2013-07-19 19:00 | 2013-07-19 | AGREEMENT STATE REPORT - BADGE EXPOSURE EXCEEDING 5 REM ANNUAL DOSE LIMIT The following was received from the State of Oregon via email: "Oregon Radiation Protection Services was notified by phone on January 19, 2011 at 1119 PDT, a representative of Good Samaritan Regional Medical Center, of a whole body (collar) badge report for the wear period of November 1-30, 2010 that exceeded the 5 rem dose limit. The monthly badge report was received by the licensee sometime after December 28, 2010 for an authorized user showing monthly/quarterly/annual dose as follows: "Monthly (Nov 2010): DDE, LDE = 5230 mrem SDE = 5032 mrem "Quarterly (4Q2010): DDE, LDE = 5290 mrem SDE = 5091 mrem "Annual (2010) and Lifetime (hired in 2010): DDE, LDE = 5376 mrem SDE = 5175 mrem "The vendor (Landauer) performed a second read of the dosimeter that agreed with the reported doses above and stated that the imaging indicated an 'irregular exposure.' The authorized user stored his badge and ring in a 'cubby' along with his lab jacket. "On January 24th, the licensee emailed Oregon RPS with results from the licensee's investigation stating that the badge user was a student on rotation to the nuclear medicine dept. for the month of November. The user's previous WB badge results were 'normal' and no other nuclear medicine worker received a high dose reading during November. The student was '100% supervised' and is described as 'very conscientious about spills or drops.' Regardless, the licensee determined after eliminating several factors, that contamination was the most probably factor since the collar badge result was higher than the user's finger ring (4480 mrem SDE November, 5220 mrem SDE for 2010) and 'irregular exposure' noted by the dosimetry vendor. It remains unknown what isotope caused the overexposure and any Tc-99m has decayed to background. Surveys of the cubby and lab jacket were performed with negative results. In addition, the licensee stated that no 'large' iodine doses were administered for November. Remedial actions were not noted on the report. "On July 16, 2013, a review was performed of this incident and it was discovered that it was not reported to the US NRC HOO as per the NRC's Reporting Material Events (SA-300), Appendix A. The specific requirement is 10 CFR 20.2203(a) which states, in part, that radiation doses that exceed the regulatory requirements (5 rem) are to be reported (30 day requirement). The licensee was e-mailed for any remedial actions taken after this event. "On July 19, the licensee responded by e-mail stating that without a definitive cause for the overexposure, no change in procedure was instituted except heightened awareness of badge placement/location. The report was written and submitted via e-mail to the HOO on this same date. "Oregon Radiation Protection Services noted on the Incident report that US NRC Operations Center was to be notified but this was not done." State Event Number: OR-11-0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-07-29
49205 | 0 | NATIONAL TECHNICAL SYSTEMS |  |  |  |  | 2013-07-16 | 2013-07-19 13:41 | 2013-07-19 | PART 21 FIRMWARE NOTICE FOR USERS OF YOKOGAWA DX1000N AND DX2000 MODEL RECORDERS "This letter is to inform you of a potential Yokogawa data recorder lock-up condition that under specific circumstances may occur on Yokogawa DX Advanced DX1000N and DX2000 models equipped with firmware versions 3.01 through 4.14. These recorders were bought commercially from Yokogawa by National Technical Systems (NTS) and dedicated as basic components for nuclear safety related service. "The lock-up condition only impacts recorders when utilizing a 'custom trend display' option. There is no lock-up concern with these models when standard display screens are in use or on models using firmware versions earlier than R3.01. While NTS has not received any notification this lock-up condition occurred on a safety related recorder, please see the below description of the error and the appropriate corrective measures. "Background: Public Service Electric and Gas - Hope Creek NPP notified NTS and Yokogawa of a lock up condition which occurred on a newly installed non-safety data recorder in their simulator. Yokogawa studied the condition and notified NTS on June 14, 2013 that a firmware error occurs during a specific set of operating conditions and sequence of events and was identified as the root cause of the recorder lock up condition. While these conditions are highly unlikely in an operating plant because under normal practice the internal memory on the recorder would not be cleared, the recorder will lock-up if the below setup conditions occur simultaneously: "1. A 'Custom Display' that uses a trend screen is active and visible. 2. There is no trend data stored in memory (blank trend screen); this is the condition following a 'Clear 3' initialize. 3. A 'Second Speed' function is invoked via remote input activation (requires / R1 option) or front panel key activation. This is called 'Trend rate switching' a function enabled in Basic Setting Mode that allows the trend update time/division to switch between two separate speeds. "Corrective Action: This error only affects recorders if 'Custom Display' is being utilized. If this feature is not being used, no immediate action needs to be taken. If custom screens exist, then please utilize the recommendations below and update firmware when the new version (4.19) becomes available in August 2013. "A short-term countermeasure is to follow the Yokogawa operational procedure of starting to record data immediately after invoking a 'Clear 3' initialize, and then waiting for at least one trend update to occur (Display data save) before invoking a 'Second Speed' change action. "Should a lock-up condition occur, as indicated by a freeze of the display clock, the recorder simply needs to be powered off and re-started. The recorder will continue to function properly. "Based on the above, the nuclear utilities need to be notified concerning this deviation so an evaluation may be performed to determine if this constitutes a defect that could create a substantial safety hazard. NTS cannot make this determination as only the effected utilities know the way the recorders are configured and utilized. "The attached list contains the nuclear power plants which have been provided DX Advanced safety related Yokogawa recorders with firmware versions 3.01 and above by NTS. NTS has notified these utilities of the above condition via e-mail on July 16, 2013. "CENG - Nine Mile Dominion - Surry Station Dominion - North Anna Entergy - Arkansas Nuclear One Entergy - Fitzpatrick Entergy - Pilgrim Nuclear Station Entergy - River Bend Exelon - Braidwood Warehouse Exelon - Byron Exelon - Dresden Station Exelon - Limerick Generating Station Exelon - Quad Cities First Energy - Perry Plant Florida Power & Light - St. Lucie Georgia Power - Vogtle Plant AEP - DC Cook Nebraska Public Power - Cooper NextEra Energy - Duane Arnold Omaha PPD - Fort Calhoun Entergy - Palisades Progress Energy - H.B. Robinson Plant PSE&G - Salem/Hope Creek Edison - San Onofre STP Nuclear Operating Company TVA - Sequoyah Station Wolf Creek Nuclear Operating Corp. Xcel Energy - Prairie Island Nuclear" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-07-19
49204 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2010-09-01 | 2013-07-19 12:00 | 2013-07-19 | AGREEMENT STATE REPORT - MISSING DEVICE CONTAINING RADIOACTIVE MATERIAL The following was received from the State of Oregon via email: "On February 17, 2011 at 0800 PDT, OR Radiation Protection Services was notified by phone by [the licensee], HazMat Resource Coordinator, a representative of the Oregon Office of the State Fire Marshal (OSFM) regarding a missing Smith's Detection model APD2000 ECD device (s/n 1276) containing 10 mCi of Nickel-63 (source s/n is the same as device, 1276). There were no equipment problems noted. "The device was stored at Hazmat Team 7, stationed in Redmond, Oregon. The team was disbanded in late 2008 and the device was believed returned to the Salem, Oregon main OSFM office in early 2009. During equipment inventory in September (no date given, 1-30th supplemented), 2010, the device was discovered missing. OSFM personnel wrote a memo dated Sept. 2010, and addressed 'MEMO to File' stating the device was missing and that this was reported to Oregon RPS. No record of the memo having been received was found in RPS records for the license "[The licensee] stated that the remaining seventeen APD2000 units in possession were to be disposed of through the CRCPD's SCATR program sometime in the next 2 months. An incident report was started by OR RPS on this date (February 17th) for the missing device/radioactive source. "On April 8, 2011, the seventeen APD2000 units were shipped by waste broker (Thomas Gray and Associates) to affiliate company EMC in Turlock, CA. "On May 26, 2011 during regular equipment inventory at the Corvallis, Oregon Hazmat team 5B office, the missing APD2000 was located at the back of a storage cabinet. The device was removed and brought to Salem and [the State was] contacted for disposal of this device through the CRCPS SCATR program. "A leak test was taken June 7th and analyzed June 8th showing detection less than .005 microCurie for Ni-63. On June 15, 2011, the device was transferred to Thomas Gray and Associates for disposal and the license terminated on July 1, 2011. On July 16, 2013, a review was performed of this incident and it was discovered that it was not reported to the US NRC HOO as per the NRC's Reporting Material Events (SA-300), Appendix A. The specific requirement is 10 CFR 20.2201(a)(1)(ii) which states, in part, that reports of missing licensed material > 10X Appendix C value and still missing is to be reported (30 day requirement). The report was written and submitted via e-mail to the HOO on July 19th." State Event Number: OR-11-0007 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-07-29
49203 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2013-07-16 11:30 | 2013-07-18 09:30 | 2013-07-18 | AGREEMENT STATE REPORT - UNDERDOSE TO PATIENT DUE TO EQUIPMENT FAILURE The following information was obtained from the State of New Jersey via email: "At 11:30 a.m. [EDT] on July 16, 2013, a patient was being treated for three lesions with an Elekta Leksell Gamma Knife Perfexion unit, serial number 6016, at Cooper Health System in Camden, New Jersey. The prescribed total dose for all three lesions was 58 Gray. "The first two lesions were treated as planned without incident. "During treatment of the third lesion, treatment was interrupted because of mechanical failure. A 'Sensor Failure' error occurred, which caused the patient couch to retract and the shielding doors to close. An Elekta service engineer was called and no other treatments were attempted after the 'Sensor Failure'. Treatment of the third lesion was to be re-scheduled. "It is estimated that only 44.8 Gray out of the prescribed dose of 58 Gray was actually delivered, which is an underdose of greater than 20%." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2013-07-26
49202 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-07-18 08:30 | 2013-07-18 09:14 | 2013-07-18 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE "On July 18th, 2013 at approximately 0830 hours CDT, the Kewaunee Power Station will render the Auxiliary Building Special Particulate Iodine Noble Gas 'SPING' (Mid- and Hi-Range) non-functional for planned maintenance. The Emergency Response Organization (ERO) team has been notified of the Auxiliary Building SPING non-functionality due to planned maintenance. "The SPING is expected to be out of service for approximately 5 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify and classify an Emergency Action Level for offsite radiation conditions). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-18
49201 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-07-17 10:54 | 2013-07-17 17:42 | 2013-07-17 | SALT SERVICE WATER SYSTEM DECLARED INOPERABLE "On Wednesday, July 17, 2013 at 1054 hours EDT, with the reactor at 100% core thermal power (CTP) the Pilgrim Nuclear Power Station (PNPS) entered a 24-hour shutdown Limiting Condition for Operation (LCO) for Salt Service Water (SSW) inlet temperature exceeding the Technical Specification (TS) limit in TS 3.5.B.4. The LCO was subsequently exited at 1625 hours when the temperature of SSW trended to below the TS limit. "Under certain accident conditions the SSW system is required to provide cooling water to the Reactor Building Closed Cooling Water (RBCCW) system heat exchanger. When the inlet temperature to this supplied load exceeds the 75 [degrees] F limit established in the TS, the SSW system is declared inoperable until the temperature trends below this value. This condition existed for approximately 5-1/2 hours and the SSW system was declared operable and the LCO exited. A maximum temperature of 75.5 [degrees] F was recorded during this period. "At 1230 hours a power reduction was conducted to improve secondary plant parameters and Rx power is currently 85%. "The SSW temperature is being closely monitored and trended on a continuous basis. "This event has no impact on the health and safety of the public. "The licensee has notified the NRC Senior Resident Inspector." The licensee will notify the Commonwealth of Massachusetts. | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-07-17
49200 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-07-17 16:05 | 2013-07-17 17:36 | 2013-07-17 | OFFSITE NOTIFICATION DUE TO A CHEMICAL SPILL ONSITE "Today, July 17th, 2013, at approximately 1605 EDT, the New Jersey Department of Environmental Protection was notified that approximately 1 pint of sodium hypochlorite was spilled onto the lands of the State of New Jersey. The spill has been contained and cleaned-up. There was no actual or potential impact on the environment and no impact on the health and safety of the public or onsite personnel. "Due to notification of a government agency, this event is being reported under 10CFR50.72 (b)(2)(xi)." The spill did not reach the federal reportable quantities limit. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-17
49199 | 0 | PARADISE FOSSIL PLANT |  |  |  |  | 2013-07-17 10:30 | 2013-07-17 15:42 | 2013-07-17 | MOISTURE GAUGE SHUTTER STUCK IN OPEN POSITION "TVA's Paradise Fossil Plant uses a coal scan moisture monitor with a sealed source containing 3 millicuries of Cesium-137. The gauge is used to monitor the moisture in the coal being transferred on a common feed line to three units at Paradise Fossil Plant. On July 17, 2013 at 1030 CDT, the shutter on the moisture gauge was determined not to be operable. The shutter failed in the open position. The shutter failure discovery was made during the six month shutter test. The issue is being entered into the corrective action program. No personnel radiation exposure was received. The source is not shuttered, but the gauge is in the operating position and is in a safe condition. "A twenty-four hour notification is required per 10 CFR 30.50(b)(2) due to failure of the moisture monitor shutter to close. "NRC Region II Duty Officer and NRC Region I Duty Officer will be notified." Gauge model TBM-201. Licensee stated that there is no danger of personnel exposure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | KY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-07-25
49198 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-07-17 13:35 | 2013-07-17 15:05 | 2013-07-17 | PLANNED TESTING OF STACK RADIATION MONITORS "Millstone Unit 2 loss of assessment capability due to pre-planned maintenance of the Millstone Station stack radiation monitor RM-8169 at 1335 EDT on 7/17/13. This event is reportable pursuant to 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability. During the maintenance, Unit 2 was at 100% power, Mode 1. We informed the State of Connecticut, Waterford dispatch, and the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-17
49197 | -1 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE |  | 2013-07-19 12:16 | 2013-07-19 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: Test Event Updating said Test Event Retracting Test Event blah, blah, blah, blah aklsjf xxx aklsjf yyy aklsjf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | [10 empty] | NON EMERGENCY | 4 | AR | POW | [5 empty] | 0 | 2013-07-19
49196 | 0 | PILGRIM | 1 |  |  | [1] GE-3 |  | 2013-07-16 23:50 | 2013-07-17 | SALT SERVICE WATER SYSTEM DECLARED INOPERABLE "On Tuesday, July 16, 2013 at 1652 [EDT], with the reactor at 100% core thermal power (CTP) the Pilgrim Nuclear Power Station (PNPS) entered a 24-hour shutdown Limiting Condition for Operation (LCO) for Salt Service Water (SSW) inlet temperature exceeding the Technical Specification (TS) limit in TS 3.5.B.4. The LCO was subsequently exited at 1830 hours when the temperature of SSW trended to below the TS limit. "Under certain accident conditions the SSW system is required to provide cooling water to the Reactor Building Closed Cooling Water (RBCCW) system heat exchanger. When the inlet temperature to this supplied load exceeds the 75 [degrees] F limit established in the TS, the SSW system is declared inoperable until the temperature trends below this value. This condition existed for approximately 1-1/2 hours and the SSW system was declared operable and the LCO exited. A maximum temperature of 75.3 [degrees] F was recorded during this period. "The SSW temperature is being closely monitored and trended on a continuous basis. "This event has no impact on the health and safety of the public. "The licensee has notified the NRC Senior Resident Inspector." SSW temperature varies with tidal movement. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-07-17
49195 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-16 14:20 | 2013-07-16 | 60 DAY REPORT - INVALID ACTUATION OF SPECIFIED SYSTEM "This 60-day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Nuclear Service Water (RN) system. This event had no impact on public health and safety. "During work to replace a timer associated with an RN (Nuclear Service Water) level circuit, electrical adapters and jumpers were installed incorrectly, resulting in generation of an Emergency Low Pit Level signal. This resulted in an unplanned actuation for RN to realign its suction source from Lake Wylie (normal source) to the alternate source, the SNSWP (Standby Nuclear Service Water Pond). On 5/28/13, with both units at 100% power, a lo-lo level signal was received for A Train RN Pit, initiating the realignment to the SNSWP for both A and B trains. Prior to this event, both trains of RN were aligned to the SNSWP for maintenance. "The lo-lo level signal did initiate a start of all available RN Pumps. Associated valves, including RN crossover valve, return header isolation valves and non-essential header isolation valves closed as expected. This separated RN trains A and B. This was a complete actuation for Train A and the system performed as designed for existing plant conditions. This event was entered into the site corrective action program for resolution." The licensee will notify the NRC Resident Inspector, as well as, the State and local governments. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-07-16
49194 | 0 | MA RADIATION CONTROL PROGRAM | [5 empty] | 2013-07-16 10:57 | 2013-07-16 | AGREEMENT STATE REPORT - SEALED SOURCE FAILED LEAK TEST The following information was obtained from the Commonwealth of Massachusetts via facsimile: "When conducting a routine leak test for one of their Ni-63 source foils, the licensee submitted for analysis a leak test swab of the inactive side of the source foil and received on 7/12/13, at the end of the day, a leak test result of 0.008 uCi. The licensee submitted a report on 7/15/2013 to the Agency [Massachusetts Radiation Control Program] which states the source foil was in storage, it remains in storage, and was never used in any projects. Licensee reports the source foil will be decontaminated and the leak test will be repeated. All decontamination materials will be placed and sealed in a radioactive waste container and will be placed in the radioactive material storage area. "Source will remain in storage until undergoing decontamination cleaning and subsequent leak test. "Component name: Ni-63 source foil "Manufacturer: Eckert & Ziegler "Model # NER-004-13 "Manufacture date: November 2008 "Serial Number: 13-2080 "Isotope activity: 0.015 Ci "Assay Date: November 2008" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-07-24
49193 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 |  | 2013-07-16 07:48 | 2013-07-16 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: MAINTENANCE ON TECHNICAL SUPPORT CENTER / OPERATIONS SUPPORT CENTER VENTILATION "Scheduled maintenance of the Technical Support Center (TSC) / Operations Support Center (OSC) HVAC system for replacement of charcoal filters started at 0430 hours [PDT] on 7/16/13 and will last approximately 37 hours (estimated time from equipment tag out back to OPERABLE). During this time the TSC and OSC will not be available for use to support emergency response activities. Established compensatory measures direct Emergency Response Organization (ERO) members normally responding to either of these facilities to respond to alternate locations. No other emergency response facilities are impacted by the scheduled TSC / OSC Facilities HVAC maintenance work. "This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. A follow up notification will be made when HVAC maintenance to the TSC / OSC Facilities has been completed and operability of these EP Facilities has been restored." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-16
49192 | 0 | PA BUREAU OF RADIATION PROTECTION | [5 empty] | 2013-07-15 19:05 | 2013-07-15 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION LIMIT EXCEEDED ON PACKAGE The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "Notifications: On July 15, 2013 the licensee informed the Department's Bureau of Radiation Protection (Central Office) of the discovery of a radioactive materials shipping event. The event was reportable 'immediately' per 10CFR20.1906(d)(1); 10CFR71.87(i); and 49CFR173.443(a) Table 9. "Event Description: During a licensee internal review of forms during the week of July 8, 2013, it was realized that an event which occurred on May 17, 2013 was not reported properly. A package containing 1.5 curies of fluorine-18 (F-18) was received by the licensee. F-18 has a half-life of about 1.8 hours. Upon inspection on May 17th, the net surface removable contamination was found to be 395 dpm/cm2. This is in excess of the U.S. DOT beta/gamma removable contamination limit of 220 dpm/cm2. The F-18 supplier was immediately notified, along with the courier. An initial investigation by the supplier showed no issues encountered during the preparation and initial wipe tests of the shipment. More information will be given when received. "Cause of the Event: Unknown at this time. "Actions: The licensee has since reviewed their internal package acceptance procedure, along with reporting event requirements, and will retrain all personnel accordingly. The [Pennsylvania] Department [of Environmental Protection Bureau of Radiation Protection] plans a reactive inspection. "Media Attention: None at this time. "Event Report ID No: PA130019" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-07-23
49191 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-15 16:10 | 2013-07-15 | UNPLANNED LOSS OF COMMUNICATIONS DUE TO OFFSITE FIBER OPTIC CABLE DAMAGE "At approximately 0934 EDT on Monday, July 15, 2013, the Cook Nuclear Plant (CNP) experienced a loss of capability to transmit Emergency Response Data System (ERDS) information to the Nuclear Regulatory Commission (NRC). Emergency Plan Implementing Procedures provide direction to manually record ERDS data for transmission to the NRC via telephone or fax. Concurrent with the loss of ERDS was a loss of the NRC 'Red Phone' (FTS-2000). "The suspected cause of the loss was a damaged fiber optic cable located offsite in Bridgman, Michigan unrelated to CNP. This caused the failure of the internet service provider to CNP. Communications via alternate phone lines and corporate service number remain available and have been tested. CNP has contacted offsite service providers for restoration of service. The estimated time for return to service is 2000 EDT on Monday, July 15, 2013. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of communications capability which includes events that would significantly impair the ability of the licensee to implement the functions of its emergency plans if an emergency were to occur." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 7/15/13 AT 2114 EDT FROM KELLY BAKER TO DONG PARK * * * "At 2050 EDT on Monday, July 15, 2013, DC Cook Operations Department was notified by Information Technology (IT) that the offsite fiber optic cable that was damaged had been repaired. Affected equipment was verified to be working properly, specifically, Emergency Response Data System (ERDS) data is transmitting and the NRC 'Red Phone' is functional. Communication capability has been restored. "The licensee has notified the Senior NRC Resident Inspector." Notified R3DO (Hills). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-15
49190 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP |  | 2013-07-15 10:44 | 2013-07-15 | LOSS OF ASSESSMENT CAPABILITY DUE TO PREPLANNED MAINTENANCE "Loss of assessment capability due to preplanned maintenance affecting radiation monitors. Terry Turbine Radiation Monitor MSS-RE79 and Supplementary Leak Collection Release System Radiation Monitor HVR-RE19B will be out for preplanned maintenance. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-15
49189 | 0 | PILGRIM | 1 |  |  | [1] GE-3 |  | 2013-07-15 00:58 | 2013-07-17 | UNUSUAL EVENT DECLARED DUE TO LOSS OF CONTROL ROOM ANNUNCIATORS The licensee declared a Notice of Unusual Event resulting from a loss of control room annunciators for greater than 15 minutes. The EAL Condition is SU 4.1. Compensatory measures have been established per Abnormal Operating Procedures. The plant continues to operate at 100 percent power. The licensee has called for support staff to troubleshoot the issue. No other major components are out of service. The licensee has notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC and the Nuclear SSA via email. * * * UPDATE FROM KEVIN O'ROURKE TO PETE SNYDER AT 0205 EDT ON 7/15/13 * * * Annunciator indication has returned for some time and appears to be working. Engineering and electrical instrumentation and control staff are onsite to troubleshoot but have not established any cause. The licensee remains in the Unusual Event until additional confidence can be established in annunciator indication. Notified R1DO (Cook). * * * UPDATE FROM STAN PAUL TO JOHN SHOEMAKER AT 2350 EDT on 7/16/13 * * * "The NOUE declared on July 15, 2013 at 0029 EDT hours due to loss of main control room annunciation was terminated on July 16, 2013 at 2310 EDT hours when the annunciation system was declared functional." Plant personnel and vendors have completed diagnostic checks and testing, system voltages are normal, and the annunciator system is working normally. The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray), NRR EO (Hiland), IRD MOC (Grant), DHS SWO, FEMA, DHS NICC and the Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-07-15
49188 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 |  | 2013-07-14 16:29 | 2013-07-14 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 1600 CDT on Sunday, July 14, 2013, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system will be removed from service for planned preventative maintenance activities on the TSC air handling unit and air compressor units. During the maintenance, the TSC ventilation will be shut down. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 48 hours. Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing EP (Emergency Preparedness) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration, the Station Emergency Director will evacuate and relocate the TSC staff in accordance with station procedures. "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-14
49187 | 0 | PILGRIM | 1 |  |  | [1] GE-3 |  | 2013-07-11 19:49 | 2013-07-11 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for a banned substance during a random fitness-for-duty test. The employee's access to the plant has been terminated pending an ongoing investigation. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.719 |  |  |  | 0 | 2013-07-11
49186 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-11 15:26 | 2013-07-11 | PLANT EMPLOYEE TRANSPORTED OFFSITE FOR MEDICAL TREATMENT "A Plant Vogtle employee on site complained of medical issues while performing work inside Unit 2 containment at 1127 EDT. After being transported offsite to Burke County Hospital, Plant Vogtle was notified at 1426 EDT that the individual was deceased. The [NRC] Resident Inspector has been notified." The death was not known to be related to work performed at the site, and the employee was not contaminated when transported offsite. The licensee will notify OSHA. * * * UPDATE ON 7/11/13 AT 1655 EDT FROM NAVEEN KOTEEL TO DONG PARK * * * The licensee notified OSHA at 1625 EDT and will also be making a media/press release. Notified R2DO (Nease). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-11
49185 | 0 | FLORIDA BUREAU OF RADIATION CONTROL | [5 empty] | 2013-07-10 17:04 | 2013-07-10 | AGREEMENT STATE REPORT - LOST I-125 CALIBRATION SOURCES The following information was obtained from the State of Florida via facsimile: "IsoAid informed the state radioactive materials section on 20 June 2013 of 10 lost I-125 calibration sources. Sources discovered missing on or about 5 June 2013. Licensee believes they sent the 10 sources to an incorrect licensed facility. IsoAid is currently contacting 11 different facilities that were shipped sources on the same day the lost 10 were shipped. Licensee's corrective actions, so far, consists of retraining all involved departments and individuals, and adding a shipper's check list to their process to make documentation of shipped packages more traceable. [Florida] Radioactive Materials is investigating this incident. This office [Florida Department of Health] will take no further action on this incident." Each source contained 0.3 mCi of Iodine-125. Florida Incident number: 13-046 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2013-07-18
49184 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-10 16:13 | 2013-07-10 | UNIT 2 AUTOMATIC REACTOR TRIP "On July 10, 2013, at 0950 PDT, the Diablo Canyon Power Plant Unit 2 500kV line differential relay actuated. This action tripped the turbine and opened the generator output breakers to isolate the generator. With the turbine tripped and Unit 2 operating above the P-9 50% power permissive, a reactor trip was initiated from the reactor protection system. "All plant equipment responded as designed. All three Unit 2 Auxiliary Feedwater pumps started, the Containment Fan Cooling units started and ran in slow speed, and the standby Auxiliary Saltwater train started, all as expected. "Unit 2 is stable at normal operating temperature and pressure. All power transferred to the plant startup source without incident. Condenser vacuum was maintained. "The preliminary cause of the differential relay actuation was a flashover of Phase A 500 kV to ground across the Phase A lightning arrestor during maintenance activities to wash the 500 kV insulators. "NRC Resident Inspector has been informed of this event. "A press release is planned for local media." Decay heat is being removed by steam dumps to the condenser. No relief valves lifted during the transient. The steam generators are being supplied by the auxiliary feedwater pumps. There were no injuries to personnel. Unit 1 was not affected. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2013-07-10
49183 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP |  | 2013-07-10 12:46 | 2013-07-10 | LOSS OF ASSESSMENT CAPABILITY DUE TO FAILURE OF A & B MAIN STEAM LINE RADIATION MONITORS "A and B Main Steam Line Radiation Monitors 3MSS-RE75 and 76 have failed and were declared inoperable at 0513 hours July 10, 2013. Repairs have been completed and A and B Main Steam Line Radiation Monitors 3MSS-RE75 and 3MSS-RE76 were returned to service at 0900 hours July 10, 2013. The unit is in Mode 1. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(xiii) as is any event that results in a major loss of emergency assessment capability, off-site response capability, or off-site communications capability. "The licensee informed the State of Connecticut, Waterford dispatch, and the NRC Resident Inspector." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-10
49182 | 0 | ST ALPHONSUS REGIONAL MED CTR | [5 empty] | 2013-07-09 16:06 | 2013-07-09 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: MEDICAL EVENT - DOSE DELIVERED TO OTHER SITE On December 20, 2012, a patient was administered microspheres to treat the liver. On July 9, 2013 the administering facility learned that a biopsy identified microspheres in a slow healing gastric ulcer. The facility is assuming that the patient received a dose that exceeded the limits based on the presence of microspheres and the development of a gastric ulcer. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [10 empty] | 4 | ID | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2013-07-17
49181 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 |  | 2013-07-08 21:14 | 2013-07-08 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE SPILL "On July 8th, 2013, at approximately 1730 CDT, the Minnesota State Duty Officer was notified of an approximately 50 gallon sodium hypochlorite spill onsite. The spill has been contained and clean-up is in progress. There was no actual or potential impact on the environment and no impact on the health and safety of the public or onsite personnel." The licensee will also be notifying Wright County. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-08
49180 | 0 | NJ RAD PROT AND REL PREVENTION PGM | [5 empty] | 2013-07-08 14:37 | 2013-07-08 | AGREEMENT STATE REPORT - LEAKING SOURCE The following information was obtained from the State of New Jersey via email: "At approximately 1:30 p.m. [EDT] on Monday, July 8, 2013, the consulting health physicist for Hopewell Radiology Group called to inform the NJDEP's RMP [New Jersey Department of Environmental Protection Radioactive Materials Program] that a sealed vial source originally containing approximately 209 uCi of Cesium-137 on June 1, 2001, was found to be leaking. The source was manufactured by Eckert & Zeigler and has a serial number of 747-33-46. "A routine semi-annual leak test of the source revealed the presence of 0.067 uCi of removable contamination, which exceeds the limit of 0.005 uCi. "The source has been removed from service and is secured at the licensee's location. The licensee is arranging for appropriate disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2013-07-16
49179 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 |  | 2013-07-08 14:11 | 2013-07-08 | 60 DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR "This 60-day telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation of the Emergency Diesel Generators (EDGs) reportable under 10 CFR 50.73(a)(2)(iv)(A). "On the morning of May 10th, 2013, at approximately 0141 EDT the B Emergency Diesel Generator (EDG) subsystem was inoperable for a planned maintenance work window on the B EDG only (there are two EDGs per subsystem). The work was completed to the point that protective tagging removal and testing of the B EDG were the only activities left. "During the process of removing protective tagging, an operator incorrectly opened a switch-gear cubicle door that contained the potential transformer fuses for the B division emergency electrical bus (10600 bus); the system is designed such that opening the cubicle door disconnects the fuses from the circuit. The potential transformers reduce the associated bus voltage (in this case the 10600 bus), nominally 4160V, to 120V for the monitoring and control circuits. These circuits monitor the 10600 bus voltage and initiate a start signal for the EDGs should voltage be degraded or lost. After a time delay of less than or equal to 2.5 seconds, if voltage is not restored, the normal supply breaker for the 10600 bus will open and the EDG output breakers will close re-powering the bus from its emergency source. "The response of the 10600 bus control and monitoring circuits functioned as designed. An initiation signal was sent to the D EDG control system when the monitoring circuit sensed no bus voltage (potential transformer fuses removed; door open). With the immediate closure of the cubicle door, the monitoring circuit was restored and 10600 bus voltage was sensed. This resulted in the under voltage logic returning to normal hence, the 10600 bus did not disconnect from its normal station power source and the D EDG output breaker did not close to power the 10600 bus. "Subsequently the D EDG was secured (0146 EDT on May 10th) and protective tagging removal and testing of B EDG continued. The B EDG subsystem was declared operable on May 12, 2013 at 0315 EDT. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-07-08
49178 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE |  | 2013-07-08 10:57 | 2013-07-08 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE LEAK: "On July 8, 2013, at 0830 EDT, the National Response Center and the State Watch office were notified of a leak greater than the limit of 109 gal of 11% Sodium Hypochlorite onto the ground. Total amount spilled is approximately 200 gallons. While the leak is currently active, the leak has being routed to an approved injection point. "This notification is being made in accordance with 10CFR 50.72 (b)(2)(xi) due to notification of off-site agencies." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-08
49177 | 0 | GINNA | 1 |  |  | [1] W-2-LP |  | 2013-07-07 11:15 | 2013-07-07 | LOSS OF EMERGENCY SIRENS DUE TO POWER OUTAGES "At 0326 EDT on 07/07/2013, it was determined that 14 of 96 Ginna Nuclear Power Plant Emergency Offsite Sirens were nonfunctional. The apparent cause is loss of power to the sirens due to storm related power outages. The weather has since returned to normal conditions, and residential power restoration is in progress. [At the time of this report, only 3 sirens remained without power]. This event is being reported as a Loss of Emergency Preparedness Capabilities pursuant to 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-07
49176 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 |  | 2013-07-07 06:49 | 2013-07-08 | LOSS OF RADWASTE/REACTOR BUILDING VENT GASEOUS EFFLUENT RADIATION MONITORING CAPABILITY "At 0400 EDT on July 7, 2013, Nine Mile Point Unit 2 isolated the Reactor Building to comply with Tech Spec 3.3.6.2.A.1 Secondary Containment Isolation Instrumentation. Isolating the Reactor Building was the result of Refuel Floor Radiation Monitor 2HVR*CAB14A becoming inoperable on 7/6/13 at 0430 hours. As a result of the Reactor Building being isolated, the Radwaste/Reactor Building Vent Gaseous Effluent Radiation Monitor has been declared non-functional based on sample flow rates. "The Radwaste/Reactor Building Vent Gaseous Effluent Radiation Monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to the out-of-service Radwaste/Reactor Building Vent Gaseous Effluent Monitor is considered a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "Repairs and testing are currently in progress to correct the cause and restore functionality of Radiation Monitor 2HVR*CAB14A. The expected return to service time is within the next 12 hours. "Compensatory actions for the non-functional Radwaste/Reactor Building Vent Gaseous Effluent Radiation Monitor are in place to take and analyze periodic grab samples and flow estimates in accordance with the Offsite Dose Calculation Manual. "The NRC Resident Inspector has been notified." The licensee will also be notifying state authorities. * * * UPDATE ON 7/8/13 AT 1145 EDT FROM DAN CIFONELLI TO DANIEL MILLS * * * "Radiation Monitor 2HVR*CAB14A has been repaired and was declared operable at 1920 on July 7, 2013. Normal Reactor Building ventilation was subsequently re-established, and the Radwaste/Reactor Building Vent Gaseous Effluent Radiation Monitor was retumed to service at 2100 on July 7, 2013, thereby restoring emergency assessment capability. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-07
49175 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP |  | 2013-07-06 23:47 | 2013-07-07 | UNIT 1 SPENT FUEL POOL ISLAND RADIATION MONITOR INOPERABLE The Millstone Unit 1 spent fuel pool island ventilation system tripped offline for reasons unknown at the time of this report. The spent fuel pool island radiation monitor requires the ventilation system to be in service to function. Therefore, the radiation monitor was declared inoperable. The loss of the radiation monitor results in a loss of assessment capability. The licensee's chemistry department is taking compensatory samples in accordance with the Radiation Effluent Monitoring Offsite Dose Calculation Manual action statement until the spent fuel pool island ventilation can be restored. The licensee has notified the NRC Resident Inspector, state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-07
49174 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 |  | 2013-07-05 12:34 | 2013-07-05 | 60 DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID DIVISION 1 CONTAINMENT ISOLATION DUE TO MOTOR GENERATOR TRIP "On May 22, 2013, at approximately 1134 CDT, while Unit 1 was operating at 100% power, the 1A Reactor Protection System (RPS) Motor Generator (M/G) set tripped causing a loss of the A RPS bus. This caused the actuation of the Division 1 (outboard) primary containment isolation logic. This was an event that resulted in the actuation of a general containment isolation signal affecting more than one system. However, as this event meets the definition of an invalid actuation (i.e. not a response to an actual plant parameter exceeding a trip setpoint), this notification is being made in accordance with 10 CFR 50.73(a)(1) in lieu of a Licensee Event Report. "In response to the trip of the 1A RPS M/G, operators swapped the A RPS bus to the alternate power supply using the applicable response procedure. The containment isolation signal was reset and the systems were restored to their normal lineup. Reactor power was not affected by this event. All safety related equipment controlled by the affected primary containment isolation circuits operated as designed. "The 1A RPS M/G trip was due to a motor fault requiring motor replacement. Replacement of the motor was completed on 5/26/13 and the A RPS bus was restored to its normal power supply on 5/27/13." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-07-05
49173 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-03 12:51 | 2013-07-03 | LOSS OF EMERGENCY RESPONSE COMMUNICATIONS DUE TO A LOSS OF ANCILLARY POWER "At 0156 PDT on July 3, 2013, Diablo Canyon Power Plant experienced a loss of power to ancillary facilities on site. This affected power supplies to data systems used by the Emergency Response Facilities [EOF]. All plant status and performance data in the TSC [Technical Support Center] and EOF is available via telephone bridge line and control room phone talker. "Additionally, the Emergency Response Data System (ERDS) has been determined to be unavailable. "The data system loss occurred following depletion of backup batteries in the affected data center." The licensee notified the NRC Resident Inspector and will notify state and local agencies. * * * UPDATE FROM DAN STERMER TO JOHN SHOEMAKER AT 1948 EDT ON 7/3/13 * * * "At 2120 PDT on 6/23/13, Diablo Canyon Power Plant (DCPP) experienced a loss of the offsite 230 kV startup power source due to an offsite transmission system relay actuation (see EN# 49143). At 1000 PDT on 7/3/13, PG&E identified that the conditions present on 7/3/13 that resulted in loss of plant status and performance data in the Technical Support Center (TSC) and Emergency Operations Facility (EOF) (see EN# 49173) also existed on 6/23/13. This update reports the 6/23/13 loss of plant status and performance data in the TSC and EOF due to loss of power in the data center that supports those facilities. All plant status and performance data required for emergency assessment and communication remained available via a telephone bridge line and control room phone talker. The data became unavailable in the TSC and EOF following depletion of backup batteries in the affected data center. "On 7/3/13 PG&E reconfigured the TSC workstations to ensure they would function and provide data for emergency assessment capability independent of the status of the data center power supplies. "The Emergency Response Data System was also unavailable following the loss of 230 kV startup power on 6/23/13 due to loss of power to the data center. This unavailability was as designed and as expected. "This delayed event notification has been entered into the DCPP corrective action program." The licensee has notified the NRC Resident Inspector. Notified the R4DO (Gaddy) and ERDS Group via email. | 73 | 100 | 0 | 48 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-03
49172 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP |  | 2013-07-03 11:37 | 2013-07-03 | STACK RADIATION MONITOR PRE-PLANNED MAINTENANCE Millstone Unit 2 has removed the High Range Stack Radiation Monitor, RM-8168 from service for pre-planned maintenance. The radiation monitor will be restored to service after maintenance is complete. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-03
49171 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP |  | 2013-07-03 10:46 | 2013-07-03 | REACTOR TRIP FOLLOWING LOSS OF INSTRUMENT AIR TO MAIN FEEDWATER REGULATING VALVES "On July 3, 2013, at 0741 EST, the Indian Point Unit 2 CCR received a trip of both Main Boiler Feed Pumps (MBFP) and entered 2-AOPúFW-1, Loss of Feedwater. The unit was manually tripped at 0741 per 2-AOP-FWú1 due to the trip of both MBFPs. Operators entered E-O, Reactor Trip or Safety Injection. "All control rods fully inserted. All safety systems responded as expected. The Auxiliary Feedwater (AFW) System actuated as expected. Offsite power and plant electrical lineups are normal. No primary or secondary code safety valves lifted. The 23 and 24 Main Steam Isolation Valves (MSIV) failed closed as a result of the loss of Instrument Air (IA). The 21 and 22 MSIVs remain open with the Main Condensers being used for heat sink. The reactor is in Mode 3 and stable. Unit 3 was unaffected and remains at 100% power. "Preliminary investigations determined a two inch copper IA line in the switchyard which is normally buried had a failed coupling causing loss of IA to the main feedwater regulating valves. The IA line traversed an excavated area of the switchyard going to the Auxiliary Boiler Feed Pump (ABFP) Building. AFW operated using the Nitrogen backup supply to ABFP control valves until Instrument Air was restored to the ABFP building. An investigation is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-07-03
49170 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-07-03 01:15 | 2013-07-03 | UNAVAILABILITY OF TECHNICAL SUPPORT CENTER VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0115 EDT on Wednesday, July 3, 2013, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 2100 EDT on July 3, 2013. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM CHRIS PEAK TO JOHN SHOEMAKER ON 7/3/13 AT 1540 EDT * * * "The TSC ventilation system maintenance and testing was completed satisfactorily and the system was restored to service at 1430 EDT on 7/3/13. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Kunowski) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-07-03
49169 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE |  | 2013-07-03 00:24 | 2013-07-03 | NOTICE OF UNUSUAL EVENT DUE TO EXPLOSION IN A NON-SAFETY RELATED LOAD CENTER "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On 7/2/2013, at approximately 2027 MST, Palo Verde Unit 1 experienced a reactor power cutback from 100% rated thermal power due to explosion [in a non-safety related load center (1ENGNL02)]. The unit was at normal temperature and pressure prior to the cutback. "At 2035 [MST] PVNGS Unit 1 declared an Unusual Event due to the explosion EAL HU 2.2. "Unit 1 is stable at 61% rated thermal power. No ESF actuations occurred and none were required. The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public." The licensee will notify the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. * * * UPDATE ON 7/3/13 AT 0229 EDT FROM JEONG LIM TO PETE SNYDER * * * "Palo Verde Unit 1 is stable at 58% rated thermal power and is implementing abnormal operating procedures for reactor power cutback due to loss of one Main Feedwater Pump and degraded electrical power due to loss of non-class 13.8kV load center 1ENGNL02. Load center 1ENGNL02 was damaged from an apparent electrical malfunction that originated within the load center. The 13.8kV supply breaker to load center 1ENGNL02 tripped to deenergize the load center. Palo Verde Fire Department personnel responded but determined that the load center was deenergized and no fire existed and no extinguishing agents were applied. No damage to other equipment in proximity to load center 1ENGNL02 was identified during a preliminary inspection of the area around the damaged load center. The NRC Resident Inspector has been notified. "At 2315 [MST] on 07/02/2013, the Unusual Event was terminated." Notified R4DO (Gaddy), NRR EO (Nieh), IRD MOC (Gott), DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. | 61 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-07-03
49168 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 |  | 2013-07-02 10:10 | 2013-07-02 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATORS "This 60-day telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation of the Emergency Diesel Generators (EDGs) reportable under 10 CFR 50.73(a)(2)(iv)(A). Due to the shared configuration of the onsite AC Electrical Distribution System, this event is applicable to both Units 1 and 2. "On May 7, 2013, at approximately 2114 hours Eastern Daylight Time (EDT), while Operations personnel were making preparations for Unit 2 main turbine generator synchronization to the grid, a Main Generator Reverse Power Trip occurred. Main Generator Reverse Power Trip was actuated after adjusting the Manual Voltage Regulator on the Main Generator. The reverse power relay operates the Generator Primary Lockout which initiates a turbine trip and start of all four EDGs. These features functioned as designed. The main generator breaker was open at the time of the event; as such, electrical power was not lost to the emergency busses. "All four EDGs started and operated as expected. Because electrical power was never lost to the emergency busses and none of the EDGs loaded to their respective emergency busses, the actuations were considered to be partial. "The EDGs were returned to their standby line-up by 2229 hours on May 7, 2013. Since no actual bus under voltage condition existed which required the EDGs to start and the start was not in response to actual plant conditions satisfying the requirements for initiation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 24 | 0 | 100 | 24 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-07-02
49167 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 |  | 2013-07-01 21:47 | 2013-07-01 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: HIGH PRESSURE CORE SPRAY MINIMUM FLOW VALVE PRESSURE SWITCH SETPOINT FOUND OUTSIDE OF TOLERANCE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During routine Instrument Maintenance Surveillance Testing (LIS-HP-205), the High Pressure Core Spray System (HPCS) minimum flow valve pressure switch set point was found outside the Technical Specification allowable value. This could have prevented the High Pressure Core Spray System (HPCS), a single train safety system, from performing its design function. This is reportable as an 8 hour ENS notification. "The required actions of Technical Specification (TS) 3.5.1 were entered on 7/01/13 at 1646 [CDT] when the system was made inoperable for surveillance testing. At 1705, maintenance personnel reported minimum flow valve pressure switch set point was found at 112.6 psig, which is outside of the TS Allowable Value of greater than or equal to 113.2 psig (0.6 psig below the Allowable Value). The minimum flow valve pressure switch set point has been calibrated and was left within Technical Specification allowable values, HPCS was declared OPERABLE at 1815 on 7/01/13." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-07-01
49166 | 0 | PA BUREAU OF RADIATION PROTECTION | [5 empty] | 2013-07-01 18:07 | 2013-07-01 | AGREEMENT STATE REPORT - UNPLANNED FIRE AND EXPLOSION AT A REMEDIATION PROJECT SITE The following report was received via facsimile: "Notifications: On June 28, 2013 the licensee informed the PA Department of Environmental Protection's [DEP] Central Office of an explosion that occurred the previous night. The event is reportable within 24 hours per 10 CFR40.60(b)(4). [Note: a voice message was left for a DEP staff person who was off from work on the 28th, thus, the delay in notification to NRC.] "Event Description: The licensee received a call from the Pymatuning Township Fire department's emergency response team at approximately 11:15 [EDT] on June 27, 2013 reporting an explosion inside the operating area of the Whittaker Corp. remediation project site. This is a decommissioning / clean-up site where rare earth metals had been recovered, and the resultant low-level radioactive waste is being removed for license termination. The initial theory is [perhaps] a chemical and exothermic reaction resulted in a contained fire with material being ejected from the waste pile and outside the remediation area boundary. Since the site was shut down and unoccupied at the time of the event, no injuries were reported. The responding fire department did not enter the area; and there are conflicting reports on the use water or other fire-fighting agents. Due to the very low radioactivity concentrations of uranium / thorium series within the waste pile materials - release of licensed material offsite is unlikely. All work at the site has been suspended pending an investigation into the event. Radioactivity surveys and air samples were being made and collected on the 28th to confirm no off site release took place. The material that was ejected from the waste pile during the explosion was surveyed, with no significant activity identified. A sample of this material was sent to an off-site lab to determine a chemical and radiological content. Lastly, the licensee has established a 24 hour fire watch until a cause can be identified. More details will be provided when available. "Cause of the Event: Currently unknown "Actions: The licensee has suspended all work, and has restricted access to the area. The PA DEP NW and SW Regional Offices are performing reactive ES&H [Environment, Safety, and Health] and Radiation Protection Program inspections on July 1st and 2nd respectively. "Media Attention: None at this time." PA Event Report ID No: PA130016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-07-09
49165 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY |  | 2013-07-01 17:53 | 2013-07-14 | UNPLANNED CONTAMINATION EVENT THAT RESTRICTED ACCESS FOR GREATER THAN 24 HOURS "At 1409 hours [CDT] on 6/28/2013, the Plant Shift Superintendent was notified of an unplanned contamination event that occurred in the C-710 Laboratory building. The controller program for the sample cylinder wash system in room #21 failed, causing supply water to flow out of the system. The water leaked through the floor into room B-23, which is located in the basement, and spread contamination onto the floor and a table. The area of the known water leak was immediately posted as a contamination area. Chemical Operations decontaminated the area that was initially contaminated by the water leak at 1730 hours on 6/28/2013. During follow-up investigative surveys conducted by Health Physics, additional contamination was discovered in other areas of the room causing the entire room to be posted as a contamination area (CA). It was initially thought that the additional contamination which was found was legacy contamination unrelated to the water leak; however, based on further investigation and HP survey results [on 7/1/13], it appears that contamination found elsewhere in the room also came from the water leak event. All contamination related to this event was not cleaned up within 24 hours and the room remains restricted at this time. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(1)(i), 'An unplanned contamination event that: Requires access to the contaminated area, by workers or the public, to be restricted for more than 24 hours by imposing additional radiological controls or by prohibiting entry into the area'. "The NRC Resident Inspector has been notified of this event." Room B-23 remained locked over the weekend and was not accessed by plant personnel so the possibility of spreading contamination was minimized. PGDP Problem Report No. ATRC-13-1468: PGDP Event Report No. PAD-2013-05. * * * RETRACTION AT 1522 EDT ON 7/14/13 FROM DEREK WARFORD TO BILL HUFFMAN * * * "Calculations were performed by the Health Physics group of the estimated quantity of material in the release. The estimate was based on: (1) An isotopic analysis of the contamination revealed three predominant isotopes, all Uranium daughters, Pa-234, Thorium-231, and Thorium-234; (2) the estimated water volume 'released' of 8.0 liters; and (3) that the isotopic concentration in the 8.0 liters of water was homogeneous. Based on the calculations, the summation of the mixture of isotopes was 4.52E2 microcuries and is approximately 30 percent of 5 ALI [annual limit on intake] for the most restrictive isotope, Th-234 (1.5E3 microcuries). Therefore part (ii) of 10 CFR 76.120(c)(1) was not met and reporting is not required. "Based on the above information the subject notification should be retracted. "This retraction has been discussed with the NRC Senior Resident Inspector." R2DO (Nease) and NMSS EO (Benner) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2013-07-01
49164 | 0 | NE DEPT OF HEALTH AND HUMAN SERVICE | [5 empty] | 2013-07-01 17:35 | 2013-07-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received via email: "Exit signs - model 2040-50-R-10 WH, serial numbers A99977 and A99997 [each] with 11.5 Curies of H3 [tritium] were in a laboratory. The laboratory was inundated with water from a frozen pipe. The [laboratory] cleanup went down to the studs or iron beams. The facility has made a search [after the cleanup] but have not been able to locate the signs. The facility presumes that the signs were sent to a landfill. The facility will include exit signs in their next safety training, include information concerning exit signs in the Emergency Action Plan, and will make the leadership team aware of the mistake. "Cause: Inattention to detail. "Corrective Action: Personnel received additional training." Nebraska State Item Number: NE130003. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2013-07-09
49163 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP |  | 2013-07-01 15:27 | 2013-07-01 | DEGRADED CONDITION DUE TO RCP SEAL LINE PRESSURE BOUNDARY LEAKAGE "On 07/01/2013 at 1103 [EDT], inspection personnel identified leakage from a 3/4 inch small-bore pipe socket weld for RCP 1-2 first stage seal cavity vent line. At current Reactor Coolant System conditions (Normal Operating Pressure and Temperature), the leak rate is approximately 8 to 9 drops per minute. "The plant entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.13, 'RCS Operational Leakage', Condition B. Repairs to the line are being evaluated. "This pressure boundary leakage is reportable per 10 CFR 50.72(b)(3)(ii)(A). The NRC Resident Inspector has been notified." The LCO requires the licensee to be in Mode 5 by 2303 EDT on 7/2/13. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-07-01
49162 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 |  | 2013-07-01 11:38 | 2013-07-01 | FUEL OIL SPILL INTO A STORM DRAIN LEADING TO THE DELAWARE RIVER "On July 1, 2013, at 0846 [EDT] the Hope Creek Shift Manager was notified of a fuel oil spill that entered a storm drain leading to the Delaware River. The onsite Fire Department responded to the scene to contain the spill. The spill was terminated and cleanup activities were completed at 0930 [EDT]. "A 15 minute notification to the State of New Jersey Department of Environmental Protection was required and completed on July 1, 2013, at 0900 [EDT]. "The unit remains at 100% power. "The station has initiated an investigation to determine the cause of the spill and initiate immediate corrective actions. "No personnel injuries resulted from the event. "This report is being made in accordance with 10 CFR 50.72(b)(2)(xi), notification of other government agencies. "The NRC Resident Inspector has been notified. "Lower Alloway Creek Township will be notified." The licensee has also notified the National Response Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-01
49161 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP |  | 2013-06-30 22:53 | 2013-06-30 | <br><br>EN Revision Imported Date : 6/13/2018<br><br>EN Revision Text: AUXILIARY FEEDWATER SYSTEM DECLARED INOPERABLE DUE TO HIGH HOTWELL TEMPERATURES "The Auxiliary Feedwater System was inoperable due to elevated hotwell temperatures from 1720 to 1739 EDT on 6/30/13. At no time was there a risk to the health and safety of the public. The elevated hotwell temperatures resulted from the loss of multiple cooling tower fans due to a lightning strike. "Cooling tower fans and hotwell temperatures have been restored. Power was slightly reduced solely to maintain condenser vacuum until cooling tower fans were restored." At Catawba, the hotwell is a credited water supply for the auxiliary feedwater system. The unit is currently in a power ascension back to 100%. No other plant equipment was affected by the lightning strike. The licensee will be notifying the state warning points in both North and South Carolina and local warning points in Gaston, York, and Mecklenburg counties. They have notified the NRC Resident Inspector. | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2013-06-30
49160 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION |  | 2013-06-30 09:51 | 2013-06-30 | ENTRY OF AN UNAUTHORIZED INDIVIDUAL INTO THE PROTECTED AREA Actual entry of an unauthorized person into the Controlled Access Area. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2013-07-08
49159 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP |  | 2013-06-29 22:48 | 2013-06-29 | AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP TRIP "Automatic trip of Reactor Coolant Pump 1-2 due to an electrical differential current fault resulted in an RPS actuation on Flux/Delta Flux/Flow. Startup Feedwater Valve 1 did not respond as expected post-trip and has been placed in manual control. All secondary side steam reliefs initially re-seated following reactor trip. Subsequent Main Steam Line #1 Safety Valve leakage mitigated during post-trip recovery actions. All other systems have functioned as expected. The plant is stable in Mode 3 - Hot Standby." All rods inserted into the core during the trip. Decay heat is being removed via turbine bypass valves to the main condenser with normal feedwater to the steam generators. The plant is in its normal shutdown electrical lineup. The licensee characterized the trip as uncomplicated. The licensee will be notifying Lucas and Ottawa counties, the State of Ohio and will be issuing a press release. They have notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-06-29
49158 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP |  | 2013-06-29 18:30 | 2013-06-29 | DIGITAL RADIATION MONITORING SYSTEM OPERATING INTERMITTENTLY "At 1214 EDT on June 29, 2013, Beaver Valley Power Station (BVPS) Unit 2 determined that the Digital Radiation Monitoring System (DRMS) was operating intermittently resulting in an intermittent loss of control room radiation monitor indication and alarm capability. BVPS Unit 2 DRMS was declared non-functional. Repair efforts were initiated and at 1415 EDT DRMS was restored to functional status. Compensatory measures were established during the period of time that the DRMS was operating intermittently. "The period that BVPS Unit 2 DRMS was non-functional resulted in a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-29
49157 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-06-29 03:12 | 2013-07-02 | OFFSITE NOTIFICATION TO NORTH CAROLINA - RAIN CAUSED OVERFLOW OF HOLDUP POND TO CATAWBA RIVER "Notification is to be made to an offsite agency: North Carolina Department of Environment and Natural Resources [NCDENR]. Due to heavy rains on site, a holdup pond overflowed to the Catawba River. Holdup pond overflow included chemicals (Rotenone) used to treat macro fouling in the Standby Nuclear Service Water Pond. Notification to NCDENR will be made by telephone Saturday morning 6/29/13." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 7/2/13 AT 1139 EDT FROM BRENT BARE TO DONG PARK * * * "Due to continued rains on site, the holdup pond continues to overflow to the Catawba River. The overflow includes a new chemical, Potassium Permanganate, used to neutralize the Rotenone treatment of the Standby Nuclear Service Water Pond. This new chemical has the potential to initially turn water purple, which is normal when applied. The North Carolina Department of Environment and Natural Resources (NCDENR) has been updated." The licensee notified the NRC Resident Inspector. Notified R2DO (Freeman). | 100 | 37 | 0 | 100 | 37 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-07-01
49156 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION |  | 2013-06-28 20:13 | 2013-06-28 | UNPLANNED MEDICAL TREATMENT OF TWO CONTAMINATED INDIVIDUALS "Two employees reported to the on-site dispensary this afternoon with chemical burns to their shoulders at approximately 1645 CDT. The plant nurse and doctor administered treatment to the employees and then sent them home. A whole body survey of the employees in their plant clothing was performed while in the dispensary. The maximum amount of contamination found was present on one of the employee's boots, 20,745 dpm/100cm2. Prior to leaving the Restricted Area, the employees removed all plant clothing, changed into their personal clothing, and exit monitored from the facility. The employees were free of contamination upon release." The licensee plans to notify NRC R2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-06-28
49155 | 0 | ULTRA ELECTRONICS, NSPI | [5 empty] | 2013-06-28 16:57 | 2013-06-28 | PART 21 INTERIM REPORT - LINEAR INDICATIONS/CRACKS IN PRESSURE TRANSMITTER FLANGE FORGING "Description of the Deviation or Failure to comply that is being evaluated: Linear indications/cracks were discovered in the flange forging on four N-E13DM pressure transmitters recently supplied by Ultra Electronics, NSPI to Omaha Public Power District (OPPD), Fort Calhoun Station FC-1-5 Plant. These transmitters with the identified indications had been received by Fort Calhoun but were not installed. Three of the four transmitters have been returned to Ultra Electronics, NSPI for evaluation and analysis. At this time, the fourth transmitter is in process of being returned for additional evaluation. "Evaluation Status: Ultra Electronics, NSPI has performed an initial assessment and determined that the indication/crack penetrates the forging beyond the specified minimum wall thickness. At this time Ultra Electronics, NSPI is in the process of contracting a third party metallurgical research laboratory to assist with evaluation and root cause analysis. Ultra Electronics, NSPI will supply forging samples to the metallurgical research laboratory for analysis including material/composition characteristics as well as the structure and physical characteristics of the indications. Ultra Electronics, NSPI will continue to work with the forging vendor to determine root cause and the extent of the affected material. "Completion of the Evaluation: The evaluation is expected to be completed on or before August 31, 2013" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-06-28
49154 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP |  | 2013-06-28 16:34 | 2013-06-28 | AUTOMATIC REACTOR TRIP DUE TO OFFSITE ELECTRICAL FAULT "On June 28, 2013 at 1330 [EDT], Watts Bar Nuclear Plant Unit 1 reactor automatically tripped due to an electrical fault causing a main generator lockout and subsequent turbine trip. The electrical fault generated an 'A' Main Bank Transformer Differential Relay actuation. Suspected cause is due to an offsite fault. "This is being reported under 10CFR50.72(b)(2)(iv)(B). "Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. This is being reported under 10CFR50.72(b)(3)(iv)(A). "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater, steam dumps and the main condenser. The station is in a normal shutdown electrical alignment. "The NRC Senior Resident has been notified." There were no primary or secondary relief valve actuations during the plant transient. The cause of the electrical fault is being investigated. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-06-28
49153 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 |  | 2013-06-28 14:18 | 2013-06-28 | DOOR INTERLOCK MALFUNCTION RESULTED IN BRIEF LOSS OF SECONDARY CONTAINMENT "At 0749 CDT on June 28, 2013, indication was received in the Control Room that two Secondary Containment doors, in one access opening, were opened simultaneously. The interlock mechanism preventing both doors from operating simultaneously did not operate as expected. This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2. As a result, entry into Technical Specifications 3.6.4.1 Condition A was made due to Secondary Containment being declared inoperable. "The doors were secured at 0749 CDT [total time with both doors open was 7 seconds] and Secondary Containment was declared operable. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-06-28
49152 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 |  | 2013-06-28 04:07 | 2013-06-28 | HIGH PRESSURE CORE SPRAY AND DIVISION 3 DIESEL GENERATOR INOPERABLE FOR 20 MINUTES "At 1758 [PDT] on June 27, 2013, an alarm signaling heating, ventilation and air conditioning (HVAC) trouble in the Division 3 diesel and high pressure core spray (HPCS) room was received in the main control room. Follow-up investigation determined that the switch for the normal room supply fan (DMA-FN-32) was off. It is believed that the switch may have been inadvertently mispositioned during ongoing work in the vicinity. A worker was moving a vacuum nearby and stopped when he heard the local alarm. Columbia Generating Station is performing further investigation to determine if there are other possibilities for DMA-FN-32 control switch being mispositioned. "The fan was returned to service at 1819 [PDT]. An Operation's supervisor was present when returning the switch to ON and verified the switch operated as expected. Loss of DMA-FN-32 results in both the HPCS diesel (DG-3) and the HPCS system being inoperable due to inadequate cooling of those systems. Offsite power for Division 3 was verified to be operable while DG-3 was inoperable. The loss of the HPCS system results in the loss of safety function for a single train system and thus is reportable under the 10 CFR 50.72 sections noted above. "Appropriate Technical Specification actions were entered and exited for DG-3 and HPCS inoperability times. There was no radiological release associated with this event. No safety system actuations or isolations occurred." The licensee notified the NRC Resident Inspector. | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-06-28
49151 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 |  | 2013-06-27 11:33 | 2013-06-27 | 60 DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 1307 CDT on May 2, 2013, with the Duane Arnold Energy Center (DAEC) operating at 100% power, an invalid Group 3 isolation on the 'A' side of the Primary Containment Isolation System occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by a human performance error that led to a blown fuse. Specifically, the fuse failed during pre-planned maintenance on a differential pressure switch when a test clip made inadvertent contact with an energized part of the switch. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-06-27
49150 | 0 | HARRIS | 1 |  |  | [1] W-3-LP |  | 2013-06-27 04:46 | 2013-06-27 | TECHNICAL SUPPORT CENTER VENTILATION PLANNED MAINTENANCE "This is a non-emergency notification. Planned maintenance activities will be performed today which will temporarily affect Technical Support Center (TSC) ventilation. The maintenance will be completed in approximately 20 hours and is scheduled to be worked to minimize out-of-service time. "In the event of an emergency, specific conditions may warrant relocating the TSC to the alternate facility per existing procedures. No other emergency response facilities are impacted by the maintenance. This event is reportable per 10CFR50.72(b)(3)(xiii) because the scheduled maintenance affects an emergency response facility." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-27
49149 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-06-26 10:40 | 2013-06-26 18:33 | 2013-06-26 | INADVERTENT CLOSURE OF OPPOSITE TRAIN VALVE RENDERS SAFETY TRAINS INOPERABLE "At 1040 [EDT], on June 26, 2013, with the Unit 1B Low Pressure Injection (LPI) and Reactor Building Spray (RBS) trains inoperable for planned maintenance, a motor operated isolation valve (1LP-21) was inadvertently closed, rendering the 1A LPI and RBS trains inoperable. The intended action was to close 1LP-22 in the Unit 1B train. 1LP-21 was closed due to a human error. Unit 1 entered Tech Spec 3.0.3 for both trains of LPI and RBS being inoperable. At 1053, on June 26, 2013, the Unit 1A train of LPI and RBS were restored to operable by opening 1LP-21, and Tech Spec 3.0.3 was exited. Units 1, 2 and 3 were stable at 100% power during and after this event. No other safety or non-safety systems were degraded or lost as a result of this event. The event was determined to be reportable under 10 CFR 50.72(b)(3)(v) A, B, C and D "Event or Condition that Could Have Prevented Fulfillment of a Safety Function." "Initial Safety Significance: None. There was no event on-going at the time of discovery that required the Unit 1 LPI and RBS systems to function, and the safety function was restored when the 1A LPI and RBS trains were restored to operability. Although declared inoperable, the Unit 1B LPI and RBS trains were available during the time 1LP-21 was closed. "Corrective Actions: The Unit 1A LPI and RBS trains were restored to operable, an event investigation was commenced and the event was entered into the Oconee Corrective Action Program." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2013-06-26
49148 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-06-25 21:58 | 2013-06-26 01:59 | 2013-06-26 | PLANT SHUTDOWN REQUIRED DUE TO RHR SYSTEM SOCKET WELD LEAK "At 2158 PDT, plant personnel identified a through-wall leak in a Diablo Canyon Power Plant Unit 1 socket weld inside containment that provides a flow path to a relief valve that protects a common portion of both trains of the Residual heat Removal (RHR) system. The as-found condition did not comply with the requirements of equipment control guideline 7.6 and the ASME acceptance criteria. PG&E accordingly declared both Unit 1 trains of RHR inoperable and initiated plant shutdown at 2237 PDT in accordance with requirements of Technical Specification 3.0.3. "PG&E will complete shutdown to Mode 4 and will perform repairs to restore compliance with ASME code requirements." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1303 EDT ON 6/26/13 FROM WESLEY FIANT TO PETE SNYDER * * * "Pacific Gas and Electric Company is submitting an update based on a press release issued at 0915 PDT detailing the above information to local television, newspaper, and radio media outlets. San Luis Obispo County and State of California Offices of Emergency Services have already been notified." The licensee notified the NRC Resident Inspector. Notified R4DO (Pick). | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | ACCIDENT MITIGATION | OFFSITE NOTIFICATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) | 50.72(b)(2)(xi) | 0 | 2013-06-26
49147 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-06-24 16:15 | 2013-06-24 22:07 | 2013-06-24 | EMERGENCY DIESEL GENERATORS UNAVAILABLE FOR AUTO-START "At 16:15 PDT on 6/24/13, an operator performing a post-event annunciator alarm review of the event reported in EN #49143 identified that the operators the previous night had momentarily disabled all three Unit 1 emergency diesel generators, prior to restoring them to their automatic standby control alignment. Between 22:01:10 PDT and 22:02:54 PDT, on 6/23/13, less than the required minimum two diesel generators were available to automatically respond to a design basis accident. Due to the event reported in EN #49143, the start-up 230 kV power source was also unavailable at this time. "At the time of this event the operators were in the procedurally guided process of placing the running diesel generator controls to manual, shutting down the running diesel generators, and returning them to the automatic standby control alignment. In this event the operators placed all the diesel generators in manual and shut them down before returning them to automatic control. During this time the operators would have responded to a plant event by returning the affected diesels to auto, whereupon the normal starting and loading sequence would have resumed in accordance with existing accident analyses. "At the time of discovery all offsite and onsite power sources were operable." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-06-24
49146 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-06-24 11:30 | 2013-06-24 15:23 | 2013-06-24 | AGREEMENT STATE REPORT - SCRAP METAL SHIPMENT FOUND TO CONTAIN UNIDENTIFIED RADIOACTIVE MATERIAL The Oregon Department of Radiation Protection Services received notification, from a scrap metal recycler in Portland, Oregon, that a shipment of scrap metal, for recycling, contains unidentified radioactive material causing low levels of radiation outside the transport vehicle. The shipment originated from a company located in Missoula, Montana. The shipment is under special permit DOT-SP-10656 without a determination of materials meeting or not meeting the regulatory definition of radioactive material. The shipment is a minor radiological concern [approximately 6,000 cpm] based on considerations of the U.S. Department of Transportation and the state official aligning this shipment approval document. The radioactive material was detected in a truck at a scrap metal recycler's portal monitor in Portland, Oregon. The unidentified item is suspected to be located on the left side, near the landing gear, and on the floor of the trailer. The driver was directed to not rearrange the contents of the truck and the shipment will be returned to the originating company in Missoula, Mt. There is no suspected release of radioactive material, radiation exposures, or personnel injury or contamination. The state is continuing it's investigation and has notified the Montana Department of Public Health. Oregon State Incident Docket # 13-0457 and RPS # 13-0024. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-07-02
49145 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-06-20 | 2013-06-24 11:06 | 2013-06-24 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of New York via fax: "The RSO of NYS (New York State) Licensee C2274 called to report a moisture/density (Troxler Model 4640-B 'thin layer') gauge was damaged at a worksite in Far Rockaway, NY. The source (8 mCi of 137 Cs) was in the safe position when it got damaged and the source is within the unit as determined by survey meter readings. The operator was about 5 ft. away from the gauge when it was run over by a roller. The RSO visited the site took measurements to confirm the source was still in the gauge. He called the QC Resources and took a leak test measurement. He is awaiting the results before shipping the gauge to QC Resources. A written report is forthcoming." New York State Event Report: NY-13-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-07-02
49144 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP |  | 2013-06-24 04:49 | 2013-06-27 | PLANNED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER BACKUP GENERATOR "A condition is being reported per TRM 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities performed on the backup diesel generator that supplies TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54 (q) evaluation has been performed for this planned maintenance activity. The NRC resident inspector has been notified." * * * UPDATE FROM MATT HORN TO HOWIE CROUCH AT 2015 EDT ON 6/27/13 * * * The backup diesel generator was returned to service at 1641 EDT on 6/27/13 which restored the TSC to functional status. The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Franke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-24
49143 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-06-23 21:20 | 2013-06-24 04:35 | 2013-08-21 | LOSS OF 230 KV OFFSITE POWER RESULTS IN THE AUTOMATIC START OF EMERGENCY DIESEL GENERATORS "At 2120 PDT, Diablo Canyon Power Plant experienced a loss of the offsite 230 kV startup power source due to an offsite transmission system relay actuation, resulting in valid anticipatory starts of Units 1 and 2 three emergency diesel generators on each unit. All diesels successfully started but were not loaded. All systems operated as designed with no problems observed. "The 230 kV startup power source is the only offsite power system designed to be immediately available following an accident. However, the safety related onsite emergency diesel system would have provided power to mitigate the consequences of an accident while the 230 kV was unavailable. "Restoration of the 230 kV offsite power system is in progress." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM MICHAEL KENNEDY TO HOWIE CROUCH AT 1618 EDT ON 8/21/13 * * * "230 kV was restored to Operable on 06/24/13 at 0200 PDT. Normal 500 kV Offsite Power remained operable and was unaffected by this event. "Following further review, Diablo Canyon Power Plant (DCPP) has determined that the loss of the 230 kV system was not a condition that could have prevented fulfillment of the safety function of a system credited to mitigate the consequences of an accident. This power source is not considered to be a safety-related system that is credited to mitigate any accident as described in the DCPP UFSAR, Chapters 6 and 15 accident analyses. PG&E concludes that the emergency diesel generators are the only power source needed to fulfill the accident mitigation function, and they did not become inoperable as a result of this event." The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Werner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-06-22
49142 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE |  | 2013-06-23 20:39 | 2013-06-30 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PRE-PLANNED FACILITY UPGRADES "On June 24, 2013, at 0000 EDT, the Technical Support Center (TSC) will be unavailable due to a pre-planned facility upgrade project. The TSC is expected to be restored to operational status on July 1, 2013. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures, and the TSC staff will be located at a preplanned alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility (ERF). An update will be provided once the TSC has been restored to operational status. The NRC Resident Inspector has been notified." The upgrades will require structural changes to the TSC. * * * UPDATE ON 6/30/13 AT 2020 EDT FROM FRED POLLAK TO HUFFMAN * * * "The Technical Support Center functionality has been restored as of 1953 EDT on 6/30/13. The NRC Resident Inspector has been notified." R2DO (Franke) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-23
49141 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-04-24 04:04 | 2013-06-22 13:04 | 2013-06-22 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified in 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to report an event involving an invalid actuation signal affecting the Auxiliary Feedwater (AFW) and Essential Service Water (ESW) systems. "Initial conditions on 04/24/2013: refueling outage was in progress, there was no fuel in the reactor vessel (No MODE), a B safety-related train outage was in progress, and the A ESW train was in operation to support cooling of the A train safety-related equipment. Some separation group 2 bistables were in a tripped condition because instrument power bus NN02 was de-energized. "At approximately 0400 [CDT] on 04/24/2013, Separation Group 4 DC bus NK04 experienced a ground condition. Plant personnel were using a plant procedure to search for the ground. When breaker NK5409 was opened, some unexpected Engineered Safety Features Actuation System (ESFAS) signals occurred. Opening the breaker removed power to the B ESFAS cabinet. With power removed to the B ESFAS cabinet, the circuit cards that generate cross-train trips failed to a tripped condition (thus generating cross-train trip signals) which resulted in some A train ESFAS actuations, in particular, auxiliary feedwater actuations for the A motor-driven and the turbine-driven AFW pumps. Additionally, an AFW Low Suction Pressure (LSP) circuit card tripped, and when combined with the bi-stable that was in a tripped state because bus NN02 was de-energized, the 2-out-of-3 logic was made up, resulting in an auxiliary feedwater LSP actuation. The LSP actuation resulted in the A Train ESW pump receiving a start signal, and the A motor-driven and the turbine-driven AFW pump suction supply valves receiving an actuation signal to transfer the suction supply from the normal source to the ESW system. "Neither the motor-driven nor the turbine-driven auxiliary feedwater pumps started because they had been properly removed from service earlier in the outage. The A ESW pump was already running. No water was transferred from the ESW system to the AFW system since system tagging had been previously placed to isolate the two systems. "The actuations were considered invalid because they were caused by opening breaker NK5409 which resulted in loss of power to the B ESFAS cabinet. "The Senior Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | MO | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-06-22
49140 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-06-21 10:30 | 2013-06-21 10:50 | 2013-06-21 | TECHNICAL SUPPORT CENTER TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "A condition is being reported per TRM 13.13.1 Emergency Response Facilities Action B.2. The Functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities performed on TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54 (q) evaluation has been performed for this planned maintenance activity. The NRC Resident Inspector has been notified." * * * UPDATE AT 1444 EDT ON 06/21/13 FROM THOMAS BUSSIERE TO S. SANDIN * * * "Exit TRM 13.3.1: The functionality of the TSC has been restored and scheduled maintenance activities performed complete and satisfactory at 1410 EDT on 6/21/13. The NRC resident inspector has been notified." Notified R2DO (Desai). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-21
49139 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-06-01 | 2013-06-20 15:39 | 2013-06-20 | AGREEMENT STATE REPORT - MISSING Sr-90 SOURCE IDENTIFIED DURING STATE INSPECTION "The facility is a General License: 056-0600-0G that went out of business effective June 1, 2012. [North Carolina State] did an inspection on June 11, 2013 and [the licensee] had no records of inventory or sources or records of disposal. [The state] was able to determine from [state] records that [the licensee] had disposed of all sources except one on [the licensee's] inventory dated 6/13/1995. [The missing device contains] a Sr-90 [source] with a less than 25 micro Curie source, S/N 49874, that was purchased from CMI. [The state] called CMI and the RSO [Radiation Safety Officer] did not have any records of [the device] being disposed. The source is lost and missing so [the state] is filing this incident with the NRC today." North Carolina Incident Report Number: 13-12. The state considers this incident to be closed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-06-28
49138 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-06-20 11:18 | 2013-06-20 13:20 | 2013-06-20 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR MAINTENANCE "On June 20, 2013 at 1118 CDT, Byron Station removed part of the Technical Support Center (TSC) ventilation (i.e., 0VV23C) system from service to facilitate necessary maintenance on the supply fan. This work is expected to last approximately 2 hours. This maintenance affects the ability of the TSC ventilation to maintain adequate habitability during the duration of an emergency. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. If the TSC becomes uninhabitable, the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility because of the unavailability of the ventilation system. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified [by the Licensee]." * * * UPDATE FROM NICK CRAWFORD TO JOHN SHOEMAKER ON 6/20/13 AT 1635 EDT * * * Maintenance has been completed and the TSC ventilation system has be restored to service. The licensee will notify the NRC Resident Inspector. Notified R3DO (Daley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-20
49137 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-06-20 06:00 | 2013-06-20 10:29 | 2013-06-20 | SULFURIC ACID SPILL REQUIRING OFFSITE NOTIFICATION "In the owner controlled area, the plant has a tank of sulfuric acid (93% concentration, UN # 1830) for chemical control of the Circulating Water system used in the non-safety related electrical power production portion of the plant. "At 0600 [CDT], a routine inspection of the tank found acid within the berm surrounding the tank. A leak was discovered in the berm and sulfuric acid leaked onto the surrounding area and nearby drainage ditch. The quantity of leaked acid has been estimated to be 120 gallons. The source of the leak has been determined to be a pipe on the tank and it has been isolated with a closed valve. The tank level has been stable for 4 hours. The leaked acid is contained within approximately 70 linear feet of the [limestone] ditch and has not left the site. On-site operations and chemistry personnel are neutralizing the acid with soda ash and a tanker truck was contracted to arrive on site this morning to empty the acid tank contents until a repair can be accomplished." The leak was discovered at 0600 and isolated about 0630 CDT. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-06-20
49136 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-06-19 14:10 | 2013-06-19 15:30 | 2013-06-19 | UNUSUAL EVENT DECLARED DUE TO CO2 RELEASE IN THE AUXILIARY BUILDING At 1410 CDT, Grand Gulf declared an Unusual Event for EAL H.U.5, release of toxic and flammable gases adverse to normal operation of the plant. CO2 was discharged in the electrical switchgear room in the auxiliary building. No injuries or fatalities were found after an initial search of the area. The cause of the CO2 discharge is under investigation. The NRC Resident Inspector was notified. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. * * * UPDATE ON 1748 EDT AT 6/19/2013 FROM RUSSELL BURDITT TO DONG PARK * * * "All areas of the auxiliary building have been verified to have no oxygen deficiency." The Unusual Event was terminated at 1628 CDT. The NRC Resident Inspector was notified. Notified R4DO (Walker), NRR EO (Giitter), and IRD (Marshall). Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-06-19
49135 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2013-06-19 10:15 | 2013-06-19 10:15 | 2013-06-19 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "Planned breaker maintenance activities will be performed today (Wednesday, June 19, 2013) which will temporarily remove power to the Quad Cities Station TSC. The maintenance will be completed in approximately 2 hours and is scheduled to be worked continuously to minimize out-of-service time. "If TSC activation is required during this period, compensatory measures have been established to direct ERO [Emergency Response Organization] members to an alternate location. No other emergency response facilities are impacted by the breaker maintenance. This event is reportable per 10CFR50.72(b)(3)(xiii) since the scheduled maintenance affects an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-19
49134 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-06-19 03:07 | 2013-06-19 08:03 | 2013-06-19 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "An alarm was observed in the Technical Support Center (TSC). Initial investigation revealed the TSC to be warmer than usual and alarm 'TSC Vent Air Handling Unit B001 Disch Low Flow' was annunciated on the local panel. Annunciator response was followed as per 34SO-X75-002-0 with maintenance assistance. Further investigation revealed that the 1X75B001 Air Handling Unit fan belt was broken which made the TSC non-functional. The availability of the alternate TSC was verified as required. Actions are in place to return the TSC to functional status. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC as long as habitability conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 and TRM T3.10.1 since the facility was rendered non-functional for greater than 30 minutes. "The TSC was returned to FUNCTIONAL status at 0430 EDT on 6/19/2013." The licensee notified the NRC Resident Inspector | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-19
49133 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-06-18 | 2013-06-18 18:18 | 2013-06-18 | AGREEMENT STATE REPORT - SOURCE DISCONNECT EVENT The following information was received via E-mail: "On June 18, 2013, the Department [Colorado Department of Public Health and Environment] was notified by the Corporate RSO of Libertytown USA 2 (Colo. 1191-01), a radiography company, that they had experienced a source disconnect event earlier that day. The Corporate RSO reported that a crew had been performing radiographic operations in Meade, Colorado and the onsite radiographer was unable to retract the source following a shot. The radiographer secured the area and contacted the local Colorado RSO who responded to the site and took command of the situation. After consultation and assessment by phone with the Corporate RSO, the Colorado RSO was able to retract the source back into the exposure device. The camera was secured and taken out-of-service pending inspection, maintenance, or repair. The initial cause of the event is under investigation. The licensee is in the process of obtaining reports from personnel involved and will submit a final report to the Department within 30 days. The Corporate RSO reported an exposure of 3 mrem to the Colorado RSO and 10 mrem to the radiographer during the recovery operations. The site of the event was a remote location and no members of the public were exposed as a result of the source disconnect. The Department will investigate further, pending additional information from the licensee. "Camera: Industrial Nuclear Company, Model: IR-100, Serial Number: 4138. "Source: Industrial Nuclear Company, Model: 32, Serial Number: T994, Isotope: Iridium-192." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-06-26
49132 | 0 | PARKER HANNIFIN CORPORATION |  |  |  |  | 2013-06-18 | 2013-06-18 17:50 | 2013-06-18 | PART 21 - 304L STAINLESS STEEL USED INSTEAD OF 316 STAINLESS STEEL After being notified that tubing fittings which should have been machined from 316 Stainless Steel appeared to have been machined from 304 Stainless Steel instead, Parker Hannifin had chemical and mechanical property testing performed on the fittings. The testing confirmed that the material was actually 304L SS not 316 SS. Parker Hannifin compiled a list of all potential part numbers and customers affected by this nonconformance. Parker Hannifin reviewed the records related to each of the seventeen safety-related part numbers shipped within the applicable time frame. The only order invoking 10CFR Part 21 that shipped with the corresponding heat code was shipped to South Texas Project. STP received 150 pieces of part number 4-2 FBZ-SS-CNQ. Parker Hannifin is notifying STP of this nonconformance. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-06-18
49131 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-27 14:33 | 2013-06-18 16:42 | 2013-06-18 | REACTOR HEAD NOZZLE PENETRATION FLAWS IDENTIFIED "On April 27, 2012, while the Harris Nuclear Plant was shutdown for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with Inservice Inspection Program requirements. Examinations were being performed to identify flaws before they grow to a size that could effect the structural integrity of the reactor vessel. Those examinations identified flaws in four head penetration nozzles that exhibited characteristics of Primary Water Stress Corrosion Cracking. The four nozzles were repaired using the inner diameter temper bead welding process. Examinations performed following the repairs confirmed the repairs were successful. "This was originally submitted as a voluntary report on May 29, 2012 at 1511 EDT. The condition has since been determined to be reportable per 10CFR50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-06-18
49130 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-18 08:20 | 2013-06-18 11:24 | 2013-06-18 | SPENT FUEL POOL ISLAND RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE The licensee removed the Spent Fuel Pool Island Radiation Monitor from service for pre-planned maintenance. The licensee will notify state and local government agencies. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-18
49129 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-18 08:12 | 2013-06-18 11:24 | 2013-06-18 | STACK RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE The licensee removed the Stack Radiation Monitor from service for pre-planned maintenance. The radiation monitor was returned to service at 1056 EDT. The licensee will notify state and local government agencies. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-18
49128 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP |  | 2013-06-17 18:34 | 2013-07-16 | POTENTIAL UNANALYZED CONDITION - CARBON DIOXIDE FIRE SUPPRESSION SYSTEM DOES NOT MEET DESIGN REQUIREMENTS "At approximately 1615 CDT on June 17, 2013, station personnel identified a potential unanalyzed condition based on the following: "The 1998 design calculation for the carbon dioxide fire suppression system protecting the Relay Room is in part based on an unverified leakage rate for the enclosure. Recent testing and subsequent calculations have found the room leakage rate is higher than the leakage rate specified in the 1998 design calculation. As such, more carbon dioxide would be required to meet design requirements. The minimum required level for the system storage tank would not currently provide two shots of carbon dioxide (design requirement) to suppress a fire. "The minimum required quantity in the tank would be sufficient to provide one shot of carbon dioxide to suppress a fire; however, since this doesn't meet the design requirement, a continuous fire watch was initiated." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 5/16/13 AT 1648 EDT FROM MARK LOOSBROCK TO DONG PARK * * * "Further evaluation determined that the as-found configuration did not meet the minimum design requirements. However, the CO2 concentration was adequate to suppress a fire within the relay and cable spreading room." The licensee has notified the NRC Resident Inspector. Notified R3DO (Hills). | 100 | 82 | 0 | 100 | 82 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-06-17
49127 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-06-17 12:27 | 2013-06-17 18:16 | 2013-06-20 | LOSS OF RADWASTE / REACTOR BUILDING VENT GASEOUS EFFLUENT RADIATION MONITORING CAPABILITY "At 1227 EDT on June 17, 2013, Nine Mile Point Unit 2 determined that the Radwaste / Reactor Building vent gaseous effluent radiation monitor had failed its source check and was, therefore, non-functional. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to the out-of-service Radwaste / Reactor Building vent gaseous effluent monitor is considered a loss of emergency assessment capability and is reportable per 10CFR50.72(b)(3)(xiii). "Troubleshooting is currently in progress. The expected out-of-service time is unknown at this time. Compensatory actions are in place to take and analyze periodic grab samples in accordance with the Offsite Dose Calculation Manual. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DANIEL CIFONELLI TO JOHN SHOEMAKER ON 06/20/13 AT 1300 EDT * * * "The Radwaste/Reactor Building vent gaseous effluent radiation monitor has been repaired and was returned to service at 0330 [EDT] on June 20, 2013, thereby restoring emergency assessment capability. "The NRC Resident Inspector has been notified" The licensee will notify the state. Notified R1DO (Rogge). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-17
49126 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-06-17 11:11 | 2013-06-17 14:37 | 2013-06-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO NON-FUNCTIONAL CLASS 1E ELECTRICAL A/C UNIT "Class 1E A/C Unit SGK05A cools safety related electrical train 'A' and was declared non-functional at 1111 hours. As a result, the following supported safety related electrical equipment was declared inoperable: 4.16 KV Bus NB01, 480 volt Buses NG01 and NG03, 120 volt Instrument AC Inverters and Buses NN11, NN13, NN01 and NN03, 125 VDC Chargers and Buses NK11, NK13, NK01 and NK03. T/S 3.0.3 was entered from T/S 3.8.7 due to two out of four 120 volt AC Inverters (NN11 and NN13) being inoperable. All electrical systems listed above remain available but are declared inoperable due to inadequate room cooling capability. Plant shutdown to mode 5 commenced at 1125 hours. No major equipment is out-of-service. All systems have functioned normally. Plant is currently at 55% power ramping down. Plant must be in mode 3 by 1811 CDT. No compensatory measures have been established. "The NRC Resident Inspector has been notified. " | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-06-17
49125 | 0 | MILLSTONE | 1 | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-17 13:28 | 2013-06-17 14:21 | 2013-06-17 | SAFEGUARDS REPORT Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-06-17
49124 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-06-15 | 2013-06-17 12:35 | 2013-06-17 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following information was received via E-mail: "On June 16, 2013, the licensee reported to the Agency [Texas Department of State Health Services] they had experienced a source disconnect on June 15, 2013. The radiography team cranked the Iridium-192 source out of the Delta 880 camera for the first shot of the day and then they were unable to retrieve the source back into the camera. The source retrieval was performed by authorized persons. From initial reports, using pocket dosimeters readings, the largest whole body dose received was 195 mrem. Dosimetry badges have been sent for processing. The licensee is investigating the cause of the disconnect and will send the equipment to the manufacturer/service company for evaluation. No member of the general public received any dose from this event. More information will be provided as it becomes available, per SA 300." Texas Incident #: I 9092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-06-25
49123 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-06-16 18:45 | 2013-06-16 20:27 | 2013-06-16 | SAFEGUARDS REPORT Discovered vulnerability in management of safeguards information that could allow unauthorized access to safeguards information. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-06-16
49122 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2013-06-16 04:56 | 2013-06-16 13:32 | 2013-06-16 | BROKEN DAMPER BLADE LINKAGE FOUND ON TECHNICAL SUPPORT CENTER VENTILATION LINE "At 0456 CDT, while performing scheduled maintenance on HVL-AOD408, HVL-AHU1 Suction AOD [Air Operated Damper], the linkage inside the damper connecting the two damper blades was found to be broken. HVL-AHU1, Service Bldg. TSC A/C Unit, provides ventilation to the Technical Support Center. With the linkage on HVL-AOD408 broken, there is the potential that a filtered air supply cannot be provided to the TSC. As a result the TSC ventilation was placed in Emergency Mode and positive pressure could not be maintained. Investigation revealed, in addition to [the broken linkage on] HVL-AOD 408, a broken seal on bottom of door SB-123-19. "A contingency plan is in place to relocate personnel if needed per EIP-2-018, 'Technical Support Center' and EIP-2-016, 'Operations Support Center.'" The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-16
49121 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-06-16 | 2013-06-16 02:42 | 2013-06-16 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO SMALL REACTOR COOLANT LEAK ON A RECIRCULATION FLOW CONTROL VALVE VENT LINE "This event is being reported in accordance with 10 CFR 50.72(b)(2)(i) and 50.72(b)(3)(ii)(A). "On June 16, 2013 at 0200 EDT, the Perry Nuclear Power Plant commenced a controlled plant shutdown. The shutdown was due to a small leak through the base of a vent line on the 'B' Reactor Recirculation Flow Control Valve. "On June 15, 2013 at 2250 EDT, the leak was identified and was subsequently determined to require a plant shutdown in accordance with Technical Specification 3.4.5, Action (C) which requires the plant to be in Mode 3 within 12 hours. "The NRC Resident Inspector has been notified." The licensee will also be notifying state and local authorities. The licensee had come down in power to make a drywell entry and investigate drywell leakage indications. Steam was observed to be coming from a vent line that comes off the top of the recirc flow control valve. The licensee was unable to characterize the leak rate other than a small leak. The licensee stated that the steam appeared be coming from a weld location where the vent line comes out of the flow control valve which would classify it as pressure boundary leakage. | 8 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2013-06-16
49120 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-06-15 12:22 | 2013-06-15 18:38 | 2013-06-15 | DIVISION 1 AND 2 EMERGENCY DIESEL GENERATORS POWER BUSES AFTER MOMENTARY OFFSITE POWER LOSS "Columbia Generating Station is shutdown for a refueling outage and is currently in Mode 4. At 1222 PDT June 15, 2013, the 115 kV offsite power to the backup transformer relayed off and then came back on. Both Division 1 and Division 2 4.16 kV critical switchgear buses were powered from the backup transformer at the time of the loss of backup power. "Upon detection of under voltage conditions, Emergency Diesel Generators 1 and 2 started and powered the Division 1 and Division 2 4.16 kV critical switchgear buses after approximately 5 seconds. The temporary loss of power to the Division 1 and Division 2 4.16 kV critical switchgear buses also resulted in the closure of containment isolation valves in the Reactor Water Cleanup System, Equipment Drain System and the Floor Drain System. Shutdown cooling had previously been secured in preparation of performing the reactor pressure vessel hydro test. Investigation into the cause of the temporary loss of the 115 kV offsite power is on-going. "The Division 1 and Division 2 4.16 kV critical switchgear buses are currently being powered from the 230 kV offsite power through the startup transformer. "There were no radiological releases as a result of this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-06-15
49119 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-06-14 11:00 | 2013-06-14 18:28 | 2013-06-14 | INVALID CONDITIONS DISCOVERED DUE TO EXCLUSION OF SMALL BORE PIPING FROM ANALYSIS "While revising calculations for the station analyses for potential high-energy line breaks outside of containment, the station determined that the conditions required to validate the exclusion from analyzing for a break in some small-bore (1- to 4-inch diameter) piping could not be validated. The piping is contained within the station's auxiliary building. In the unlikely event of a break of one of these lines during power operations, the plant may not have been able to respond as expected. The plant is currently in cold shutdown, with the fuel removed from the core." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-06-14
49118 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-11-19 | 2013-06-14 14:16 | 2013-06-14 | AGREEMENT STATE REPORT - ILLEGAL TRANSFER OF A DEVICE CONTAINING AMERICIUM-241 The following information was receive from the State of Arizona via e-mail: "On May 16th, 2013, the Agency [Arizona Radiation Regulatory] received notification from the State of Texas that an illegal transfer of a device containing 30 millicuries of Americium-241 occurred on November 19, 2012. The device is a Thermo Niton XLP818 and the device serial number is 6380. The device was shipped from Longview Scrap & Metal, Inc. in Texas to an individual. The address that was given was to a mailbox company where the device was picked up. The company was not able to look up the reference number, due to it being 6+ months since the shipping date. "The Agency continues to investigate the location of the device." AZ First Notice: 13-010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2013-06-24
49117 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2013-06-13 15:39 | 2013-06-14 11:20 | 2013-06-14 | FAILURE OF IN-CORE THERMOCOUPLE "Description of Event: "During operations at full power (500 kWth), the Senior Reactor Operator (SRO) on duty noticed that the fuel temperature thermocouple reader indicated a temperature of 202 [degrees] C, approximately 60 - 70 [degrees] C below the expected value. The SRO recognized that the problem was likely caused by a fuel thermocouple wire grounding to its conduit. A trainee was instructed to move the wires to avoid grounding. Following this action, the thermocouple reader indicated the proper value. "Upon review of the log book, the SRO noticed that the faulty fuel temperature reading had been logged for several days without corrective action. The facility Technical Specifications (TS) require at least one fuel temperature indication to be operable during operation, and define a system as 'operable' when it is capable of performing its intended function in a normal manner. "Therefore the fuel temperature indication was not operable as defined in the TS. Since the reactor was not immediately secured nor was the indication immediately fixed, the event constitutes a Reportable Occurrence per facility TS 6.9.2. "Background: "For the four days of reactor operations during which the problem with the thermocouple existed, the reactor was operated for short amounts of time (approximately 10 -15 minutes) at various power levels in order to characterize a new beam port configuration and test an experimental apparatus. The total time above 100 kWth was 2 hours and 51 minutes. The reactor was typically staffed by a trainee at the panel, supervised by a licensed reactor operator (RO). "The indicated temperature is the average reading of three thermocouples. One thermocouple is at the fuel midplane, one is 2 [inches] above the midplane, and one is 2 [inches] below the midplane. The fuel temperature indication, when partially grounded, is approximately correct below the point of adding heat (approximately 10 kWth). It differs from the expected value by approximately 15 [degrees] C at 100 kWth, and by approximately 65 [degrees] C at 500 kWth. The fuel temperature readout at the control panel is used to provide an automatic scram at 400 [degrees] C. This setpoint is set well below the Safety Limit of 750 [degrees] C fuel temperature during steady state reactor operations. The fuel temperature scram is NOT required by TS. Normal operations at the reactor do not approach this scram setpoint or the Safety Limit. "The logbooks are reviewed daily as part of the pre-operation reactor checkout procedure. The staff is trained to review logs back to the most recent time they were on duty, to check for changes to the reactor, problems with instruments, etc. The staff is not trained to audit the previous days' logs for anomalous readings. "Timeline: "The following timeline of operations is taken from the reactor logbook. Only operations at or above 100 kWth are listed, because the difference between measured and expected temperature is small at lower power levels. All times are local (Central Daylight Time). Date Time Power T (Measured, [degrees] C) T (Expected, [degrees] C) 6/7/2013 0946-1001 500kW 200 265 6/7/2013 1037 - 1050 500kW 202 265 6/7/2013 1441 - 1446 500kW 202 265 6/10/2013 0937 - 0950 100kW 83 100 6/10/2013 1005 - 1015 100kW 87 100 6/10/2013 1029-1041 100kW 84 100 6/12/2013 0906 - 0919 100kW 84 100 6/12/2013 0934 - 0959 530kW 217 270 6/12/2013 1611 - 1633 100kW 74* 100 6/13/2013 1103 - 1143 500kW 201 265 6/13/2013 1352 - 1406 530kW 209 270 *Temperature was logged while it was still rising toward an equilibrium value. "6/13/2013 - 1559 - Problem observed and corrected by repositioning thermocouple wires. "6/14/2013 - 1020 - Reportable occurrence reported to NRC Headquarters Operations Center. "Causes: "The facility has identified the following as contributing causes to the event. "1. Licensed operators were not sufficiently attentive when supervising trainees at the control panel. The licensed operators were focused on reactor power indications and did not pay sufficient attention to other TS related indications. "2. The log book review required prior to daily operations was not conducted with sufficient rigor to detect the improper thermocouple readings logged the previous day. The review was instead focused on noting changes to the reactor facility and problems with instrumentation since the operators' previous duty at the panel. "3. Only one functioning instrumented fuel element was used to provide the required fuel temperature indication channel. Therefore no redundant readout was available to check against the indicated fuel temperature. "4. The sharp edge on the instrumented fuel element conduit can cut through the insulation on the thermocouple wires, causing grounding. "Corrective Actions: "The facility will perform the following corrective actions. All changes to the reactor systems, such as thermocouple wire insulation, are subject to review per the requirements of 10CFR50.59. "Time: Prior to operation; "Action: Attempt to improve insulation on thermocouple wires, using electrical tape, shrink tubing, or spray-on insulation. "Time: Prior to operation; "Action: Attempt to repair thermocouple wires for a currently installed but non-functional instrumented fuel element to provide an independent fuel temperature indication channel. "Time: Prior to operation; "Action: Install a new instrumented fuel element. This will bring the total number of independent channels of fuel temperature indication to 2 - 3. "Time: Prior to operation and as part of requalification training program; "Action: Train reactor staff on the importance of vigilance when supervising trainees and the importance of attentiveness to all channels of information at the control console, as opposed to focusing on a few specific indicators, such as reactor power channels. "Time: Prior to operation and as part of requalification training program; "Action: Train reactor staff to check for anomalous values in the prior days' log entries during the daily reactor checkout. "Time: Upon approval by Reactor Safeguards Committee, but not necessarily prior to operation; "Action: Append Procedure 15 - Reactor Startup with a list of observed instrument values for different reactor power levels to be used as a reference by trainees and licensed staff. "A copy of this report will be provided to the Kansas State University Reactor Safeguards Committee for review." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | KS | NPR | [5 empty] | 0 | 2013-06-14
49116 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-06-14 08:35 | 2013-06-14 09:20 | 2013-06-14 | UNUSUAL EVENT DECLARED DUE TO HIGH CO2 LEVELS IN THE TURBINE BUILDING "Beaver Valley Unit 2 declared an Unusual Event (EAL HU.5, Toxic Gas Release) at 0835 EDT hours due to a CO2 (Toxic Gas) discharge in the turbine building. No report of fire and no injuries resulted from discharge. At 0851 EDT, the turbine building was clear of any detectible CO2. There was no operational impact from the CO2 discharge. The cause of the CO2 discharge is under investigation. The required states and counties were notified. The Resident NRC inspector was notified." The inadvertent CO2 discharge was from the turbine fire protection system which now isolated while troubleshooting is in progress. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. * * * UPDATE FROM JAMES SCHWER TO CHARLES TEAL ON 6/14/13 AT 1006 EDT * * * "Beaver Valley Unit 2 has terminated the Unusual Event at 0955 EDT * * * Notified R1DO (Dentel), NRR EO (Chernoff), IRD (Grant), DHS SWO, FEMA, DHS NICC, and Nuclear SSA via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2013-06-14
49115 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-06-13 21:27 | 2013-06-14 03:25 | 2013-06-14 | LOSS OF ONE OF TWO NATIONAL WEATHER SERVICE TONE ALERT RADIO TRANSMITTERS "At 9:27 p.m. EDT June 13, 2013, the National Weather Service reported a loss of the National Weather Service (NOAA) Tone Alert Radio Transmitter, WXL-58 located in Chapel Hill, NC serving the northeast Piedmont on 162.550 MHz, due to damage or power failure sustained during the passage of severe thunderstorms. The National Weather Service expects the transmitter to be out of service through at least Friday morning June 14, 2013. "The purpose of the National Weather Service (NOAA) Tone Alert Radio transmitters is a redundant means to the 83 Harris Nuclear Plant Emergency Sirens to warn the public within the 5 mile radius of the plant of an actual event. The 83 Harris Nuclear Plant Emergency Sirens were verified at 12:05 a.m. EDT June 14, 2013 to be in service and fully functional to alert the public within the 5 mile radius of the plant of an actual event should an event occur. "There is no impact to public health and safety due to this condition. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2013-06-14
49114 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-06-13 18:30 | 2013-06-13 22:03 | 2013-06-13 | NOTIFICATION OF NORTH CAROLINA EMERGENCY MANAGEMENT DUE TO SPILL OF DIESEL OIL "At 6:30 PM EDT on 6/13/13 an all spill was identified which resulted in approximately one quart of fuel oil spilled to the ground from a diesel powered portable light which overturned during a storm. The oil spill was outside of the dike containment in which the light unit was located and was approximately 10 feet from waters of the Harris Lake (waters of the US). No oil entered the lake. This event was reportable to the state of North Carolina because it occurred within 100 feet of the Harris Lake. At 7:03 PM EDT on 6/13/13 Harris Environmental Services Section personnel made the oil spill notification to North Carolina Emergency Management which was acting on behalf of the North Carolina Department of Environment and Natural Resources. "The spill was cleaned up by removing the topsoil in the area. "This event is reportable per 10 CFR 50.72(b)(2)(xi) as described in NUREG-1022, based on an event related to protection of the environment for which a notification to other government agencies has been made. "There is no impact to public health and safety due to this condition. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-06-13
49113 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-06-13 14:30 | 2013-06-13 22:02 | 2013-06-13 | EMERGENCY DIESEL GENERATORS START "While preparing for an equipment test Thursday afternoon, Monticello Nuclear Generating Plant lost off-site power on its normal off-site power feed. Power for safety related loads was automatically transferred to the alternate off-site power source. The Emergency Diesel Generators started as designed but did not load onto the safety related busses due to the availability of off-site power. Operators stabilized the plant, which is shutdown for a refueling and maintenance outage, in less than an hour and are investigating the cause of the event. The current plant focus is on restoring the normal off-site power feed. The event posed no danger to the public or plant workers, and no one was injured. There was no release of radiation. Plant safety systems continue to be powered by the backup off-site power feed, with the emergency diesel generators available if needed. "Event Specifics: "At approximately 1430 CDT, during a refueling outage with the plant in Mode 4, reactor level at approximately 200 inches, and a full Scram already inserted, a loss of normal off-site power occurred due to a fault in a non-safety related bus supply breaker. The fault was in the 13.8 KV supply breaker to the #11 bus. This caused the Station 2R transformer to lockout, resulting in a loss of the normal off-site power to Essential Busses 15 and 16. Shutdown Cooling (SDC) was lost for approximately 1 hour due to loss of supply power and isolation of the common suction valves. "Both 11 and 12 Emergency Diesel Generators (EDGs) automatically started but did not load onto their respective busses (as designed) due to the 1AR emergency off-site transformer re-energizing both 15 and 16 bus. This essential bus transfer is being reported as a 'Valid actuation of emergency AC electrical power systems' under 10CFR50.72(b)(3)(iv). "During the event the decision was made to shut down the EDGs which rendered them inoperable for a short period of time until the Fast Start capability was reset. The period of time that the EDGs were inoperable is being reported as a 'Condition that could have prevented the fulfillment of the safety functions to remove residual heat, control the release of radioactive material, and mitigate the consequences of an accident under 10CFR50.72(b)(3)(v)(B), (C), and (D). Both EDGs have been restored to Automatic Standby Status and are operable. "The loss of power resulted in a Group II Containment Isolation signal causing secondary containment to isolate and Standby Gas Treatment and Control Room Emergency Filtration to initiate as well as associated Group II Containment Isolation Valves to close. This is being reported as a 'General containment isolation signal ESF actuation' under 10CFR50.72(b)(3)(iv). The containment isolation has been reset, and SDC and SFPC have been restored. Reactor temperature rose approximately 4 degrees F during the event from 161 degrees to 165 degrees which remained in the prescribed operating band. Reactor level did not change. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2013-06-13
49112 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-06-13 08:05 | 2013-06-13 16:55 | 2013-06-13 | UNANALYZED CONDITION "The station is reporting an unanalyzed condition involving the steam driven auxiliary feedwater pump. A postulated high energy line break in the room containing the pump could result in steam communicating with equipment in the safety related switchgear and battery rooms which are immediately above the room. The plant is currently in cold shutdown with the fuel removed from the core." The licensee stated that in the event of a postulated high energy line break, steam could possibly enter the switchgear and battery rooms via a stairwell and ventilation ductwork. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-06-13
49111 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-06-12 | 2013-06-13 16:26 | 2013-06-13 | AGREEMENT STATE REPORT - FAILURE OF GAUGE SHUTTERS TO OPERATE "On June 13, 2013, the licensee notified the Agency [State of Texas] that after completing maintenance on cables on Hoppers that one of the retest was to operate shutters on all nuclear gauges. The failures were identified on June 12, 2013. Eight gauge shutters failed to operate. The shutters are on Thermo Fisher Model #5197 gauges each containing 100 mCi of Cesium-137. The licensee stated that open is the normal operating position for the shutter and the gauge does not pose an exposure risk to any individual. The sources are not accessible to the general public or workers in the area. The licensee stated that a service provider will most likely remove and possible replace the gauges. The gauges have been in operation for approximately 30 years. Additional information will be provided as it is received in accordance with SA 300." Texas Incident # I-9091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-06-21
49110 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-06-13 02:52 | 2013-06-13 09:41 | 2013-06-13 | DISCOVERY OF PRESSURE BOUNDARY LEAKAGE "On 6/13/13 at approximately 0252 EDT, during the initial walk down of the drywell of the Hope Creek Unit 1 forced outage, water was observed leaking from a 40% circumferential crack in a weld in the RHR vent line adjacent to the outboard isolation valve (BCV-597). The estimated leakage rate through the crack is less than one gallon per minute. The RHR vent line is one-inch ASME Class 1 piping. Hope Creek Unit 1 is stable in Operational Condition 3, Hot Shutdown. "This report is being made under 10CFR50.72(b)(3)(ii)(A) for a weld or material defect in the primary coolant system which cannot be found acceptable under applicable ASME standards. "The NRC Resident Inspector has been notified. The only safety-related equipment out of service at the time event was the 'C' Service Water Pump, which was tagged for scheduled maintenance. "No personnel injuries occurred. No radiation releases occurred." The licensee entered a 24 hr. action statement under T.S. 3.4.3.2, Condition A to be in mode 4 by 0252 EDT on 6/14/13. The licensee will be notifying the Lower Alloways Creek township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-06-13
49109 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-06-12 16:38 | 2013-06-12 21:36 | 2013-06-13 | TONE ALERT SYSTEM FAILURE "Vermont Yankee Control Room was notified by E-Plan personnel at 1638 [EDT] that the tone test initiated by the National Weather Service from Albany, NY, failed to activate tone alert radios via the Ames Hill NOAA transmitter and would be out for greater than one hour. At 1712 [EDT] the tone alert radios were functionally tested from the backup transmitter link (WTSA Radio Studio) satisfactorily verifying the ability to activate tone alert radios is available." The licensee suspects a phone service change was not sufficiently tested. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MIKE FRENCH TO NESTOR MAKRIS ON 6/13/13 AT 1207 EDT * * * On 6/13/13 at 1045 EDT, the Ames Hill transmitter was returned to service after restoration of the transmission link between Ames Hill and the National Weather Service. The licensee notified the NRC Resident Inspector. Notified R1DO (Dentel). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-12
49108 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-06-12 13:33 | 2013-06-12 16:59 | 2013-06-12 | CIRCULATING WATER PUMP TRIP LEADS TO REACTOR SCRAM "This is a report of a manual RPS actuation and manual RCIC actuation per 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). "At 1332 [EDT], on 6/12/13, the 'B' Circulating Water Pump tripped with a stuck open discharge valve resulting in a vacuum transient. Operators lowered reactor power from 100% in an effort to stabilize condenser vacuum. When vacuum reached 6.5 inches, the operators inserted a manual reactor scram at 1333 [EDT]. All control rods inserted as required. No automatic ECCS or RCIC initiations occurred. No primary or secondary containment isolations occurred. The plant is stable in OP CON 3 HOT SHUTDOWN with the condensate pumps in service. The Reactor Recirculation Pumps are in service. "At the time of the event, a RCIC surveillance was in progress, but did not contribute to the event. The RCIC pump was secured and subsequently placed in service for inventory control. The only safety-related equipment out of service at the time of the scram was the C Service Water Pump, which was tagged for scheduled maintenance. "No personnel injuries occurred. No radiation releases occurred. The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-06-12
49107 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-05-29 | 2013-06-12 09:58 | 2013-06-12 | AGREEMENT STATE REPORT - LOST/MISSING LICENSED MATERIAL The following information was received from the State of Tennessee via email: "On June 11, 2013, RbM Services, LLC contacted the [Tennessee] Division of Radiological Health to report that on May 29, 2013, 6 Bracco Diagnostics Inc. Rubidium Generators (Sr-82/Sr-85 Solid Strontium Mixture) were shipped to Los Alamos National Labs in Los Alamos, NM via Common Carrier. "On May 31, 2013, it was discovered that two of the shipments of generators (78.78 mCi of Sr-85 and 49.37 mCi of Sr-85) had not arrived in Los Alamos. The tracking numbers showed the 2 shipments were still in Memphis, TN. On June 3, 2013, [the] Common Carrier's tracking update via phone stated the 2 shipments were enroute to Los Alamo's zip code. "On June 4th, after learning the shipment had not been delivered, RbM contacted [the] Common Carrier and Bracco, the manufacturer of the generators. As of June 5th, [the] Common Carrier informed RbM that an extensive search for the packages was being made and a trace had been placed on the shipment. "On June 6th, RbM contacted [the] Common Carrier and instructed them to contact Los Alamos National Labs to see if the shipment was delivered; Los Alamos confirmed those 2 shipments had not arrived. "On June 10th, [the] Common Carrier did not have any additional information and advised RbM to contact their regulatory authority [Tennessee Division of Radiological Health]." Event Report ID No. TN-13-104 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-06-20
49106 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-06-11 21:05 | 2013-06-12 01:33 | 2013-06-12 | UNIT 1 AUTOMATIC REACTOR TRIP DUE TO THE LOSS OF A START-UP TRANSFORMER "This is a report of an automatic RPS actuation and automatic ESF actuation per 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). Additionally, this is to report intentions for a press release per 10CFR50.72(b)(2)(xi). "At 2105 CDT on 6/11/13, Farley Unit 1 experienced an automatic reactor trip from 100% power. The initiating event was the loss of the 1B Start up Transformer which resulted in de-energization of the B-Train ESF 4KV buses and the 1B and 1C Reactor Coolant Pump Buses. The 1B Emergency Diesel Generator auto started and tied to the B-Train 4KV Emergency buses. "Both MDAFW (Motor Driven Auxiliary Feedwater) Pumps and the TDAFW (Turbine Driven Auxiliary Feedwater) Pump auto-started and are supplying AFW flow to the steam generators. Decay heat removal is via the steam dumps to the main condenser. "The cause of the loss of the 1B Start-up Transformer is unknown and is currently under investigation. All other systems functioned as expected in response to the loss of the 1B Start-up Transformer and reactor trip. "The NRC Senior Resident Inspector has been notified. "A press release is planned." All control rods fully inserted. There is no impact on Unit 2. Currently the licensee does not plan to restart the 1B and 1C Reactor Coolant Pumps. Pressurizer spray has been isolated from the 1B loop per procedure. Main Condenser vacuum is adequate for decay heat removal. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) |  | 0 | 2013-06-12
49105 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-11 10:18 | 2013-06-11 13:09 | 2013-06-11 | RADIATION MONITOR OUT-OF-SERVICE FOR PLANNED MAINTENANCE The licensee removed the Spent Fuel Pool Island Radiation Monitor from service for pre-planned maintenance to change the air filter. The radiation monitor was returned to service at 1030 EDT. The licensee notified the NRC Resident Inspector, state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-11
49104 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-06-09 | 2013-06-11 10:59 | 2013-06-17 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The State of Kansas was notified by the licensee that on 6/9/2013, personnel dosimetry indicated that one assistant radiographer had received a potential overexposure, and two other assistant radiographers had received potential elevated exposure. The licensee reported that the dosimetry had been stored improperly and in close proximity to a location where a source change out had occurred. Corrective actions taken by the licensee include establishment of a controlled dosimetry storage location and additional training of personnel on the use of dosimetry. The individual with the potential overexposure was removed from radiography duties and given alternate work assignments. All three individuals were notified of the dosimetry readings. The dosimeter readings were 5.046 rem, 1.133 rem and 0.633 rem. * * * UPDATE FROM JAMES HARRIS VIA FAX AT 1050 EDT ON 6/17/13 * * * The following information was obtained from the State of Kansas via fax: "Based on the last dosimetry report [received by the licensee], several employees have received a high dose. The reported doses are Employee 1 - 5046 mR, Employee 2 - 1133 mR, and Employee 3 - 633 mR. "The three employees are radiographers assistants acting under one of the 4 licensed radiographers. The three radiographers assistants never worked together on any single job. The only common denominator between the three assistants is that their film badges were stored in the same general area. The licensed radiographers that were assigned to them received no such high dose rates. The three assistants also did not have any off-scale readings from dosimetry nor did they report any unusual incidences. All three also stated they did not believe that they could possibly have received an unusually high dose during that time period based on dosimetry, rate alarm, and survey meter readings. "Upon further investigation, it was discovered that the three were leaving their film badges in their [work] uniforms in a controlled area within the shop between shifts. During this time period, radiographic operations were conducted at the shop facility. Additionally, there was a source change conducted by two radiographers in the controlled area of the shop during this time. During times these employees were not working, their [work] uniforms would have been located in the controlled area allowing their badges to be exposed during radiographic operations. "In conclusion, there are two possible explanations for the substantial increases in exposure to the three assistants badges. Conclusion one would be that excessive heat and humidity played a role in the increased readings found with the badges. Conclusion two would involve film badges in close proximity to the area where radiographic operations were being conducted with the individuals assigned to those badges being absent at the time, therefore creating an erroneous reading leading to the obvious assumption that the badges alone were exposed, not the individuals associated with these badges being exposed. "Corrective action taken at this time: Badges will be stored in the office, [with the proper controls in place] when not being worn. Retraining [was] conducted on the physical properties of the film badge and how badges become exposed through various means. "Based on the reading of employee 1's badge, he will not be involved in radiographic operations nor be allowed in the controlled areas near radiation in the shop until a full investigation is completed." The State of Kansas is still investigating this event. Kansas Case No.: KS130005 Notified R4DO (Walker) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-06-19
49103 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-04-11 01:28 | 2013-06-10 17:06 | 2013-06-10 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified in 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to describe an invalid actuation signal affecting the emergency feedwater system. "While the plant was in Mode 5 on 4/11/2013, during performance of a maintenance procedure for AMSAC system logic verification, an invalid MDAFAS occurred. (Note: AMSAC is ATWAS Mitigation System Actuation Circuitry and MDAFAS is Motor Driven Auxiliary Feedwater Actuation Signal). Both trains of the Motor Driven Auxiliary Feedwater Pumps (MDAFPs) started. While generation of the actuation signal is an expected result of the procedure, the actuation occurred several steps earlier in the procedure than expected. Additionally, the Control Room Operators were not expecting the MDAFPs to start. The pumps were manually stopped. "The actuation was caused by procedural guidance not containing a sufficiently prescribed sequence of activities that should occur when simulating plant conditions leading to the intended actuation of the AMSAC system. The plant was not in a condition where feedwater was required. "The Senior NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-06-10
49102 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-22 | 2013-06-10 16:53 | 2013-06-10 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL OVERDOSE The following report was received via e-mail: "On May 26, 2013 during a transfer of electronic treatment planning records to a new system, the University of Minnesota (license number 1049-211-27) discovered a medical event that occurred on August 20-22, 2012 at the university of Minnesota Medical Center in Minneapolis with the Nucletron HDR. The licensee reported that dosimetry staff were testing the transfer of information from previously treated patients into a brachytherapy check program, and it was discovered that in this particular case the source position data was entered into the HDR planning system incorrectly. The licensee is calculating the exact doses delivered and it appears as though the dose to unintended regions by greater than 50% for several areas. The Minnesota Department of Health was notified of the potential event on May 27, 2013. A final report will be submitted when the report is received from the licensee." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2013-06-18
49101 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-06-07 15:50 | 2013-06-07 20:21 | 2013-06-07 | OFFSITE NOTIFICATION DUE TO AN ONSITE EMPLOYEE FATALITY "This is a report of an on-site fatality and planned press release per 10 CFR 52(b)(2)(xi). "An off-duty Farley employee was supporting a non-work related activity on the plant site [within the Owner Controlled Area] and sustained a suspected weather related fatal injury. The individual was located outside of the protected area but on the plant property. The individual was transported to the plant nurses station and CPR initiated. CPR was terminated at 1550 [CDT] at the direction of ambulance personnel with the individual being unresponsive. "The Houston County Sheriff was notified at approximately 1600 [CDT] and responded to the site with the county coroner. "The NRC resident was notified on 6/7/2013 at 1650 [CDT]. "A press release is planned." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-06-07
49100 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-07 13:51 | 2013-06-07 15:11 | 2013-06-07 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE On June 7, 2013 at 1351 EDT, Millstone Unit 2 rendered the Main Steam Line Radiation Monitors (RM-4299 A/B/C) out-of-service for planned maintenance. The maintenance activity was completed and the radiation monitors were returned to service at 1355 EDT. The licensee has notified the NRC Resident Inspector as well as the State and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-07
49099 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-06-07 12:03 | 2013-06-07 13:50 | 2013-06-07 | MANUAL SCRAM DUE TO A REACTOR WATER LEVEL TRANSIENT DURING STARTUP "At approximately 1203 [EDT] on June 7, 2013, Susquehanna Steam Electric Station Unit One reactor was manually scrammed during reactor startup. Pressure setpoint was being adjusted to the normal operating setpoint, from 750 psig to 934 psig, when all turbine bypass valves unexpectedly opened. Reactor Feed Pumps, Main Turbine, HPCI and RCIC tripped on the high level setpoint Level 8 (+54 inches) due to the resultant reactor level swell. The reactor operator then inserted a manual scram. "All control rods inserted. Reactor water level lowered to approximately -10 inches causing Level 3 (+13 inches) isolations. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected. The cause of the Turbine Bypass valve opening is under investigation. "Unit 2 was unaffected." The licensee notified the NRC Resident Inspector and will notify the Pennsylvania Emergency Management Agency. | 0 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-06-07
49098 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-06-07 | 2013-06-07 09:48 | 2013-06-09 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The following was received from the State of Oklahoma via email: "Building and Earth Sciences has reported that a Troxler Model 3430 (S/N 36097) was stolen from a location in Ponca City, OK. The case was in the back of a truck and some time during the night it was opened and the gauge removed. The RSO is on the way to the site now, [the Oklahoma Department of Environmental Quality] will provide more information as it becomes available." Troxler Model 3420 Density gauges typically contain Cs-137 8 mCi and Am-241/Be 40 mCi sources. * * * UPDATE FROM MIKE BRODERICK TO JOHN SHOEMAKER AT 1100 EDT ON 6/9/2013 * * * The State of Oklahoma reports that the gauge has been recovered and is now in the possession of the licensee. A private citizen found the missing gauge on the side of a road near the location where the gauge was stolen in Ponca City, OK. The source rod was still locked and it is believed that no exposures have occurred. The licensee will return the gauge to a secure storage location. Notified R4DO (Spitzberg) and FSME Events Resource and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2013-06-17
49097 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2013-06-04 15:45 | 2013-06-06 16:39 | 2013-06-06 | AGREEMENT STATE REPORT - EXPOSURE TO AN EMBRYO GREATER THAN 500 MILLIREM The following information was received by facsimile: "On June 4, 2013, the Radiation Safety Officer for the University of South Alabama, Mobile, Alabama, notified the Alabama Office of Radiation Control of a fetal/embryo dose that was in excess of 500 millirem. "On April 2, 2013, a 30 [year old] female was referred to the University of South Alabama Medical Center for treatment of symptomatic hyperthyroidism via Sodium Iodide-131. The patient was interviewed regarding pregnancy by the authorized user and a blood test was collected for qualitative serum hCG testing. After a negative pregnancy testing and the patient's statements, the patient was given 15 millicuries of Sodium Iodide-131. The patient was also counseled to avoid pregnancy for six months. "On May 30, 2013, eight weeks and two days later, the patient reported to her physician a positive pregnancy diagnosis by her OB/GYN physician. The patient reported that her OB/GYN physician determined that she was in the tenth week of pregnancy. This would place the patient approximately 10 days pregnant at the time of administration." Alabama Incident: 13-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2013-06-14
49096 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-06-06 08:00 | 2013-06-06 16:24 | 2013-06-06 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACT SUPERVISOR ARRESTED OFFSITE "At approximately 0800 hours on June 6, 2013, it was determined that a non-licensee contract supervisor had been arrested off-site for possession of a controlled substance. Access has been terminated and additional information documented in the Personnel Access Data System (PADS)." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2013-06-06
49095 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-06 10:05 | 2013-06-06 14:45 | 2013-06-06 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE On June 6, 2013, at 1005 EDT, Millstone Unit 2 rendered the High Range Stack Radiation Monitor, RM-8168, out-of service for planned maintenance. The maintenance activity was completed and the radiation monitor was returned to service at 1320 EDT. The licensee has notified the NRC Resident Inspector as well as the State and local agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-06
49094 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2013-06-06 03:11 | 2013-06-06 10:31 | 2013-06-06 | SERVICE WATER RADIATION MONITOR REMOVED FROM SERVICE FOR MAINTENANCE "At 0311 EDT on June 3, 2013 Nine Mile Point Unit 1 removed the Service Water Radiation Monitor from service for planned maintenance. Due to expanded scope of the work, the Service Water Radiation Monitor will not be returned to service within 72 hours. The Chemistry department has been performing periodic grab samples per the requirements of the Offsite Dose Calculation Manual (ODCM) as a compensatory measure with the Service Water Radiation Monitor out of service. "The Service Water Radiation Monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification. The inability to classify an EAL due to an out of service monitor is considered a loss of assessment capability per CFR 50.72(b)(2)(xiii). Compensatory actions remain in place to sample per the requirements of the ODCM. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). A follow up notification will be made when the equipment has been returned to service. "The NRC Resident inspector has been notified." * * * UPDATE ON 6/6/2013 AT 1545 EDT FROM DANIEL COLEMAN TO DANIEL MILLS * * * "The Service Water Radiation Monitor maintenance is complete and the Radiation Monitor has been returned to service. Emergency Assessment Capability has been restored." The licensee will notify the NRC Resident Inspector. Notified R1DO (Burritt) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-06
49093 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-06-04 10:30 | 2013-06-06 10:32 | 2013-06-06 | AGREEMENT STATE REPORT - ADMINISTERED DOSE LESS THAN DESCRIBED DOSE The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "On June 5, 2013 the licensee informed the Department's [PA Department of Environmental Protection] Southeast Regional Office of the Medical Event. The event is reportable within 24 hours per 10 CFR 35.3045(a)(1)(i). "Event Description: At approximately 10:30 a.m. [EDT] on June 4, 2013 the SIR-Sphere procedure took place leading to a microcatheter becoming occluded. The licensee replaced catheters and based on residual measurements of original catheter the patient received 57% of the intended dose. "Cause of the Event: Microcatheter became occluded. "Actions: The licensee is aware of the requirements to notify the patient and referring physician. A reactive inspection will be scheduled and conducted." PA Event Report ID No.: PA130014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-06-14
49092 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-06-06 08:00 | 2013-06-06 09:27 | 2013-06-06 | TECHNICAL SUPPORT CENTER EMERGENCY POWER SUPPLY REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) has removed the emergency power supply to the TSC from service as of 0900 EDT. If a loss of the normal power supply to the TSC were to occur during this period, the TSC would be rendered non-functional. The repair to the power supply is expected to last 6 hours. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be expedited to restore the emergency power supply to service. This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC emergency power supply has been restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 6/6/13 AT 1614 EDT FROM STEPHEN SPEIRS TO DANIEL MILLS * * * "The TSC diesel generator has been returned to functional status." The NRC Resident Inspector has been notified R3DO (Lipa) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-06
49091 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-06-05 10:39 | 2013-06-05 17:09 | 2013-06-05 | LOSS OF COMMUNICATIONS WITH THE INTEGRATED PLANT COMPUTER "This is a report of a loss of emergency assessment capability as required by 10CFR50.72(b)(3)(xiii). "At 1039 CDT on June 5, 2013, Farley Unit 2 experienced a communication failure of the Integrated Plant Computer (IPC). This represents a loss of Unit 2 automated SPDS and ERDS capability. This also rendered the Technical Support Center (TSC) non-functional for Unit 2 since the TSC relies on IPC data displays for event assessment. "The Unit 2 IPC was returned to service at 1115 CDT, restoring all affected emergency response capability. Investigation to determine the cause of the failure is ongoing. "With the exception of the Unit 2 IPC all systems functioned as required. "The NRC Resident Inspector has been informed." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-05
49090 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-06-04 | 2013-06-05 11:19 | 2013-06-05 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was obtained from the State of Texas via email: "On June 5, 2013, the licensee's Radiation Safety Officer (RSO) reported to the Agency [Texas Department of Health] that on June 4, 2013, one of its radiography crews had been unable to retract the Iridium-192 source back into the SPEC 150 camera they were using in a fixed bay. The disconnect occurred after the first shot. The RSO was notified and he and two other employees performed the source retrieval. Readings from the pocket dosimeters were: RSO - 21.3 mrem; other employees performing source retrieval received 53.9 and 26.9 mrem. No member of the public received any exposure from this event. Cause of the event unknown at this time. Further information will be provided as it is obtained, per SA-300. "Radiography Camera: Spec 150, SN: 407 "Source: Iridium-192, SN: UE2912" Texas Event Number: I-9089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-06-13
49089 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-06-03 | 2013-06-04 13:33 | 2013-06-14 | AGREEMENT STATE REPORT - SOURCE RETRACTION FAILURE The following was received from the State of Texas via email: "On June 3, 2013, the Agency [State of Texas] was notified by the licensee that on June 3, 2013, a medical event had occurred. The licensee reported a source retraction failure with a Novoste Beta-Cath intravascular brachytherapy system containing a 45.1 mCi strontium - 90 source. When the treatment was completed, upon source retraction, the source got stuck in another area of the blood vessel roughly 5 cm away from the treatment site for 1 minute. "The unintended absorbed dose to that area of the vessel is in the range of 5-6 Gy. The source open in air time was roughly 3 seconds from being retracted from the patient before being secured in a bail out box. Personnel exposure issues or concerns are not expected, however, dosimeters will be assessed. A technical representative was notified and during the next several days will inspect the system and assist in packaging the system for return shipment back to the manufacturer. Additional information will be provided as it is received in accordance with SA-300." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM CHRIS MOORE TO PETE SNYDER AT 1118 EDT ON 6/14/13 * * * The following updated information was provided from the State of Texas via email: "The Methodist Hospital reported an equipment failure that involved a source retraction during an intravascular brachytherapy treatment performed on 6/3/2013. The intravascular brachytherapy system (Best Vascular Beta-Cath A1000 series) contained a 1.67 GBq (45.1 mCi) Sr-90 source. When the treatment was completed and upon source retraction, the source became stuck in another area of the blood vessel approximately 5 cm from the treatment site for one minute. The unintended absorbed dose to the area of the aortic arch was approximately 40 cGy at 10 mm on the wall of the arch. A technical representative was notified and will inspect the system within the next several days and assist in packaging the system for return to the manufacturer." The State of Texas determined that this event is no longer classified a medical event and has been updated to equipment failure. Notified R4DO (Gepford) and FSME Events Resource email. Texas Incident #: I-9088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-06-12
49088 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-06-04 08:30 | 2013-06-04 09:49 | 2013-06-04 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE "On June 4, 2013, at 0830 CDT, the Kewaunee Power Station rendered the Auxiliary Building Special Particulate Iodine Noble Gas 'SPING' (Mid and Hi Range) and the Reactor Building 'SPING' (Mid and Hi Range) non-functional for planned maintenance. The Emergency Response Organization (ERO) team has been notified of the Auxiliary Building SPING and Reactor Building Vent SPING non-functionality due to planned maintenance. "The SPINGs are expected to be out of service for approximately 7 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify the upper two emergency action levels for offsite radiation conditions). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-06-04
49087 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-06-03 10:25 | 2013-06-03 13:47 | 2013-06-03 | UNPLANNED MEDICAL TREATMENT "An employee reported to the dispensary this morning with a finger laceration [at approximately] 1025 CDT. The plant nurse administered first aid and decided to send the employee to an offsite medical facility. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination was present on his right boot, 55,039 dpm/100 cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was re-surveyed. The employee was free of contamination upon release." The licensee notified NRC RII (Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-06-03
49086 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2013-06-01 21:29 | 2013-06-02 04:38 | 2013-06-02 | VALID ACTUATION OF EMERGENCY DIESEL GENERATOR "On June 1, 2013 at 2129 [EDT], a valid actuation of the 'B' Emergency Diesel Generator occurred when power was lost to the 'B' 4160V engineered safeguards bus due to failure of the 'B' Unit 6900 V bus feeder breaker 3104. There were no interruptions of spent fuel pool cooling during this event. "This event is reportable as an 8-hour notification per 10 CFR 50.72(b)(3)(iv)(B)(8). "This condition has no adverse affect on the public's or employees' health and safety. NRC Region II has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-06-02
49085 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-05-31 14:00 | 2013-05-31 19:05 | 2013-05-31 | UNANALYZED CONDITION CONCERNING FLOODING MITIGATION "On May 31, 2013, during an aggregate review of issues raised during a focused self assessment of external flooding mitigation, it was concluded that the A.6 Acts of Nature procedure may not adequately protect equipment required to maintain safe shutdown from the external probable maximum flood. "The plant is currently in Mode 4, Cold Shutdown for refueling. MNGP [Monticello Nuclear Generating Plant] is addressing the inadequacies. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) Unanalyzed Condition." Compensatory measures are being prepared including procedure changes, additional barriers, and contingency actions. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-05-31
49084 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-04-02 09:46 | 2013-05-31 15:07 | 2013-05-31 | 6O-DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified in 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to describe an invalid actuation signal affecting containment isolation valves in more than one system. "On April 2, 2013, Nine Mile Point 2 (NMP2) received a Division 2 reactor building area high ambient temperature isolation signal when lifting a lead for trip unit E31-N638B while performing surveillance N2-IPS-LDS-Q010, Reactor Building General Area Temperature Instrumentation Channel Functional Test. The isolation signal provided a closure signal to two Reactor Core Isolation Cooling System (RCIC) valves, and three Residual Heat Removal (RHR) system containment isolation valves. "As a result of the isolation signal one of the RCIC containment isolation valves, 2ICS*MOV128 closed. The other four valves were already in their normal closed position. The RHR system valves are associated with the RHR Shutdown Cooling System and second RCIC isolation valve is used to warmup and place the RCIC system in standby following an isolated condition. All affected isolation valves responded as designed. As a result of 2ICS*MOV128 closing the RCIC system was declared inoperable. Technical Specification 3.5.3, RCIC System, Condition A was entered. Action A.1 required verifying the High Pressure Core Spray System (HPCS) was operable immediately. Action A.2 requires restoring RCIC to operable within 14 days. "After the instrumentation system was restored to normal, the RCIC system was subsequently restored to available later that day at 1205 [EDT] and operable at 1500 [EDT]. "The actuation signal was not valid because it resulted from maintenance activities when leads were lifted, and the trip unit had not been bypassed as required by the procedure. There were no isolation logic signals in response to actual plant conditions or parameters. "This event was entered into the corrective action system as Condition Report (CR) 2013-002461. There were no actual safety consequences or impact on the health and safety of the public as a result of this event." The licensee notified the NRC Resident Inspector and the State. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-05-31
49083 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2013-05-31 | 2013-05-31 12:09 | 2013-05-31 | PART-21 INTERIM REPORT - INCORRECT PRESSURIZER SUPPORT LOADS FOR AP1000 "The deviation being evaluated is an identified inconsistency between the applied design loads for the AP1000 plant pressurizer support columns and embedments and the calculated actual loads. As a result, certified for construction drawings have been delivered to customers of the AP 1000 plant new build projects with an incorrect pressurizer support column embedment design configuration. The planned changes to the embedments to correct this deviation for the pressurizer support columns will be reflected on revised certified for construction drawings but do not require changes to the current licensing basis. The certified for construction drawings have been delivered to U.S. AP1000 plant new build customers, V.C. Summer Units 2 and 3, and A.W. Vogtle Units 3 and 4." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-05-31
49082 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2013-05-31 07:12 | 2013-05-31 10:26 | 2013-05-31 | MANUAL REACTOR TRIP DUE TO AN ANTICIPATED LOSS OF CONDENSER COOLING "On May 31, 2013 at 0712 [EDT], Unit 2 [reactor] was manually tripped due to high differential pressure on the debris filter for the 2A1 Condenser Waterbox which required a trip of the 2A1 Circulating Water Pump. The 2A2 Condenser Waterbox and the 2A2 Circulating Water Pump were already removed from service due to a suspected condenser tube leak. "All CEAs [Control Element Assembly] fully inserted into the core. Decay heat removal is from main feedwater and steam bypass to the main condenser. The cause of the rising differential pressure on the 2A1 debris filter was potentially due to an influx of algae. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the reactor trip." The reactor trip response is considered uncomplicated and the unit is stable in Mode 3 at normal temperature and pressure. Unit 2 is in a normal shutdown electrical lineup. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-05-31
49081 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-04-30 | 2013-05-30 15:28 | 2013-05-31 | AGREEMENT STATE REPORT - XENON VIALS LOST DURING TRANSPORT "A report of a missing package containing 4.67 GBq of Xe-133 was reported to the Radiation Control Program in Massachusetts by the licensee Lantheus Medical Imaging at 3:12 pm on 05/30/13. The package was intended to be shipped, [on 4/30/13], to Cardinal Health in Duncansville, PA. Cardinal Health is a nuclear pharmacy. "[The shipper] has been actively searching the Memphis facility over a 30 day period and has not found the package. They have scan records showing that the package did arrive, but no evidence that it has been shipped away. "The search has been abandoned since approximately 5.7 half lives [half life of 5.243 days] have passed and the material will be radioactively inert in another 10 days. "The Radiation Control Program will follow-up to determine the cause if one can be found." * * * UPDATE AT 1352 EDT ON 5/31/2013 FROM KENATH TRAEGDE TO MARK ABRAMOVITZ * * * " For further clarification, the package was shipped on 04/24/13. It was reported as missing to Lantheus Medical Imaging by Cardinal Health on 04/30/13. The package was reported as missing to [the shipper] by Cardinal Health on 04/24/13. Lantheus ran a trace on the tracking number and discovered there was no confirmation of delivery. They then contacted [the shipper] on 04/30/13 to confirm the missing package. [The shipper] confirmed the status. So, there was a little over a 6 day delay from the date of shipment to the date of Lantheus had confirmation that the package was missing. "Lantheus Medical Imaging, working in concert with [the shipper], attempted to locate the package over the 30 day period and was unsuccessful. Lantheus reported the missing package to our Agency [Massachusetts Radiation Control Program] on 05/30/13 in fulfillment with Agency Regulation 120.281(A)(2), 'Reports of Stolen, Lost, or Missing Licensed Material or Registered Sources of Radiation,' which allows a 30 day period from the date of discovery for the licensee to report the event to us. The NRC equivalent is 10 CFR 20.2201(a)(1)(ii). "The reported activity at the time of measurement (calibration) that was listed on the shipping record was 4.67 GBq on 04/24/13. Converting this to curies is 0.1262, or 126.2 millicurie. On the date and time of the day it was reported missing the Xe-133 would have decayed to a level of 1.85 GBq, or approximately 50 millicurie, confirming the information above." Notified the R1DO (Holody) and FSME Resources (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-06-07
49080 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2013-05-30 09:00 | 2013-05-30 10:16 | 2013-05-30 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM MAINTENANCE "On May 30, 2013, at 0900 [CDT], the Exelon LaSalle Station Technical Support Center (TSC) ventilation system was removed from service for planned TSC ventilation system maintenance. "The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The ventilation system is expected to be out of service for approximately 8 hours. "This telephone notification is provided in accordance with Exelon Reportability Manual SAF 1.10. 'Major Loss of Emergency Preparedness Capabilities', and 10CFR50.72(b)(3)(xiii). "The licensee has notified the NRC Senior Resident Inspector of the issue." * * * UPDATE AT 2040 EDT ON 5/30/2013 FROM MARK SMITH TO MARK ABRAMOVITZ * * * "The scheduled TSC ventilation system maintenance is expected to continue for approximately an additional 12 hours. "The licensee has notified the Senior Resident Inspector of the issue." The replacement fan belts came off and the cause is being investigated. Notified the R3DO (Orth). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-30
49079 | 0 | CLIFF'S NATURAL RESOURCES |  |  |  |  | 2011-08-09 | 2013-05-30 06:49 | 2013-05-30 | PROCESS GAUGE SHUTTER WILL NOT CLOSE The shutter on a process gauge used to measure iron ore density was discovered to be stuck open on 08/09/11 during a routine 6-month check. The gauge is in a remote location which is not easily accessible by personnel. The licensee has procedurally restricted access to the site and stated that it planned to have the gauge repaired when other process equipment in the vicinity of the gauge required maintenance or repair. During a recent NRC Regional inspection, the inspector became aware of this condition. The licensee was informed the event should have been reported to the NRC Operations Center when it was discovered. The gauge in question is a Kay Ray with a 200 millicurie Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-06-07
49078 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2013-05-29 22:40 | 2013-05-29 23:33 | 2013-05-29 | SAFEGUARDS REPORT Actual entry of an unauthorized person into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-05-29
49077 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-04-09 05:06 | 2013-05-29 11:06 | 2013-05-29 | 60 DAY REPORT OF AN INVALID PRIMARY CONTAINMENT SYSTEM ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On April 9, 2013, at 0506 hours Central Daylight Time (CDT), during placement of clearance 2-TO-2013-0003, section 2-099-0001, Browns Ferry Nuclear Plant (BFN), Unit 2, received Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolation signals. The PCIS Groups 2, 3, 6, and 8 isolations caused the initiation of all three trains of the Standby Gas Treatment (SBGT) system and Control Room Emergency Ventilation (CREV) subsystem 'A', and isolations of the BFN, Unit 2, Reactor Zone ventilation and BFN, Units 1, 2, and 3, Refuel Zone ventilation. Operations personnel responded to the PCIS initiation, ensured all equipment operated as designed, and stopped the clearance placement. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The apparent cause for this condition was the outage tagging personnel did not prepare clearance 2-TO-2013-0003 section 2-099-0001 as a stand alone clearance, detail the effect on PCIS initiation on cover placement instructions, place clearance 2-TO-2013-0003 in the right sequence, and perform a thorough review of clearance 2-TO-2013-0003 section 2-099-0001 to identify the missing detail related to PCIS initiation. Personnel performance issues are being addressed in accordance with the Tennessee Valley Authority policies and processes. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 711266. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-05-29
49076 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-05-29 09:34 | 2013-05-29 09:59 | 2013-05-29 | LOSS OF REDUNDANT ASSESSMENT CAPABILITY "Loss of one of two National Weather Service (NOAA) Tone Alert Radio Transmitters. "This is a non-emergency notification. "At 09:34 AM EDT on May 29, 2013, the National Weather Service reported that they plan to remove the National Weather Service (NOAA) Tone Alert Radio Transmitter, WXL-58 located in Chapel Hill, NC., serving the northeast piedmont on 162.550 MHZ, from service for maintenance. The maintenance is expected to last 4 hours. The purpose of the National Weather Service (NOAA) Tone Alert Radio transmitters is a redundant means to the 83 Harris Nuclear Plant Emergency Sirens to warn the public within the 5 mile radius of the plant of an actual event. The 83 Harris Nuclear Plant Emergency Sirens are in service and fully functional to alert the public within the 5 mile radius of the plant of an actual event should an event occur. "Compensatory Measure is in place as a back-up route alert to the public within the 5 miles radius (affected counties; Wake, Chatham, Harnett) upon declaration of an event. "There is no impact to public health and safety due to this condition. "The NRC Resident has been notified." This is the same NOAA Tone Alert Radio Transmitter as reported in NRC Event #49074. * * * UPDATE FROM RAYMOND MOORE TO VINCE KLCO ON 5/29/13 AT 1618 EDT * * * The NOAA Tone Alert Radio Transmitter was returned to service on 5/29/13 at 1538 EDT. The licensee will notify the NRC Resident Inspector. Notified the R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2013-05-29
49075 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-05-28 15:07 | 2013-05-28 18:09 | 2013-05-28 | MANUAL REACTOR TRIP DUE TO A FEEDWATER TRANSIENT "On May 28, 2013, at 1507 [EDT], Unit 2 was manually tripped from approximately 98 percent power due to decreasing steam generator levels as a result of a main feedwater system transient. The main feedwater system transient was initiated when the 'C' Main Feedwater Pump Discharge Motor-Operated Valve, 2-FW-MOV-250C, spuriously closed. The cause of the spurious closure of 2-FW-MOV-250C is unknown at this time. "The Operations crew entered the reactor trip procedure and stabilized Unit 2 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip. The reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater (AFW) pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the AFW system is reportable per 10CFR50.72 (b)(3)(iv)(A) for a valid actuation of an ESF system. The AFW pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 2 is in the normal shutdown electrical line-up. "Unit 1 was not affected by this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-05-28
49074 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-05-28 10:52 | 2013-05-28 11:36 | 2013-05-28 | LOSS OF REDUNDANT ASSESSMENT CAPABILITY "Loss of one of two National Weather Service (NOAA) Tone Alert Radio Transmitters. "This is a non-emergency notification. "At 10:52 AM EDT on May 28, 2013, the National Weather Service reported that they plan to remove the National Weather Service (NOAA) Tone Alert Radio Transmitter, WXL-58 located in Chapel Hill, NC., serving the northeast piedmont on 162.550 MHZ, from service maintenance. The maintenance is expected to last 4 hours. The purpose of the National Weather Service (NOAA) Tone Alert Radio transmitters is a redundant means to the 83 Harris Nuclear Plant Emergency Sirens to warn the public within the 5 mile radius of the plant of an actual event. The 83 Harris Nuclear Plant Emergency Sirens are in service and fully functional to alert the public within the 5 mile radius of the plant of an actual event should an event occur. "There is no impact to public health and safety due to this condition. "The NRC Resident has been notified." * * * UPDATE FROM RAYMOND MOORE TO CHARLES TEAL AT 1420 EDT ON 5/28/13 * * * At 1415 EDT on 5/28/13 the Tone Alert Radio Transmitter WXL-58 was returned to service. The licensee will notify the NRC Resident Inspector. Notified R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2013-05-28
49073 | 0 | MILLSTONE | 1 | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-28 10:06 | 2013-05-28 10:32 | 2013-05-28 | RADIATION MONITORS OUT OF SERVICE FOR PLANNED MAINTENANCE The Station Stack Radiation Monitor, RM-8169, and the Unit 1 Spent Fuel Pool Island Rad Monitor have been removed from service for preplanned maintenance for filter change out. During this time period, the licensee will not have normal assessment capability for radiation releases via these pathways. Compensatory monitoring methods are in place for the duration of the maintenance activity. The radiation monitors will be restored upon completion of the filter change-out. The expected completion time is before the end of day shift on 5/28/13. The licensee has notified the NRC Resident Inspector along with state and local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Decommissioned | Power Operation |  | Decommissioned | Power Operation |  | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-28
49072 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-05-27 15:45 | 2013-05-27 18:49 | 2013-05-27 | OFFSITE NOTIFICATION DUE TO DROWNING AT LAKE ANNA "At 1545 hours on 05/27/2013, the North Anna Control Room was notified by local authorities that a potential drowning had taken place at the number 3 Dike in Lake Anna. This incident has been reported to the FERC [Federal Energy Regulatory Commission] Regional Engineer under FERC requirements. Therefore, this is reportable to the NRC under 10CFR50.72(b)(2)(xi). In addition, this incident has received significant media interest. The identity of the victim is not known at this time." The licensee notified the NRC Resident Inspector and the Louisa County Administrator. | 100 | 96 | 0 | 100 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-27
49071 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-05-27 13:30 | 2013-05-27 15:22 | 2013-05-27 | SAFEGUARDS REPORT The licensee reported an abnormal condition involving safety related equipment that was suspected of being the result of tampering. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-05-27
49070 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-05-26 18:39 | 2013-05-26 21:52 | 2013-05-26 | TONE ALERT RADIOS OUT OF SERVICE "At 1839 EDT on May 26, 2013, with the James A. FitzPatrick (JAF) Nuclear Power Plant performing power ascension from 98% reactor power, Oswego County Emergency Management notified JAF that the Tone Alert Radios had been out of service since 1745 EDT. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8-hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "At 2111 EDT May 26, 2013, JAF was notified by Oswego County Emergency Management that the Tone Alert Radios had been returned to service "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed." | 100 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-26
49069 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-05-26 18:39 | 2013-05-26 21:32 | 2013-05-26 | TONE ALERT RADIOS OUT OF SERVICE "At 1839 EDT on May 26, 2013 Oswego County Emergency Management notified Nine Mile Point (NMP) that the Tone Alert Radios had been out of service since 1745 EDT. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF [James A. FitzPatrick] Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(iii). "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "At 2111 EDT on May 26, 2013, NMP was notified by Oswego County Emergency Management that the Tone Alert Radios had been returned to service. "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-26
49068 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-05-24 14:00 | 2013-05-24 14:47 | 2013-05-24 | HEATING VENTILATION AND AIR CONDITION SYSTEM INADEQUATELY ANALYZED FOR HEAT LOAD "There is no current event in progress at Oconee Nuclear Station (ONS). This notification is [being made] to complete a required 10 CFR 50.72 report that was not made at the time of discovery. During a review of the guidance in NUREG 1022, Rev. 2, ONS recognized conditions that were reported to the NRC in LER 269/2013-001-00 on April 8, 2013, (ADAMS Accession ML13101A307), which met the 8-hour reporting requirements of 10 CFR 50.72(b)(3)(ii)(B) -- 'Unanalyzed Condition,' and 10 CFR 50.72(b)(3)(v)(A,B,C&D) -- 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function,' but were not previously reported per 10 CFR 50.72(b)(3). LER 269/2013-001-00 previously documented Duke Energy's conclusion that emergency power equipment could be adversely impacted by a licensee identified, original design issue involving inadequate analysis of electrical equipment heat loads and weaknesses in the Heating Ventilation and Air Conditioning (HVAC) system design. Nothing in this notification modifies or supplements the information provided in LER 269/2013-001-00. This legacy event notification completes the action required by 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(A,B,C&D). The need to perform a 10 CFR 50.72 notification was not recognized during the reportability evaluation. "Initial Safety Significance: None. This is a legacy event notification. Oconee's emergency power equipment is currently operable, but nonconforming with Oconee's license. "Corrective Action(s): Compensatory measures are in place, and modifications are in progress to address the legacy design issue. The issue of not reporting as required under 10 CFR 50.72(b)(3) is entered into Duke Energy's corrective action program. "The Oconee NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2013-05-24
49067 | 0 | WATERFORD | 3 |  |  | [3] CE | 2013-05-24 12:30 | 2013-05-24 13:44 | 2013-05-24 | OFFSITE NOTIFICATION DUE TO INTAKE BARRIER BEING STRUCK BY OIL TANKER "At 0835 CDT, the Entergy Transmission Operations Center notified the Waterford 3 control room that a crude oil tanker had struck the dolphins at the cooling water intake structure on the Mississippi River. There were 4 out of 5 dolphins damaged, with 3 of these having substantial damage. "The dolphins are hard structures anchored around the cooling water intake structure [which provide] protection from river traffic. "Waterford 3 operations was unaffected by this event and thermal power remains at 100%. The intake structure, including the Circulating Water System, was unaffected by this event. "Possible near-term effects of the event are a loss of protective barrier between river traffic and the intake structure due to the physical damage to the dolphins and hazards to navigation due to the loss of the dolphin lights. "At 1230 CDT, the United States Coast Guard was notified of this event in accordance with Waterford 3 procedures. This notification is subsequent to the notification of the United States Coast Guard per 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-24
49066 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-05-24 03:34 | 2013-05-24 11:23 | 2013-05-24 | AUTOMATIC START OF EMERGENCY DIESEL GENERATOR DUE TO BUS UNDERVOLTAGE "At 0334 (CDT) on 5/24/2013 MNGP [Monticello Nuclear Generating Plant] experienced a loss of power to Bus 15 (Division 1 4kV Essential Bus) during performance of preoperational testing on the 2R reserve transformer which initiated an Essential Bus Transfer of Bus 15 and automatic start of 12 Emergency Diesel Generator. "MNGP was in Mode 5 operations with water level >21 feet 11 inches above the top of the RPV flange and all credited safety systems were lined up to Bus 16 (Division 2 4kV Essential Bus) which was unaffected by this event. "Bus 15 was automatically repowered from the 1AR reserve transformer as designed. During this evolution all critical safety functions remained green and all systems responded as expected to the Essential Bus transfer. The cause of the sequence of events that led to the Bus 15 loss of power is being investigated. "This event is reportable under 10CFR50.72(b)(3)(iv) as an event that results in a valid actuation of 12 Emergency Diesel Generator. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-05-24
49065 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-05-23 14:16 | 2013-05-23 18:25 | 2013-05-23 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR TESTING POSITIVE FOR ALCOHOL A non-licensed, supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2013-05-23
49064 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-05-23 10:50 | 2013-05-23 18:07 | 2013-05-23 | HPCI DECLARED INOPERABLE DURING POST MAINTENANCE TESTING "At 1050 hours on Thursday, May 23, 2013, with Pilgrim Station in the Startup/Hot Standby Mode and with the reactor coolant pressure at approximately 525 psig, the High Pressure Coolant Injection (HPCI) system was declared inoperable. The HPCI system was being operated in accordance with plant procedures to complete post maintenance test requirements. The flow controller could not achieve required system flow rates with the flow controller in the automatic mode. Plans to restore the automatic flow control capability are in progress. "The plant is in a safe condition and plant personnel are investigating the cause. "The [NRC] Resident Inspector has been informed of this notification. "The licensee will notify the Massachusetts Emergency Management Agency (MEMA)." | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-05-23
49063 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-05-23 | 2013-05-23 16:40 | 2013-05-23 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT The following was received from the State of Texas via email: "On May 23, 2013 the Agency [State of Texas] was notified by a licensee that while performing work at a remote site, a radiographer crew was unable to retract a source into a Spec 150 exposure device. The event occurred when a pipe jack fell on the source guide tube and crimped it to where the source connector would not pass through it. The radiographers contacted their Radiation Safety Officer (RSO) who responded to the scene. The source was covered with bags of lead shot to reduce the dose rates in the area. The RSO was able to un-crimp the guide tube using a pair of pliers enough to allow the source to be returned to the exposure device. The RSO received 45 millirem for the entire operation. No exposure limits were exceeded. The RSO stated that they disposed of the guide tube." Texas Incident #: I-9085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-05-31
49062 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2013-05-23 10:19 | 2013-05-23 15:45 | 2013-05-23 | TEMPORARY LOSS OF METEOROLOGICAL MONITORING SYSTEM DURING PLANNED MAINTENANCE "At 1019 CDT, AC power was removed from the site meteorological monitoring system (MET) equipment for planned maintenance in order to remove abandoned equipment left in place since installing the new meteorological system in October 2012. Removing AC power was not expected to have an effect since all MET information would continue to be available due to an 8-hour battery backup system installed at the meteorological tower. However, when power was removed, all onsite meteorological data was lost to the control room via the Plant Management Information System (PMIS). PMIS is the only display of local direct meteorological conditions available. Subsequently, [Cooper Nuclear Station] CNS determined the interface between MET system and PMIS was not powered from the 8 hour MET battery backup system which accounted for the lost MET indication. CNS corrected the condition and restored meteorological data to the control room via the PMIS system at 1219 CDT. "Site backup assessment capability relies on Meteorological model estimates from the National Weather Service out of Valley, Nebraska or on default values derived from historical local weather patterns. Since there was no direct information of site meteorological conditions during the period of lost power, CNS considered this to be a major loss of assessment capability and reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-23
49061 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-05-23 04:55 | 2013-05-23 12:42 | 2013-05-23 | PRIMARY CONTAINMENT DECLARED INOPERABLE DURING HPCI TESTING "At 0455 hours on Thursday, May 23, 2013, with Pilgrim Station in the Startup/Hot Standby Mode and reactor coolant pressure approximately 550 psig, primary containment was declared inoperable due to a leak on the High Pressure Coolant Injection system (HPCI) turbine exhaust line while performing the HPCI system flow rate test. Power ascension was suspended pending investigation and repair. Repair plans to restore system integrity are in progress. "The plant is in a safe condition and plant personnel are investigating the cause. The Resident Inspector has been informed of this notification. This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(C) and (D). The licensee will notify the Massachusetts Emergency Management Agency (MEMA)." The licensee has entered Technical Specification 3.7.A.2 to be in cold shutdown within 24 hours. | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2013-05-23
49060 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-05-20 | 2013-05-22 16:03 | 2013-05-22 | LOST TRITIUM EXIT SIGNS The following information was obtained from the State of Colorado via email: "A representative from Chair Rental, reported receiving the documentation for 2013 Self Certification, Registration, and Inventory report from the [Colorado State] Radioactive Materials Unit's annual General License notifications. The report requires the company to verify the use and location of the exit signs at the site noted within the reports. "[The company representative] contacted the [State's] Radioactive Materials Unit - General License section to report two exit signs were not located during the inventory check on May 20, 2013. The signs are kept in a storage room within a warehouse. Further details are being investigated. "During the investigation, Chair Rental was asked to complete a corrective action plan and was made aware of the importance of accounting for exits signs within their business. The following information is provided for compliance. Maker of sign: Forever-Lite, Inc. Model Number: SLXTU16U10 Serial Number: 228,338 and 228,340 Date of Manufacture: May, 2010 Date of Loss: Unsure Location of Sign: When Lost: Unsure "Other Details: Signs are kept in a storage room for use in larger tents. When letter was received, [the company] went to do an inventory and two [signs] were missing. [The company is] unsure if they are lost in the building or if they are lost on a job site. "Corrective Action Plan: [The company has] briefed our employees to check certain job sites in the hope that we may recover them. [The company] will also be using a sign out sheet for the signs that will include where they are going to and who is checking them out." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-05-30
49059 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-05-22 09:51 | 2013-05-22 13:50 | 2013-05-22 | FALSE INFORMATION ON PERSONAL HISTORY QUESTIONNAIRE A contract non-supervisor employee provided false information on the personal history questionnaire. The employee's plant access has been terminated. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-05-22
49058 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-05-22 05:16 | 2013-05-22 11:06 | 2013-05-22 | LOSS OF REDUNDANT ASSESSMENT CAPABILITY "Loss of both National Weather Service (NOAA) Tone Alert Radio Transmitters. "At 5:16 AM EDT on May 22, 2013 the National Weather Service reported a loss of the National Weather Service (NOAA) tone alert radio transmitters, WXL-58 located in Chapel Hill, NC, serving the northeast Piedmont on 162.550 MHZ, and WNG-706 located in Garner, NC, serving the eastern Piedmont and coastal plain on 162.450 MHZ. The National Weather Service expects to return both transmitters to service no earlier than 8:00 AM on May 22, 2013. The purpose of the National Weather Service (NOAA) tone alert radio transmitters is a redundant means to the 83 Harris Nuclear Plant emergency sirens to warn the public within the 5 mile radius of the plant of an actual event. The 83 Harris Nuclear Plant emergency sirens are in service and fully functional to alert the public within the 5 mile radius of the plant of an actual event should an event occur. "There is no impact to public health and safety due to this condition. "The NRC Resident has been notified." The tone alert radio transmitters were returned to service at 11:30 AM. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2013-05-22
49057 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-05-13 | 2013-05-22 11:13 | 2013-05-22 | SHIPPING DRUM EXCEEDED NON-REMOVABLE CONTAMINATION LIMITS The following information was obtained from the State of Washington via email: "Surface contamination levels exceeded limits for package. PermaFix Northwest received a shipment from Moravek Biochemicals [based in Brea, CA] that consisted of (14) 55 gallon drums, and was shipped as an exclusive use shipment. Upon receipt, the drums were surveyed and 1 drum was found to exceed the 49 CFR 173.443 non-removable contamination limit of 2,200 dpm/cm2 for an exclusive use shipment. The drum survey results were reported as 35,538 dpm/100 cm2 H-3 and 1391 dpm/100 cm2 C-14. Taking into account the 10% wipe efficiency, the contamination levels on this drum exceeded the DOT contamination limits for packages. This drum was manifested with only H-3 and C-14. " Washington Incident Number: WA-13-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-05-30
49056 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-05-21 12:00 | 2013-05-21 22:15 | 2013-05-21 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED CONTRACT SUPERVISOR A non-licensed, contract supervisory employee failed a random fitness-for-duty test. The employee's access to the plant has been revoked. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2013-05-21
49055 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-03-24 10:09 | 2013-05-21 16:46 | 2013-05-21 | INVALID ACTUATION OF HPCI SUCTION VALVES "On March 24, 2013, at 1009 EDT, while personnel were entering the torus compartment to perform planned maintenance activities via permanently installed plant ladder, the sensing line to transmitter 2E41-N062D was inadvertently bumped. [This] was confirmed to be the cause for an invalid torus high water level alarm and a HPCI [High Pressure Core Injection] pump suction swap. This resulted in the HPCI suction swapping from its normal lineup, condensate storage tank (CST), to the torus as designed. Once actuated the suction swap occurred as designed. The cause was attributed to the close proximity between an individual descending/ascending the fixed ladder and the affected sensing line in conjunction with a loose tubing restraint which made the line more sensitive to being bumped. After confirming that the actuation on high torus level was invalid, HPCI suction was realigned to the CST. "The HPCI pump suction was subsequently realigned to the CST and the loose tubing restraints were tightened." The licensee notified the NRC Resident Inspector. | 0 | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-05-21
49054 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-05-21 05:33 | 2013-05-21 06:20 | 2013-05-21 | MANUAL REACTOR TRIP AFTER A FEED PUMP TRIP "Reactor trip. All safety functions met with normal heat removal. 22 SGFP [Steam Generator Feedpump] exhibited high vibrations and signs of coupling damage. Further investigation will be performed." All control rods fully inserted on the trip. Steam Generator level is being maintained with the remaining feedpump. Decay heat is being dumped to the main condenser. Electrical power is in the normal shutdown lineup. No relief or safety valves lifted during the trip. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-05-21
49053 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-05-20 03:53 | 2013-05-20 07:54 | 2013-05-20 | OFF-SITE NOTIFICATION DUE TO FIRE IN TURBINE BUILDING "At 0353 hours [EDT] on Monday, May 20, 2013 Pilgrim Station responded to indications of a fire in the Turbine Building (TB) Lubricating Oil Room. The Pilgrim Fire Brigade responded to the fire and was able to extinguish a small fire associated with the 'A' Auxiliary Oil Pump Motor. The plant was in start-up at the time of the event with the reactor critical and reactor coolant system temperature approximately 180 degrees F. "The Plymouth Fire Department was contacted and responded to the site. The event did not require entry into the Emergency Action Levels (EALs). The plant is in a safe condition and plant personnel are investigating the cause. The plant will be restarted after a thorough evaluation and any necessary repairs are completed. "This informational notification is being made in accordance with 10 CFR 50.72(b)(2)(xi). The licensee has notified the Massachusetts Emergency Management Agency (MEMA) . "The Resident Inspector staff has been informed of this notification." This was an electrical fire confined to the aux oil pump motor and was extinguished using hand held CO2 and dry chemical extinguishers. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-20
49052 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-05-19 14:21 | 2013-05-19 18:51 | 2013-06-04 | PLANNED OUTAGE OF RADIOLOGICAL AND SEISMIC MONITORING CAPABILITY "During Refueling Outage 21, at approximately 0700 PDT on May 20, 2013 the following plant's gaseous effluent radiation monitoring systems and seismic monitoring systems will be removed from service due to a planned power outage: " - Reactor Building Stack Radiation Monitor: Low Range; Intermediate Range; and High Range Detectors. [NOTE: The Reactor Building Stack Radiation Monitors were removed from service as of 1421 PDT on 19 May 2013 (24 hours before the power outage) to allow for a gradual warming up of the sensors] " - Rad Waste Building Vent Exhaust Low Range Radiation [Rate Meter] and Exhaust Air Monitor Radiation Indicating Switch " - Turbine Building Radiation Indicating Switch and Exhaust Air Radiation Indicating Switch " - Seismic Instrument Accelerometers " - Seismic Instrument Accelerographs "The listed equipment is expected to be re-energized at approximately 1400 PDT on May 22, 2013. The Reactor Building Stack Radiation Monitors is expected be operational approximately 48 hours after they are re-energized to allow for sensor cooling requirements to be established. "To compensate for the loss of the radiation monitoring equipment, an additional Health Physics (HP) Technician trained to acquire offsite dose assessment information on offsite releases will be on shift. The additional personnel will be pre-staged in support of the radiation monitoring system outage and will be deployed in accordance with guidance in site procedures and the compensatory measure instructions. "To compensate for the loss of the seismic monitoring capability, an entry into the abnormal operating procedure 'EARTHQUAKE' will be made when an earthquake is felt in the control room or when information is received from plant personnel that an earthquake has been felt. Earthquake severity will be estimated in accordance with abnormal operating procedure 'EARTHQUAKE' in lieu of instrumentation being available. Information from the US Geological Survey (USGS), if available, will supplement the estimation of earthquake severity. "This event is being reported as a loss of emergency assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). A follow up notification will be made when the equipment has been returned to service. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM DIEGO SUAREZ TO CHARLES TEAL AT 1932 EDT ON 6/4/13 * * * "The Columbia Seismic Instruments (Accelerometers and Accelerographs) were returned to service on May 30, 2013, at 0440 PDT. "The Columbia radiation monitoring instruments listed below were returned to service on June 2, 2013, at 1814 PDT: - Reactor Building Stack Radiation Monitor: Low Range; Intermediate Range; and High Range Detectors - Rad Waste Building Vent Exhaust Low Range Radiation [Rate Meter] and Exhaust Air Monitor Radiation Indicating Switch - Turbine Building Radiation Indicating Switch and Exhaust Air Radiation Indicating Switch" The licensee will notify the NRC Resident Inspector. Notified R4DO (Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-19
49051 | 0 | CRANE NUCLEAR INC |  |  |  |  | 2013-05-17 | 2013-05-17 20:56 | 2013-05-17 | NOTIFICATION OF VALVE BODY LEAKAGE Subject: 10CFR21 Notification on Potential Valve Body Leakage - 20 Valve Assemblies. Crane Nuclear, Inc. has been advised by one customer about leakage on the body of an installed 2" valve assembly. The valve body identified as leaking or weeping was cast from alloy SB 148 UNS 95200. While it was the customer that identified the valve body leakage to Crane Nuclear, a notification letter with their purchase order history was sent to Dominion / Millstone today in accordance with their purchase order notification requirements. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-05-17
49050 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-05-17 | 2013-05-17 17:28 | 2013-06-10 | EMBEDMENT DEPTH FOR SEISMIC ANCHORS INADEQUATE "It has been determined that some instrument racks in the Containment and Auxiliary buildings do not meet their design basis capacity due to inadequate embedment depth of the seismic anchors. Assumptions made about embedment depth for a previous event were determined to be incorrect; therefore, the design basis capacity cannot be assured. This report is being made under 10 CFR 50.72(b)(3)(ii)(B), 'Unanalyzed condition'." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 6/10/2013 AT 1630 EDT FROM DAVID ORTIZ TO MARK ABRAMOVITZ * * * "Additional evaluation has determined that the instrument racks are adequately anchored. Therefore, this event is not reportable." The licensee notified the NRC Resident Inspector. Notified the R4DO (Gepford). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-05-17
49049 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-05-17 | 2013-05-17 16:55 | 2013-05-20 | MASSACHUSETTS AGREEMENT STATE REPORT - MEDICAL EVENT CONCERNING GAMMA KNIFE THERAPY A patient was undergoing a second gamma knife treatment when the treatment was delivered to the wrong side of the brain. The patient and the prescribing physician were informed. The patient received 75 Gy to the brain. No serious effects are expected. The Commonwealth of Massachusetts will be providing an update to this event. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM MICHAEL WHALEN TO JOHN SHOEMAKER AT 1350 EDT ON 5/20/13 * * * The following report was received via email. "Event Occurred on 5/17/2013 at approximately 1000 [EDT]. "With a Gamma Knife Manufacturer: Leksell Gamma System Model: Model 24001 Type C "Sealed Sources information: Manufacturer: Elekta Model number: 43685 "Prescribed treatment was for one fraction [the daily dose] of 75 Grays to be delivered to the left side of brain. However, the right side of the brain received the treatment." Notified R1DO (Gray) and FSME EVENTS RESOURCE via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-05-27
49048 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-05-17 15:27 | 2013-05-17 16:34 | 2013-05-17 | PLANT PROCESS COMPUTER REMOVED FROM SERVICE FOR MAINTENANCE AND UPGRADES "This is a non-emergency 8-hour notification for a planned loss of emergency assessment capability. This event is reportable in accordance with 10CFR50.72(b)(3)(xiii) because the work activities affects the functionality of the Plant Process Computer System. Monticello Nuclear Generating Plant will remove the Plant Process Computer System (PPCS) from service on 5/17/13 at 1527 [CDT] to perform system upgrades and planned maintenance. The PPCS system is planned to be non-functional for less than 4 hours. While the system is out of service, the Emergency Plan can still be implemented as assessment capabilities are available under alternate means and communication of the assessment results using communication equipment. ERDS will be out of service during this period. Compensatory measures for the loss will be implemented. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-17
49047 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-17 04:39 | 2013-05-17 12:05 | 2013-05-23 | UNANALYZED CONDITION FOR REACTOR COOLANT SYSTEM TEMPERATURE BELOW REQUIRED VALUE "On May 17, 2013 at 0439 EDT, with the unit in Mode 3, operators identified RCS temperature decreased below 551 deg. F with the reactor trip breakers closed. The condition existed for approximately one hour after which operators identified this was below the procedurally required value identified to support power range nuclear instrumentation trip operability. The condition was then immediately corrected. "The plant remains stable in Mode 3. "This condition is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition. The NRC Senior Resident Inspector has been notified." The reactor trip breakers were closed to support rod testing at the time this event occurred. RCS temperature was decreasing due to Terry turbine testing which was being performed at the same time. The reactor trip breakers were opened when the operators identified RCS temperature below 551 degrees. The RCS temperature was returned to above 551 degrees. This temperature limit is specified in Millstone 3 FSAR section 15.4.1, "Uncontrolled rod cluster control assembly bank withdrawal from a subcritical or low power startup condition". The licensee notified state and local authorities. * * * RETRACTION FROM WILLIAM BARTRON TO DONALD NORWOOD AT 1053 EDT ON 5/23/2013 * * * "The purpose of this call is to retract the report made on May 17, 2013, Event Number 49047. "Upon further review, the condition in which Reactor Coolant System (RCS) temperature decreased below a procedural limit while in Mode 3 did not result in an unanalyzed condition. Engineers verified that RCS boron concentration was sufficiently high that criticality could not have occurred during any inadvertent control rod withdrawal. The details of the engineering review have been provided to the NRC Senior Resident Inspector." Notified R1DO (Gray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-05-17
49046 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-05-16 15:25 | 2013-05-16 17:56 | 2013-05-16 | AGREEMENT STATE REPORT - CONTAMINATION EVENT REQUIRES AREA TO BE RESTRICTED FOR GREATER THAN 24 HOURS The following information was obtained from the State of Texas via E-mail: "On May 16, 2013 at 1525 [CDT], the licensee contacted the Agency [Texas Department of State Health Services] to report a contamination event which required access to an area to be restricted for more than 24 hours due to an unplanned contamination event. The licensee had received a drum containing 18 nuclear gauges from a facility licensed in the State of North Carolina (NC). The Texas licensee was to dismantle the gauges and dispose of the sources. The Texas licensee stated the gauges had been leak tested by the NC licensee and the leak test results were below regulatory levels. The Texas licensee stated they performed a contamination survey of the drum before they began removing the gauges. A licensee's worker removed the first gauge in preparation to remove the source. The gauge was a Berthold model LB 7400 gauge containing a Cs-137 source. When the worker opened the shutter of the gauge to remove the source, they found a piece of lead inside the gauge cavity between the gauge shutter and the source. As the worker removed the piece of lead they noted the background radiation readings where increasing. The worker stopped work and notified his supervisor. A contamination survey found that the workers hands, shirt sleeves, the table top, the floor in the immediate work area, and the worker's personal dosimetry were contaminated. The workers contaminated shirt and dosimetry were removed and his hands were decontaminated. The worker's face was surveyed for contamination, none was detected. The licensee's Radiation Safety Officer (RSO) stated that worker was decontaminated within 15 minutes of the event occurring. The RSO stated that the individual had not exceeded any exposure limits based on their electronic dosimeter reading. The licensee attempted to decontaminate the table top and the floor in the work area, but some areas remain contaminated. Access to the area remains restricted. The Texas licensee has contacted the NC licensee and notified them of the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-05-24
49045 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-05-16 15:25 | 2013-05-16 17:06 | 2013-06-05 | SAFEGUARDS REPORT A contract security guard would have been denied unescorted access based on information developed during the administrative review of access records. The individual's unescorted access was suspended pending further investigation. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ROBYN SAVAGE TO DANIEL MILLS AT 1528 EDT ON 06/05/2013 * * * This event has been retracted. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. Notified the R4DO (Spitzberg) and 73.71 Group via email. | 12 | 100 | 0 | 12 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-05-16
49044 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-05-14 | 2013-05-16 16:47 | 2013-05-16 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE INTO RADIOGRAPHY CAMERA The following information was obtained from the State of Texas via E-mail: "On May 15, 2013, the licensee's Radiation Safety Officer (RSO) reported to the Agency [Texas Department of State Health Services] that on May 14, 2013, one of its radiography crews had been unable to retract the source back into the QSA Model 880 camera they were using. The radiography crew had dropped and damaged the crank assembly when it was moving the equipment between shots. The crew apparently failed to thoroughly check the crank assembly prior to the next shot. Following the next shot, the source could not be retracted. The RSO was notified and he and another licensee employee, with assistance from the radiographers, performed the source retrieval (the camera and equipment had to be lowered to the ground from 40 feet inside a tank where the radiography was being performed in order to retrieve the source). The RSO reported that the connector at the end of the cable, which connects the cable to the pigtail, had come off of the cable. [The connector] was apparently damaged in the crank assembly accident. Readings from the pocket dosimeters were: RSO received 240 mrem; other employee performing source retrieval received 40 mrem; and, the 3 [other] radiography crew members received 300 mrem, 110 mrem, and 80 mrem, respectively. No member of the public received any exposure from this event. Further information will be provided as it is obtained, per SA-300. "Radiography Camera: QSA Model 880, SN: D11097, Source: SN: 93674B" Texas Incident #: I-9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-05-24
49043 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 |  | 2013-05-16 16:46 | 2013-06-27 | PRIMARY CONTAINMENT AIRLOCK NON-FUNCTIONAL DUE TO DEGRADED SEAL ON INNER DOOR CONCURRENT WITH PERSONNEL PASSING THROUGH THE OUTER DOOR "At approximately 1934 EDT on May 15, 2013, maintenance personnel entered the primary containment personnel air lock to determine the cause of the inability to attain test pressure during a type B leak rate of the airlock. The inner door seal was found degraded and partially rolled from its required position allowing air from inside the airlock to enter the primary containment. During the limited time the outer airlock door was opened for access into the airlock concurrent with the degraded seal on the inner door, a condition existed that could have prevented the fulfillment of the safety function of the structure to control the release of radioactive material. "The inner door seal was subsequently replaced and the leak rate of the personnel air lock completed with satisfactory results. During the seal replacement activity, the outer airlock door remained closed to provide the barrier against the release of radioactive material should it be required. "This is a notification per 10 CFR 50.72(b)(3)(v) for a condition that could have prevented the control of the release of radioactive material. It is recognized that this notification [was] not within eight hours of the event. "The condition has been entered into the station's corrective action program." The licensee will notify the New York State Public Service Commission and the NRC Resident Inspector. * * * RETRACTION ON 6/27/13 AT 1549 EDT FROM KROCK TO HUFFMAN * * * "This notification is being made to retract Event Notification #49043, which reported a condition that could have prevented the control of the release of radioactive material when the primary containment airlock inner door seal was found degraded concurrent with the outer door being open. "Further analysis by engineering of the actual conditions which were recorded when the airlock Type B leak rate test was being performed and calibration checks of the leak rate monitor instrumentation used for the test, has determined that the leakage through the degraded inner airlock door seal, when combined with the Appendix J As-Left Minimum Pathway Type B and C leak rates, remains below the Technical Specification Primary Containment As-Left Minimum Pathway Leakage Limit of 0.6 La. "Therefore, for the period in which the inner airlock door seal was degraded and the outer airlock door was open, the primary containment function to control the release of radioactive material was maintained and the initial notification per 10 CFR 50.72(b)(3)(v) is being retracted." The licensee has notified the NRC Resident Inspector and the New York State Public Service Commission. R1DO (Ferdas) notified. | 23 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-05-16
49042 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-16 09:25 | 2013-05-16 12:52 | 2013-05-16 | STACK RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE At 0925 EDT on 5/16/13, Stack Radiation Monitor RM-8169 was removed from service for pre-planned maintenance. There are no automatic actuations or initiations associated with this radiation monitor. The radiation monitor will be restored to service following completion of maintenance. The licensee has notified the NRC Resident Inspector and the state and local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-16
49041 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-05-15 | 2013-05-16 12:50 | 2013-05-16 | TEXAS AGREEMENT STATE REPORT - BROKEN RADIOGRAPHY CAMERA DRIVE CABLE The following information was obtained from the State of Texas via email: "On May 15, 2013, the licensee reported that one of its radiography teams had been unable to retract an iridium-192 source back into a QSA Model 880 radiography camera at a temporary field site in Galena Park, Texas. The licensee's RSO and a supervisor responded to the site. "The RSO covered the collimator containing the source with lead shot bags then an individual authorized to perform source retrieval responded and secured the source. The pocket dosimeter readings for the three were: RSO received 60 millirem; the supervisor received 50 millirem; and the individual performing source retrieval received 40 millirem. "The licensee reported that the drive cable had broken right behind the ball. No member of the public received any exposure as a result of this event. The source, camera, and equipment will be taken to the licensee's facility and the licensee will contact the manufacturer. "Further information will be provided as it is obtained in accordance with SA-300. "Radiography camera: QSA Model 880, SN: 2735. Source SN: 91360B" Texas Incident # I-9078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-05-24
49040 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-05-15 | 2013-05-16 10:28 | 2013-05-16 | FIXED GAUGE SHUTTER HARD TO OPEN The following information was submitted by the Commonwealth of Virginia via fax: "On May 15, 2013, the licensee reported that the shutter of one of its fixed gauges was not 'functioning per the design.' The problem was detected during the periodic shutter checks on May 15, 2013. The shutter could be closed but needed strong force to open it. The gauge is a Ronan Engineering Company, Model SA1-F37, Serial number M-2232. The gauge contains 50 mCi of Cs-137 as of the manufacturing date (remaining activity as of the incident date is 34.3 mCi). "Ronan Engineering Company was contacted and a schedule has been arranged for shutter repair. "A radiation survey was performed by the licensee and found to be within design parameters and regulatory limits. There are no public health or safety issues involved. The Virginia Radioactive Material Program will follow up with the licensee." Virginia Event Report ID: VA-13-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-05-24
49039 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP |  | 2013-05-16 10:20 | 2013-07-10 | MANUAL REACTOR TRIP DURING CONTROL ROD TESTING "On May 16, 2013, at 0256 EDT, while in Mode 3 (subcritical), operators manually opened the reactor trip breakers as directed by procedure. During rod drop testing, demand position and digital rod position indication did not agree within procedural limits. As directed by procedure, operators opened the reactor trip breakers. The cause of the discrepancy is under investigation. The plant responded as expected and all rods inserted as required. The plant remains stable in Mode 3. "This condition is reportable pursuant to 10 CFR 50.72(b)(3)(iv). "The NRC Senior Resident Inspector has been notified." * * * RETRACTION FROM TODD STRINGFELLOW TO DANIEL MILLS ON 7/10/2013 AT 1418 EDT * * * "The purpose of this call is to retract the report made on May 16, 2013, Event Number 49039. Operators manually opened the reactor trip breakers in MODE 3 during hot control rod drop testing as directed by procedure. The condition has been determined to be an invalid actuation of the RPS since boron concentration, and not control rods, were being relied upon for safety function during rod testing. The details of the engineering review will be provided to the NRC Senior Resident Inspector." Notified R1DO (Cook). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-05-16
49038 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-05-15 06:49 | 2013-05-15 19:55 | 2013-05-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO DISCOVERY OF AN UNACCEPTABLE FLAW DURING DATA REVIEW "On May 13, 2013, during a secondary review of ultrasonic data of the reactor vessel head penetrations performed during Harris Nuclear Plant spring 2012 refueling outage, it was determined that the results for one of the penetrations appeared to not meet the applicable acceptance criteria. Further evaluation completed on May 15, 2013, characterized the flaw as a 0.26 inch flaw on nozzle 49 that overlaps the J-grove weld and exhibits characteristics of primary water stress corrosion cracking. The original examinations were performed per NRC requirements. "Initial evaluation indicates that the flaw is not through wall and there is no evidence of leakage based on inspections performed on the top of the reactor vessel head during the spring 2012 refueling outage. Operators are shutting down the unit to make the necessary repairs. There is no impact to the health and safety of employees or the public. "The NRC resident inspector has been informed. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A), discovery of a degraded condition, 10 CFR 50.72(b)(2)(i), plant shutdown required by technical specifications, and 10 CFR 50.72(b)(3)(v)(C), a condition which could have prevented the fulfillment of a safety function to control the release of radioactive material." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION | POT UNCNTRL RAD REL |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  | 0 | 2013-05-15
49037 | -1 | NV DIV OF RAD HEALTH |  |  |  |  | 2013-05-14 09:45 | 2013-05-15 16:54 | 2013-05-16 | AGREEMENT STATE REPORT - WRONG DOSE ADMINISTERED TO PATIENT The following information was obtained from the State of Nevada via email: "The patient was to undergo a HIDA [hepatobiliary] scan for abdominal pain (Tc-99m; 5mCi, abdomen), but given syringe for MDP [bone scan] (Tc-99m; 30mCi; bone). A wrong dose of Tc-99m (600% the prescribed dose) was administered to the patient due to human error. "Corrective action: Better training in cross-checking and confirming patient identity with prescribed dose information." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. Item Number: NV130006 * * * RETRACTION FROM SNEHA RAVIKUMAR VIA E-MAIL ON 5/16/13 AT 1329 EDT * * * "This is with regard to the wrong dose administration that was reported yesterday. [The State of Nevada] heard back from the RSO regarding the Effective Dose Equivalent: "What should have been administered was 5 mCi of HIDA (Mebrofenin) = (3E-02) x 5 rem = 0.15 rem. "What was administered was 30 mCi of MDP = (2E-02) x 30 rem = 0.60 rem. "So, this would not be reportable." Notified R4DO (Walker) and FSME Events Resource via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2013-05-23
49036 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-05-15 | 2013-05-15 15:00 | 2013-05-15 | MISSING LICENSED MATERIAL This is a non-emergency 30 day notification for missing licensed material. This event is reportable in accordance with 10CFR20.2201(a)(1)(ii). On April 16, 2013, while performing the required semi-annual source leak check and inventory, Radiation Protection personnel could not locate the source label tag or cable for source RMC-0169 on radiation monitor 1EMF44H (This monitor has not been in use since 1995). The monitor's pre-amplifier box had been removed as well. 1EMH44H was inspected and the source was not found within the housing. A search was conducted for this missing source, however it could not be located. During the previous source leak check and inventory on October 4, 2012, the source was in its expected location. Source RMC-0169 is a 200 milligram depleted uranium source. The total original activity of the source was 9.998E-02 microCuries (3.03E-02 micro curies; U-234; 1.98E-03 microCuries; U-235, 6.77E-02 microCuries; U-238). The reportable limit for U-234 (the shortest-lived isotope in the source is U-234 with a half-live of 2.46E+05 years) is 0.01 microCuries per 10CFR20, Appendix C. Based on the activity of U-234 present in the source of 0.03 microCuries, this 30 day phone notification to the NRC is being provided pursuant to 10CFR22.2201(a)(1)(ii). The external dose to an individual from this source is negligible due to the small quantity and the type of material involved. Therefore, this event has no adverse effect upon the health and safety of employees or the public. The required written report pursuant to 10CFR20.2201(b)(1) will be provided to the NRC within 30 days of the telephone notification. The NRC Resident Inspector has been notified. The licensee with notify State and local authorities. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-05-23
49035 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-04-24 | 2013-05-15 13:49 | 2013-05-29 | AGREEMENT STATE REPORT - FOUND RADIUM 226 SOURCE "On April 24, 2013, The Colorado Department of Public Health and Environment [Department] received notification from the Mesa County Landfill located in Grand Junction, Colorado, that a load of trash had alarmed the gate monitor. The roll-off in question came from a residential spring clean-up event sponsored by the city of Grand Junction. "That same day, a member of the Department responded to the alarm and the roll-off was moved to a secure location after an initial radiation survey on the outside of the roll-off had been completed. "On May 7, 2013, members of the Department examined the contents or the roll-off and a small section of plastic pipe (1 foot length) and a small source bound with tape were identified. It appeared that the source had been taped to the side of the plastic pipe at one time, and the word 'source' was written on the pipe. Using an Identifinder multi-channel analyzer, the isotope was identified as Ra-226. "Dose rates were measured at greater than 200 millirem per hour on contact with the source (the limit of the inspector's instrument), and 10 millirem per hour at 1 foot. The dimensions of the source appeared to be approximately 3 mm by 2 cm. The source is currently stored in a secured location. "The Department is conducting an investigation, and a press release is being issued to encourage anyone with information about the source to contact the Department." * * * UPDATE FROM ED STROUD TO VINCE KLCO ON 5/29/13 AT 1459 EDT * * * The following information was received by email: "Following the initial event notification on 5/15/13 regarding a found Ra-226 source in Grand Junction, CO, the Colorado Department of Public Health and Environment issued a press release that requested anyone with additional information to please contact the DOH. Several days later a member of the public contacted DOH with a possible lead. Using that information, inspectors were able to trace the source back to a private residence in Grand Junction. On 5/24/13, inspectors visited a house in a residential neighborhood and found additional radioactive materials in the attached garage. However, the inspectors were not permitted to enter the residence. Radioactive materials found included 2 more Ra-226 sources and a half dozen small jars containing an unknown radioactive powder, which appeared to be uranium mill tailings. The radioactive materials were removed by the inspectors and taken to a secure storage location where additional measurements/analysis can be conducted. The elderly female resident at the house told inspectors that her late husband and his business associates manufactured Geiger counters during the uranium boom years. "Additional information will follow as it is obtained." Notified R4DO (Azua) and FSME Resources via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-05-23
49034 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-15 04:00 | 2013-05-15 11:55 | 2013-05-15 | LEAKING CONTAINMENT AIR LOCK EQUALIZING VALVE "On May 15, 2013, at 0400 EDT, it was discovered that an equalizing valve for the outer containment air lock was leaking by its seat rendering the outer containment air lock inoperable. This condition was discovered by maintenance personnel as they were exiting containment through the inner containment air lock. "The containment inner door was open for transit, which resulted in the Loss of Containment Integrity. "With both containment air lock doors open at the time of discovery of the leaking equalizing valve, this condition is reportable pursuant to 10 CFR 50.72(b)(3)(v). The inner air lock door was immediately closed and has remained closed since. "Technical Specification 3.6.1.1 Primary Containment Integrity is applicable in Modes 1,2,3, and 4. Since Primary Containment Integrity was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to control the release of radioactive material. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-05-15
49033 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2013-05-14 22:09 | 2013-05-15 11:03 | 2013-05-15 | RESEARCH REACTOR REPORTABLE EVENT - CONTROL ROD DRIVE MECHANISM JAM "This preliminary event report is in compliance with Technical Specification 6.6.2 Special Reports confirming in writing the initial report made by telephone to the USNRC Operations Center. "During reactor shutdown after normal steady state operation on May 14, 2013 at 2209 CDT, shim safety 1 jammed at 30% withdrawn (70% inserted). Operators lowered the remaining rods with no other issues and after determining the reactor was shut down at 2250 CDT, operators began investigating the cause of the jam. The shutdown margin in this configuration was determined to be $2.91 [negative reactivity] with shim safety 1 jammed at 30%. The Technical Specification requirement for shutdown margin is $0.25 [negative reactivity] which meant the reactor was well within acceptable limits for shutdown. "The reactor was determined to be in a safe shutdown state. During inspection a rope that was attached to an experiment was found to be caught inside the Control Rod Drive Mechanism (CRDM) for shim safety 1 about 10 feet from the surface of the pool. This caused a jam in the drive mechanism not allowing the rod to go below 29% and above 32%. "A fuel handling team was assembled at 0945 CDT on 5/15/13 in order to remove the control rod assembly for shim safety 1. The rope connecting the experiment to the CRDM was cut in order to allow proper removal of the CRDM. The CRDM was successfully removed and the piece of rope caught inside the drive was removed. After further inspection of the CRDM no other issues were found and it was reinstalled into its normal position. "Operability and scram time tests were performed and completed satisfactory at 1130 CDT. The fuel handling team was disbanded at 1137 CDT and the reactor was determined to be operational. At no point during this event was there any danger to the general public or Nuclear Science Center personnel." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | TX | NPR | [5 empty] | 0 | 2013-05-15
49032 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-05-14 23:23 | 2013-05-15 02:52 | 2013-05-15 | OFFSITE NOTIFICATION DUE TO LEAK FROM TURBINE BUILDING SUMP CONTAINING TRITIUM "Sample exceeding the industry groundwater protection initiative related to radioactivity in groundwater for which a news release is planned and notification to other government agencies will be made." "A leak greater than 100 gallons containing tritium has the potential to reach groundwater. The source has been identified. Actions to isolate this source are being initiated." The licensee has identified a leak in a fiberglass discharge pipe from the turbine building sump. The licensee estimates that greater than 100 gallons of water has been discharged through the leak at the present time. The licensee is in the process of installing a temporary sump pump in the turbine building sump in order to isolate the discharge path. Samples indicate a tritium concentration of 8.964 E-6 uCi/mL. The licensee will notify state and local government agencies. A press release is planned. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-15
49031 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-05-14 15:02 | 2013-05-14 18:37 | 2013-05-31 | PLANNED POWER OUTAGE AT TSC AND OSC "During Refueling Outage 21, at 1502 PDT on 5/14/13, power to the Technical Support Center (TSC) and Operations Support Center (OSC) was removed as part of transferring the facility to temporary power during a bus outage impacting the normal facility power supply. The TSC and OSC will be unavailable for use for several hours until temporary power has been established. "Established compensatory measures direct ERO members normally responding to either of the two impacted centers to respond to alternate locations. No other emergency response facilities are impacted by the bus outage. "This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The resident inspector has been notified. A follow up notification will be made when temporary power has been established and the facility is available for use." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SANDRA CHRISTIANSON TO PETE SNYDER AT 1637 EDT ON 5/15/13 * * * "This is a follow-up courtesy notification to EN# 49031. Temporary power has been established to the TSC and OSC, and both are available for emergency response. Normal power to TSC and OSC is expected to be restored on or about June 2, 2013 at 0600 PDT and will require a similar removal of power to the facility. A separate notification will be made when swapping off of temporary power." The licensee has notified the NRC Resident Inspector. Notified R4DO (Hay). * * * UPDATE AT 1735 EDT ON 5/31/2013 FROM SANDRA CHRISTIANSON TO MARK ABRAMOVITZ * * * "On 5/31/13, power to the Technical Support Center (TSC) and the Operations Support Center (OSC) was removed as part of transferring the facility from temporary power back to the normal facility power supply. The duration of the power outage will last approximately 90 minutes. The TSC and OSC are unavailable for use during this time for support of emergency response activities. Established compensatory measures direct Emergency Response Organization (ERO) members to respond to alternate locations. No other emergency response facilities are impacted. This event is being reported as a loss of emergency preparedness capabilities in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. A follow up notification will be made when normal power has been reestablished and the facility is available for use." Notified the R4DO (Azua). * * * UPDATE AT 2050 EDT ON 5/31/2013 FROM LISA WILLIAMS TO MARK ABRAMOVITZ * * * "At 1700 hours [PDT] on 5/31/13, normal power has been reestablished to the TSC and OSC, and both are available for emergency response. The licensee has notified the NRC Resident Inspector." The licensee notified the NRC Resident Inspector. Notified the R4DO (Azua). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-14
49030 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-05-14 10:44 | 2013-05-14 18:22 | 2013-05-14 | FAILED FITNESS-FOR-DUTY TEST A licensed operator had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2013-05-14
49029 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2013-05-14 12:15 | 2013-05-14 17:20 | 2013-05-14 | HIGH STEAM FLOW ISOLATION CAPABILITY IDENTIFIED AS NON-FUNCTIONAL "Emergency Cooling Loop 11 High Steam Flow Isolation capability not functional due to inadequate water level in differential pressure transmitter reference legs. "Emergency Cooling Loop 11 High Steam Flow transmitter for channel 11 alarmed due to gross failure at 0840 hours [EDT] on May 14, 2013. At 1154 hours channel 12 Emergency Cooling Loop 11 High Steam Flow transmitter experienced a gross failure. With both transmitters failed, the isolation capability of Emergency Condenser Loop 11 on high steam flow is not available. "At 1215 hours, a manual isolation of Emergency Cooling Loop 11 was initiated fulfilling the safety function. "Subsequent troubleshooting has revealed that the reference legs of the differential pressure transmitters for high steam flow were not filled properly. "This is an 8 hour notification per 10 CFR 50.72(b)(3)(v) for a condition could have prevented the mitigation of the consequences of an accident." The licensee notified the NRC Resident Inspector and will notify the State of New York. | 3 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-05-14
49028 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-14 09:07 | 2013-05-14 09:31 | 2013-05-14 | RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE The licensee is taking the spent fuel pool island radiation monitor out of service for pre-planned maintenance to change the air filter. The maintenance is expected to take approximately 5 minutes. The licensee notified the NRC Resident Inspector, state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-14
49027 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-05-13 10:10 | 2013-05-13 11:22 | 2013-05-17 | PLANNED OUTAGE OF SIRENS DUE TO SCHEDULED UPGRADES "Planned intermittent outages of all FCS sirens will occur the week of 5/13/13-5/17/13 due to scheduled upgrades to the radio system. Based on the planned maintenance, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) will be nonfunctional for various amounts of time. Prior notifications and coordination with Local Law Enforcement will be completed with compensatory measures established prior to work each day to support notification of the public in case of an actual emergency during the scheduled maintenance. Updates will be made to the NRC on 5/13/13 when the work starts, and upon completion of the work not to exceed 5/17/13. Work is currently scheduled to be complete 5/17/13. "Also, contingencies have been established to back out if required in support of the plant or Law Enforcement activities. "Work is scheduled to commence today, 5/13/13, at 10:10 AM. "This is being reported per 10CFR50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability.'" The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0915 EDT ON 5/17/2013 FROM LUKE JENSEN TO MARK ABRAMOVITZ * * * The work was completed on 5/16/2013 at 1700 CDT. The licensee notified the NRC Resident Inspector. Notified the R4DO (Walker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-13
49026 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-05-12 17:55 | 2013-05-12 21:58 | 2013-05-12 | SERVICE WATER EFFLUENT LINES NON FUNCTIONAL "At 1755 [CDT] on 05/12/13, R-16, Service Water System Effluent Line (Containment Fan Cooling) and R-20, Service Water System Effluent Line (Auxiliary Building Service Water Header) were declared NON-FUNCTIONAL due to low SW [Service Water] sampling flow. R-16 and R-20 are used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that exceeds the requirements of the Offsite Dose Calculation Manual for an Unusual Event and an Alert, and is therefore being reported under 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability." The Licensee is investigating to determine an appropriate recovery plan. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-12
49025 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-05-12 17:43 | 2013-05-12 19:15 | 2013-05-29 | UNUSUAL EVENT DUE TO FIRE ON AUXILIARY TRANSFORMER INSIDE PROTECTED THE AREA At 1743 CDT on 05/12/13, Grand Gulf Nuclear Station declared an Unusual Event due to a fire lasting greater than 15 minutes in an auxiliary transformer inside the Protected Area (PA). The transformer was isolated. The plant continues to operate at 100% power. The license remains in a Unusual Event pending further investigation. The licensee notified the NRC Resident Inspector and State and Local Authorities. Notified DHS SWO, FEMA, and DHS NICC. * * * UPDATE FROM ROBERT BRINKMAN TO JOHN SHOEMAKER AT 2112 EDT ON 5/12/13 * * * The Licensee terminated the Unusual Event at 1921 CDT on 5/12/13 based on electrically isolating the auxiliary transformer and termination of smoke coming from the transformer. At no time were flames seen during this event. The transformer is located outside of the turbine building and is used to supply various loads and office space during outages. There was no other impact on the plant. The licensee notified the NRC Resident Inspector and State and Local Authorities. Notified R4DO (Drake), NRR EO (Bahadur), IRD (Marshall), DHS SWO, FEMA, and DHS NICC. * * * RETRACTION FROM CHRISTOPHER ROBINSON TO JOHN SHOEMAKER AT 1057 EDT ON 5/29/13 * * * "EN #49025 documents an emergency declaration of Notification of Unusual Event due to a fire lasting greater than 15 minutes within the protected area. The basis for retraction is that this event did not meet the definition of FIRE in NEI 99-01 Rev 5, 'Methodology for the Development of Emergency Action Levels'. This document was endorsed by the NRC on February 22, 2008 (see ADAMS ascension # ML080450149) and is part of the Grand Gulf Nuclear Station's current licensing basis. Per the guidance, a FIRE is defined as: "Combustion characterized by heat and light. Sources of smoke such as slipping drive belts or overheated electrical equipment do not constitute FIRES. Observation of flame is preferred but is NOT required if large quantities of smoke and heat are observed. "Grand Gulf performed interviews of operators and personnel responding to the event and subsequently examined photos of the affected auxiliary transformer. According to eyewitness reports from personnel, flames were not observed at any time nor was there any light emanating from the source of smoke. Personnel also reported that at the immediate vicinity of the smoke source, heat was not at a level which would be indicative of a fire. Photos of the affected transformer did not show signs of charring, burns, warping, or deformation as would be expected during a FIRE. Additionally, the definition of a FIRE specifically excludes overheated electrical equipment." Notified R4DO (Azua), NRR EO (Chernoff), and IRD (Morris). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-05-12
49024 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-05-10 09:05 | 2013-05-10 18:08 | 2013-05-10 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR TESTING POSITIVE FOR ALCOHOL "A Non-licensed, Supervisory employee had a confirmed positive alcohol test during a random fitness-for-duty test. The employee's access to the Plant has been removed." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2013-05-10
49023 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-05-10 09:20 | 2013-05-10 15:56 | 2013-05-10 | FITNESS-FOR-DUTY REPORT INVOLVING DISCOVERY OF ALCOHOL CONTAINER INSIDE THE PROTECTED AREA "[The licensee] discovered a small bottle of alcohol within the Protected Area. The 50ml bottle was approximately 2/3 full. The seal ring had been broken. The clear liquid smells of alcohol as the label of the bottle indicates. The bottle was discovered beneath a deck structure to a temporary trailer that workers were demolishing. "This event is reportable under 10CFR26.719 Fitness-For-Duty." The license informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2013-05-10
49022 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-10 12:09 | 2013-05-10 15:56 | 2013-05-10 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED TESTING OF RADIATION MONITORS At 1209 EDT on 5/10/13, Stack Effluent radiation monitors RM8168 and RM8132 and Main Steam Line radiation monitors RM4299 A, B, and C were removed from service for planned testing. At 1458 EDT on 5/10/13, all radiation monitors were restored to service following completion of testing. The licensee has notified the NRC Resident Inspector and the State and Local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-10
49021 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-05-10 11:08 | 2013-05-10 12:42 | 2013-05-10 | UNIT 3 MANUAL REACTOR TRIP DUE TO MALFUNCTION OF TURBINE VALVES "This is a non-emergency event notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification). "On 5/10/13 [at 1108 EDT] Unit 3 was stabilizing at 25% [power] during a controlled shutdown from an initial power level of 38% [power]. Prior to the planned insertion of the trip at 25% [power], a malfunction of the turbine valves (not yet understood) caused a loss of load and a manual reactor trip was performed at 1108 [EDT]. Unit 3 is currently in Mode 3 [Hot Standby] and stable. Source Range Nuclear Instrument N-3-32 malfunctioned (loss of detector voltage). All other plant systems are working as designed." Unit 3 is stable in Mode 3 [Hot Standby] at normal operating temperature and pressure. All control rods fully inserted. All other Nuclear Instrumentation is operable. Decay heat removal is via main feedwater and atmospheric steam dumps however, the condenser steam dumps are available but not preferred for Tave control. There is no known primary to secondary leakage. Unit 3 is in a normal shutdown electrical lineup. The cause of the turbine valves malfunction is not known at this time. There is no impact on Unit 4. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-05-10
49020 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-05-10 06:12 | 2013-05-10 08:20 | 2013-05-10 | MANUAL REACTOR TRIP DUE TO HIGH TURBINE BEARING VIBRATION "On May 10, 2013 at 0612 hours [EDT], Unit 2 was manually tripped from 60% power due to increased vibrations and a report of arcing on bearing #9 of the main turbine. Unit 2 was in the process of increasing power following a refueling outage when this event occurred. The Operations crew entered the reactor trip procedure and stabilized Unit 2 in Mode 3 at normal operating temperature and pressure. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater system is reportable per 10CFR50.72(b)(3)(iv)(A) for a valid actuation of an ESF system. The Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 2 is in a normal shutdown electrical lineup." The #9 bearing is on the main generator exciter. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector and will be notifying local government agencies. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-05-10
49019 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-05-09 18:00 | 2013-05-10 00:19 | 2013-05-10 | INLET/OUTLET TURBIDITY FLOCCULATOR NOT RECORDING DATA "The following is a non-emergency notification in accordance with 10CFR50.72(b)(2)(xi) due to the notification requirement to other government agencies that will be made within 48 hours. "At 1800, May 9, 2013, the Columbia Generating Station main control room received notification that PWC-XR-1 had been found to be not recording data. A review of the stored data indicated that the data collection had been stopped since 5/2/2013 at 0934. The screen does show real time data, although that data is not being stored. Some of the data is recorded manually by chemistry technicians and operators during rounds that may be used for reporting purposes. "Automatic functions for high turbidity shutdown and low chlorine setpoints remain active when the data is not being stored. The data collected by PWC-XR-1 includes inlet and outlet flocculator turbidity, water temperature, flow rate and free residual chlorine. Washington Administrative Code, WAC, 246-290-664 outlines the requirements for monitoring filtered systems. WAC 246-290-480 section 2.a requires this failure to be reported as a failure to comply with monitoring requirements to the Washington Department of Health within 48 hours. "PWC-XR-1 data storage has been re-initiated and is working as expected." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-10
49018 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-05-09 | 2013-05-09 17:29 | 2013-05-13 | AGREEMENT STATE REPORT - REPORT OF MISSING GENERAL DEVICES The following is a list of missing general devices reported by the State of Colorado, missing between 1998-2011, via email. The following table details the type and number of devices that the State previously neglected to report: Type of Device Number Reported as Missing 1998-2011 - Exit Signs 1096 - Calibration 7 - Dust Monitor 1 - Electron Capture Detector 13 - Gas Chromatograph 6 - Standard Reference Materials 1 - Gauge 2 - Static Eliminator 44 - Unknown 1 - X-Ray Florescence 14 The State does not believe these devices represent a risk to human health or the environment and has taken steps to improve the general licensing registration program to ensure accurate reporting in the future. See EN #48609 for a list of missing general devices in 2012. * * * UPDATE FROM J. OPILA TO V. KLCO ON 5/13/2013 AT 1634 EDT * * * The following information was excerpted from a received facsimile: The State of Colorado checked with the general licensee and there was a report error. A Pepsi Bottling Group LLC source (Am-241; 100 mCi) was never missing and still is in the possession of the licensee. Notified the R4DO (Hay), ILTAB and FSME Resources via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-05-17
49017 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-03-11 00:43 | 2013-05-09 16:10 | 2013-05-09 | INVALID ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM "This 60-day telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation of the Unit 3 Auxiliary Feedwater (AFW) System reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). "On March 11,2013 at approximately 0043 [EDT], while starting the 3B Steam Generator Feed Pump (SGFP) for a one minute run, both trains of AFW started. Operators then manually closed the AFW flow control valves. AFW Trains 2 and 1 were restored to operable standby status at approximately 0112 [EDT] and 0117 [EDT], respectively. "AFW actuation occurred because of a misunderstood procedure step and unnecessarily placed jumpers in AFW actuation logic in preparation for start of the 3B SGFP, which resulted in the invalid signal. At the time, the level in the steam generators was being maintained by the 3A Standby Steam Generator Feed Pump (SBSGFP). "Because no actual loss of normal feedwater condition existed (with the 3A SBSGFP in service) which required AFW to start, and the start was not in response to actual plant conditions satisfying the requirements for actuation, this event is an invalid actuation." The licensee will notify the NRC Resident Inspector. | 3 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-05-09
49016 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-05-09 | 2013-05-09 14:18 | 2013-05-30 | AGREEMENT STATE REPORT - LOST IONIZING STATIC DISSIPATER The licensee reported to the state that a ionizing static dissipater, licensed under a General License [GL] and used on lines for clearing small parts of dust, was lost. The device is Model: NRD P-2021-8101 with Serial Number: A2HN439 and contained a Po-210 with an up to a 10 mCi source, on 1/18/12, which has decayed to approximately 0.9 mCi as of 5/9/13. The licensee has properly returned all other devices for destruction from the facility. The State has initiated an investigation and will assign an event number as new information is obtained. * * * UPDATE ON 5/30/2013 AT 1430 EDT FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * The following update was received via e-mail: "The agency [Massachusetts Radiation Control Program] conducted a site visit on 5/29/13. The general licensee implemented a search through facilities and determined the missing device may have been inadvertently dispositioned during recent building renovations and subsequent departmental reorganizations and relocations. The missing device was last used in 2012. The general licensee is seeking to terminate GL registration due to GL devices having been phased out and replaced with non-RAM [radioactive material] equipment. All other GL devices were accounted for and have already been dispositioned. The missing device component is a small metallic cylindrical object 0.5 inches in diameter and 2.7 inches in length. "The agency considers this event to be CLOSED." Massachusetts Event Docket #17-0766 NMED Item #130233 Notified the R1DO (Holody) and FSME Event Resources (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-05-17
49015 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-05-08 15:40 | 2013-05-09 09:36 | 2013-05-09 | UNPLANNED MEDICAL TREATMENT OF CONTAMINATED INDIVIDUAL "An employee reported to the dispensary yesterday afternoon with a potential knee injury at approximately 1540 CDT. The plant nurse administered first aid and decided to send the employee home. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination was present on his right boot, 17,936 dpm/100 cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was re-surveyed. The employee was free of contamination upon release." The licensee notified NRC R2 (Richard Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-05-09
49014 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-05-09 05:09 | 2013-05-09 07:18 | 2013-05-09 | REACTOR COOLANT PRESSURE BOUNDARY LEAKAGE "During Callaway refueling outage 19 on 5/8/13 at approximately 1900 hour CDT, water was observed dripping from piping insulation in the overhead by RCS loop 4. Further investigation determined it was near Safety Injection (EP) vent valve EPV0109. A scaffold was built and insulation was removed to perform an inspection. At approximately 0509 hours CDT on 5/9/13, engineering inspected the piping and determined there was a crack in the socket weld where 3/4 inch vent valve EPV0109 is connected to the 'B' train injection piping to RCS loop 4 Cold Leg. The estimated leakage rate through the crack is 6 (six) drops per minute. The configuration of this vent valve is a 3/8 inch flow restrictor socket welded to the six inch piping and a 3/4 inch vent valve socket welded to the flow restrictor. The crack is in the socket weld between the ASME code class 1 flow restrictor socket and the ASME code class 2 vent piping. "Callaway plant was in mode 6 with refueling pool level greater than 23 feet above the reactor vessel flange at the time of the discovery. The 'A' RHR train which discharges to RCS loops 1 and 3 Cold Legs is the currently operable RHR train. 'B' RHR train was declared inoperable when the weld crack was identified. Only one RHR train is required to be operable at the present plant Mode of applicability. Repair plans are being developed. "Basis for Reportability: This condition constitutes abnormal degradation of a principle safety barrier due to unacceptable welding defects within the primary coolant system." There is a check valve between this leak and the reactor coolant system. Therefore, this is considered unisolable and pressure boundary leakage. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-05-09
49013 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-05-08 17:00 | 2013-05-09 00:51 | 2013-05-09 | MAIN ANNUNCIATOR SYSTEM INOPERABLE DUE TO MAINTENANCE "On May 8, 2013 at 1700 hours with the reactor in a Cold Shutdown condition and the Reactor Mode Select Switch in Refuel, the main control room annunciator system became inoperable during a preplanned activity to repair the associated 120VAC/125 VDC instrument power supply transfer switching scheme. The reactor cavity is flooded, the fuel pool gates are removed, shutdown cooling is in service and reactor vessel reassembly activities are in progress. The appropriate abnormal procedure was entered and compensatory actions including periodic monitoring of bus voltages and field annunciator panels were implemented for systems in service at the time of the loss. Station risk is green and all key safety functions are green. Troubleshooting is in progress however, return to service time has not been determined. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). The USNRC Resident Inspector has been notified. This event has no impact on the health and safety of the public." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-09
49012 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-05-08 21:47 | 2013-05-09 00:09 | 2013-05-09 | AUTOMATIC REACTOR TRIP The reactor automatically tripped at 2147 EDT. All control rods fully inserted on the trip and all systems responded as expected. Decay heat removal is to the main condenser. The plant is in its normal shutdown electrical lineup. The licensee is investigating the cause of the reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-05-09
49011 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-05-08 10:00 | 2013-05-08 17:03 | 2013-05-09 | AGREEMENT STATE REPORT - POTENTIALLY LOST RADIOACTIVE SOURCE SHIPMENT Two, Category 2, IR-192 industrial radiography sources, loaded in a QSA Global model 650L source changer, left Wilmington, MA at 1416 EDT, 5/6/13 headed for Norfolk Naval Shipyard, Norfolk, VA. The source changer was expected to be delivered early the morning of 5/8/13. Norfolk Naval Shipyards notified QSA Global when the source changer did not arrive as scheduled. The transportation company was then notified. The transportation company began searches of its facilities in Newark, NJ and Boston, MA for the source changer. The last known shipping scan of the source changer was at 2342 EDT, 5/6/13 in Newark, NJ. The source changer is a metal container measuring 8 1/4 inches x 10 inches x 13 inches that weighs approximately weighs 90 lbs. The transportation company is continuing to search for the source changer. * * * UPDATE FROM CHARLES ELLARS (QSA Global) TO CHARLES TEAL ON 5/9/13 AT 0902 EDT * * * The sources were found in the Newark, NJ facility and the shipment is expected to arrive at Norfolk Naval Shipyard on 5/10/13. Notified R1DO (Dwyer), R2DO (Ayers), R3DO (Peterson), R4DO (Vasquez), IRD (Marshall), ILTAB (Whitney), FSME (McDermott), FSME Event Resources via email, DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA and Nuclear SSA via email. * * * UPDATE FROM KENATH TRAEGDE (MA STATE) TO JOHN SHOEMAKER ON 5/9/13 AT 1444 EDT * * * The state was notified, by QSA Global, at 0825 EDT on 5/9/13 that the source was found at 0450 EDT on 5/9/13. The state will submit a follow-up report. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-05-16
49010 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-05-08 06:23 | 2013-05-08 09:41 | 2013-05-08 | EMERGENCY SIREN SPURIOUS ACTUATION "On 5/8/2013 at 0623 (CDT) MNGP was informed by Wright County Sheriffs Department of a spurious actuation of one emergency response siren in Wright County (for about 2 seconds). This activation was confirmed by vendor system monitoring. The source of the activation has not been determined. At this time all aspects of the public notification system are functional." The licensee notified the NRC Resident Inspector and will notify the state and local governments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-05-08
49009 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2013-05-06 | 2013-05-07 15:05 | 2013-05-17 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following information was received via E-mail: "Licensee reported a stuck radiography source that occurred at approximately 2315 CDT on May 6, 2013. Licensee's RSO [Radiation Safety Officer] responded to incident site, increased barricades, maintained perimeter, and notified Chevron RSO. Licensee's source was fully retracted into the shielded position at 0100 CDT [on May 7, 2013]. The Licensee's RSO received 20 mR conducting the source retrieval." The incident occurred while performing work at the Chevron Pascagoula Refinery. Mississippi Report Number: MS-13002 * * * UPDATE RECEIVED FROM JAYSON MOAK TO JOHN SHOEMAKER ON 5/17/13 AT 1250 EDT * * * The following report was received via e-mail: "On 5/6/2013, the Licensee had a two man crew performing industrial radiography at the Chevron Plant. The radiographer was unable to crank the source back into the camera after his third exposure. The source was then cranked back into the collimator. The radiographer repositioned the cranks and tried to retract the source again without success. The radiographer and assistant radiographer extended the restricted area boundary and called the Licensee's night safety officer on site. The Licensee's RSO then notified Mistras Group's CRSO [Corporate Radiation Safety Officer] and plant personnel of the incident. "The Licensee's RSO, once on site, discovered from conversation with the radiographer that the drive cable was hitting a melted area of the conduit and not letting the drive cable pass through. The melting of the (black) return conduit of the cranks occurred because it was placed over a non-insulated pipe from the plant's furnace. The Licensee's RSO made the decision to cut the conduit at the melted area of the cranks to save time and reduce exposure while trying to retract the source. This provided clearance for the drive cable to pass through and allowed the source to retract back into the fully shielded position inside the camera. The camera, guide tube, and cranks were surveyed by the RSO upon source retraction." The State (Mississippi) has closed this case. Notified the R4DO (Walker) and FSME Events Resources via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2013-05-15
49008 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-05-06 17:33 | 2013-05-06 20:16 | 2013-05-06 | TECHNICAL SPECIFICATION SHUTDOWN REQUIRED DUE TO NON-FUNCTIONAL CLASS 1E AIR CONDITIONING UNIT "Class 1E Air Conditioning Unit SGK05A cools safety related electrical Train 'A' and was declared non-functional at 1733 hours. As a result, the following safety related electrical equipment was declared inoperable: 4.16 KV Bus NB01; 480 volt buses NG01 and NG03; 120 volt Instrument AC inverters and buses NN11, NN13, NN01 and NN03; 125 VDC chargers and buses NK11, NK13, NK01 and NK03. T/S 3.0.3 was entered at 1733 from T/S 3.8.7 due to two out of four 120 volt AC inverters (NN11 and NN13) being inoperable. Plant shutdown to Mode 5 commenced at 1801 hours. "All electrical systems listed above remain functional but are declared inoperable due to inadequate room cooling capability." The licensee plans on performing a controlled plant shutdown using normal rod insertion following approved plant procedures. Per the licensee, Mode 3 conditions must be met by 0033 CDT 5/7/2013 and Mode 5 conditions must be met by 0033 CDT 5/8/2013. The licensee notified the NRC Resident Inspector. | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-05-06
49007 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-05-06 08:00 | 2013-05-06 18:07 | 2013-05-06 | AGREEMENT STATE REPORT - SOURCE SHIPMENT DID NOT ARRIVE AS EXPECTED "QSA Global reported a lost source. The location of the source is not known. The shipment contains Ir-192." QSA expected this source to arrive at their Baton Rouge, LA location at about 0800 CDT on 5/6/13. QSA contacted the common carrier to locate the item at some time after that. The last known location was Memphis, TN. * * * UPDATE FROM MIKE FULLER (QSA) TO PETE SNYDER AT 1915 ON 5/6/13 * * * At about 1915 EDT, QSA personnel learned from the common carrier that the item had been located at the Memphis, TN shipping location. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-05-14
49006 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2013-05-03 | 2013-05-06 16:12 | 2013-05-08 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The following information was received via E-mail: "After conducting a recent inventory, the licensee called in to report that one of their portable radiation gauges was missing and/or stolen. Specifically, a Troxler gauge, model 3430, serial number 27283 cannot be currently accounted for." The Georgia Radioactive Materials Program will update this event when more information is available. Georgia Incident Summary: GA-CTS-07990 * * * UPDATE FROM ERIC JAMESON TO DONALD NORWOOD AT 1532 ON 5/7/2013 * * * The following report was received via e-mail: "The licensee reports that the gauge's last recorded use was on 4/24/2013. The licensee made the report of the lost or stolen gauge to both the Department [Georgia Radioactive Materials Program] and local law enforcement on 5/2/2013. The licensee also stated the gauge has a sticker on it indicating a reward if found and returned." Notified R1DO (Dwyer) and FSME Events Resource. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2013-05-14
49005 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-04-19 | 2013-05-06 14:37 | 2013-05-06 | AGREEMENT STATE REPORT - FOUND ORPHAN RADIUM SOURCES The following information was received via E-mail: "On 4/19/13 the [Ohio] Bureau of Radiation Protection (BRP) received a call from the RSO of broad-scope licensee Ohio State University (OSU). The RSO stated that he had received a call from a woman who had been helping an elderly neighbor clean out a garage after her husband's death. The husband had been a college professor. The woman and widow had discovered a large, five-gallon can filled with what appeared to be lead. The widow indicated that she believed it contained radium needles. "On 4/21/13 the woman contacted BRP to arrange pickup of the device and deliver it to OSU. OSU has volunteered to store the device pending disposal. On 4/22/13, three BRP inspectors went to the home to perform radiological surveys of the container. Wipes were taken of the outside and a field scan of the wipes identified no removable contamination. The maximum dose rate reading at contact was 1.7 mrem/hr. The inspectors were unable to verify that the material was radium. The device was loaded into the BRP truck and transferred to the OSU Radiation Safety Office and placed in a secure radioactive material storage area. "On 4/23/13, BRP contacted the US-EPA to request assistance in identification and disposal of the container and material, assuming it to contain one or more radium needle orphan source(s). BRP is also contacting the CRCPD [Conference of Radiation Control Program Directors] for assistance in disposal. "On 5/2/13 BRP inspectors visited the widow's home, at her request, to ensure there were no other similar containers or materials present. The inspectors discovered a second container that was identified as containing radium. This container was also taken to OSU and placed in a secure radioactive material storage area. US-EPA was contacted about this second device for inclusion in their investigation. "BRP is currently working to obtain more information on the origin of the radioactive materials. No further information is available as of this date (5/6/13)." BRP indicated that the 'containers' appear to be homemade lead pigs. The second container has a maximum dose rate reading of 2.5 mrem/hr at contact. Gamma spectroscopy analysis of the second container, along with a partial label found, indicate that the contents may be Radium-226. Ohio Item Number: OH130013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2013-05-14
49004 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-05-06 10:16 | 2013-05-06 13:34 | 2013-05-06 | ONE OF TWO NATIONAL WEATHER SERVICE TONE ALERT RADIOS OUT OF SERVICE "At 10:16 AM EDT on May 6, 2013, the National Weather Service (NWS-NOAA) reported a loss of the [NWS-NOAA] Tone Alert Radio Transmitter, WXL-58 located in Chapel Hill, North Carolina, which serves the Northeast Piedmont on 162.550 MHZ. The NWS-NOAA does not have an expected return to service time. The NWS-NOAA Tone Alert Radio Transmitters are in place to provide a redundant means to alert residents within five miles to an emergency at the plant. Eighty-three Alert and Notification System (ANS) sirens are located throughout the ten mile radius of the plant. The ANS sirens have the same function as the Tone Alert Radios, but extend out to ten miles. "All ANS sirens are currently in service and fully functional. Therefore, there is a means to alert the public within the 10 mile radius of the plant if an actual emergency were to occur. There is no impact to public health and safety due to this condition. "The NRC Resident Inspector has been notified." This report was also made per a requirement of licensee procedure PLP-201. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-06
49003 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-05-05 19:15 | 2013-05-05 22:36 | 2013-05-05 | BOMB THREAT MADE TO FACILITY Bomb threat made to the facility. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2013-05-13
49002 | 0 | PALISADES | 1 |  |  | [1] CE | 2013-05-05 01:12 | 2013-05-05 01:45 | 2013-05-05 | TECHNICAL SPECIFICATION SHUTDOWN - SAFETY INJECTION REFUELING WATER TANK DECLARED INOPERABLE DUE TO LEAK "At 0112 EDT on May 5, 2013, the plant commenced a shutdown due to water leakage from the SIRW (Safety Injection Refueling Water) Tank exceeding the operational decision-making issue process trigger point of 34 gallons per day, causing it [the SIRW] to be declared inoperable and requiring entry into Technical Specification LCO 3.5.4 Condition B. LCO 3.5.4 Condition B requires the SIRW Tank to be returned to Operable status within one hour or entry into Condition C which requires the plant to be in Mode 3 within 6 hours and Mode 5 within 36 hours. "This event had no impact on the health and / or safety of the public. "The NRC Resident has been notified. "The exact location of the leakage has not been determined at this time. The Plant will be taken to Mode 5." The licensee has been operating with SIRW leakage at a rate of less than 34 gallons per day. The leakage has increased for unknown reasons to a calculated value of approximately 90 gallons per day. See EN #48018 dated 06/12/12 for similar report on a technical specification shutdown for the SIRW tank leakage. | 88 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-05-05
49001 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2013-05-03 | 2013-05-03 16:49 | 2013-05-03 | PART 21 REPORT - FUEL INJECTORS FAILED PRESSURE TEST The following is a summary of information received via fax: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 02/19/13 upon pressure leakage testing of three (3) fuel injectors, part number 40084720 (s/n 11K23136, 12K20318 & 12K20385), that were returned by TVA-Browns Ferry because they failed a pressure test at the site prior to installation in the engine. Another fuel injector was later returned by TVA (s/n 12K20330) for the same reason. On 3/11/13, ESI received a fuel injector (s/n 12H23003) from First Energy-Davis Besse because the injector failed their on-site pressure leakage test. The pressure test specifies applying 2000 psi to the fuel injector and verifying the pressure does not fall below 1500 psi after 30 seconds. "TVA has been working with ESI to evaluate the reported deviation. ESI has also been working with EMD and EMD's fuel injector supplier to determine the cause of the injector leakage. All parties involved were not able to complete the deviation evaluation within the 60 day time period specified in 10CFR Part 21; therefore, TVA issued an interim report to the NRC about this issue on March 22, 2013 [NRC EN No. 48844]. This report is a follow-up to TVA's interim report. "This evaluation was concluded on 05/02/13 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. The fuel injector pressure leakage has been attributed to debris that entered the injectors during assembly of the filter elements into the injector body at the manufacturer. A leaking or otherwise improperly functioning fuel injector could affect the load carrying capability of the diesel engine. Fuel dilution of the engine lubricating oil could also occur as a result of a leaking fuel injector. Either of these conditions could impact the operability of the diesel engine and thereby prevent the diesel generator from performing its safety related function." The following licensees may potentially be affected: FP&L-St. Lucie, Energy Northwest-Columbia, Nextera-Point Beach, Exelon-Dresden, TVA-Browns Ferry, First Energy-Davis Besse, Dominion Va. Power-Surry, Entergy-ANO, and First Energy-Beaver Valley. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-05-03
49000 | 0 | VALLEY QUARRIES, INC. |  |  |  |  | 2013-05-03 | 2013-05-03 17:03 | 2013-05-15 | LOST TROXLER MOISTURE DENSITY GAUGE The licensee from Chambersburg, PA, was doing work in West Virginia under a reciprocity agreement. The authorized user was conducting a reading when he was asked by his supervisor to pick-up a fellow employee at the construction yard approximately 1.5 miles from the reading site. After the reading was done, the user placed the gauge in the back of his pickup truck and proceeded to the construction yard. Once he arrived at the yard, he saw that his truck tailgate was down and the gauge was missing. The gauge was not in its shipping container. The user and his co-worker doubled back in search of the gauge but did not find it. When the RSO arrived, another employee told him that he saw someone stopping along the highway to pick up what appeared to be the gauge and then driving off. At that time, the employee was unaware a gauge was missing so he didn't pay much attention to the vehicle. The gauge is identified as a Troxler Electronics Laboratories Model # 3430, Serial # 32506. It contains 8 mCi of Cs-137 and 40 mCi of Am-241. The RSO notified the West Virginia State Police, the local newspaper and the regional television station. The licensee is considering offering a reward for the return of the gauge. * * * UPDATE AT 2244 EDT ON 5/15/13 FROM THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION TO SNYDER * * * The gauge has been recovered and is now in the possession of the licensee. Notified R1DO (Schroeder), ILTAB (Hahn), and FSME Events Resource (E-Mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-05-13
48999 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-02-20 | 2013-05-03 13:54 | 2013-05-03 | AGREEMENT STATE REPORT - FETAL EXPOSURE TO IODINE-131 The following information was obtained from the State of California via email: "A female patient was treated with 176.9 mCi of Iodine 131 on 2/20/13. A serum pregnancy test conducted on 2/18/13 came back negative. On 4/22/13, Radiological Associates received a phone call from the patient's endocrinologist informing them that the patient was pregnant. An ultrasound evaluation of the patient performed on 3/18/13 determined that the fetus would have been approximately two weeks old at the time of the Iodine 131 dose administration. The dose to the fetus was determined to be 47 rad, which may meet the requirement for an abnormal occurrence." "The [California Radiologic Health Branch] will be reviewing this event." California Event: 5010-050313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-05-13
48998 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2013-05-03 | 2013-05-03 10:50 | 2013-06-17 | PART 21 REPORT - INSUFFICIENT PROCESS CONTROL ON PUMP IMPELLER The following is a summary of information received via fax: "In January 2013, Curtiss-Wright Electro Mechanical Corporation completed final testing on AP1000 Reactor Coolant Pump (RCP) Serial Number 9, part number 6D70795G05, Revision 8, which contained a sand cast impeller (S/N 3021) cast by Wollaston Alloys of Braintree, MA. When it was disassembled for inspection it was discovered that a piece of an impeller blade approximately 3 inches by 2 1/2 inches had separated from the main impeller casting. The separated piece was the leading edge of one blade, and it was subsequently recovered intact from the pump test loop. "This incident was investigated as a significant condition adverse to quality with the potential to create a substantial safety hazard; but, was deemed not a reportable incident since all cast impellers were either: 1) in CW-EMD control, or 2) exported to customers in the People's Republic of China. "Our customers (Westinghouse Electric Company and the Chinese customers and regulatory authorities) were kept informed as the investigation progressed and root cause was identified. "The physical cause of the failure is most likely due to a flaw present in both the cast material and weld overlay applied to the impeller blade. The original flaw was most likely a consequence of tensile overload failure due to cooling stresses introduced by the welding process. Subsequent weld repairs were insufficient in remediating the original flaw, which went undetected by NDT methods. Ultimately, AP1000 RCP Serial Number 3021 failed by high cycle fatigue followed by ductile failure. "As a result of the above investigation, CW-EMD is concerned that the identified lack of process control at Wollaston Alloys, Inc., could result in other significant conditions adverse to quality with the potential to create a substantial safety hazard. "Because of the nature of the issue, CW-EMD is unable to complete a full extent of condition investigation, and is reporting this issue to the Commission to ensure full awareness within the industry. "Name and address of the individual or individuals informing the Commission: James A. Drake, General Manager Curtiss-Wright Electro-Mechanical Corporation 1000 Wright Way Cheswick, Pa 15024" * * * UPDATE FROM STEVE GRIEF TO JOHN SHOEMAKER ON 5/17/13 AT 1549 EDT * * * Subject: Report of Potential Substantial Safety Hazard in accordance with Title 10 Code of Federal Regulations, Part 21. Wollaston Alloys is submitting this interim report as a result of product concerns discovered by Curtiss Wright EMD during the investigation of an impeller blade failure occurring during testing as noted in Curtiss Wright EMD's notification to the NRC dated May 3, 2013. Wollaston is requesting an additional 30 days to identify any current or previous orders where 10 CFR 21 is invoked and to determine if there is evidence that a condition exists that could create a substantial safety hazard. Notified R1DO (Schroeder), R2DO (Bartley), R3DO (Riemer), R4DO (Walker), and Part 21 Reactors via email. * * * UPDATE FROM STEPHEN GRIEF TO PETE SNYDER ON 6/17/13 AT 1752 EDT * * * Subject: Report of Potential Substantial Safety Hazard in accordance with Title 10 Code of Federal Regulations, Part 21. "Wollaston Alloys, Inc. is submitting this report as an update to the interim report submitted on May 17, 2013 resulting from product concerns identified by Curtiss Wright EMD during the investigation of an impeller blade failure as noted in Curtiss Wright EMD's notification to the Nuclear Regulatory Commission (NRC), dated May 3, 2013. This investigation did not include the Curtiss Wright impeller failure since it is not considered a reportable incident, but addresses the identified concerns with regards to other products supplied to domestic users. The previously submitted interim report requested an additional 30 days to identify basic components supplied under the requirements of 10 CFR Part 21 and to determine if there is evidence that a defect or failure to comply exists. "Name and address of the individual or individuals informing the Commission: Stephen M. Grief, Quality Manager Wollaston Alloys, Inc. 205 Wood Road Braintree, MA 02184" The complete report has been summarized as follows: Wollaston Alloys, Inc. determined the cases in which Wollaston Alloys, Inc. supplied components to which the requirements of 10 CFR Part 21 applied. After a review of all records pertaining to those purchase orders, Wollaston Alloys, Inc. found no evidence of a defect or failure to comply. Notified R1DO (Rogge), R2DO (Ehrhardt), R3DO (Daley), R4DO (Walker), and Part 21 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [10 empty] | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-05-03
48997 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-05-03 05:42 | 2013-05-03 10:39 | 2013-05-03 | LOSS OF MAIN CONTROL ROOM ANNUNCIATORS DURING PLANNED SPDS MAINTENANCE "On May 3, 2013 at 0542 [EDT] hours with the reactor in Cold Shutdown and Reactor Mode Switch in Refuel, the Safety Parameter Display System (SPDS) was removed from service as part of a preplanned activity in order to repair the associated 120VAC instrument power supply transfer switching scheme. The reactor cavity is flooded the fuel pool gates are removed and refueling activities are in progress. Station risk is green and all key safety functions are green as well. It is anticipated the repair will be completed in approximately ten hours. "Following the planned de-energization, it was determined that an apparent equipment failure resulted in the loss of main control room annunciator system. The appropriate abnormal procedure was entered and compensatory actions including periodic monitoring of bus voltages and field annunciator panels implemented for systems in service at the time of the loss. The annunciator system was restored on May 3, 2013 at 0640 hours. "This USNRC Senior Resident Inspector has been notified. "This event has no impact on the health and safety of the public." The licensee will notify the Commonwealth of Massachusetts. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-03
48996 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2013-05-03 | 2013-05-03 09:25 | 2013-06-17 | INTERIM PART 21 REPORT OF POTENTIAL DEFECT IN A RELIEF VALVE BELLOWS The following was excerpted from a fax: (ii) Identification of the basic component supplied for such facility or such activity within the United States which may fail to comply or contains a potential defect. Target Rock P/N: 303480-1, Bellows, Manufactured by Target Rock. (iii) Identification of the firm supplying the basic component which fails to comply or contains a defect. Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation 1966E Broadhollow Road East Farmingdale, NY 11735 (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. During as-found steam testing on March 5, 2013 of a Pilgrim Main Steam Safety Relief Valve (MS-SRV) (TR Model 09J-001, valve assembly S/N 5, pilot assembly S/N 23, bellows PIN 303480-1 S/N 607) a loud pop was heard and as-found testing was secured. Subsequently, the pilot assembly was removed from the valve assembly and subjected to a leak test and would not hold pressure. The pilot assembly was disassembled and a visual inspection of the P/N 303480-1 bellows convolutions revealed a through wall failure in one of the convolutions. It is noted the steam testing was performed at an offsite test facility and the valve did not fail installed in the plant. The bellows acts as a pressure sensor responsible for initiating the opening of the MS-SRV at set pressure. Failure of the bellows does not directly impact the integrity of the Reactor Coolant System (RCS) pressure boundary, which is maintained by the bonnet assembly that surrounds it, but does impair the ability of the MS-SRV to provide over-pressure protection of the RCS. This technology has an extensive history of reliability in nuclear power systems and has been used in Commercial Nuclear Power Plants (NPPs) since the 1970s. This is the first reported incident regarding a thru wall bellows failure. Target Rock initiated a comprehensive root cause evaluation pursuing several areas of investigation. In parallel, Entergy is conducting an independent investigation and we are cooperating with them. A complete review of our paperwork confirms all manufacturing procedures and processes were performed in accordance with all specified requirements. This includes: - Raw material analysis - Dimensional inspections - Cleaning - Heat Treatment - Manufacturing processes - Testing - Review of design stresses Preliminary metallurgical analysis of the failed bellows indicates cracks forming in an inter-granular manner as would be expected from Inter Granular Stress Corrosion Cracks (IGSCC) originating at pit like location on the interior pressurized surface. The source of this cracking is the focus of on going investigations. Target Rock has also visually inspected two other bellows of the same part number, one manufactured from the same material lot and another manufactured from an earlier material lot. Both of these bellows were installed in valves steam tested at Target Rock. One of these valves bellows was also full flow tested at Wyle Labs. Neither of these additional bellows contained pit-like locations and may indicate this potential failure mechanism is an isolated incident. However, to date, neither Target Rock nor Pilgrim can draw final conclusions with the information collected and analyzed. The mode of failure has not been determined; however, in order to address the potential for a common mode failure, Target Rock is continuing metallurgical testing of the failed bellows and the two other bellows with the same part number. Based on these results, it is likely we will need to evaluate bellows that have been installed in other NPP as they become available. (v) The date on which the information of such defect or failure to comply was obtained. The as-found steam test and identification of the potential defect occurred on March 5, 2013. (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. The following plants are running with bellows P/N 303480-1 installed: Limerick 1 & 2, Pilgrim, and J.A. Fitzpatrick. (vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. The root cause of the potential defect is not yet known as of the date of this report. Therefore, no specific corrective actions have been initiated. Target Rock Corrective Action Request CAR 13-013 will document the corrective actions when they are determined. This determination will be based on further mechanical and material evaluations. TR anticipates completing these evaluations within 45 days; however, in the event the evaluations are not completed, TR will forward another interim report within 45 days. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. Target Rock will recommend that the end user perform a detailed visual inspection of the interior convolutions of installed bellows P/N 303480-1 at the next opportunity to determine if any areas of pitting or cracking exist on the interior walls of the bellows. This is a difficult inspection to perform due to the following: internal geometry of the convolutions, a trained inspector is required and specific inspection technology is needed to yield reliable results. * * * UPDATE FROM JOHN DEBONIS TO HOWIE CROUCH VIA EMAIL AT 1109 EDT ON 6/17/13 * * * The following are excerpts from an email sent by Target Rock, a business unit of Curtiss-Wright Flow Control Corporation: Our [Target Rock] investigation indicates the bellows failed due to in-situ hydrogen embrittlement and this hydrogen embrittlement may have been promoted by inadequate cleaning of the bellows. The inadequate cleaning may have induced formation of surface pits during heat treatment providing for localized concentration of hydrogen. Based on these results, we [Target Rock] are notifying end users with the P/N 303480-1 bellows in service (listed below) to perform field inspections at the next available opportunity. Note, the ASME Code requires these valves to be as-found tested at a maximum 5-year interval. A procedure to inspect the bellows will be forwarded to the applicable plants in parallel with this notification. In addition to this inspection Target Rock recommends, as a preventive measure, the P/N 303480-1 bellows be replaced with a P/N 300083-1 or -3 bellows, as applicable, to negate the effects of hydrogen embrittlement. Finite element analysis of the P/N 300083-1 or -3 bellows shows significantly lower stresses at plant operating conditions. The lower stress levels provide an incremental increase in safety margin so that hydrogen embrittlement need not be considered a significant degradation mechanism. Target Rock is implementing corrective actions to improve in-process cleaning and inspection, with emphasis on cleaning prior to heat treatment, to address this root cause. The corrective actions will be completed within 60 days of this letter. Should you have any questions regarding this matter, please contact Steven Pauly, Vice President Energy Products at (631) 293-3800, ext. 4640. Limerick 1 & 2 has 28, Pilgrim has 4, and FitzPatrick has 3 of these items. Notified NRR Part 21 Group (email), R1DO (Rogge) and R3DO (Daley) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-05-03
48995 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-05-03 01:11 | 2013-05-03 07:54 | 2013-05-03 | TEMPORARY LOSS OF BOTH TRAINS OF EMERGENCY GAS TREATMENT SYSTEM "On May 3, 2013, at 0111 [EDT], Technical Specification Limiting Condition of Operation (TS LCO) 3.0.3 was entered due to the loss of both trains of Emergency Gas Treatment System (EGTS). The Train B EGTS had been removed from service for scheduled maintenance and at 0111 the Train A auxiliary air dryer stopped functioning. On May 3, 2013, at 0155, Train B EGTS was restored to service and declared Operable, and TS LCO 3.0.3 was exited. "The auxiliary air system is required to support multiple safety related systems. The auxiliary air system is the safety grade air supply for EGTS. As Train A auxiliary air was no longer Operable, and the B train EGTS system was inoperable, the safety function supported by EGTS was not available. The EGTS establishes a negative pressure in the annulus between the shield building and the steel containment vessel. Filters in the system then control the release of radioactive contaminants to the environment. "Watts Bar Unit 1 remained in Mode 1 at 100% power. No reactivity was added to the plant. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) and (D) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-05-03
48994 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-05-03 05:20 | 2013-05-03 06:20 | 2013-05-03 | OUTAGE OF FT. CALHOUN STATION SIRENS FOR PLANNED MAINTENANCE "A planned outage of all FCS [Ft. Calhoun Station] sirens will occur today at 0530 CDT to transfer in-service zone controllers. During the planned maintenance, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) are nonfunctional. Prior notifications and coordination with Local Law Enforcement have been completed with compensatory measures established to support notification of the public in case of an actual emergency during the scheduled maintenance." The licensee has notified the NRC Resident Inspector, Washington, Harrison, and Pottawattamie counties. * * * UPDATE FROM SCOTT MOECK TO CHARLES TEAL ON 5/3/13 AT 0641 EDT * * * "The maintenance has been completed and the EPZ sirens have been returned to service. Local Law Enforcement has been notified that the scheduled maintenance is complete and the primary method of alerting the public with sirens is restored." The licensee has notified the NRC Resident Inspector. Notified R4DO (Haire). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-03
48993 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-05-02 22:07 | 2013-05-02 23:56 | 2013-05-03 | RADIATION MONITORS TAKEN OUT OF SERVICE FOR PRE-PLANNED RADIOGRAPHY Main Steam Line radiation monitors, MSS-RE75, RE76, RE77, RE78 and Terry Turbine Radiation monitor MSS-RE79 have been taken out of service for pre-planned radiography and plant conditions. This results in a loss of assessment capability since the radiation monitors are used for EAL classification. The radiation monitors will be restored prior to entering Mode 4. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-03
48992 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-04-24 | 2013-05-02 13:31 | 2013-05-02 | AGREEMENT STATE REPORT - PROSTATE SEED IMPLANT EARLY TERMINATION "A prostate seed implant procedure was terminated after the insertion of 2 needles. Only 5 of 106 intended seeds were implanted (1.55mCi of 32.86mCi). The patient's anatomy (pubic arch) presented interference to the placement of needles/seeds for proper dose distribution. The patient will now be treated with external beam IMRT [intensity modulated radiation therapy] once post implant CT and dose assessment have been performed in approximately 3 weeks. The patient and referring physician have been notified. The facility notified NYS DOH [New York State Department of Health] same day, written report with corrective actions has been received. To prevent recurrence the urologist will verify during planning volume study that there are no anatomical obstructions to needle placement." Report No. NY-13-02 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-05-10
48991 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-05-02 07:48 | 2013-05-02 11:27 | 2013-05-02 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM On May 2, 2013, a non-licensed employee supervisor tested positive for alcohol on a random fitness for duty test. The individuals site access has been terminated. The licensee notified the NRC Resident Inspectors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2013-05-02
48990 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2013-04-30 13:20 | 2013-05-01 14:16 | 2013-05-01 | AREA ACCESS RESTRICTED FOR MORE THAN 24 HOURS DUE TO INCREASED RADIOLOGICAL CONTROLS "On 04/30/13, while changing the feed from Position 3 East to Position 3 West autoclaves, Operators noticed a pressure spike on the 3 East cylinder to approximately 47 psia. After disconnecting the cylinder in Position 3 East with Health Physics (HP) assistance, HP found a contamination spread on the cylinder, on the grating within the autoclave, and on the autoclave locking ring. Due to the contamination spread, access requirements to the area will be increased for more than 24 hours. Decontamination efforts are underway but will not be completed within 24 hours from the time that radiological controls were increased. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(1)(i) 'An unplanned contamination event that: Requires access to the contaminated area, by workers or the public, to be restricted for more than 24 hours by imposing additional radiological controls or by prohibiting entry into the area.' "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2013-05-09
48989 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-04-26 14:57 | 2013-05-01 13:28 | 2013-05-01 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILS TO RETRACT The following information was received via fax: "On 04/26/2013, the RSO for IRIS, was notified by one of his radiography crews working at the Marathon Refinery that a source was not retracting into the shielded area of the camera. "This incident involved a QSA Global Exposure Device, Model Delta 880, S/N D6458, loaded with an Ir-192 source. Associated equipment was used with the exposure device. The problem occurred when the crew used a magnetic source tube stand as opposed to a non-magnetic support stand. "Source retrieval was accomplished by the RSO around 2:53 pm. Using safety equipment, maintaining a 2 mR boundary, and time, the highest exposure received was by the RSO which was 75 mR. The other exposures recorded were from normal work activities. The Department [Louisiana Department of Environmental Quality] was notified after source retrieval was completed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-05-09
48988 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-05-01 05:00 | 2013-05-01 10:41 | 2013-05-02 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "A condition is being reported per TRM 13.13.1 Emergency Response Facilities Action B.2 The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities performed on TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity. The NRC Resident Inspector has been notified. " The licensee anticipates the maintenance will be complete at 1630 EDT on 5/1/13. * * * UPDATE FROM PARKER TO SNYDER AT 1702 EDT ON 5/1/13 * * * The TSC was returned to service at 1607 EDT on 5/1/13. Notified R2DO (O'Donohue). * * * UPDATE FROM ASHTON PARKER TO CHARLES TEAL AT 1123 EDT ON 5/2/13 * * * The TSC has been taken out of service to perform planned maintenance. The NRC Resident Inspector has been informed. Notified R2DO (O'Donohue). * * * UPDATE FROM PARKER TO SNYDER AT 1747 EDT ON 5/2/13 * * * The TSC was returned to service at 1733 EDT on 5/2/13. Notified R2DO (O'Donohue). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-05-01
48987 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-04-22 | 2013-05-01 09:43 | 2013-05-01 | AGREEMENT STATE REPORT - SHUTTERS FOUND THAT WERE DIFFICULT TO OPERATE ON TWO PROCESS GAUGES The following was received from the State of Louisiana via facsimile: "On 4/22/2013, the Radiation Safety Officer (RSO) for ExxonMobile Chemical was performing his annual inventory and operational checks on the level gauges at the Baton Rouge facility. During the checks, two level gauges were found with shutters that were difficult to operate. "The gauges detected were Ronan Engineering Gauges, devices involved, Model Number SAF-F37. One gauge is S/N 0781GK loaded with 100 mCi of Cs-137 and S/N 4585GH loaded with 25 mCi of Cs-137. Ronan Engineering has been contacted to fix the problem or repair the gauge. These gauges are installed on process and pose no safety threat to the general public or the employees. This is not considered a safety equipment failure, just being installed on a process in a very harsh corrosive environment. "This is a two shutter malfunction on level gauges installed on processes. These devices do not pose a radiation exposure threat to the general public. They will remain in operation on the process until and after repair. "The department considers this event closed." Event Report ID No.: LA-120016, T146449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-05-09
48986 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-04-30 13:42 | 2013-04-30 16:37 | 2013-05-01 | POTENTIAL LOSS OF CONTROL OF SAFEGUARDS MATERIAL Potential loss of control of safeguards material. The licensee will notify the NRC Resident Inspector. * * * RETRACTION BY KENNETH WEITH TO DONALD NORWOOD AT 1418 EDT ON 5/1/2013 * * * Upon further review of site and regulatory reporting guidance, a determination was made by the licensee that this event should have been classified as a Safeguards Event Log Report (loggable event) vice a Safeguards Event Report (1-hour notification). The licensee notified the NRC Resident Inspector. Notified R4DO (Haire). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-04-30
48985 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-30 09:45 | 2013-04-30 13:15 | 2013-04-30 | PLANNED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER SUPPORT SYSTEMS "A condition is being reported per TRM [Technical Requirements Manual] 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance activities performed on TSC support systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity. At 102 EDT on 4/30/13, the "TSC has been restored to a functional status. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-30
48984 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-30 08:40 | 2013-04-30 10:45 | 2013-04-30 | PLANNED MAINTENANCE OF RADIATION MONITORS USED FOR EAL CLASSIFICATION "Systems affected: Unit 1 Spent Fuel Pool Island Vent Rad Monitor "Actuations & their initiation signals: None. "Causes: Preplanned Chemistry maintenance "Effect of event on plant: Loss of assessment capabilities from radiation monitors used for EAL [Emergency Action Level] classification. "Actions taken or planned: Chemistry to perform scheduled maintenance "Additional information: Radiation monitor will be out of service for approximately 30 minutes." The licensee has notified the NRC Resident Inspector and applicable state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-30
48983 | 0 | HUMBOLDT BAY |  |  |  | ISFSI | 2013-04-27 | 2013-04-30 10:25 | 2013-04-30 | SECURITY REPORT INVOLVING FAILURE TO MEET MINIMUM STAFFING REQUIREMENTS Safeguards system degradation related to minimum staffing requirements. Compensatory measures taken upon discovery. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2013-04-30
48982 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-30 01:20 | 2013-04-30 05:06 | 2013-04-30 | PLANNED MAINTENANCE OF RADIATION MONITORS USED FOR EAL CLASSIFICATION "Systems affected: Main steam line radiation monitors, MSS-RE75, RE77, and Terry Turbine radiation monitor MSS-RE79. "Actuations & their initiation signals: None. "Causes: Preplanned electrical maintenance of radiation monitors power supplies. "Effect of event on plant: Loss of assessment capabilities from radiation monitors used for EAL [Emergency Action Level] classification. "Actions taken or planned: Maintenance of electrical power supplies to radiation monitors. "Additional information: Radiation monitors will be removed from service for approximately 48 hours." The licensee has notified the NRC Resident Inspector and applicable state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Defueled; FMode3: Defueled | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-30
48981 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-04-29 14:17 | 2013-04-29 17:50 | 2013-04-29 | OFFSITE NOTIFICATION OF A FREON LEAK "Offsite notification to the New York DEC [Department of Environmental Conservation] to report a Freon (R-22) release to the air of 8 lbs. 11 ozs. This release came from the cafeteria kitchen walk-in cooler." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-29
48980 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-29 09:00 | 2013-04-29 08:41 | 2013-05-03 | TSC VENTILATION SYSTEM OUT OF SERVICE FOR SCHEDULED MAINTENANCE "At 0900 EDT on Monday, April 29, 2013, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room, if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 1200 EDT on Thursday, May 2, 2013. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM GREG KANDA TO HOWIE CROUCH ON 5/2/13 AT 1448 EDT * * * "Due to scheduling issues, the restoration of the Technical Support Center (TSC) air conditioning and charcoal filtration systems has been delayed. The TSC ventilation systems are expected to be returned to service by 0000 EDT on Friday, May 3, 2013. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Duncan). * * * UPDATE FROM DEAN BRUCK TO CHARLES TEAL ON 5/3/13 AT 0515 EDT * * * "The restoration of the Technical Support Center (TSC) air conditioning and charcoal filtration systems has been delayed but is in progress. The TSC ventilation systems are expected to be returned to service by 0600 EDT on Friday, May 3 2013. "The licensee will notify the NRC Resident Inspector." Notified R3DO (Duncan). * * * UPDATE FROM GREG KANDA TO VINCE KLCO AT 0822 EDT ON MAY 3, 2013 * * * "The Technical Support Center (TSC) air conditioning and charcoal filtration systems were restored at 0818 EDT. The TSC is fully functional. "The NRC Resident Inspector has been notified. " Notified the R3DO (Duncan). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-29
48979 | 0 | SHAW AREVA MOX SERVICES, LLC |  |  |  |  | 2013-04-29 | 2013-04-29 07:59 | 2013-04-29 | BASIC COMPONENT WHICH FAILS TO COMPLY OR CONTAINS A DEFECT "(i) Name and address of the individual or individuals informing the Commission. "Kelly D. Trice President and Chief Operating Officer Shaw AREVA MOX Services Savannah River Site P.O. Box 7097 Aiken, SC 29804-7097 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility which fails to comply or contains a defect. - The Mixed Oxide Fuel Fabrication Facility is affected by the procurement of Types 304L and 316L SS pipe where some of the delivered pipe contains a defect. An extent of condition was performed based on the initial discovery of a defect in 1/2" (0.109 MW), Type 304L SS pipe. This investigation determined that eight additional heat/size combinations had similar defects including both 304L and 316L pipe as given below. 1/2" (0.109 MW), Type 304L - 5 heats (41789, 44266, 43599, 40900, 41123) 3/4" (0.113 MW), Type 304L - 1 heat (42635) 1-1/2" (0.145 MW), Type 304L - 1 heat (41586) 4" (0.237 MW), Type 304L -1 heat (41880) 3/4" (0.113 MW), Type 316L - 1 heat (44464) "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. - The Type 304L and 316L SS pipe is being supplied to MOX Services as a basic component by CB&I Laurens (formerly BF Shaw). "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. - Through independent testing, MOX Services has identified nine heats/sizes of 304L and 316L SS pipe supplied by CB&I Laurens (formerly BF Shaw) that fail required ASTM A262 testing and cannot be used in their specified application. Test results provided by CB&I Laurens (formerly BF Shaw) with the pipe indicate that it passes the Practice A test. The pipe was manufactured by Tubacex for CB&I Laurens (formerly BF Shaw), and ASTM A262 Practice A testing was performed by Welding Testing Lab prior to supply of the pipe to MOX services. Both entities have been qualified by CB&I Laurens (formerly BF Shaw) as approved suppliers. - Testing of these heat/size combinations of material has been performed by an independent test lab contracted by MOX Services with failing results thus indicating that the pipe is susceptible to intergrannular corrosion if utilized in an environment with electrolytic potential (e.g., nitric acid, oxalic acid). The heats/sizes of SS pipe in question are intended for use where these environments exist for many processes. - In total, 124 heat/size combinations of Type 304L SS pipe and 64 heat/size combinations of Type 316L supplied by CB&I Laurens (formerly BF Shaw) were retested to validate original testing results. Eight heats/sizes of Type 304L SS pipe fail both ASTM A262 practice A and C and the one heat/size of Type 316L SS pipe fails ASTM practice A making this pipe unusable for the MOX Project in certain applications. "(v) The date on which the information of such defect or failure to comply was obtained. - The deviation was initially identified in a test report provided by Savannah River National Laboratory on May 14, 2012. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. - MOX Services does not possess information as to whether other facilities have been supplied a similar basic component by CB&I Laurens (formerly BF Shaw). "(vii) The corrective action, which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. - Corrective actions are being addressed via MOX Services' corrective action program. The major activities associated with this issue include, tagging and segregation of impacted pipe spools, retesting samples for the affected pipe, generating/dispositioning non-conformance reports for heats of pipe that fail the re-test, and investigating the test protocol at both Welding Testing Lab and the MOX Services independent laboratory. The majority of the samples requiring retest have been retested. Initial nonconformance reports have been generated. Additional nonconformance reports will be generated as retesting is completed and affected heats are mapped to affected pipe spools. Test protocols at both Weld Test Lab and the MOX Services independent laboratory have been observed. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. - The following two excerpts are from ASTM A262 and pertain to the advice offered by MOX services. 5.2 The intent is to test a specimen representing as nearly as possible the surface of the material as it will be used in service. Therefore, the preferred sample is a cross section including the surface to be exposed in service. Only such finishing should be performed as is required to remove foreign material and obtain a standard, uniform finish as described in 5.3. For very heavy sections, specimens should be machined to represent the appropriate surface while maintaining reasonable specimen size for convenient testing. Ordinarily, removal of more material than necessary will have little influence on the test results. However, in the special case of surface carburization (sometimes encountered, for instance, in tubing or castings when lubricants or binders containing carbonaceous materials are employed) it may be possible by heavy grinding or machining to completely remove the carburized surface. Such treatment of test specimens is not permissible, except in tests undertaken to demonstrate such effects. 6.2 The etched cross-sectional areas should be thoroughly examined by complete traverse from inside to outside diameters of rods and tubes, from face to face on plates, and across all zones such as weld metal, weld-affected zones, and base plates on specimens containing welds. - Based on these excerpts, MOX Services offers the following advice. - Sample preparation is an area that should be carefully controlled in regards to detection of piping with 10 sensitization. Heavy cleaning or deburring in sections of the sample to be tested is proven to impact test results. Follow up surveillance at both Welding Testing Lab and the MOX Services independent laboratory determined that standard protocol is for samples to be taken from newly cut sections without sanding or deburring. - Procurement specifications should clearly indicate that micrographs should be done perpendicular to the forming direction, and should be representative of the worst case area of the cross section including the pipe 10 when appropriate. In a number of cases represented herein, only the inner portions of the pipe walls were sensitized to the point of ditching in which case a complete traverse of the cross-sectional area is needed to detect the condition. In a follow up survey of both Welding Testing Lab and the MOX Services independent laboratory, ASTM A262 practices were reviewed and it was determined in both cases that testing practices and procedures are in compliance with the ASTM standard including a full traverse of the cross-section. "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "This is not an early site permit concern." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-29
48978 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2013-02-28 15:36 | 2013-04-28 14:47 | 2013-04-28 | INADVERTENT ACTUATION OF THE TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "This is a 60-day optional telephonic notification of an invalid actuation of the Unit 1 Turbine Driven Auxiliary Feed Water Pump (TDAFWP). This report is being made under 10CFR50.73(a)(2)(iv)(A). "On 28 February 2013, at 1534 CST, during restoration of the Unit 1 TDAFWP from steam admission valve maintenance, steam was inadvertently admitted to the TDAFWP turbine, resulting in the TDAFWP delivering auxiliary feed water flow to the steam generators. "On 28 February 2013, the Unit 1 TDAFWP was removed from service for replacement of the hand switch and air-supply solenoid to the TDAFWP steam admission valve. The tagout utilized for this maintenance closed the TDAFWP trip-throttle valve to ensure that steam remained isolated from the TDAFWP. During the replacement of the hand switch and air-supply solenoid, the normally closed steam admission valve failed to the open position. This went unnoticed by Operations personnel. When the TDAFWP trip throttle valve was reopened during post-maintenance restoration, the failed-open steam admission valve provided a steam path to the TDAFWP. The TDAFWP started and supplied approximately 60-70 gpm feed water flow to each steam generator for approximately one minute prior to being secured by the operators. No main turbine load reduction was required to maintain reactor power within limits. "This was an invalid actuation of the TDAFWP due to no automatic actuation signals being present and no operator actions being taken with the intent of starting the TDAFWP. "During a normal TDAFWP start, the steam admission valve is opened in concert with steam supply valves aligned in series with the steam admission valve. During this event, the steam supply valves remained closed (steam flow bypassed these valves through normally open warm-up valves). Therefore, this event was a partial actuation of the TDAFWP. "The TDAFW Pump is a third, independent train of AFW. No other portions of the auxiliary Feed Water System actuated or received actuation signals during this event. "The primary cause of this event was determined to be not complying with the tagging checklist when sequencing the tagout restoration steps. Corrective actions are scheduled to complete on 30 May 2013." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-04-28
48977 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2013-04-27 21:24 | 2013-04-28 00:48 | 2013-04-28 | TECHNICAL SPECIFICATION REQUIRED PLANT SHUTDOWN "This notification is being provided in accordance with 10CFR50.72(b)(2)(i), Plant Shutdown required by Technical Specifications, and 10CFR50.72(b)(3)(ii)A, Degraded or Unanalyzed Condition. "At 2245 CDT on 04/27/13, LaSalle Unit 1 commenced a Technical Specification required plant shutdown, due to identification of pressure boundary leakage. At 2124 CDT on 04/27/13, a through-wall leak was identified in the body of 1E51-F076, Reactor Core Isolation Cooling system steam supply inboard isolation bypass warmup valve. This qualifies as pressure boundary leakage, which requires entry into Technical Specification 3.4.5, Reactor Coolant System Operational Leakage, Required Action C, to be in Mode 3, Hot Shutdown, by 0924 [CDT] on 04/28/13, and Mode 4, Cold Shutdown, by 0924 [CDT] on 04/29/13. This leakage is significantly less than 10 gpm and therefore does not meet the threshold for entry into the Emergency Action Plan. At the time of discovery, Unit 1 was in startup mode following a forced outage. A unit shutdown has been initiated. A repair plan is being prepared at this time, and the unit will remain in Cold Shutdown until repairs are complete." The leak is located inside the primary containment and was visually identified during a containment walk-down. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2013-04-28
48976 | 0 | ITT ENGINEERED VALVES, LLC |  |  |  |  | 2013-04-26 13:54 | 2013-04-26 17:25 | 2013-04-26 | DIAPHRAGMS MAY NOT BE QUALIFIED FOR SPECIFIC RADIATION DESIGN CONDITIONS The following report was received from ITT Engineered Valves, LLC via facsimile: "It is my duty as the Responsible Officer of ITT Engineered Valves, LLC (ITT) to inform the Nuclear Regulatory Commission of a defect with certain items of our nuclear diaphragm valve product line which may be considered Basic Components. The components are ITT's Nuclear M1 diaphragms, sizes 3 inch and 4 inch that may have been sold to certain customers for specific design conditions. The defect does not affect all 3 inch and 4 inch M1 diaphragms that have been sold. It only applies to those that were sold for a particular service condition of Code Case N31 (250?F and 220 psi with 40 year radiation exposure of 1E8 Rad). "The nature of the defect is best described by 10 CFR Section 21.3 Defect Definition #5, as 'an error, omission or other circumstance in a design certification or standard design approval that... could create a substantial safety hazard.' In this case, ITT inadvertently qualified the 3 inch and 4 inch M1 diaphragms for a design condition that includes the effect of radiation when in fact our recommendation was erroneously based on diaphragm testing that did not include irradiated diaphragm test results for those sizes. The potential safety hazard stems from the fact that if one of these diaphragms sees radiation in this particular service, there is no data to indicate that the diaphragm will perform its function in that service condition. Until such time that we can conduct additional irradiated diaphragm testing to additional sample diaphragms and test for this condition, we need to consider the parts that are in this service as potentially unsafe. "ITT is in the process of identifying all facilities for which the diaphragms were sent, either as spare parts or diaphragms incorporated into valve assemblies. We are also preparing to do further verification tests of the 3 inch and 4 inch M1 diaphragms in an attempt to ascertain the true performance rating at the noted condition. "Per 10 CFR 21 policy guidelines, this initial notification will be followed by a written notification by May 27, 2013." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-26
48975 | -1 | BEAUMONT HEALTH SYSTEMS |  |  |  |  | 2013-02-21 | 2013-04-26 13:45 | 2013-04-29 | SURFACE CONTAMINATION OF RADIOACTIVE MATERIAL SHIPMENT EXCEEDED LIMITS During an audit of a satellite facility associated with Beaumont Health Systems, the Radiation Safety Officer (RSO) determined that a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits had been received but not reported to the NRC as required per 10 CFR 20.1906(d)(1). The package was received on February 21, 2013 and wipe tests performed on the external surface of the package. Removable contamination levels were found on the package of 19,070 dpm/300 cm2. This level exceeds the reportable limits specified in 10 CFR 71.87(i). The package contained Technetium-99m that had been shipped and delivered by Beaumont's Troy Hospital facility. The receiving facility did not find any damage or contamination on the Tech-99m vial or inside the ammo case used to transport the vial. The audited receipt inspection report revealed the external package contamination event was documented but not reported to the company's RSO. Troy Hospital was notified at the time of the event and contamination surveys were performed at the packaging location, on the transport vehicle, and on the driver. The only contamination found was a wipe used to wipe the area where the package had been stored in the truck (wipe-down of radioactive material lay-down area is routine protocol for the licensee). The RSO stated that corrective actions are being taken related to improving contamination controls while packaging these shipments. In addition, improvements in the process related to reporting events to the RSO and the NRC are being explored. * * * RETRACTION AT 1415 EDT ON 4/29/2013 FROM CHERYL SCHULTZ TO MARK ABRAMOVITZ * * * The removable contamination of 19070 dpm/300cm2 equates to 63 dpm/cm2 which is below the reportable limit of 220 dpm/cm2. Therefore, this event is retracted. Notified the R3DO (Duncan) and FSME Resources (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2013-05-06
48974 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-04-26 08:55 | 2013-04-26 12:55 | 2013-04-26 | MANUAL REACTOR SCRAM DUE TO RAPIDLY DECREASING LEVEL IN THE EHC OIL RESERVOIR "On 4/26/13 at about 0855 CDT while operating at rated electrical power, operators initiated a manual reactor scram due to rapidly decreasing level in the main Electro Hydraulic Control (EHC) oil reservoir. All systems responded as expected with no complications. The cause of the main EHC decrease in level is under investigation. The plant is stable in mode 3. "The NRC Resident Inspector has been notified." The licensee reports that bypass valves remain available via a separate EHC system and decay heat is being routed to the condenser. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-04-26
48973 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-04-26 10:00 | 2013-04-26 12:25 | 2013-04-26 | FITNESS FOR DUTY REPORT - LICENSED OPERATOR HAD A CONFIRMED POSITIVE FOR ILLEGAL DRUGS A licensed operator had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The licensed operator's plant access has been terminated. The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2013-04-26
48972 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-03-04 08:04 | 2013-04-26 12:21 | 2013-04-26 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATORS "This 60-day telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation of the Emergency Diesel Generators (EDGs) reportable under 10 CFR 50.73(a)(2)(iv)(A). Due to the shared configuration of the onsite AC Electrical Distribution System, this event is applicable to both Units 1 and 2. "On March 4, 2013, at approximately 0804 EST, while performing a planned maintenance activity associated with the Unit 2 Start-Up Auxiliary Transformer (SAT), the SAT lock-out relay was inadvertently energized. This occurred when a Transmission Maintenance electrician closed the fault pressure device oil isolation valve without having previously opened the fault pressure cutoff switch. This action resulted in energizing the SAT lock-out relay and, per design, started all four EDGs. "All four EDGs started and operated as expected. Because electrical power was never lost to the emergency busses and none of the EDGs loaded to their respective emergency busses, the actuations were considered to be partial. "The EDGs were returned to their standby line-up by 1023 [EST] hours on March 4, 2013. Since no actual bus under voltage condition existed which required the EDGs to start and the start was not in response to actual plant conditions satisfying the requirements for initiation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-04-26
48971 | 0 | PREFIX CORPORATION |  |  |  |  | 2013-04-18 | 2013-04-26 12:00 | 2013-04-26 | LOST POLONIUM-210 STATIC ELIMINATOR SOURCE Prefix Corporation uses static control ionizers for applying coatings in some of its product processes. These static control ionizers are leased from NRD LLC and contain less than 0.1 millicuries of Polonium-210. In early April, 2013, Prefix was preparing to return one of its leased Nuclecel Ionizers to NRD and discovered it was missing. The source was last used in November of 2012. A search was conducted for the source without success and Prefix considers the source to be lost. The source is small and cylindrical and could have rolled off its storage location onto the floor and been swept-up as trash. Prefix sent a written notification to NRC Region 3 on April 18, 2013, but had not previously reported the event to the NRC Operations Center. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-05-06
48970 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-26 04:42 | 2013-04-26 08:19 | 2013-04-26 | UNATTENDED VEHICLE ADJACENT TO THE OWNER CONTROLLED AREA "On April 26, 2013 at 0442 EDT operations personnel were notified of an unattended vehicle discovered on a public road adjacent to the owner controlled area [OCA]. Investigation revealed evidence of an individual briefly entering the owner controlled area and exiting. The Berrien County Sheriffs department was contacted and participated in a search of the immediate area with DC Cook Security personnel. The search was completed at 0721 EDT and did not identify anything unusual. "This event is reportable under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report. "The licensee has notified the NRC Resident Inspector." The licensee observed the individual via security camera. The person exited the OCA within 5 minutes. The licensee notified the State of Michigan and the St. Joe FBI field office. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-26
48969 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2013-04-25 20:19 | 2013-04-25 22:23 | 2013-04-25 | MANUAL REACTOR SCRAM FOLLOWING TRIP OF CIRC WATER PUMPS "This report is being made pursuant to 10CFR50.72(b)(2)(iv)(B), RPS Actuation (scram). At 2019 CDT on April 25, 2013, LaSalle Unit 2 was manually scrammed due to a loss of Condenser Circulating Water. The Unit was manually scrammed after the condenser circulating water pumps tripped due to high level in the turbine building condenser pit. The high level in the condenser pit was caused by a leak on the upper manway of the condenser water box during a maintenance activity. MSIV's were isolated due to loss of heat sink. The safety relief valves were used in pressure control mode. Current plant status: reactor level is stable and reactor pressure is stable. The condenser water box manway leak has been isolated. The plant will remain in hot shutdown pending investigation and repairs." Reactor Core Isolation Cooling (RCIC) is being used in the pressure control mode. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 57 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-04-25
48968 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-04-25 17:59 | 2013-04-25 20:51 | 2013-04-29 | VENT STACK RADIATION MONITORS DE-ENERGIZED FOR SHORT DURATION DURING PRE-PLANNED MAINTENANCE "This is a report of a loss of emergency assessment capability as required by 10 CFR 50.72(b)(3)(xiii). "On April 25, 2013 at 1759 CDT, with Unit 2 in Mode 6 during a refueling outage, power was interrupted to all Unit 2 vent stack radiation monitors as part of a pre-planned activity to connect the radiation monitors to an alternate temporary power supply to support de-energizing the normal power source for preventative maintenance. The connection to the alternate supply was completed and power was restored to the vent stack radiation monitors at 1845 CDT. While the radiation monitors were without power, pre-planned compensatory measures were implemented to monitor vent stack discharge and to minimize activities that posed a potential for release. "At the completion of the preventive maintenance on the normal power supply, power to the vent stack radiation monitors will again be briefly interrupted to reconnect the normal power source to the monitors. The pre-planned compensatory measures will again be utilized during this power interruption. An update to this report will be provided following the restoration of normal power to the radiation monitors. "The NRC Resident inspector has been informed." * * * UPDATE AT 0400 EDT ON 4/29/13 FROM BRANNON PAYNE TO S. SANDIN * * * "On 28 April, 2013, power was again interrupted to the Unit 2 vent stack radiation monitors to restore the connection to their normal power supply. The radiation monitors were out of service from 2315 until 2340 CDT. Pre-planned compensatory measures were again implemented to monitor vent stack discharge and minimize potential for vent stack release. "The reported time for the initial loss of vent stack radiation monitoring on April 25, 2013 was incorrect. The correct time was 1759 CDT. "The NRC Resident has been notified." Notified R2DO (Sykes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-25
48967 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-04-23 | 2013-04-25 14:52 | 2013-04-25 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY SOURCE TO FULLY RETRACT The following information was received from the State of Texas via E-mail: "On April 24, 2013, the Agency [Texas Department of State Health Services] was notified by the licensee that they were unable to fully retract an Iridium-192 source into a QSA model 660 radiography device. The radiographers attempted to retract the source several times, but were unable to get the device to lock the source in the fully shielded position. The radiographers contacted the Radiation Safety Officer who responded to the location along with the licensee's Source Retrieval Supervisor. The supervisor attempted to retract the source and on the second attempt, dose rates indicated that the source was fully shielded, but the device's locking device had not tripped. The supervisor inserted the source shipping plug into the device to secure the source in place. The source crankout device was dismantled and they discovered the connector on the end of the drive cable had separated from the drive cable. The crankout device has been shipped to the manufacturer for inspection and repair. The crankout device was placed in service by the licensee on April 11, 2013. The exposure device was inspected by the licensee and found to operate normally. No significant exposure was received by any individual involved in this event. Additional information will be provided in accordance with SA-300." Texas Incident #: I-9074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-05-03
48966 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2013-04-18 13:25 | 2013-04-25 12:23 | 2013-04-25 | LOW PRESSURE CORE SPRAY INOPERABLE "On 4/18/2013, while attempting to raise Unit 1 reactor level with the Low Pressure Core Spray (LPCS) system, LPCS injection valve 1E21-F005 failed to open as required when the associated control switch was held in the 'OPEN' position. The Unit Supervisor declared the LPCS system inoperable, and the appropriate Technical Specification time clocks were entered. Troubleshooting determined that the problem was a faulty control switch. "The control switch has been replaced and LPCS returned to an operable status. "Initial review of this event determined that it was not reportable; however, subsequent review caused the event to be re-evaluated and classified as reportable under 10CFR50.72(b)(3)(v)(D) and 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The station is continuing to evaluate the reportability of this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-25
48965 | 0 | DIABLO CANYON |  |  |  | ISFSI | 2013-04-24 09:02 | 2013-04-24 18:15 | 2013-04-24 | LOADING PROCEDURE FOR ISFSI MULTI-PURPOSE CANISTERS PLACED THEM IN AN UNANALYZED CONDITION "On April 24, 2013, at 09:02 PDT, Diablo Canyon Power Plant (DCPP) determined that the loading procedure for the independent spent fuel storage installation (ISFSI) multi-purpose canisters (MPCs) placed the MPCs in an unanalyzed condition. The procedure (approved for use in 2009) contained steps to install vent caps on the MPC vents while the MPC contained an air/water mixture. This placed the MPC in an isolated condition without any relief path while water was in the MPC (a condition previously not analyzed in the DCPP ISFSI FSAR). "The MPC vents that prevent MPC over pressurization were disabled while the vent caps were installed with no alternative over pressurization protection provided, therefore the condition is a 24-hour reportable event under 10 CFR 72.75(d)(1). "This process was used for 23 casks, beginning in 2009. The amount of time each cask was isolated was approximately 40 - 60 minutes. DCPP expects that no appreciable MPC pressure increase occurred, since the MPC contains an air void, and the activity is performed expeditiously. Based on engineering judgment, a conservative evaluation of the potential pressure rise during this period shows an increase of less than 2 psig. Since the MPC is vented prior to isolation, a 2 psig increase does not challenge the MPC design pressure of 100 psig. Therefore, there is no reason to believe that the integrity of any of the 23 previously loaded MPCs has been challenged at the DCPP ISFSI. "This evaluation will be confirmed and documented in a formal calculation as part of issue resolution." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 72.75(d)(1) |  |  |  | 0 | 2013-04-24
48964 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-24 14:11 | 2013-04-24 17:15 | 2013-04-24 | VALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR DUE TO A LOSS OF TRAIN A RESERVE FEED TO THE SITE "On 4/24/13 at 1411 EDT, a fault occurred on the Unit 1 101 CD Reserve Auxiliary Transformer causing the 12 CD 34kV Reserve Feed Breaker to open resulting in a loss of Train A Reserve Feed to Unit 1 and Unit 2. The cause of the fault is still under investigation. "Unit 2 remains stable in 100% power. Unit 2 entered LCO 3.8.1, AC Source - Operating, Condition A, one required offsite circuit inoperable Restore Unit 2 reserve feed to operable status within 72 hours. "Unit 1 is currently in a refueling outage and offline. Unit 1 CD Emergency Diesel Generator (EDG) automatically started and loaded as expected. "North Spent Fuel Pit Cooling Train lost power due to a load shed, which resulted in a 2 degree Fahrenheit rise in the Spent Fuel Pool Temperature. The North Spent Fuel Pit Cooling Pump was restarted on 1 CD EDG at 1447 EDT. South Spent Fuel Pool Cooling Train remained in-service the entire time. "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-04-24
48963 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-04-24 16:00 | 2013-04-24 16:50 | 2013-04-24 | NON-LICENSED EMPLOYEE SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL "A non-licensed, supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been restricted." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2013-04-24
48962 | 0 | RHODE ISLAND ATOMIC ENERGY COMM |  |  |  | 2000 KW POOL | 2013-04-24 10:00 | 2013-04-24 10:58 | 2013-04-24 | UNQUALIFIED RADIATION SAFETY OFFICER AT A NON-POWER REACTOR Based on a review of qualifications of the current RSO (Radiation Safety Officer) at the Rhode Island Nuclear Science Center, it was determined that the individual did not meet the licensee's Technical Specification 6.2.2 for education or experience requirements. This review is a follow-up to an NRC inspection report dated March 25, 2013. This non-compliance is reportable in accordance with licensee Technical Specifications 1.25, item 8, which delineates administrative and procedural requirements. Immediate actions was to shut down operations until such time that inadequacies can be remedied. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | RI | NPR | [5 empty] | 0 | 2013-04-24
48961 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-23 20:58 | 2013-04-23 22:39 | 2013-04-23 | LOSS OF ASSESSMENT CAPABILITIES FROM A RADIATION MONITOR USED FOR EMERGENCY CLASSIFICATION Secondary leak collection and release radiation monitor RE19 A/B power supply was removed from service at 2058 EDT on 4/23/13 for planned maintenance activities. This radiation monitor is relied upon for emergency classifications. Expected duration of the maintenance activities is 72 hours. The licensee notified the State of Connecticut, the town of Waterford, and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-23
48960 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2013-04-19 | 2013-04-23 16:32 | 2013-04-23 | PART 21 REPORT - ESI REFURBISHED EMERGENCY DIESEL GENERATOR CYLINDER HEADS MAY HAVE VALVE KEEPER SEALS MISSING The following information is a summary of a report faxed to the Operations Center from Engine Systems, Inc. (ESI) concerning a condition reportable under 10 CFR 21: "Engine Systems Inc. (ESI) began a 10 CFR 21 evaluation on 02/19/13 following the failure analysis of a cylinder head returned by South Texas Project (STP). The cylinder head had been installed on an emergency diesel generator set at STP and, during routine prestart checks, oil was found leaking from the Kiene valve while barring over the engine. This cylinder head had been previously refurbished in 2004 under ESI's 10 CFR 50 Appendix B program. ESI's investigation revealed that the refurbished cylinder head was returned to the customer without keeper seals installed. "The evaluation was concluded on 04/19/13 and it was determined that this issue is a reportable defect as defined by 10 CFR 21. Omission of the keeper seals from the cylinder head of the KSV emergency diesel generator set could allow engine lubricating oil to migrate through the cylinder head and into the combustion chamber during engine standby conditions. Presence of this oil could damage the engine to the point that it is unable to perform its safety related function." ESI began dedicating refurbished cylinder heads in 2001 but the refurbishment scope did not include valve train components. Refurbishments that included valve train components were first shipped in 2003. Procedure steps were included in 2007 to verify valve keepers were installed. Therefore, only cylinder heads refurbished between 2003 and 2007 are affected. A review of purchase orders have determined that the following plants received a total of 26 cylinder heads that may not have valve keeper seals installed: Byron Station - 3 heads South Texas Project - 21 heads Cooper Nuclear Plant - 2 heads Affected cylinder head part numbers are 10-KSV-11-3-RR, 12-KSV-11-3-RR AND 13-KSVR-11-6-RR. ESI will be notifying affected customers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-23
48959 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2013-03-26 | 2013-04-23 13:50 | 2013-04-23 | AGREEMENT STATE REPORT - FETUS/EMBRYO DOSE EXCEEDED 500 MILLIREM The following information was obtained from the State of Alabama via facsimile: "On April 9, 2013, [the Certified Nuclear Medicine Technician] for Baptist Medical Center-Princeton, Birmingham, Alabama, notified the Alabama Office of Radiation Control of a fetal/embryo dose that could be over 500 milliRem. "On March 1, 2013, a 36 year old female had a thyroidectomy due to thyroid cancer. Following surgery on March 6, the patient had general lab work which included a negative pregnancy test. On March 26, the patient returned for a 50 millicurie I-131 treatment on the remaining thyroid tissue. The technologist administering the test did not confirm, nor was told, that the patient had another pregnancy test prior to the dosing. The pregnancy test conducted on March 26, 2013 was positive. It was confirmed that the embryo exposure was greater than 500 millirem threshold. "The patient was immediately notified of the positive pregnancy results and was consulted by a OB/GYN physician. The patient received an ultrasound which confirmed the pregnancy at 4 to 5 weeks. "The information is complete as of 12:45 pm CDT, April 23, 2013." Alabama Incident 13-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2013-05-01
48958 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-04-23 03:30 | 2013-04-23 11:13 | 2013-04-23 | STATE NOTIFICATION LINE OUTAGE "James A. FitzPatrick Nuclear Power Plant (JAF NPP) was notified by NYS Warning Point that the RECS [Radiological Emergency Communication System] line and all land lines to NYS were non-functional beginning at approximately 0330 [EDT] on 4/23/13. Due to this condition, JAF NPP did not have any communications with the NYS Warning Point available via NORMAL or BACKUP methods per Emergency Plan Procedures. "At 0449 [EDT] on 4/23/13, the JAF NPP control room was provided with an alternate means of contacting the NYS Warning Point via cell phone and hence a viable means of BACK-UP communications was established. Per 10 CFR 50.72 (b)(3)(xiii), 'any event that results in a major loss of off-site communications capability (off-site notification system between licensee and off-site officials - NYS) is reportable via 8-hour report.' "Subsequent to this event at approximately 0930 [EDT] 4/23/13, functionality of the RECS was restored and tested satisfactorily." The licensee notified the NRC Resident Inspector as well as the State and local governments. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-23
48957 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-04-23 03:30 | 2013-04-23 10:39 | 2013-04-23 | STATE NOTIFICATION LINE OUTAGE "Nine Mile Point Nuclear Station (NMP1 and NMP2) was notified by NYS Warning Point that the RECS [Radiological Emergency Communication System] line and all land lines to NYS were nonfunctional beginning at approximately 0330 [EDT] on 4/23/13. Due to this condition, NMPNS did not have any communications with the NYS Warning Point available via NORMAL or BACKUP methods per Emergency Plan Procedures. "At 0734 [EDT], the NMP1 and NMP2 control rooms were provided an alternate means of contacting the NYS Warning Point via cell phone and hence a viable means of BACKUP communications was established. Per 10 CFR 50.72 (b)(3)(xiii) any event that results in a major loss of offsite communications capability (offsite notification system between licensee and off site officials - NYS) is reportable via 8-hour report. "Subsequent to this event at approximately 0930 [EDT], functionality of the RECS line was restored." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-23
48956 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-23 08:15 | 2013-04-23 09:46 | 2013-04-23 | STACK RADIATION MONITOR PLANNED MAINTENANCE "System Affected: Site Stack Radiation Monitor; RM-8169 "Causes: Planned Maintenance "Effect on Plant: Loss of Assessment Capabilities "Actions Taken or Planned: Pre-planned maintenance of the RAD monitor. "Additional Information: RM-8169 will be removed from service at approximately 1100 [EDT] on 4/23/13 for a period of approximately 3 hours." The licensee notified the state and local government. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-23
48955 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2013-04-22 16:23 | 2013-04-22 23:23 | 2013-04-24 | EMERGENCY OPERATIONS FACILITY NOT AVAILABLE "On 4-22-13, at 1623 [CDT], the ANO Unit 2 control room was notified of a loss of ventilation capability to the Emergency Operations Facility (EOF). The main control boards associated with the variable speed drives on both air handling units at the EOF have failed. Therefore, there are no means to filter air for the EOF. If the EOF is staffed, the EOF will be required to relocate to the Alternate EOF in the event of a release that causes the EOF evacuation criteria to be exceeded, as directed by approved emergency response procedures. "The on-site Operations Support Center, on-site Technical Support Center and off-site Alternate EOF remain fully functional to perform emergency assessment activities. Efforts are underway to expedite repairs. "This notification is required by 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 4/24/13 AT 1003 EDT FROM STEVE COFFMAN TO DONG PARK * * * At 1637 EDT on 4/23/13, the EOF ventilation has been restored and the EOF has full functionality. The licensee has notified the NRC Resident Inspector. Notified R4DO (Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling Shutdown | Cold Shutdown |  | Refueling | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-22
48954 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-04-20 | 2013-04-22 19:18 | 2013-04-29 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK IN GUIDE TUBE The following was received from the State of Washington via email: "Mistras Group, Inc. was conducting industrial radiographic operations at Shell Puget Sound Refinery. After a routine exposure, the radiographer attempted to crank the source back into the camera, but the source became stuck. The source could not make it past a crimp in the guide tube, which was caused earlier when the camera fell on it. The radiography crew moved their restricted area boundaries to increase the size of the restricted area and to provide additional protection to anyone in the area. Fortunately, nobody other than the radiography crew were in that portion of the refinery. The radiography crew and assistant radiation safety officer were able to manually pull the source back into the shielded position in the camera. The highest exposure to any person, as read from a pocket dosimeter, was 10 millirem. Note: This is a preliminary report - we [State of Washington] will obtain additional information from the licensee and provide a more complete report in the near future." Washington Item Number: WA130001 * * * UPDATE ON 4/29/2013 AT 1931 EDT FROM JAMES KILLINGBECK TO MARK ABRAMOVITZ * * * The following information was received via fax: "An industrial radiography crew retracted the source, checked to verify that the source was fully retracted and locked, and discovered that it was not. The crew made more attempts to retract the source, but were unsuccessful. They attempted to straighten out the crank assembly, then the radiographic exposure device fell about 46 inches from a pipe onto a platform, after which the drive cable would not move using the crank handle. The restricted area was expanded to the 2 mR/hr line and facility management and the licensee's radiation safety personnel were notified and traveled to the site. The guide tube was moved onto the platform and lead shot bags were placed onto the collimator to provide extra shielding. Licensee radiation safety staff found that the drive cable was hung up in the crank assembly conduit but moved freely in the source tube. So, the staff manually pulled on the drive cable and returned the source to the fully retracted and locked position in the radiographic exposure device. It was discovered that there was a crimp in the crank assembly conduit that kept the drive cable from moving. The highest pocket dosimeter reading was 18 millirem. The radiographic exposure device was sent to the manufacturer for evaluation." Notified the R4DO (Haire) and FSME Event Resources (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-04-30
48953 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-22 09:00 | 2013-04-22 14:58 | 2013-04-23 | EMERGENCY OPERATIONS FACILITY NOT AVAILABLE "The Comanche Peak Nuclear Power Plant Emergency Operations Facility (EOF) is not available due to the loss of HVAC and filtering capabilities resulting from a failed Emergency Operations Facility (EOF) ventilation fan. The condition was discovered at 0900 CDT on 4/22/13. Repair parts are expected by the morning of 4/23/13 and the EOF is projected to be available by the end of the day on 4/23/13. "Compensatory measures are in place to staff and activate the Alternate EOF in the event of a declared emergency. "The NRC Resident Inspector has been informed." * * * UPDATE FROM MIKE STAKES TO HOWIE CROUCH AT 1426 EDT ON 4/23/13 * * * The Emergency Operations Facility vent fan was returned to service at 1400 EDT on 4/23/13. The licensee has notified the NRC Resident Inspector. Notified R4DO (Whitten). | 45 | 100 | 0 | 45 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-22
48952 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-04-21 01:04 | 2013-04-22 10:13 | 2013-04-22 | SOURCE JAMS AS IT IS MOVED FROM DRYWELL TO SOURCE HOLDER The following information was received via facsimile from the State of Kansas: "We [Frontier El Dorado Refining] attempted to move a source from its drywell, into its source holder. The source seems to be stuck in the drywell. There were no reportable personnel exposures. Because of the position of this source, 2 feet inside a large vessel with 5 [inch] steel walls, it is shielded at least as well as inside its holder. "The shutter in question is on an Ohmart/VEGA model SHLM-CR3 source holder S/N 19077661, containing 2 Ci of Cs-137 in a model A2102 sealed source S/N 0586CO. "The source is located at approximately 100 feet above the ground. Operations and maintenance personnel were notified of the issue. A wipe sample was collect to check for gross leakage. None was indicated. "We [Frontier El Dorado Refining] will contact VEGA Americas (formerly Ohmart/VEGA) to arrange for repairs." Item Number: KS130004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-04-30
48951 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-04-21 02:11 | 2013-04-21 02:48 | 2013-04-21 | SECURITY CHANGES MADE DUE TO REPORTED UNUSUAL EVENT ONSITE Certain security changes were made that resulted from the Notice of Unusual Event condition onsite (EN #48950). The licensee notified local law enforcement and the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-04-21
48950 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-04-21 02:11 | 2013-04-21 02:29 | 2013-04-21 | NOTIFICATION OF UNUSUAL EVENT DUE TO SHOTS FIRED WITHIN THE OWNER CONTROLLED AREA An unidentified individual fired a shot at a site security vehicle. "Watts Bar Nuclear Plant Declared a Notice of Unusual Event (NOUE) at 0211 EDT April 21, 2013. [The licensee notified] Rhea and Meigs County Sheriff departments for on-site support. "A notification of the event discussed above was made to the State of Tennessee. A notification of the event discussed above was made [to the] U.S. Department of Energy (DOE) Electricity Delivery and Energy Reliability." The licensee notified the NRC Resident Inspector. Notified DHS, FEMA, USDA, HHS, DOE, NICC, EPA, FBI SIOC and Nuclear SSA via email. * * * UPDATE FROM DAMON FEGLEY TO PETE SNYDER AT 0634 EDT ON 4/21/13 * * * "This information is being provided to the NRC for a 10CFR50.72(b)(2)(xi) notification. "TVA is planning on making a news release to local media affiliates and posting the news release on TVA's website. This news release is in reference to the Notification of Unusual Event (NOUE) Watts Bar Nuclear Plant recently entered for a security condition." Notified R2DO (Vias). * * * TERMINATION AT 1301 EDT ON 4/21/2013 FROM MICHAEL BOTTORFF TO MARK ABRAMOVITZ * * * "[At] 1230 EDT Watts Bar Nuclear plant terminated the Notification of Unusual Event. "TVA is planning on making an additional news release to local media affiliates and posting the news release on TVA's website. This news release is in reference to the Notification of Unusual Event (NOUE) Watts Bar Nuclear Plant recently terminated. "The licensee notified the NRC Senior Resident Inspector." Notified the R2 IRC, IRD (Grant), NSIR (Wiggins), NRR (Uhle), ILTAB (Johnson), DHS, FEMA, USDA, HHS, DOE, NICC, EPA, FBI SIOC and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2013-04-21
48949 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-20 04:22 | 2013-04-20 09:46 | 2013-06-13 | ACCIDENT MITIGATION - COMMON CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM "Salem Unit 2 was placed in a configuration that affected the ability to mitigate the consequences of an accident due to an inadvertent actuation of the common control room emergency air conditioning system (CREACS). CREACS was actuated as a result of an invalid Control Room air intake duct radiation monitor signal initiated on April 20, 2013 at 0422 hours [EDT]. "Salem Unit 1 is currently in Mode 6 with core offload in progress. Salem Unit 2 is in Mode 1 at 100% power. Unit 2 has two shutdown LCOs in effect. The first is for the CREACS, which is shared between Unit 1 & 2, being aligned for single train operation with the Unit 1 CREACS train out of service per LCO 3.7.6. The second shutdown LCO is for single source of offsite power due to scheduled maintenance. "With Unit 1 having an invalid radiation monitor signal, the CREACS automatically aligned to accident pressurized mode. This mode of actuation starts the CREACS fans, isolates the Control Room Envelope from the normal control room ventilation system and aligns the two sets of CREACS outside air intake dampers. With a Unit 1 radiation monitor signal the Unit 1 CREACS intake dampers close and the Unit 2 CREACS intake dampers open. These damper positions are locked in until manually reset. With only one train of CREACS operable, the dose analysis indicates that the requirements of General Design Criteria (GDC) 19 can only be met during the worst case design basis accident if the Unit 2 CREACS intake dampers are closed and the Unit 1 CREACS intake dampers [are] open. Therefore, until the CREACS intake dampers were reset and realigned, Salem Unit 2 would not have been able to mitigate the consequences of an accident and is reportable in accordance with 10CFR50.72(b)(3)(v). "The CREACS system actuation was reset after the failed radiation monitor (2R1B ch. II) was removed from service and the dampers were realigned to their pre-actuation alignment at 0457 hours, restoring Salem Unit 2 to within the assumptions of the dose analysis. Total duration in the condition was 35 minutes. "The only pieces of major equipment out of service on Salem Unit 2 are the 4 Station Power Transformer and 23 Station Power Transformer which are out of service for scheduled maintenance." The licensee will notifying Lower Alloways Creek township and the NRC Resident Inspector. * * * RETRACTION FROM DAVID LAFLEUR TO PETE SNYDER AT 1304 EDT ON 6/13/13 * * * "On April 20, 2013, Salem Unit 2 was placed in a configuration that was contrary to the current dose analysis of record due to an invalid actuation of the common Control Room Emergency Air Conditioning System (CREACS). The CREACS was initiated as a result of an invalid actuation of Control Room Air Intake Duct Radiation Monitoring Channel, 2R1B Channel 2. At the time of the actuation, the Unit 1 Train of CREACS was out of service due to scheduled maintenance leaving only the Unit 2 CREACS train operable. Unit 2 was at 100% power and Unit 1 was in Mode 6. With one train of CREACS out of service at the start of an accident the dose analysis of record requires that the CREACS Emergency Air Intake Dampers for the accident unit go closed and the opposite unit's emergency intake dampers go open. The actuation of the radiation monitoring channel 2R1B Channel 2 caused the Unit 2 Emergency Air Intake Dampers to open. If a design basis LOCA were to have occurred on Unit 2 during that period the alignment would have been contrary to the dose analysis-of-record. "Subsequent to this event, an evaluation was performed utilizing the assumptions of the dose analysis of record with two exceptions. Actual measured Engineered Safety Feature system leakage outside containment and Containment Leakage at the time of the event were utilized in the evaluation. This evaluation determined that if a design basis LOCA had occurred on Unit 2 with the CREACS in accident pressurized mode with Unit 1 Emergency Intake Dampers closed and Unit 2 Emergency Intake Dampers opened, Control Room design dose limits would not have been exceeded. Based upon this evaluation, the CREACS system would have been able to maintain dose to Control Room operators below the limits of GDC-19 and the dose analysis of record. Since the CREACS was capable of performing its accident mitigation function, this event is being retracted." The licensee will notify the NRC Resident Inspector. Notified R1DO (Dentel). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-20
48948 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2013-04-19 17:20 | 2013-04-19 18:08 | 2013-04-23 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES "An Unusual Event was declared on Unit 4 at 1730 EDT due to a loss of offsite power for greater than 15 minutes. Emergency buses are being powered from the Emergency Diesel Generators. All rods inserted. The plant is stabilizing on natural circulation in Mode 3. Emergency buses failed to auto-transfer to the startup transformer." AFW initiated and is supplying water to the steam generators. There was no impact on Unit #3. The failure of the auto-transfer of the startup transformer is under investigation. Notified DHS, FEMA, NICC and NuclearSSA via email. The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. * * * UPDATE FROM ROBERT PELL TO CHARLES TEAL ON 4/19/13 AT 1911 EDT * * * "At 1854 EDT Turkey Point Unit 4 continues to be in an Unusual Event due to a loss of offsite power. The emergency buses were energized from the start up transformer at 1824 EDT. Two reactor coolant pumps have been started and are running. The plant is stabilizing in Mode 3. In addition, per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) notifications are being made for the Reactor Protection Actuation for loss of power and the Emergency Safety Function actuations of the Emergency Diesel Generators and Auxiliary Feedwater." The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. Notified R2DO (Vias), NRR (Skeen), and IRD (Grant). * * * UPDATE FROM ROBERT PELL TO CHARLES TEAL ON 4/19/13 AT 1943 EDT * * * "All emergency buses are powered from offsite power. Unit 4 is stable in Mode 3. The Unusual Event was terminated at 1915 EDT on 4/19/13." The licensee notified State of Florida, Miami Dade county, the NRC Resident Inspector. Notified R2DO (Vias), NRR (Skeen), and IRD (Grant). Notified DHS, FEMA, NICC and NuclearSSA via email * * * UPDATE FROM KEITH MAESTAS TO BILL HUFFMAN ON 4/23/13 AT 1959 EDT * * * "In addition to the 10 CFR 50.72 sections initially identified, this event is also reportable in accordance with 10 CFR 50.72(b)(3)(v)(D). "Turkey Point was performing a 3rd Harmonic Relay Power Ascension Test after an Extended Power Upgrade outage. Unit 4 was approximately 173 MW electric with the auxiliary transformer supplying the site safety related 4.16KV busses. The test required maneuvering the Unit 4 main generator voltage downward to place the generator in the lead. As the Unit 4 main generator voltage was lowered, the Load Center degraded voltage relays initiated sequencer operation, 4.16KV bus stripping, starting the EDGs, and loading the 4.16KV buses onto EDGs. "Offsite power was available at all times." The licensee will notify the NRC Resident Inspector. R2DO (Sykes) notified. | 0 | 0 | 0 | 0 | 29 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2013-04-19
48947 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-04-19 15:18 | 2013-04-19 15:56 | 2013-04-19 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO INABILITY TO CONFIRM A FIRE IN THE PROTECTED AREA WITHIN 15 MINUTES "Fire within the Protected Area not verified within 15 minutes. Emergency Action Level HU 2.1 declared at 1518 EDT. Confirmation of no fire completed at 1526 EDT." The fire alarm occurred in the Rad Waste Building. Due to the location of the alarm, the licensee was not able to validate alarm within 15 minutes which led to the emergency declaration. Once access to the area was obtained, there was no fire observed. The cause of the inadvertent fire alarm is under investigation. The licensee has notified Lower Alloways Creek Township, the State of New Jersey, the State of Delaware and the NRC Resident Inspector. Notified DHS, FEMA, NICC and NuclearSSA via email. * * * UPDATE FROM MARTIN FRANKLIN TO HOWIE CROUCH AT 1731 EDT ON 4/19/13 * * * At 1725 EDT, the licensee terminated the Notification of Unusual Event. The affected fire alarm was placed out of service and a fire watch has been established. The licensee has notified Lower Alloways Creek Township, the State of New Jersey, the State of Delaware and the NRC Resident Inspector. Notified R1DO (Cook), IRD (Grant), NRR EO (Skeen), DHS, FEMA, NICC, and NuclearSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-04-19
48946 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-03-13 | 2013-04-19 14:29 | 2013-04-19 | AGREEMENT STATE REPORT - STUCK SHUTTER ON KAY-RAY DENSITY METER The following was received by the State of Louisiana via fax: "Louisiana Dept. of Environmental Quality was notified on April 2, 2013, by a written letter from Cornerstone Chemical Company. A Kay-Ray Cs-137 50 mCi (decay corrected to 31 mCi) density meter, model number 7062BP, serial number S93C1706 was removed in order to service a pipe during a turnaround activity. After the device was removed, the shutter was discovered to be stuck in the half closed position and would not completely close. An employee who carried the density meter was calculated to receive a radiation exposure of 1.8 mR total dose. BBP Sales serviced the shutter, reinstalled the density gauge, performed a leak test, and installation survey. Notification was given to all Cornerstone Chemical maintenance planning personnel and supervision in the acid unit to contact the RSO for any activities concerning radiation sources. All activities are to be conducted by licensed contractors. "The general license registration is in the stages of being modified to a specific license." State event report number: LA-13-0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-04-29
48945 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-18 23:12 | 2013-04-19 12:30 | 2013-04-19 | INADVERTENT ACTIVATION OF AN EMERGENCY SIREN "On 4/18/13 at 2312 EDT, Emergency Siren 955 inadvertently actuated for approximately 5 minutes. The cause of the actuation is under investigation but believed to be due to rain water intrusion. The siren stopped on its own, and was subsequently disconnected by the siren vendor to prevent further erroneous actuation. The siren remains out service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ). There are a total of 70 sirens. "The siren is located in a state park not currently inhabited by campers; due to the siren location and time of activation the impact on the surrounding population was minimal. The event was therefore determined to not be reportable. "A subsequent review of the event, considering communications made between Cook Nuclear Plant and the Berrien County 911 Dispatch Center, as well as recent industry operating experience of similar events, was performed; its conclusion was to conservatively make a report under 10 CFR 50.72(b)(2)(xi). "The licensee has notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-19
48944 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2013-04-17 | 2013-04-19 09:05 | 2013-04-19 | AGREEMENT STATE REPORT - SHUTTER MECHANISM FAILURE ON A FIXED GAUGE The following information was received from the State of Iowa via fax: "On April 18, 2013, the licensee (3M Company - Ames) reported to the Iowa Department of Public Health that a shutter mechanism had failed to close on a fixed gauge at their Ames, Iowa facility. The device is a Thermo EGS Gauging, model ASC-185, serial number KA1527 containing a nominal activity (May 25, 2006) of 1250 millicuries Krypton-85. The licensee's RSO and trained maintenance staff proceeded to troubleshoot the cause of the failure to close. They identified that screws holding the shutter mechanism had become stripped and loose causing the source shutter to not operate properly. The gauge was removed and is now stored in a locked cabinet under the RSO's control. The RSO is currently pursuing the purchase of new screws so that the shutter mechanism can be repaired. Additional corrective actions include a more detailed inspection of the shutter screws during six month inspections." The sealed source (Krypton-85) is manufactured by Isotope Products Lab, S/N NER-588. IA Item Number: IA130003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2013-04-29
48943 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2013-04-18 14:00 | 2013-04-18 21:32 | 2013-04-18 | PIN HOLES LEAKS IDENTIFIED IN HIGH PRESSURE CORE SPRAY SYSTEM "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), 'Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident', and also 10CFR50.72(b)(3)(ii)(A), 'Degraded or Unanalyzed Condition'. At 1400 [CDT] on 4/18/13, 3 pin hole leaks were identified in the Unit 2 High Pressure Core Spray System (HPCS) minimum flow valve flow line, between the minimum flow valve and the Primary Containment Suppression Pool in the Reactor Building Raceway. The leak is approximately ¢ gallon per minute. This could have prevented the Primary Containment, a single train safety system, from performing its design function, and also results in the nuclear power plant, including its principal safety barriers, being seriously degraded. In addition, the Unit 2 HPCS System, a single train system, has been declared inoperable, and has also lost function due to the minimum flow line leak. This is reportable as an 8 hour ENS [Event Notification System] notification. "At the time the leak was identified, Both LaSalle Unit 1 and 2 are in Hot Shutdown, following a loss of Offsite Power on 4/17/13. Unit 2 will remain shut down until repairs are made to the Unit 2 HPCS minimum flow line leak." Unit 2 will be placed in Mode 4 and remain in Mode 4 until repairs are complete. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-04-18
48942 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2013-03-16 | 2013-04-18 17:07 | 2013-08-07 | AGREEMENT STATE REPORT - MALFUNCTIONING GAUGE SHUTTER The following report was received via email: "The licensee RSO [Radiation Safety Officer] notified [Mississippi] DRH [Division of Radiological Health] of malfunctioning gauge shutter discovered upon leak testing on 3/16/13. The gauge is a Kay Ray 7700 J, Source Model Kay Ray 7064 and is mounted on functioning pipe and is currently in use, however, the shutter will not close. The [licensee] RSO, stated a technician was on-site to deliver an estimate to be received by the following week. Until then, the licensee stated the gauge would continue to be used as usual. "Update: On 4/5/13, [the license RSO] called to notify [Mississippi] DRH the gauge is still being used, he has received the quote for the repair, and is waiting for the appointment scheduled by the technician (3 weeks from this date). "Update: Formal report received by SABIC on 4/17/13 which includes description of the incident, as stated above. At this time, [the licensee RSO] is still awaiting the appointment for repair or replacement of the gauge." Mississippi Report #: MS-13001 * * * UPDATE FROM BRANDY FRAISER TO PETE SNYDER AT 1630 EDT ON 8/7/13 * * * On 5/29/13, [the licensee Radiation Safety Officer] emailed a notification to [Mississippi] DRH [Division of Radiological Health] via email that the shutter on the gauge in question has been repaired and is operating properly. Notified R4DO (Vasquez) and FSME Event Resource (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2013-04-26
48941 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-18 11:20 | 2013-04-18 13:52 | 2013-04-18 | LOSS OF ASSESSMENT CAPABILITY DUE TO FAILURE OF A RADIATION MONITOR BYPASS PUMP "System(s) Affected: Site Stack Radiation Monitor, RM-8169 "Causes: Failure of radiation monitor bypass pump. "Effect of Event on Plant: Loss of assessment capabilities from radiation monitor. "Actions taken or planned: Repair of radiation monitor. "Additional information: Radiation monitor inoperable at 2030 [EDT] on 4/16/13. Further review identified the reportable condition." The licensee informed the State of Connecticut, Waterford dispatch, and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-18
48940 | -1 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2013-04-17 16:00 | 2013-04-17 23:19 | 2013-06-12 | DEGRADED CONDITION DUE TO SUSPECTED VALVE BODY LEAKAGE "On April 17, 2013 at 1600 [EDT], while performing a valve inspection/repair of the Unit 2 'A' Reactor Coolant Loop Fill Valve (2- RC-HCV-2556A), the as-found inspection results identified evidence of a suspected flaw causing leakage from the valve body to the threads of a stud housing of the valve. This valve is a 2 [inch] 316 SS [Stainless Steel] cast ASME XI (Class 1) 1500 psi valve body of a globe style design. Due to this design and the installed orientation, the RCS pressure medium fills the upper portion of the valve bonnet where the leak is located during normal plant operations. Therefore, this leakage would be considered pressure boundary leakage. 2-RC-HCV-2556A is currently isolated from the Reactor Vessel and is at atmospheric pressure. "This inspection was performed in response to dry discolored boric acid identified during the normal operating pressure boric acid accumulation inspection procedure during the Spring 2013 Unit 2 refueling outage shutdown. An engineering evaluation of the suspected defect will be performed and corrective actions implemented. "This event is reportable in accordance to 10CFR50.72(b)(3)(ii)(A) for, 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded'." The licensee notified the NRC Resident Inspector and local County Commissioners. * * * RETRACTION FROM BOB PAGE TO CHARLES TEAL ON 6/12/13 AT 1109 EDT * * * "Event Number 48940 was made on April 17, 2013 in accordance with 10CFR50.72(b)(3)(ii)(A) to document a suspected flaw resulting in RCS pressure boundary leakage on Unit 2 'A' Reactor Coolant Loop Fill Valve (2-RC-HCV-2556A). North Anna Power Station is retracting this notification following completion of a cause analysis and metallurgical examination. The analysis determined that the valve leakage was due to the body-to-bonnet gasket joint. The original valve body was especially susceptible to gasket creep, which lead to a loss of sufficient sealing stress. This resulted in body-to-bonnet leakage, not a through-wall leak. Based on this analysis, the reporting requirements of 10CFR50.72(b)(3)(ii)(A) are not met and this event report is being retracted. "The licensee has notified the NRC Resident Inspector." Notified R2DO (Ehrhardt). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-04-17
48939 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2013-04-17 15:11 | 2013-04-17 16:59 | 2013-04-21 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER FROM A LIGHTNING STRIKE "LaSalle Unit 1 and LaSalle Unit 2 have both experienced an automatic reactor scram, in conjunction with a loss of offsite power. This was caused by an apparent lightning strike in the main 345kV/138kV switchyard during a thunderstorm. 138kV line 0112 has been inspected in the field, and heavy damage has been noted on the insulators on two of the three phases on a line lightning arrestor line side. "The plant systems have all responded as expected. All five diesel generators started, and have loaded on to their respective buses as designed. All rods went full in on both units during the respective scrams. HPCS [High Pressure Core Spray] system was started on each unit and automatically aligned for injection for initial level control." The MSIVs [Main Steam Isolation Valves] are shut on both units with decay heat being removed via the safety relief valves. Suppression pool cooling is in progress. The licensee will notify the NRC Resident Inspector and has notified the State. Notified DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE FROM DON PUCKETT TO VINCE KLCO AT 2113 EDT ON 4/17/2013 * * * "In addition to information [previously provided], LaSalle Unit 2 received a high drywell pressure signal [1.77 psig] due to loss of containment cooling from the loss of power. At the time of this high drywell pressure signal, high pressure core spray pump and 2B residual heat removal [RHR] pump was already in operation, the low pressure core spray system and 2A residual heat removal system was secured and [placed] in pull to lock. When the signal was satisfied the ECCS [Emergency Core Cooling Systems] signal was processed but only the 2C RHR pump would have started. In this case, the 2C RHR pump tripped when the signal was received. There is no evidence of reactor coolant leakage. There was no additional ECCS systems discharging into the RCS [Reactor Coolant System]. As [initially stated], level was controlled using High Pressure Core Spray and level control is now being maintained using the Reactor Core Isolation Cooling [RCIC] systems. The 2C RHR pump trip is under investigation. "Due to the initial loss of offsite power for both Unit 1 and Unit 2 reported at 1511 [CDT], multiple containment isolation valves isolated and closed as expected. Once initial containment isolations were verified, two Unit 2 primary containment vent and purge valves were opened to vent the Unit 2 containment. Once Unit Two containment pressure reached 1.77 [psig], these two vent valves isolated as expected. "Due to the loss of offsite power, the Station Vent Stack Wide Range Gas Monitor (WRGM) and the Standby Gas Treatment Wide Range Gas Monitor (VGWRGM) also lost power. Manual sampling has been implemented and power is restored to the VGWRGM, however the VGWRGM has not been declared operable yet. Normal radiation levels have been reported from the manual sampling. [This is being reported in accordance with 10CFR50.72(b)(3)(xiii).]" The licensee notified the NRC Resident Inspector and the State of Illinois. Notified the R3 IRC, NRR EO(Skeen), IRD MOC (Grant). * * * UPDATE AT 0057 EDT ON 04/18/13 FROM MIKE LAWRENCE TO S. SANDIN * * * "After the Unit 2 primary containment vent and purge system isolated on the Unit 2 containment High Pressure signal, Venting of the Unit 1 primary containment was commenced. At 2005 CDT, Unit 1 primary containment pressure reached the Group 2 primary containment isolation system setpoint (1.77 PSIG) causing the primary containment vent and purge valves being used to vent the Unit 1 containment to isolate. Unit 1 primary containment venting was being performed through the Standby Gas Treatment system which is a filtered system. "In addition to the primary containment isolation signal on high drywell pressure, an ECCS initiation on high drywell pressure also occurred. The ECCS signal resulted in an auto start of the 1C RHR system. The 1B RHR system was already running in suppression pool cooling mode. 1A RHR and LPCS had been secured to prevent overloading the common diesel generator for division 1. The common diesel generator supplies both Unit 1 and Unit 2 division 1 ESF busses." The licensee informed the NRC Resident Inspector. Notified NRR EO (Skeen), IRD MOC (Grant) and R3IRC (Louden). * * * UPDATE AT 0947 EDT ON 04/18/13 FROM JUSTIN FREEMAN TO PETE SNYDER * * * "LaSalle has terminated the unusual event which was initiated at 1511 on 4/17/13 and reported under EN 48939. This unusual event has been terminated based on meeting the following established criteria. This report is being made in accordance with 10CFR50.72.(c)(1)(iii). "1) Off-site power has been restored to all ESF busses "2) Fuel Pool Cooling has been restored on both units "3) Primary Containment Chillers have been restored on both units "4) Drywell pressure is less than ECCS initiation setpoint "5) ECCS signals cleared to allow diesels to be placed in stand by "Recovery of remaining plant systems will be managed through the Outage Control Center (OCC)." The licensee informed the NRC Resident Inspector. Notified R3DO (Orth), NRR EO (Chernoff), IRD (Grant), DHS, FEMA, USDA, HHS, DOE, NICC, EPA, and Nuclear SSA via email. * * * UPDATE AT 1711 EDT ON 4/21/2013 FROM GREG LECHTENBERG TO MARK ABRAMOVITZ * * * "In addition to the 10 CFR 50.72 Sections initially identified, the Loss of Offsite Power was also reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of systems needed mitigate the consequences of an accident. This event is considered a safety system functional failure for both Units 1 and 2." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Orth). | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | EMERGENCY DECLARED | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2013-04-17
48938 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  | 1000 KW TRIGA MARK III | 2013-04-16 17:01 | 2013-04-17 15:53 | 2013-04-17 | TEST REACTOR EXCEEDED LICENSED POWER LIMIT DURING A SCRAM The following information was excerpted from an email from the licensee: On April 16, 2013 at 1701 EDT, the research test reactor automatically shutdown from 100% power (1 MW) due to a valid high power condition. The duty Senior Reactor Operator removed a timed irradiation sample from the core that added positive reactivity. Both the digital (non-safety system) and the analog safety system acted on the high power condition and initiated the shutdown. All systems functioned as designed. The short duration power transient reached a peak power of about 1.3 MW. There was no increase in radiation levels, personnel radiation exposure, or release of radiation from the facility. No emergency event entry criteria were met. The plant was placed in a secured condition and an event review investigation was conducted. The event is (potentially) reportable in that the Maximum Power Level observed during the short duration (< 1 second) transient exceeded the steady state power limit for non-pulse mode operation as described in Technical Specification(TS) 3.1.1 Non-pulse mode operation sub-section b. The maximum power level shall be no greater than 1.1 MW (thermal). The reactor was returned to routine service at approximately 1300 EDT on April 17, 2013. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | PA | NPR | [5 empty] | 0 | 2013-04-17
48937 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2013-04-16 23:23 | 2013-04-17 05:20 | 2013-04-20 | DEGRADED FLOW IN EMERGENCY SERVICE WATER SYSTEM 'A' "The Perry Nuclear Power Plant is reporting an event or condition pursuant to 10 CFR 50.72(b)(3)(v)(D). "On April 16, 2013, at 2323 EDT, it was identified that Emergency Service Water (ESW) pump 'A' was inoperable due to an inability to maintain minimum flow requirements. As a result, ESW 'A' and the supported Division 1 Emergency Diesel Generator (EDG) were declared inoperable. Coincident with this discovery, a test of the Division 2 emergency systems was in progress with the associated ESW 'B' pump and Division 2 EDG inoperable. Division 2 EDG was available to support the Shutdown Defense In-Depth Strategy. Division 3 EDG was operable and could supply High Pressure Core Spray system injection, if needed. "Both EDGs were inoperable simultaneously and Technical Specification 3.8.2 'AC Sources-Shutdown' was entered and required actions taken. These actions included immediately suspending core alterations and immediately initiating actions to restore the required EDG. The test of Division 2 emergency systems was suspended and ESW 'B' and the Division 2 EDG were restored to operable status at 0135 EDT on April 17, 2013. "The failure of ESW 'A' minimum flow is currently under investigation. "The Resident Inspector has been notified." * * * RETRACTION FROM JOHN PELCIC TO CHARLES TEAL ON 4/20/13 AT 1355 EDT * * * "Engineering personnel performed an immediate investigation of the ESW 'A' minimum flow condition. The investigation results showed that the ESW 'A' pump flow exceeded the minimum flow requirement to protect the ESW 'A' system. Therefore, continued operation of ESW 'A' was acceptable and the minimum flow condition originally reported did not cause the Division 1 Emergency Diesel Generator to be inoperable. "The condition would not have prevented the fulfillment of a safety function to mitigate the consequences of an accident. Reporting is not required under 10 CFR 50.72(b)(3)(v)(D) and this notification is retracted. "The NRC Resident Inspector has been notified." Notified R3DO (Orth). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-17
48936 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-04-16 21:42 | 2013-04-17 02:11 | 2013-04-17 | SPECIFIED SYSTEM ACTUATION DURING TURBINE STOP VALVE LOGIC TESTING WHILE SHUTDOWN "During outage main turbine stop valve RPS logic surveillance testing, an invalid RPS actuation occurred due to an error in executing main turbine surveillance testing procedures. A Turbine Stop Valve closure RPS signal occurred due to an error in the restoration sequence of restoring the RPS bypass signal and a subsequent manual trip of the main turbine. This resulted in a full scram and a trip of both reactor recirculation pumps. "The site post-scram response procedure was entered, which required that the mode switch be placed in the locked SHUTDOWN position. This caused an expected but valid RPS actuation. "No control rod motion occurred due to all control rods were inserted at the time of the invalid RPS actuation and subsequent valid RPS actuation." The license has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-04-17
48935 | -1 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-04-16 22:47 | 2013-04-17 01:16 | 2013-04-18 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED TO OFFSITE MEDICAL FACILITY "Contract worker suffered a non-occupational medical emergency while working inside the Unit 2 Containment Building (105' elevation). The worker was working in a contaminated area when the event occurred. He was transported to Southeast Alabama Medical Center via ambulance. The worker is potentially contaminated. Health Physics provided escort in the ambulance. "Farley Nuclear Plant [was] notified by Health Physics on 4/17/13 at 0028 [CDT] that [the] individual was surveyed and no contamination was found." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM JOSH CARROLL TO JOHN SHOEMAKER ON 4/18/13 AT 2243 EDT * * * Farley Nuclear Plant is retracting this notification based on the following additional information not available at the time of the notification: Health Physics personnel have completed surveys that determined that the contract worker, ambulance, and hospital are free of contamination. The initial report was made based on the individual being potentially contaminated due to radioactive surveying being deferred to allow prompt medical attention. Based on the subsequent determination that the individual was not contaminated the reporting requirements of 10CFR50.72(b)(3)(xii) are not met and this event report is being retracted. The licensee will notify the NRC Resident Inspector. Notified R2DO (Vias). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2013-04-17
48934 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-04-16 21:30 | 2013-04-16 23:50 | 2013-04-17 | FITNESS FOR DUTY REPORT - LICENSED OPERATOR HAD A CONFIRMED POSITIVE FOR ALCOHOL A licensed operator had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's plant access has been revoked. The licensee informed the NRC Resident Inspector and the State of Connecticut. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 26.719 |  |  |  | 0 | 2013-04-17
48933 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-04-15 | 2013-04-16 17:45 | 2013-04-19 | AGREEMENT STATE REPORT - CONTAMINATED RADIOGRAPHY CAMERA The State of Oklahoma received a report from the licensee, that a new SPEC-150 Radiographer camera was giving an unexpected high radiation reading of 20 mrem. The State responded to the licensee's location to investigate. Contamination was detected on the exterior of the camera, guide tube, and cable. Contamination was also detected on the truck used to transport the camera. The camera had been used at a natural gas plant in Wheeling, Texas. There was no apparent damage to the camera and efforts to decontaminate the camera were unsuccessful. The licensee has placed the camera in a container and stored it in a secure location. It is believed the camera may have a manufacturer defect. The manufacturer has been notified. The truck has been decontaminated. The State of Texas has been notified and they will determine if any contamination is present at the natural gas plant in Wheeling, Texas. The radiographer and his assistant were checked for contamination and none was found and no internal exposure is expected. The radiographer's dosimeter indicated 10 mrem and the assistant's dosimeter indicated 0 mrem. Both radiographer's film badges have been sent out for processing. The States of Oklahoma and Texas will continue their investigations and provide additional information when it is available. * * * UPDATE AT 1557 EDT ON 04/18/13 FROM KEVIN SAMPSON TO JOHN SHOEMAKER VIA EMAIL * * * The following update was received from the State of Oklahoma by email: "On Monday afternoon, April 15, 2013, radiographers of Hi-Tech Testing Service, (Oklahoma license OK-32150-01 located in Seiling, OK) were working at a natural gas plant near Wheeler, Texas. After doing their survey following retracting the source, they noted high levels of radiation coming from the right rear truck bed. The camera was not nearby, and there was no obvious source for the radiation. They contacted their RSO [Radiation Safety Officer] and after ensuring that the source was properly retracted and in the camera, and all known sources of radiation were accounted for, they still had the anomalous high reading. The RSO instructed them to return to the office. After some work, the RSO was able to remove the contamination with duct tape. He reported that using an ND-2000 radiation meter in near contact, the duct tape registered approximately 1 R/hour [Rem] (1000 mrem/hour). He reported that the bed was now showing no radiation, and that the radiography camera and associated equipment were showing no radiation. He secured the contaminated tape in his vault, and advised Oklahoma DEQ [Department of Environmental Quality] of this on Monday evening. On Tuesday [4/16/13] morning, DEQ inspectors arrived at the facility to investigate. As a courtesy, we [Oklahoma DEQ] had advised Texas DSHS [Department of State Health Services] radiation control of the report, and possible contamination concerns at the work site in Texas. "[Oklahoma] DEQ inspectors checked the area and equipment, including the radiography camera and associated equipment, the radiography truck used during the event, and the shop area where the camera and equipment had been worked on by the RSO. Contamination was found on the bed of the truck in a location where radiographers reportedly assemble and disassemble the camera and associated equipment. Removable contamination was found on the collimator that had been used during the exposures. Radiation was measured from the guide tube and from the crank cable. The radiation in the crank cable extended for several feet from the end of the cable that attaches to the radiography camera, consistent with contamination of the cable from contact with the (presumably contaminated) interior of the guide tube. Other than the bed of the truck, no contamination of the truck was found in this survey. The exterior of the camera was wiped, but no removable contamination was found. Analysis with a portable gamma spec showed that all contamination was Ir-192. Measured radiation levels in near contact on the equipment and truck varied, but were in the hundreds of microR/hour, with the highest being about 800 microR/hour on the collimator. It is important to note that none of this contamination was detectable with the radiography company's instrument, an ND-2000. "Separately, we [Oklahoma DEQ] verified the licensee RSO's measurements of the contaminated duct tape that he had used to remove the bulk of the contamination from the truck bed. The tape was under lead shielding in an ammo box that had been used as a transport container, and we did not remove the tape from the container, but got readings in the hundreds of milliR/hour, consistent with the one R in contact figure reported by the company RSO. "The radiographers involved live a long distance from the licensee office and were not available to be surveyed or interviewed in person while we were on site. The licensee reports this was the first time that the camera, guide tube, and crank cable had been used (see dates below). We are told that this equipment had been used only together, and had not been used with other equipment, and that it had only been used at the Wheeler, TX. job site. "[Oklahoma] DEQ staff worked with the company RSO to remove the remaining contamination from the bed of the pickup truck. Contamination appeared to be in discrete spots on the bed, and removal appeared to be an all or nothing matter Attempts to remove the contamination with duct tape would fail repeatedly, then after another attempt it appeared that all contamination associated with that spot had been removed. Some of the people participating claimed to be able to see a small dark spot on the tape after the successful removal, consistent with a small chip of Ir-192 remaining on the tape. When we concluded our work, all levels we could find on the truck bed were 10 microR/hour or less in near contact. "The contaminated guide tube, crank cable, collimator, and all wastes associated with the decontamination efforts were placed in plastic bags where possible, placed in a large trash can, and secured in the licensee's vault for removal. The work bay where all surveys had taken place was surveyed and found to be uncontaminated. "[Oklahoma] DEQ staff and the licensee RSO called SPEC, manufacturer and distributor of the equipment, and advised them of the situation. DEQ requested that SPEC arrange for packaging and shipment of all contaminated material back to SPEC. SPEC representatives were at the licensee facility on Wednesday, April 17, 2013 and packaged all contaminated material and equipment for shipment to SPEC. To our knowledge, the actual shipment has not occurred yet. We were advised verbally that the SPEC staff found very low (no further information is available at this time) contamination on the truck, and that they surveyed the two radiographers and the clothes they had worn during the incident, and found low (no further information available at this time) contamination on one radiographer's shirt sleeve. The radiographer estimates he wore the shirt for about 13 hours on the day of the incident, and had not worn it since. SPEC has taken custody of the contaminated shirt. We were told that SPEC personnel surveyed the homes and privately-owned vehicles of the radiographers last night and found no contamination. We are expecting a written report from SPEC. "The tentative opinion of the [Oklahoma] DEQ inspectors and the licensee RSO is that our findings are consistent with the presence of a limited number of particles of Ir-192 that had been present on the outside of the source. How the contamination came to be there is unclear. However present, it seems likely that the contamination was deposited inside the guide tube during the initial exposures, and some contamination fell out of the guide tube during assembly and disassembly of the camera. The 'all-or-nothing' removal of contamination from each area suggests that the contamination was in the form of relatively sizable chips, not in the form of a very fine particulate. "[Oklahoma] DEQ will continue to investigate. We have cooperated with Texas [DSHS] staff as described above, and have informed the state of Louisiana. We were told that Texas staff visited the job site in Texas, and were guided to a single location of use by facility staff, where Texas staff found no contamination. In interviews with the radiographers, Oklahoma DEQ staff were told by the radiographers that radiography had been conducted at several sites in the plant over several days. We informed Texas of this discrepancy and the possibility of additional sites that might need to be checked for contamination. We understand that Texas staff are meeting at the job site this afternoon with the licensee RSO, one of the radiographers, and SPEC staff to check for contamination at all sites where radiography was performed. "This is an interim report based on initial investigations and phone conversations with many of the actors, and has not undergone substantial review. More information will be provided later of further actions, or of any corrections or clarifications needed. "Camera was used for shooting at the job site from April 8-12, 2013 and on April 15, 2013. "Areas of interest that appear to [Oklahoma] DEQ at this time include: "1) The licensee RSO was not able to detect contamination remaining on the truck bed, and had never identified any contamination on the associated equipment. [Oklahoma] DEQ found contamination at levels of definite concern present on both of these. The RSO was using an NDS-2000, a very common industrial radiography survey meter that is optimized for measuring high levels of radiation. Based on this experience, this model (and possibly similar instruments optimized for radiographer use) may not be sensitive enough to reliably detect contamination of this sort. [Oklahoma] DEQ was readily able to detect the contamination with a MicroR meter, portable gamma spec, and with a pancake probe. "2) How the source came to be contaminated with Iridium is of interest, especially how the source was shipped with external contamination present, if that was indeed the case." * * * UPDATE FROM KEVIN SAMPSON TO CHARLES TEAL ON 4/19/13 AT 1208 EDT * * * The following update was received from the State of Oklahoma via email: "On Thursday afternoon, Texas radiation control and SPEC personnel met with the licensee RSO and one of the radiographers involved in the incident at the Wheeler, TX job site. We are told they did surveys of all locations where radiography had been performed, and no contamination was detected." Notified R4DO (Drake) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2013-04-24
48932 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-04-16 16:25 | 2013-04-16 17:15 | 2013-06-04 | POTENTIAL CABLE SIZE AND BREAKER MISMATCH "During investigation of a documentation discrepancy, a potential cable size and breaker mismatch was identified to exist in a non-safety related DC panel. Initial evaluation has shown that the cable may heat and be potentially damaged if exposed to a 'smart' high impedance fault for an extended period. This discovered condition has not been previously analyzed for NFPA [National Fire Protection Association] 805 common enclosure circuit coordination. "Fire watches were established as a compensatory measure immediately following identification of the issue on April 8, 2013. An initial review of fire protection analysis was completed on April 16, 2013. Fire watches remain in place until a modification which will restore coordination is complete. "The licensee notified the NRC Resident Inspector." * * * RETRACTION FROM JOHN CAVES TO CHARLES TEAL AT 1400 EDT ON 6/4/13 * * * "An analysis demonstrated that adjacent cables in the common enclosure would not be damaged, therefore, the condition does not significantly degrade plant safety." The licensee has notified the NRC Resident Inspector. Notified R2DO (McCoy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-04-16
48931 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-04-16 | 2013-04-16 16:05 | 2013-04-18 | AGREEMENT STATE REPORT - TRUCK ACCIDENT INVOLVING A FIXED DENSITY GAUGE The following information was provided by facsimile: "On April 16, 2013, the Agency [Texas Department of State Health Services] was notified that one of the licensee's trucks had had a blowout on one of its tires which caused the vehicle to roll. The driver was killed in the accident. On the truck is a densitometer which includes a Thermo-Fisher Scientific Model 5192 fixed gauge that contains 200 millicuries of Cesium-137 (original activity). These devices are a USA DOT 7A Type A container. The licensee reported that the gauge is still [within] of the truck--there is no indication of radiation leakage or exposures to any individual. The licensee's Radiation Safety Officer is enroute and will make necessary radiation surveys and conduct an investigation. Local law enforcement responded to the accident. More information will be provided as it is obtained, per SA-300." Texas State Report # I-9067 * * * RETRACTION FROM KAREN BLANCHARD TO JOHN SHOEMAKER ON 04/18/13 AT 1708 EDT * * * The following retraction was received via email: "This event does not meet the reporting criteria referenced in SA-300, specifically 49 CFR171.15 (b)(1) and (2), in that the individual's death in this incident was not the 'direct result of hazardous materials' as stated in the 171.15(b)(1)." Notified R4DO (Drake), NMSS (Benner), and FSME EVENTS Resources via email only. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-04-24
48930 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2013-03-25 | 2013-04-16 13:32 | 2013-04-16 | AGREEMENT STATE REPORT - RADIOACTIVE SEED MIGRATED DEEPER INTO TISSUE AND WAS NOT REMOVED The following information was received by facsimile: "A patient for axillary node dissection with radioactive seed localization had an 8.33MBq 123 I [Iodine] seed placed at tumor site under ultrasound guidance by radiologist. The surgeon successfully removed the tumor and lymph node, however the seed had migrated deeper into tissue and was not removed. The surgeon determined that the new seed location prevented safe extraction due to scarring from previous node removal, mastectomy and reconstructive, surgery. NYS DOH [The New York State Department of Health] received verbal notice within 24 hours and written notice within 15 days. The patient, referring physician, medical oncologist, and radiologist have all been notified. A localized dose at 0.5 cm from the seed of 22.9Gy was calculated, negligible dose at 6 cm. As a corrective action the facility will no longer use radioactive seed localization for axillary node lesions. [Licensee] Policy updates and staff notifications are to be evaluated during the next routine inspection." Event Report Identification Number: NY-13-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2013-04-24
48929 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-04-16 09:14 | 2013-04-16 11:32 | 2013-04-16 | INADVERTENT EMERGENCY SIREN ACTIVATION DUE TO PERSONNEL ERROR "On Tuesday April 16, 2013 at approximately 0914 EDT, the Oswego County Emergency Management Office notified Nine Mile Point via the Radiological Emergency Communications System RECS line of an inadvertent activation of Siren 17. The activation occurred during a normally scheduled Oswego County bi weekly test and was due to a human performance error. Activation occurred at approximately 0845 EDT and lasted for approximately 2 minutes. "This notification is applicable to both NMP Unit 1 and 2 as well as the James A Fitzpatrick station, a separate notification will be communicated from JAF station. The Oswego County Emergency Management Office has issued a press release and the NRC resident inspector has been notified." The licensee will also notify the State. See related EN #48927. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-16
48928 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-04-16 04:14 | 2013-04-16 11:20 | 2013-04-16 | TECHNICAL SUPPORT CENTER (TSC) UNAVAILABLE DUE TO PREPLANNED MAINTENANCE "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, based on LOSS of ASSESSMENT capability. This is a non-emergency notification. This condition does not affect the health and safety of the public or the operation of the facility. At approximately 0414 [EDT] on April 16, 2013, preplanned maintenance will be performed that will affect the Technical Support Center (TSC) ventilation system. The scope of the maintenance is to inspect and clean all Air Handler Units, Fans, and Outside Air Condensing Units that support TSC Ventilation. This maintenance is scheduled to be performed and completed within approximately 50 hours. "TSC functionality requires all occupied areas of the TSC be maintained between 60.8 degrees F and 82.4 degrees F. Actual TSC area temperatures have been verified to be less than 78 degrees F. If an emergency condition should occur, the ventilation system will be restored, but potentially not within the time required for activation of the TSC. If the facility were activated with full staff, temperatures could rise above the 82.4 degrees F limit. Should the TSC need to be activated for an event, we have compensatory measures which would include relocating the TSC to the Alternate Emergency Facility per PEP-240. This decision would be based on the existing event conditions and coordinated with the Emergency Response Manager, Main Control Room - Site Emergency Coordinator, and Radiological Control Manager. The Alternate TSC has been verified to have electrical power, ventilation, and communication capability. The Technical Support Center - Site Emergency Coordinator has been notified. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-16
48927 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-04-16 08:45 | 2013-04-16 10:17 | 2013-04-16 | INADVERTENT EMERGENCY SIREN ACTIVATION DURING WEEKLY TESTING DUE TO PERSONNEL ERROR "The purpose of this report is to provide a telephone notification under 10CFR50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of the Oswego County emergency notification sirens at approximately 0845 [EDT] on 4/16/13. Oswego County was performing routine weekly testing and siren #17 was inadvertently actuated for approximately 2 minutes. "The Oswego County Emergency Management Office issued a News Release identifying the inadvertent actuation of the emergency siren. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-16
48926 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-04-16 00:37 | 2013-04-16 08:55 | 2013-04-16 | LOSS OF MAIN CONTROL BOARD ANNUNCIATION DURING LOSS-OF-OFFSITE-POWER TEST "This is an 8-hour report of a loss of emergency preparedness capabilities as required by 10CFR50.72(b)(3)(xiii). "At 0037 CDT on 4/16/13, during the performance of an 'A' train loss-of-offsite-power test per procedure FNP-2-STP-80.14, Farley Unit 2 experienced a complete loss of main control board annunciation. Emergency Power Board annunciators are unaffected. No emergency action level criteria have been exceeded as a result of the loss of annunciation, however, annunciators normally relied upon for emergency assessment are not functional. Troubleshooting to identify the cause of the loss of annunciation is in progress. No estimate for restoring annunciator power is currently available. Compensatory measures for critical parameter monitoring have been established and implemented. Unit 2 plant conditions remain stable in mode 5. Unit 1 is unaffected by this event. There has been no release of radioactivity to the environment. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DARRIN GARD TO CHARLES TEAL AT 1444 EDT ON 4/16/13 * * * The Unit 2 main control room annunciators were restored at 0907 EDT on 4/16/13. The cause of the failure was determined to be a relay in the annunciator power supply circuit. The licensee will notify the NRC Resident Inspector. Notified R2DO (Vias). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-16
48925 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-04-15 10:18 | 2013-04-15 12:27 | 2013-04-15 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT ACTIVATION OF A SIREN "At approximately 1018 CDT on April 15, 2013, the licensee was notified that the Pierce County Sheriff Dispatch reported an inadvertent activation of an emergency siren (P-43), in Pierce County, WI. The cause of the siren activation is unknown. The siren was deactivated at 1022 CDT after sounding for approximately 28 minutes. The siren vendor (NELCOM) has been contacted to repair the siren. The siren remains out of service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ). "NRC Resident has been informed [by the licensee]." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-15
48924 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-04-14 22:16 | 2013-04-15 06:04 | 2013-06-13 | PRIMARY CONTAINMENT AIR LOCK FAILED INTEGRATED LEAK RATE TEST "On Sunday, April 14, 2013 at 2216 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in Start-up, the turbine generator previously removed from service, and the reactor sub-critical on Intermediate Range Monitors Range 2 and lowering, the PNPS Containment Personnel Air Lock failed integrated air lock testing as required by TS 4.7.A.2. "10CFR50 Appendix J requires that primary reactor containment meet certain leakage rate testing requirements. These test requirements ensure that 1) Leakage through the containment or systems and components penetrating the containment do not exceed allowable leakage rates specified in Technical Specifications and 2) The integrity of the containment structure is maintained during its service life. The test requirements include local leakage rate testing of containment air locks. The test criteria establishes a limit of less than or equal to 10.525 SLM, actual leakage was 16.7 SLM. "PNPS was in the process of shutting down for a scheduled Refueling Outage during the scheduled testing. "This event had no impact on the health and/or safety of the public. "The USNRC Resident Inspector will be notified. "This 8-hour notification is being made in accordance with 10CFR50.72(b)(3)(v)(c)." * * * RETRACTION FROM BOB O'NEILL TO PETE SNYDER AT 1700 ON 6/13/13 * * * "Subsequent investigation of the test failure determined that an o-ring in the Airlock Inner Pressure Equalizing Device (PED) was not properly seated resulting in exceeding the established leakage rate limit. Leakage was not observed on the Airlock Outer Boundary Surface. Thus, with the Airlock Outer Boundary Surface intact, the Airlock was capable of performing the safety function to control the release of radioactive material. "In addition, even with the Airlock leakage of 16.7 standard liters per minute (SLM), the Technical Specification Primary Containment As-Found Minimum Pathway Leakage Limit of 0.6 La for all Type B and C leakage tests was not exceeded. "Therefore, the initial 50.72(b)(3)(v)(C) report is being retracted." The licensee will notify the NRC Resident Inspector. Notified R1DO (Dentel). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-04-15
48923 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-04-14 22:17 | 2013-04-15 02:01 | 2013-04-15 | SPECIFIED SYSTEM ACTUATIONS WHILE SHUTTING DOWN "On Sunday, April 14, 2013 at 2217 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in Start-up, the turbine generator previously removed from service, and the reactor sub-critical on Intermediate Range Monitors Range 2 and lowering, a manual reactor scram was inserted due to reactor pressure lowering beyond established control bands. At the time of the manual reactor scram PNPS was conducting a planned reactor shutdown to commence refueling outage (RFO) -19. All control rods fully inserted and Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All plant systems responded as designed. Off-site power was unaffected and was supplied by the start-up transformer (normal power supply for refuel and reactor shutdown operations). "The Main Steam Isolation Valves (MSIV) were manually closed to terminate the reactor pressure reduction and the High Pressure Coolant Injection (HPCI) system was manually started in the reactor pressure control mode. The Reactor Protection System (RPS) was reset as were the reactor building and reactor water clean-up system isolation signals. Currently, the plant cooldown is continuing with the HPCI system in pressure control and reactor water level being maintained within normal bands with the condensate and feedwater system. The cause of the lowering reactor pressure has not been determined and remains under review. "This event had no impact on the health and/or safety of the public. "This 8-hour notification is being made in accordance with 10 CFR 50.72 (b)(3)(iv)(A)." The NRC Senior Resident Inspector has been notified. The licensee will also be notifying state authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-04-15
48922 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-14 14:00 | 2013-04-14 13:47 | 2013-04-17 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 1400 EDT on Sunday, April 14, 2013, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions, the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 1400 EDT on Wednesday, April 17, 2013. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM GREGORY KANDA TO CHARLES TEAL AT 1456 EDT ON 4/17/13 * * * "The Technical Support Center (TSC) air conditioning and filtration systems have been returned to service following maintenance. The TSC is fully functional. "The NRC Resident Inspector has been notified. " Notified R3DO (Orth). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-14
48921 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2013-04-14 06:20 | 2013-04-14 13:24 | 2013-04-14 | CONTAINMENT SPRAY CHEMICAL ADDITION FLOW PATH ISOLATED "At 0620 CDT on 4/14/13, the Unit 1 Sodium Hydroxide Tank outlet valve was found to be shut. This valve isolated the flow path for both trains of containment spray chemical addition and resulted in LCO 3.6.7 (Spray Additive System) not being met, which resulted in a condition reportable pursuant to 10 CFR 50.72(b)(3)(v)(D). "At 0651 CDT on 4/14/13, the Unit 1 Sodium Hydroxide Tank outlet valve was restored to its required locked open position and TSAC [Technical Specification Action Conditions] 3.6.7.8 was exited." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-14
48920 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-04-13 11:09 | 2013-04-13 18:21 | 2013-04-13 | SERVICE WATER SYSTEM EFFLUENT LINE NON-FUNCTIONAL "At 1109 CDT on 4/13/13, R-20, Service Water System Effluent Line (Auxiliary Building Service Water Header) was declared non-functional due to low SW [Service Water] sampling flow. R-20 is used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that exceeds the requirements of the Offsite Dose Calculation Manual for an Unusual Event and an Alert, and is therefore, being conservatively reported under 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-13
48919 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-04-12 22:00 | 2013-04-13 03:18 | 2013-04-13 | UNANALYZED CONDITION DUE TO ISOLATED DIFFERENTIAL PRESSURE SWITCH ON SAFETY RELIEF VALVE TAILPIPE "On April 12th, 2013 at 2200 CDT, investigation into the inability to complete a Safety/Relief Valve (S/RV) discharge line excess flow check valve test determined that a relief valve discharge monitoring instrument valve had been inappropriately closed since late June, 2011. The closed valve isolated two differential pressure switches that impact the operation of 'E' Low-Low Set (LLS) valve. The LLS logic and instrumentation were affected by the loss of two 'E' S/RV tailpipe discharge pressure switches which indicate S/RV open status and start two inhibit timers which prevent plant operators or the LLS S/RV logic from immediately re-opening the valve to allow the water leg in the S/RV discharge line to recede. The LLS logic and instrumentation is designed to mitigate the effects of postulated thrust loads on the S/RV discharge lines by preventing subsequent actuations with an elevated water leg in the S/RV discharge line. It also mitigates the effects of postulated pressure loads on the torus shell or suppression pool by preventing multiple actuations in rapid succession of the S/RVs subsequent to their initial actuation. The valve found closed has been returned to its normal open position. This condition resulted in the 'E' S/RV LLS function being aligned contrary to its design configuration and as such is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-04-13
48918 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2013-04-12 10:10 | 2013-04-12 14:45 | 2013-04-12 | UNANALYZED CONDITION - MISSING BACKFLOW PREVENTER "On 4/12/2013 at 1010 EDT, it was determined that a floor drain line between the Turbine Building and Intermediate Building did not have a backflow preventer as expected. Backflow protection is provided to prevent the possible spread of a fire via the drain system. The Turbine Building and the Intermediate Building are considered two different fire areas within the scope of the fire protection program. The discovery of this condition is being reported as an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(B). "In accordance with the Technical Requirements Manual, an hourly fire watch inspection and fire detector operability verification have been established until an equivalent level of protection is provided or until permanent corrective actions can be implemented. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-04-12
48917 | -1 | U.S. ARMY |  |  |  |  | 2013-04-11 13:00 | 2013-04-12 11:46 | 2013-04-24 | TRITIUM LAMP BROKEN DURING MAINTENANCE OF A MORTAR SIGHT On 4/11/13 at 1300 EDT, a 1 Ci tritium lamp was broken during routine maintenance on a M64 mortar sight unit. The sealed source tritium lamp broke when a wrench hit the tritium module. Surveys were conducted, but the results will not be available until next week. Bioassays are being perform on 4 individuals and based on historic records, the RSO expects minimal intake of less than 5 mrem. The device was bagged, tagged and placed in a secure storage area for future disposal. The licensee attempted to notify R3 (McCraw). * * * RETRACTION FROM THOMAS GIZICKI TO VINCE KLCO ON 4/24/13 AT 1004 EDT * * * The US ARMY is retracting this event due to a miniscule bio-assay indicated dose rate to the four workers (maximum dose of 0.9 mRem to an individual) and survey results of the maintenance shop indicating no contamination. The device has been secured and properly stored for future disposal. The licensee notified R3 (McCraw). Notified the R1DO (Joustra), R3DO (Hills) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2013-04-22
48916 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2013-04-11 13:00 | 2013-04-11 21:10 | 2013-06-03 | DEGRADED ELECTRICAL CONNECTIONS "On April 11, 2013, at 1300 hours, during the performance of On-Line Automatic Depressurization System (ADS) Blowdown Logic Testing, two poor wiring connections were identified (the electrical leads were not properly compressed at their termination point). The electrical leads are associated with the B and C ADS valves. Quad Cities has five ADS valves which can be used to depressurize the Reactor Pressure Vessel under accident conditions. While the solenoids of these valves were actuated successfully during the recent Unit 1 refueling outage (which ended on April 8, 2013), the less than optimum configuration could have prevented the valves from actuating under design basis conditions. The degraded wiring for both valves was restored at 1741 hours [CDT]. "Given the potential impact on the ADS depressurization function, this event is reportable under 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/3/13 AT 1138 EDT FROM FRED SWIHART TO DONG PARK * * * "The purpose of this notification is to retract the ENS Report made on April 11, 2013, at 2110 EDT (ENS Report # 48916). "Further evaluation performed by Quad Cities Station confirms the Unit 1, 3B and 3C Automatic Depressurization System (ADS) valves would have performed their safety functions when required. Based on this subsequent evaluation, ENS Report # 48916 is being retracted. "Note: On April 11, 2013, at 1741 CDT the degraded wiring for the Unit 1, 3B and 3C ADS valves was repaired and both valves were returned to operable status." The licensee notified the NRC Resident Inspector. Notified R3DO (Orth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-11
48915 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-04-11 15:41 | 2013-04-11 18:19 | 2013-04-11 | TECHNICAL SUPPORT CENTER COOLERS OUT OF SERVICE "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, based on 'Loss of Assessment' capability. "This is a non-emergency notification. This condition does not affect the health and safety of the public or the operation of the facility. At approximately 15:41 EDT on 4/11/2013, AH-11 and AH-17, Technical Support Center (TSC) Air Handling Units' coolers were not working. The cause of the condition has not been identified. However, troubleshooting efforts are being planned and will be worked immediately. "TSC functionality requires all areas of the TSC be maintained between 60.8 degrees F and 82.4 degrees F. Actual TSC area temperatures have reached 77 degrees F. If the facility were activated with a full staff, temperatures could rise above the 82.4 degree F limit. Should the TSC need to be activated for an event, we have compensatory measures which would include relocating the TSC to the Alternate Emergency Facility per PEP-240. This decision would be based on the existing event conditions and coordinated with the Emergency Response Manager, SEC-MCR, and Radiological Control Manager. The Alternate TSC has been verified to have electrical power, ventilation, and communication capability. The Technical Support Center-Site Emergency Coordinator has been notified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-11
48914 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-04-11 15:10 | 2013-04-11 16:47 | 2013-04-12 | UNUSUAL EVENT FOR A FIRE LASTING GREATER THAN 15 MINUTES "The fire started at 1455 CDT in the turbine building southeast stairwell and on the auxiliary boiler room roof. Fire fighting efforts continue as fire exists inside the wall between the turbine building and the auxiliary boiler room. The licensee notified the NRC Resident Inspector, state, and local governments. Notified DHS, FEMA, and the NICC. * * * UPDATE FROM WARREN BRANDT TO PETE SNYDER AT 0100 EDT ON 4/12/13 * * * "Wolf Creek declared a NOUE at 15:10 CDT on 4/11/13 due to a fire that started at 14:55 [CDT] in the Turbine Building SE stairwell and on the Auxiliary Boiler room roof. The fire was extinguished at 15:19 [CDT], and cool to the touch at 16:48 [CDT]. No offsite fire response support was required. The fire did not impact any safety related equipment. "The NOUE was terminated at 17:03 CDT 4/11/13. The cause of the fire is under investigation." Notified R4DO (Deese), NRR EO (Monninger), IRD (Marshall), DHS, FEMA and NICC (via email). * * * UPDATE FROM PIERCE MOORE TO JOHN SHOEMAKER AT 1400 EDT ON 4/12/13 * * * "Update to Termination of NOUE due to Fire on roof of Auxiliary Boiler. "Wolf Creek declared a NOUE at 15:10 CDT on 4/11/13 due to a fire that started at 14:55 [CDT] in the Turbine Building SE stairwell and on the Auxiliary Boiler room roof. The fire was extinguished at 15:19 [CDT], and cool to the touch at 16:48 [CDT]. The Offsite Fire Department was called and responded but their support in fire suppression was not required, they did assist in clean up and fire investigation efforts. The fire did not impact any safety related equipment. "The NOUE was terminated at 17:03 CDT 4/11/13. The cause of the fire is under investigation." Notified R4DO (Deese), NRR EO (Monninger), IRD (Marshall) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-04-11
48913 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2013-04-10 23:26 | 2013-04-11 04:29 | 2013-04-11 | FBI NOTIFIED DUE TO DEGRADED SECURITY RADIO COMMUNICATIONS "At 2253 PDT on 4/10/13, SONGS experienced degraded on-site radio communications during planned maintenance on radio systems. Radio communications were restored at 2315 PDT." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Cold Shutdown | Defueled |  | Cold Shutdown | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-11
48912 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-04-10 09:52 | 2013-04-10 20:40 | 2013-04-10 | REACTOR BUILDING STACK ACCESS DOOR NOT FULLY CLOSED "On April 10, 2013, at 0952 [PDT] it was discovered that an access door to the reactor building stack was not fully closed. The door was subsequently closed by operations. On March 16, 2013, the reactor building exhaust flow rate took a step change decrease. Initially the reduction in flow was thought to be a reactor building ventilation damper issue. On April 3, 2013, after walkdown of the reactor building dampers and verification of proper system lineup, the reactor building exhaust flow rate monitor was declared inoperable and a substitute value was used for the exhaust flow rate in accordance with station procedures. "Had an actual event involving an offsite release occurred during the time period from March 16, 2013, to April 3, 2013, an inaccurate reactor building exhaust flow rate might have been used to calculate offsite dose. This would only impact dose calculations at lower doses and potentially delay declaration of an Unusual Event. This is being reported as a major loss of assessment capability. At higher dose rates, the reactor building ventilation isolates and Standby Gas Treatment is operated. Standby Gas Treatment flow rate measurement would be unaffected. The intermediate and high range radiation monitors for the reactor building effluent remained fully functional and would have provided an accurate measure of activity concentration. "Upon closure of the reactor building stack door, the reactor building exhaust flow rate returned to normal and emergency preparedness assessment capability was restored." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-10
48911 | 0 | CRANE NUCLEAR |  |  |  |  | 2010-03-25 | 2013-04-10 20:29 | 2013-04-10 | PART 21 INVOLVING A POTENTIAL WELD DEFECT The following information was received via fax as a supplement to a report originally submitted to the NRC Document Control Desk: "This is a supplement to the above subject Part 21 letter issued by Crane Nuclear, Inc. on March 25, 2010 and NRC ref. ML100920093. "In the referenced letter, Crane Nuclear Inc., located at [860 Remington Boulevard, Bolingbrook, Illinois 60440], filed a 10CFR21 Notification of a Potential Weld Defect to the US Nuclear Regulatory Commission and also the affected customers. Copies of these letters were provided to the NRC. "This letter is intended to supplement that initial notification letter by providing further details on when Crane Nuclear became aware of the issue and the potential safety hazard associated with the issue. "During the NUPIC [Nuclear Procurement Issues Committee] Audit of Crane Nuclear the week of February 2, 2010 an audit finding was issued to Crane Nuclear for not effectively reviewing a customer complaint. The complaint was relative to a potentially undersized fillet weld and the audit finding documented that Crane Nuclear did not review the issue through to completion, or with regard to potentially affecting other customers. In response to the NUPIC Audit Finding, Crane Nuclear generated a Corrective Action Report (CAR) CAR 10-22 on 03/01/10. This CAR identified two required actions and they were: 1) Create a formal procedure that ensures all customer complaints are thoroughly investigated until they are complete and that Part 21 applicability is considered for the initial complaint and the potential it affects other customers; and, 2) Evaluate the complaint on the potentially undersized fillet weld to determine if Part 21 reporting is required. "During that NUPIC Audit, Crane was asked to provide a statement relative to the potential defect or failure and the safety hazard which is created or could be created by a potentially undersized weld and the following statement was provided to the NUPIC Audit team and as of today this statement has been provided to the customers that received the initial notification - the following is the Statement that was provided to NUPIC and the notified customers: "Assessment of Undersized Weld on Valve Safety Function "Auxiliary connections on valve bodies, bonnets and covers are used for drains, vents or leak-off. The welds used to attach these connections are tested as part of the pressure boundary and subjected to ASME/ANSI hydrostatic test pressure (1.5 X cold working pressure). Because the pipe nipples used are short and fairly rigid, if the lines remained capped and not connected to a piping system it is unlikely that the combined stresses due to pressure and bending at the weld due to seismic accelerations would exceed the stress due to the pressure load applied during the hydrostatic test. However, a complete and instantaneous failure of the weld could result in a capped line becoming a missile and pressure boundary violation. If a line was connected to a piping system, if properly supported it is also unlikely the welded joint would see loads that would over stress the weld. However, if loads were generated at the welded connection that exceeded the strength of the weld a crack could be initiated and the pressure boundary violated. "In response to the first required corrective action, Crane Nuclear created and released a robust customer complaint procedure CCP-1 titled, 'Customer Complaint Procedure.' This procedure requires a documented management review by the Customer Service Manager, Engineering Manager, Site Leader and Quality Director, for each and every customer complaint. The complaint form requires completion of a 'yes or no' check box that needs to be completed with respect to 10CFR21 applicability and it also has a 'yes or no' check box to document whether other customers are affected. "In response to the second required action on the CAR, all Crane Nuclear designs with any kind of bleed off or other venting/leak type designs using fillet welds were isolated and each inspection 'as-built' record for each design and order were reviewed. The review of the 'as-built' inspection records confirmed that the fillet welds were in compliance with the drawing except for potentially those that were identified in the Part 21 notification referenced above. The review of all inspection documentation was completed on Friday March 19th and in accordance with our procedure the President was notified at 8:48PM that evening and the notification was completed on March 2, 2010. CAR 12-26 was later generated on 07/27/12 and closed on 08/21/12 for filing the report on the 6th day. If you have any further questions please contact [Rosalie Nava] at one of the following, phone 630-226-4940, email rnava@cranevs.com., or by fax 630-226-4646." Affected licensees include Dominion, Duke Energy, Omaha Public Power District and TVA Nuclear. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-10
48910 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2012-12-06 08:00 | 2013-04-10 16:44 | 2013-04-10 | FAILURE TO COMPLY WITH CONDITIONS OF CONSTRUCTION PERMIT "50.55(e) initial notification for failure to comply with requirements of 10 CFR 50 Appendix B, Criterion VII for procurement of safety-related components associated with AP1000 Nuclear Power Plant construction by CB&I (formerly Shaw Nuclear). "This 50.55(e) initial notification addresses a failure to comply by CB&I, an agent of South Carolina Electric & Gas (SCE&G) for Virgil C. Summer 2 & 3, to meet the requirements of Appendix B, Criterion VII. It is concluded that the QA programmatic issues, as identified by the root cause analysis associated with NRC violation 05200025/2012-004-02, could have produced a defect and this condition is reportable in accordance with 10 CFR 50.55(e)(3)(iii)(C). The root cause of the programmatic procurement problems was that the existing Shaw Nuclear procurement and quality oversight and inspection program did not include a sufficiently strategic, integrated, and graded approach to assure the required quality of material, equipment, and services. This notification closes the interim report submitted on February 4, 2013 by SCE&G. "This 50.55(e) initial notification is being submitted pursuant to the requirements of 10 CFR 50.55(e)(3)(iii)(C)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 50.55(e) |  |  |  | 0 | 2013-04-10
48909 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-04-10 13:14 | 2013-04-10 16:19 | 2014-01-15 | MASSACHUSETTS AGENCIES NOTIFIED REGARDING NEUTRALIZING SUMP DISCHARGE LINE INSPECTION "At 1314 hours on Wednesday, April 10, 2013 during a boroscopic inspection of the sub-surface portions of the Neutralizing Sump Discharge Line, Pilgrim Station discovered indications of a separation in the line. The line is currently isolated and no discharges were in progress during the planned inspection. This line is used infrequently to discharge permitted liquids that have the potential to contain radiological contamination. This notification is conservatively being made in accordance with Pilgrim site procedures with direct voluntary communications with offsite agencies. "There is no impact on the safe operation of the plant and personnel are investigating the cause. "The [NRC] Resident Inspector staff has been informed of this notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi). "The licensee will notify the Massachusetts Emergency Management Agency (MEMA) and other state agencies." * * * UPDATE AT 1700 EST ON 01/15/14 FROM STAN PAUL TO S. SANDIN * * * "Entergy Pilgrim Station has twenty three (23) groundwater monitoring wells used to sample for tritium and other radioactive nuclides in accordance with the Nuclear Energy Institute's (NEI) voluntary Groundwater Protection Initiative (GPI). One of the newly installed wells, MW-219, located in the vicinity of a Catch Basin adjacent to the Reactor Building Auxiliary Bay and in the flow path of the Neutralizing Sump Discharge Line indicated an elevated level of tritium (H3), that exceed the limits established by the NEI Groundwater Protection initiative and the Nuclear Regulatory Commission's (NRC) limits for liquid effluent release. A protocol for more frequent sampling has been instituted and an investigation of the cause is underway. To date, tritium is the only isotope detected In the groundwater monitoring well samples collected at the site. This supplemental information has been voluntarily communicated to Federal, State and local stakeholders. "The NRC Resident Inspector has been notified of this update. This is an update to the 4-hour non-emergency notification made in accordance with 50.72(b)(2)(xi) on April 10, 2013 at 1619 hours." Notified R1DO (Rogge). | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-10
48908 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-04-10 09:30 | 2013-04-10 13:13 | 2013-04-10 | LOSS OF EMERGENCY NOTIFICATION SYSTEM TELEPHONE "On April 10, 2013 at 0930 [EDT] Hope Creek Operations personnel identified that the NRC ENS phone line was unavailable for Hope Creek Generating Station. The loss of the NRC ENS line was verified by the Hope Creek Shift Manager via backup land line communication to the NRC. The NRC Operations Center has an open repair ticket with the phone service provider. "The loss of the phone line had no effect on plant operation and the unit remains at 100% power. "Additionally, Emergency Response Data System (ERDS) capability was verified to remain intact and is available to transmit data. "No personnel injuries resulted from the event. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-10
48907 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-04-10 11:30 | 2013-04-10 11:06 | 2013-04-10 | PLANNED TECHNICAL SUPPORT CENTER OUTAGE "A planned work package (52343687-01) at the James A. FitzPatrick (JAF) Nuclear Power Plant will be performed for DOP/Freon Testing TSCVASS as required per TS 5.5.8 Ventilation Filter Testing Program. The testing requires breaking the boundary into the Technical Support Center (TSC) ventilation system to obtain a charcoal sample. Therefore, the TSC ventilation system will be rendered nonfunctional during the duration of this work activity. The TSC ventilation is expected to be out of service for approximately 6 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate TSC location In accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE ON 4/10/13 AT 1717 EDT FROM DAVE RICHARDSON TO DONG PARK * * * "This is an update from EN #48907. Planned maintenance has been completed on the Technical Support Center (TSC) ventilation system. The TSC filtered ventilation system has been restored to normal standby lineup. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-10
48906 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2012-12-06 08:00 | 2013-04-10 09:47 | 2013-04-10 | FAILURE TO COMPLY WITH CONDITIONS OF CONSTRUCTION PERMIT "50.55(e) initial notification for failure to comply with requirements of 10 CFR 50 Appendix B, Criterion VII for procurement of safety-related components associated with AP1000 Nuclear Power Plant construction by CB&I (formerly Shaw Nuclear). "This 50.55(e) initial notification addresses a failure to comply by CB&I, an agent of Southern Company for Vogtle 3&4, to meet the requirements of Appendix B, Criterion VII. It is concluded that the QA programmatic issues, as identified by the root cause analysis associated with NRC violation 05200025/2012-004-02, could have produced a defect and this condition is reportable in accordance with 10 CFR 50.55(e)(3)(iii)(C). The root cause of the programmatic procurement problems was that the existing Shaw Nuclear procurement and quality oversight and inspection program did not include a sufficiently strategic, integrated, and graded approach to assure the required quality of material, equipment, and services. This notification closes the interim report submitted on February 4, 2013 by Southern Company. "This 50.55(e) initial notification is being submitted pursuant to the requirements of 10 CFR 50.55(e)(3)(iii)(C)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 50.55(e) |  |  |  | 0 | 2013-04-10
48905 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-04-09 13:15 | 2013-04-09 17:08 | 2013-04-09 | LOSS OF EMERGENCY NOTIFICATION SYSTEM TELEPHONE "On April 9, 2013 at 1315 [EDT] Hope Creek Operations personnel identified that the NRC ENS phone line was unavailable for Hope Creek Generating Station. The loss of the NRC ENS line was verified by the Hope Creek Shift Manager via backup land line communication to the NRC Operation Center at 1355 [EDT]. At that time, the NRC Operations Center submitted a repair ticket to the phone service provider. NRC ENS phone availability was verified restored to service at 1618 [EDT] with the NRC Operations Center. "The loss of the phone line had no effect on plant operations and the unit remains at 100% power. "Additionally, Emergency Response Data System (ERDS) capability was verified to remain intact during this time period and was available to transmit data. "No personnel injuries resulted from the event. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-09
48904 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-02-11 06:13 | 2013-04-09 17:07 | 2013-04-09 | MANUAL INITIATION OF REACTOR CORE ISOLATION COOLING SYSTEM "On February 11, 2013, at 0613 hours [CDT], the Reactor Core Isolation Cooling (RCIC) system was manually started during a planned Unit 3 reactor shutdown. A Reactor Feedwater recirculation piping separation resulted in the loss of condenser vacuum and subsequent unavailability of the Main Turbine Bypass Valves. The RCIC system was manually started at 9.2" of condenser vacuum in order to control reactor water level in anticipation of loss of Reactor Feedwater Pumps (RFPs) which occurs at 7" of condenser vacuum. Safety Relief Valves (SRVs) were manually operated to maintain reactor pressure. The reactor water level was controlled in the normal band by RCIC, and Reactor Pressure was controlled with a combination of Reactor Core Isolation Cooling (RCIC) system and SRV manual operation. All systems operated as designed and Reactor water level was maintained in the prescribed band. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. RCIC operation was secured at 1449 [CDT] on 2/11/2013. "This event is reportable within 8 hours per 10CFR50.72(b)(3)(iv)(A). During a review of operating logs it was identified that this event met reporting requirements and had not been reported. Therefore, this report does not comply with the 8 hour requirement. This condition has been entered into the corrective action program. Additionally, an LER is required within 60 days per 10CFR50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-04-09
48903 | 0 | SAGINAW RADIATION ONCOLOGY CENTER |  |  |  |  | 2013-04-08 10:30 | 2013-04-09 14:56 | 2013-04-09 | MEDICAL EVENT INVOLVING A MIS-POSITIONED BRACHYTHERAPY SOURCE On 04/08/13 at approximately 1030 EDT a female patient undergoing brachytherapy treatment for cervical/vaginal cancer received the first of three fractions. The prescribed dose for the first fraction was 400 cGy, however, the wrong length catheter was used. This placed the source 5 cm inferior to the intended treatment site. The actual dose received has not been determined at this time. This error was discovered on 04/09/13 during a review by the Medical Physicist. Both the prescribing physician and patient have been informed. There are no adverse health consequences anticipated due to this error in treatment. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2013-04-17
48902 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-04-03 | 2013-04-09 11:52 | 2013-04-09 | AGREEMENT STATE REPORT INVOLVING DIFFICULTY IN RETRACTING A FIXED GAUGE SOURCE The following information was provided by the State of Kansas via fax: "This letter is to inform [the Kansas Department of Health & Environment] that yesterday afternoon [on 4/3/13, the RSO] had attempted to move a source from its drywell into its source holder to prepare for maintenance activities in the vessel. The source seemed to be stuck in the drywell. Because the cable restraining the source does not allow the shutter to close until it completely retracted, the shutter would not close. Later last night, after consulting with VEGA Americas and [the company] on-site engineers, [the RSO] attempted again to remove the source and it was free. The source has been safely stored in its holder. There were no reportable personnel exposures. Because of the position of this source 8 feet inside a large vessel with 5 [inch] steel walls, it is shielded at least as well as inside its holder. "The shutter in question is on an Ohmart/VEGA model SHLM-CR3 source holder S/N 19077664, containing 2 Ci of Cs-137 in a model A2102 sealed source S/N 0587CO. "The source is located at [the company facility] in EI Dorado, KS . . .. It is approximately 140 feet above the ground. Operations and maintenance personnel were notified of the issue. A wipe sample was collected to check for gross leakage. None was indicated. "What [the RSO] believe[s] caused this situation was the combination of two (2) things. The reactor was being cooled with nitrogen over the past few days. It has also been raining and snowing. [The RSO] believe[s] water was drawn into the well during cooling and the nitrogen cooled that area of the reactor enough to freeze the water in the well. Ice was present on the cable as it was pulled out. Because the reactor was sufficiently cooled, the nitrogen purge was reduced, thus allowing the reactor to warm slightly by 8 PM when [the RSO] tried again. "[The RSO] feel[s] that this was not, in fact, a shutter issue, but an operational issue which [the RSO] will be cognizant of in the future. [The RSO] will simply make sure the internal temperature of this vessel is above 40 degrees F before attempting to remove the top source. Normally it is over 500 Degrees, so water intrusion is not an issue. Again, the source was always in a safe position. At no time were personnel exposed to any reportable levels of radiation." Kansas Item Number: KS130003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-04-17
48901 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2013-04-09 02:35 | 2013-04-09 09:42 | 2013-04-09 | POWER LOST TO METEOROLOGICAL INSTRUMENTATION "At 0235 EDT on 4-9-13, due to an offsite power transformer fault, power was lost to site support buildings and all meteorological instrumentation. This event is being reported under 10CFR50.72(b)(3), major loss of emergency assessment capabilities. "At 0455 EDT, power was restored to meteorological instrumentation in the control room. During the power outage, limited meteorological data remained available via telephone from the National Weather Service and the Fitzpatrick site met tower. Plant operations at both units 1 and 2 were not affected. Both units remain at full power." The licensee notified the NRC Resident Inspector. | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-09
48900 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-04-09 07:30 | 2013-04-09 09:05 | 2013-04-09 | AUXILIARY BUILDING VENT MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "On April 9, 2013, at approximately 0730 hours [CDT], the Kewaunee Power Station declared the Auxiliary Building Vent Special Particulate Iodine Noble Gas 'SPING' Radiation Monitor (Mid and Hi Range) nonfunctional for planned maintenance. The Emergency Response Organization (ERO) team has been notified of the Auxiliary Building Vent SPING nonfunctionality due to planned maintenance. "The SPING is expected to be out of service for approximately 3 hours. "Although manual 'grab samples' could be used as a backup, this condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify the upper two emergency action levels for offsite radiation conditions). "The NRC Resident Inspector has been notified." See similar EN #48881 and 48891. * * * UPDATE FROM GARY AHRENS TO HOWIE CROUCH AT 1018 EDT ON 4/9/13 * * * SPING was returned to service at 0819 CDT. The licensee informed the NRC Resident Inspector. Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-09
48899 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-04-02 | 2013-04-08 16:50 | 2013-04-08 | AGREEMENT STATE REPORT INVOLVING A MIS-DELIVERED SHIPMENT OF RADIOACTIVE MATERIAL The following information was provided by the State of Louisiana via email: "Event date and Time: On 04/02/2013 [the] RSO for A & O [Alpha-Omega Services, Inc.] called in a mis-delivery of an Ir-192 source intended for Radiation Oncology Center of Nevada (ROCN). ROCN is a client/customer of A & O, but [the common carrier] delivered the source to Cardinal Health (CH). ROCN and CH are both radioactive material licensees and both have facilities in Las Vegas, NV. "Event Location: Around the Las Vegas, NV area. The source was intended for ROCN in Las Vegas, NV, but was delivered to Cardinal Health, [also in] Las Vegas, NV. The source delivery occurred in the morning to CH. CH notified ROCN that their source was delivered to CH by [the common carrier]. [The common carrier] was notified and picked up the source at 1300 [PDT] and delivered it to ROCN. "Event type: Delivery of a radioactive source by the [common] carrier to the wrong licensee. Except during transport, the source was in possession of someone who was a licensee and well trained in radiation safety practices. "Notifications: A notification was made to LA DEQ [Louisiana Department of Environmental Quality] Radiation Assessment after the incident was basically over and entirely under control. The notification was made to [a Louisiana representative] located in [the Louisiana] Southwest Regional office. A & O was involved in the recovery of the source by phone after learning of the mis-delivery. The source was delivered to the wrong licensee. CH, the licensee where the source was delivered, was licensed for radioactive material and well trained in the handling of radioactive material. "Event description: [An] Ir-192 source was delivered to the wrong licensee by [the common carrier]. When the error was discovered by CH, CH notified ROCN that they were in possession of licensed radioactive material that belonged to ROCN. [The common carrier] was called and they picked up the source and delivered it to ROCN around 1300 [PDT]. The source shielding and shipping container was intact during the entire incident. It was not damaged nor was the container opened. "Transport vehicle description: [The common carrier] picked up the source from the A & O facility [in] Venton, LA which was being shipped to a client, ROCN [in] Las Vegas, NV. [The common carrier] delivered the Ir-192 source to the wrong address. The source was delivered to Cardinal Health (CH), [also in] Las Vegas, NV." Event Report ID No.: LA-120015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-04-16
48898 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2013-04-08 14:35 | 2013-04-08 16:56 | 2013-04-08 | OFFSITE NOTIFICATION TO THE MAINE DEPARTMENT OF ENVIRONMENTAL PROTECTION "A sewage line has been found broken and leaking. The area of the leak is on Maine Yankee property but outside the licensed area. Repairs are scheduled for 04/09/13." No radioactive material is involved. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | PRESS RELEASE/OFFSITE NOTIFICATION | [8 empty] | NON EMERGENCY | 1 | ME | ISF |  | 50.72(b)(2)(xi) | 72.75(b)(2) |  |  | 0 | 2013-04-08
48897 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2013-04-08 11:15 | 2013-04-08 16:09 | 2013-04-08 | HPCI DECLARED INOPERABLE DURING SURVEILLANCE TESTING "On April 8, 2013 at 0908 [EDT], the High Pressure Coolant Injection System (HPCI) was declared inoperable as part of planned Controls Functional Testing. At 1115 [EDT], during the performance of scheduled testing, an initiation signal for the HPCI system was provided and the HPCI Auxiliary Oil Pump failed to start as expected. The HPCI Auxiliary Oil Pump provides the motive force to open the HPCI Turbine Stop and Governor valves during system startup. The inability of the HPCI Turbine Stop and Governor valves to open prevents the HPCI system from fulfilling its design safety function. The HPCI system will remain inoperable until the cause of the failure has been corrected. "All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling (RCIC) system remain operable. "The unit remains at 100% power. "The station has initiated an Event Response Team to identify and correct the cause of the failure. "No personnel injuries resulted from the event. "The NRC Resident Inspector and Lower Alloways Creek Township will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-08
48896 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-08 12:40 | 2013-04-08 15:58 | 2013-04-08 | CONTROL ROOM ENS PHONE OUT OF SERVICE FOR GREATER THAN ONE HOUR "The Salem Generating Unit 1 and 2 control room ENS phone system was down for greater than one hour from 1140EDT to 1240EDT." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-08
48895 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-12-02 | 2013-04-08 14:00 | 2013-04-08 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGES The State of California provided the following information via email: "On December 5, 2012, . . . American Soil Testing notified RHB [California Radiologic Health Branch] that his storage facility had been broken into and two CPN Moisture Density gauges (Serial numbers MD00405615 & M17031878) had been stolen. The licensee was advised to post a notice and reward in the local newspapers and on Craigslist and to notify local law enforcement. "Note: Miscommunication resulted in the NRC not being notified until 4/8/13." CA 5010 Number: 120512 These CPN Moisture Density gauges contain two (2) sources each, i.e., 10 mCi Cs-137 and 50 mCi Am-241/Be. HOO Note: See EN #48867 - Report from Nevada concerning recovery of M17031878 gauge. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-04-16
48894 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-11-17 | 2013-04-07 17:47 | 2013-04-07 | AFTER THE FACT DISCOVERY OF AN UNUSUAL EVENT ENTRY CONDITION "During an extent of condition review of past radiological events, it was identified that an event on November 17, 2010 met the E-Plan entry criteria for GU1, 'Unexpected Increase In Plant Radiation Levels'. Due to an equipment deficiency, dose rates in one section of the Radwaste building rose from 0.08 mrem/hr to 80 mrem/hr. This satisfied the E-Plan criteria of a 1000 times change over normal radiation levels. This was initially identified in [Perry] Condition Report 2010-85937." The licensee notified the NRC Resident Inspector and will notify State and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2013-04-07
48893 | 0 | FLOWSERVE CONTROL - LIMITORQUE |  |  |  |  | 2013-04-04 | 2013-04-05 14:36 | 2013-04-05 | PART 21 REPORT OF LIMITORQUE VALVES WITH INCORRECT MOTOR NAMEPLATES INSTALLED The following information is a synopsis of a report received from Flowserve - Limitorque via facsimile: "During routine Motor Operated Valve testing of a Limitorque SMB-000 actuator prior to being placed into operation, Duke Energy, Catawba Nuclear Station measured motor current readings higher than expected. This actuator was equipped with a 2 ft-lb motor. This motor was returned to Limitorque and subsequently to the motor Original Equipment Manufacturer (OEM). Investigation revealed that this motor was a 5 ft-lb motor mislabeled with the nameplate from a 2 ft-lb motor which explains the measured current draw. "This notification is limited to a quantity of two motors for Limitorque SMB-000 actuators. Both affected licensees have been notified of this occurrence and both motors have been returned to Flowserve - Limitorque for replacement. [Catawba and Arkansas Nuclear One] "The defect which occurred is that the 2 ft - lb motor was identified on the nameplate as a 5 ft - lb motor. Similarly the 5 ft - lb motor was identified on the nameplate as a 2 ft - lb motor. Had these motors been placed into service, this defect has the potential to affect safety related operation due to a possible reduction of MOV capability. "The cause of the defect was due to two motor nameplates being inadvertently interchanged by Flowserve personnel during the painting process prior to shipment. The two motors which are both 48 frame, SMB-000 flanged, Baldor Reliance AC motors were being painted in the same timeframe. The painting process requires the OEM supplied nameplate to be temporarily separated from the motor. Upon the completion of the painting process, Flowserve personnel inadvertently interchanged the nameplates resulting in the 2 ft-lb motor being incorrectly identified as a 5 ft-lb motor. Similarly the 5 ft-lb motor was incorrectly identified on the nameplate as a 2 ft-lb motor. Inspections of the returned motors by Flowserve and the motor OEM confirmed the problem. "To prevent recurrence of this issue, Flowserve has reviewed and strengthened the relevant procedures regarding verification of motor identification during the installation of the OEM supplied motor nameplate. All personnel associated with this process have been trained by Flowserve QA to the latest revision of the procedures." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-05
48892 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2013-04-05 15:05 | 2013-04-05 16:59 | 2013-04-06 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation resulted during maintenance. Compensatory actions were implemented within the appropriate time frame. Contact the Headquarters Operations Officer for details. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM TERRY PALANYK TO VINCE KLCO ON 4/5/13 AT 2018 EDT * * * Safeguards systems have been restored to functional status. Compensatory actions remain in effect. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Daley) and Part 73 GRP via email. * * * *UPDATE FROM OWEN SHOGER TO VINCE KLCO ON 4/6/13 AT 1845 EDT * * * Security has completed functional testing and all safeguards systems are fully restored. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Daley) and Part 73 GRP via email. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-04-05
48891 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-04-05 07:30 | 2013-04-05 08:20 | 2013-04-05 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE "On April 5, 2013, at approximately 0730 hours [CDT], the Kewaunee Power Station declared the Reactor Building Special Particulate Iodine Noble Gas (SPING) (Mid and Hi Range) nonfunctional for planned maintenance. The Emergency Response Organization (ERO) team has been notified of this Reactor Building Vent SPING nonfunctionality due to planned maintenance. "The SPING is expected to be out of service for approximately 3 hours. "Although manual 'grab samples' could be used as a backup, this condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently indentify the upper two emergency action levels for Offsite Radiation conditions). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-05
48890 | -1 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-04-05 06:24 | 2013-04-05 07:02 | 2013-04-05 | UNUSUAL EVENT DECLARED DUE TO A FIRE ALARM IN THE STACK FILTER HOUSE "At 0624 [EDT], the Brunswick Steam Electric Plant (BSEP) declared an Unusual Event due to a fire alarm in the Stack Filter House. The classification of the Unusual Event is based on Emergency Action Level (EAL) HU2.1, 'Fire not extinguished within 15 minutes of control room notification or verification of a control room fire alarm.' Verification of fire could not be made within 15 minutes of fire alarm due to confined space conditions. Actual fire conditions did not exist; alarm was caused by environmental conditions. "There is no impact on the health and safety of the public." The licensee terminated the Unusual Event at 0650 EDT. Personnel injuries and equipment damage did not occur. Offsite assistance was not required. The licensee has notified the state and local authorities. The licensee will notify the NRC Resident Inspector. Notified DHS, FEMA, DHS NICC and NuclearSSA. * * * RETRACTION FROM WILLIAM MURRAY TO VINCE KLCO AT 1644 EDT ON 4/5/2013 * * * "This event is being retracted based upon the following: "As stated in the original event notification, an actual fire condition did not exist and the control room fire alarm was caused by environmental conditions. Because an actual fire did not exist and the fire detection system alarm was not valid, the condition described in the Emergency Action Level (EAL) HU2.1, 'Fire not extinguished within 15 minutes of control room notification or verification of a control room fire alarm,' also did not exist. The Unusual Event was terminated at 0650 [EDT]. The Unusual Event classification was appropriately made, in accordance with the EAL basis which requires the control room alarm be validated by other indications or alarms or by an actual field report, or the classification must be made. Based on the preceding information, Event Notification 48890 is retracted." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Rich) and the NRR EO (Lee). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-04-05
48889 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-04-03 | 2013-04-04 17:43 | 2013-04-04 | AGREEMENT STATE REPORT - LOST MOISTURE GAUGE The following information was from the State of California via email: "On 04/04/13, [the licensee] RSO, called RHB [California Radiologic Health Branch] to report a lost gauge. The gauge is a Model 503 DR CPN moisture gauge (S/N H33064926) containing 50 mCi (max) of Americium 241:Be. [The RSO] stated that he placed the gauge in the back of his truck next to the tailgate, then got distracted by a telephone call and started driving from 4181 Brew Master Dr, Suite 4, Ceres, CA, on Crows Landing, Hwy N 99 and then onto Hwy 88 without securing the gauge. He discovered the gauge missing [at 1600 PDT] on 04/03/13, upon arrival at a jobsite. The Ceres Police Department was notified of the lost gauge (case # 213-001653). Licensee was advised to place an advertisement in a local paper/craigslist offering a reward of $4000.00 for the safe return of the gauge. RHB will be investigating the incident and licensee will be cited for the items of non compliance associated with this incident." California Report: #040413 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-04-12
48888 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2013-03-18 | 2013-04-04 16:08 | 2013-04-04 | AGREEMENT STATE REPORT - SHIPMENT EXCEEDED SURFACE CONTAMINATION LIMITS The following information was received from the Washington State Division of Radiation Protection by email: "PermaFix Northwest received a shipment from Perkin Elmer, Inc. that consisted of 32 packages, 4 plastic drums and 28 metal drums, and was shipped as an exclusive use shipment. Upon receipt, the drums were surveyed and 2 plastic drums were found to exceed the 49 CFR 173.443 non-removable contamination limit of 2,200 dpm/cm2 for an exclusive use shipment. The drum survey results were reported as 44,391 dpm/100 cm2 H-3 and 18,080 dpm/100 cm2 C-14; 20,127 dpm/100 cm2 H-3 and 18,508 dpm/100 cm2 C-14, and 13,323 dpm/100 cm2 H-3 and 10,019 dpm/100 cm2 C-14. This most contaminated drum was manifested with only H-3 and C-14, the other 2 drums were manifested with only C-14." Washington Incident Number: WA-13-021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-04-12
48887 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2013-04-04 04:06 | 2013-04-04 08:35 | 2013-04-05 | FAILURE OF THE INTEGRATED PLANT COMPUTER SYSTEM "At 0406 [EDT] on April 4, 2013, the Fermi 2 Integrated Plant Computer System (IPCS) failed. This resulted in a loss of approximately 60 percent of data on the Safety Parameters Display System (SPDS). "While IPCS and SPDS are not fully functional, the Emergency Plan can still be implemented if a plant emergency does occur, as assessment capabilities are available under alternate means. "Investigation is in progress. A follow up message will be made when IPCS and SPDS are restored to fully functional status. "This notification is being made per the requirements of 8 Hour Non-Emergency Notification 10CFR50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM GREG MILLER TO VINCE KLCO AT 1636 EDT ON 4/5/2013 * * * "At 1627 [EDT] on April 4, 2013, plant personnel were able to restore full functionality of IPCS and SPDS. This restored full assessment capabilities to all onsite emergency response faculties." The licensee notified the NRC Resident Inspector. Notified the R3DO (Daley). | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-04
48886 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2013-04-03 10:53 | 2013-04-03 16:51 | 2013-05-28 | COOLING WATER MAKEUP PUMP FAILED TO START DURING A SURVEILLANCE TEST "At 1053 [EDT] on April 3, 2013, during the performance of a surveillance test on the Division 2 Emergency Equipment Cooling Water (EECW) system the EECW system was declared inoperable due to the Division 2 EECW makeup pump failing to start during the surveillance. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) room cooler. "A 14 day Limiting Condition for Operation (LCO) was entered for HPCI via [Technical Specification] LCO 3.5.1. Investigation into why the makeup pump did not start is currently in progress. "This report is being made pursuant to 10 CFR 50.72 (b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on a loss of a single train safety system. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BRETT JEBBIA TO VINCE KLCO ON 5/28/13 AT 1613 EDT * * * "An evaluation of Event 48886 has determined that the Division 2 Emergency Cooling Water (EECW) system was capable of supporting HPCI Room Cooler and HPCI operation for a period of time in excess of that required to perform the required safety functions as assumed in the accident analysis. Therefore, this event is retracted." The licensee notified the NRC Resident Inspector. Notified the R3DO (Orth). | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-04-03
48885 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-03 12:50 | 2013-04-03 16:40 | 2013-04-03 | FITNESS FOR DUTY REPORT INVOLVING DISCOVERY OF AN ALCOHOL CONTAINER INSIDE THE PROTECTED AREA During remodeling of a bathroom on the third floor of the Administrative Building which is located inside the Protective Area, workers discovered two very old containers of blackberry brandy after removing the ceiling tiles. This item will be entered into the licensee corrective actions program for follow up. The licensee informed the NRC Resident Inspector. HOO Note: A similar report [EN #48877] was received on 4/2/2013. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2013-04-03
48884 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-04-01 | 2013-04-03 16:20 | 2013-04-03 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE OF RADIATION WORKER The following information was received from the State of Louisiana via email: "On 04/01/2013 [the] RSO for NVI [Nondestructive & Visual Inspection], notified the Department [Louisiana Department of Environmental Quality] that his personnel monitoring processing company, Landauer, notified him that one of his monitors was processed with a result of 108 R exposure. The monitor was assigned to an individual who had been terminated at the beginning of February 2013 for chemical dependency. The individual could not be directly contacted and the monitor was missing for the month of February. The monitor appeared in the cab of a rig truck for radiography. The employee had not been employed or working in a radiation environment for NVI about 2-3 weeks when the monitor surfaced. Attempts were made to make contact with the individual, but [there was] no response. "[The RSO] stated that he was trying to reach the individual to provide him with medical assistance. At a minimum, he wanted to do blood work Cytogenetics/Biodosimetry on the individual. This is a possible but, not probable excessive exposure to this individual. "At 8:00 AM on 04/02/2013 [the RSO] called to update the Department and stated that the individual returned his call at [11:00 PM] on 04/01/2013 and consented to accept the medical assistance. The employee has not been sick or had any visible signs of radiation sickness. The trip to a physician office and a call to REACTS in Oak Ridge, TN set up the process for Monday April 8, 2013. The process needs fresh blood within 24 hours for the test. At this time, the Department considers this incident pending the outcome of the test." LA Event Report ID: LA-120014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-04-11
48883 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2013-04-03 07:39 | 2013-04-03 15:45 | 2013-04-03 | FITNESS FOR DUTY REPORT - LICENSED EMPLOYEE SUPERVISOR TESTED POSITIVE FOR ALCOHOL A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been terminated. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2013-04-03
48882 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2013-04-02 16:45 | 2013-04-03 14:13 | 2013-04-03 | FITNESS FOR DUTY REPORT - LICENSED EMPLOYEE ARRESTED FOR POSSESSION OF A CONTROLLED SUBSTANCE A licensed employee was arrested for possession of a controlled substance while off-duty. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2013-04-03
48881 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-04-03 08:00 | 2013-04-03 11:07 | 2013-04-03 | AUXILIARY BUILDING SPECIAL PARTICULATE IODINE NOBLE GAS MONITOR OUT OF SERVICE "On April 3, 2013, at 0800 CDT, the Kewaunee Power Station discovered that the Auxiliary Building Special Particulate Iodine Noble Gas 'SPING' Monitor (Mid and hi Range) was Non-Functional due to an external failure. The SPING is used to aid in assessing Emergency Action Levels. The expected out of service time is unknown at this time. Trouble shooting is currently in progress. Work will be performed with high priority. "Although manual 'grab samples' could be used as a backup, this condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability (unable to sufficiently identify the upper two emergency action levels for Offsite Radiation conditions). "The NRC Resident Inspector has been notified." * * * UPDATE AT 1448 EDT ON 4/03/13 FROM STODOLA TO HUFFMAN * * * The Particulate Iodine Noble Gas 'SPING' Monitor was recalibrated and returned to service at 1257 CDT on 4/03/13. The licensee has notified the NRC Resident Inspector. R3DO (Daley) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-04-03
48880 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-04-03 06:47 | 2013-04-03 07:32 | 2013-04-03 | NOTIFICATION OF UNUSUAL EVENT BASED ON A FIRE IN THE PROTECTED AREA LASTING GREATER THAN 15 MINUTES "Vogtle Unit 1 has declared an NOUE based on a fire within the protected area boundary not extinguished within 15 minutes of detection. "At 0632 [EDT] Unit 1 received a fire alarm in the Unit 1 control building. A systems operator was dispatched to investigate and reported back that a small flame was visible inside 1ND3I1, computer inverter. Fire brigade was dispatched in accordance with fire response procedures. No other systems or parameters affected. "At 0651 [EDT] fire brigade captain reported that the fire had been extinguished." The licensee has notified the NRC Resident Inspector as well as the state and local authorities. Notified DHS, FEMA, DHS NICC and NuclearSSA. * * * UPDATE FROM MICHAEL PARKER TO DONG PARK AT 0811 EDT ON 3/31/13 * * * The licensee terminated the NOUE at 0745 EDT based on the fire being extinguished. The licensee has notified the NRC Resident Inspector. R2DO (McCoy), NRR EO (Chernoff), and IRD (Harris) notified. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-04-03
48879 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2013-04-02 17:07 | 2013-04-02 20:30 | 2013-04-04 | OFFSITE NOTIFICATION DUE TO ELECTRICAL FAULT IN SWITCHYARD RESULTING IN PERSONNEL INJURIES "At 1707 CDT on 4/2/13 an arc flash occurred at the 'B' safeguards transformer (XMDV24) in the plant switchyard at Callaway. At the time of the flash, ground straps were being placed on the 'B' safeguards transformer which had been removed from service for maintenance. The event resulted in a loss of power to areas/buildings outside the power block. There was no impact to equipment and systems in the plant. "Four workers were injured or affected by the flash. The extent of the electrical-related injuries has not been determined. However, based on reports from the scene, all of the workers were conscious and walked away from the scene. One person was transported by helicopter and two by ambulance to a local hospital. The fourth person experienced only a minor injury. "The hazard has been isolated and investigation of the cause is in progress. "Notifications of this event are planned to be made to OSHA and the Missouri Public Service Commission." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ROB STOUGH TO VINCE KLCO AT 1955 EDT ON 4/4/2013 * * * "Ameren Missouri issued a press release about the event described above at approximately 1507 CDT on April 4, 2013. "The NRC Resident Inspector was notified." Notified the R4DO (Kellar). | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-02
48878 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-02 | 2013-04-02 16:25 | 2013-04-02 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO PLANNED MAINTENANCE "This is a non emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed on 4/3/13 to be Technical Support Center (TSC) HVAC. The work includes removal of a pressurizing ventilation fan and opening ventilation system ductwork. The planned work activity duration is approximately 48 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The NRC Resident Inspector has been notified. The State of North Carolina will be notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-04-02
48877 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-04-02 13:45 | 2013-04-02 15:52 | 2013-04-02 | FITNESS FOR DUTY REPORT INVOLVING DISCOVERY OF AN ALCOHOL CONTAINER INSIDE THE PROTECTED AREA During remodeling of a bathroom on the third floor of the Administrative Building which is located inside the Protective Area, workers discovered a very old container of gin after removing the ceiling tiles. This item will be entered into the licensee corrective actions program for follow up. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2013-04-02
48876 | 0 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2013-02-26 | 2013-04-02 14:50 | 2013-04-02 | MEDICAL EVENT INVOLVING DELIVERED DOSE EXCEEDING PRESCRIBED DOSE >20% During a review of post implant dosimetry for prostate cancer treatment at 0800 hours [MDT] on 4/02/13, it was discovered that a patient received 145 gray vice 110 gray prescribed as a "boost" treatment. The prescribing physician will inform the patient and consult with the urologist. The error occurred due to not taking into account that the prescribed dose was a "boost" to the previously delivered 45 gray on 2/14/13, and used the default value of 145 gray for initial treatment. The physician is evaluating any potential adverse consequences for the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2013-04-10
48875 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2013-03-30 17:08 | 2013-04-02 13:24 | 2013-04-02 | AGREEMENT STATE REPORT - FIRE IN PLANT MAY HAVE DAMAGED TWO PROCESS GAUGES The following information was received via facsimile: Two process gauges containing Sr-90 (approximately 50 mCi ea.) at the Goodyear Tire and Rubber Company facility in Fayetteville, NC may have sustained damage as a result of a fire. No leakage is reported. The gauges were mounted in a "LOW - Minimal or Low risk area." The State of North Carolina will be investigating. NC Incident No. 13-06. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-04-10
48874 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2013-03-29 10:06 | 2013-04-02 10:55 | 2013-04-02 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Colorado via email: "At 10:06 am on Friday, March 29, 2013 the Emergency Response Duty Officer was notified that there was an incident involving a portable moisture density gauge that had been run over by a piece of heavy construction equipment. The [Colorado] Department [of Public Health and Environment] responded by phone and contacted the RSO [Radiation Safety Officer] for Terracon, Inc., who was on site supervising the incident. The RSO reported that the gauge had been backed over by a Bobcat loader. The Bobcat loader had a counter balance weight on the rear of the equipment and this contacted the gauge damaging the outer casing. The RSO reported that the source had been fully retracted and was in the safe (shielded position). The RSO conducted a survey and the reading was 0.2 mr/hr at 1 foot. The gauge was loaded into the transport box and readied for transport back to storage at the Tarracon facility. The transport index on the box was 0.1 mr/hr and the RSO was given permission to transport gauge back to storage and perform a leak test before sending off for repair. The leak tests proved negative and the gauge was [shipped] for repair. This licensee will be issued a Notice of Violation of Part 4.26.1: 'The licensee shall control and maintain constant surveillance of licensed or registered radioactive material that is in an unrestricted area and that is not in storage or in a patient.' "Licensee causing incident: Terracon, Inc., Colo. License number 664-02 "Density gauge model and serial number: Troxler model 3430 s/n 28184 "Isotopes in gauge: Cs-137 (9mCi); Am-241 (40mCi) "Survey meter used by RSO: Radiation Alert Monitor 4, s/n 42585, Cal. Date: August 7, 2012" Incident number: I13-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-04-10
48873 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-04-02 06:55 | 2013-04-02 07:29 | 2013-04-02 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO A PROTECTED AREA Attempted introduction of contraband into a protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2013-04-02
48872 | 0 | ABB INC. |  |  |  |  | 2013-02-04 | 2013-04-01 17:29 | 2013-04-01 | POTENTIAL ISSUE CONCERNING THE ZPA RATING FOR 3 PHASE RELAY TYPE SSC-T "This letter is to notify you of a potential issue concerning the ZPA [Zero Point Acceleration] rating for our three phase relay type SSC-T. "During a Customer Audit (week of February 4, 2013 by ABB Inc., Florence, S.C.), we discovered that our Class 1E Certification database showed the ZPA rating of our three phase SSV -T and SSC-T relays was 5.6g, while our most recent qualification (dated June 14, 2012) determined that the ZPA rating was 4.79g. "A review of our Purchaser records for the last ten years indicates that one (1) affected relay was sold to WESCO: "SSC-T relay completed 10/5/2007, order number 3365-960825 and serial number 11835. "ABB does not have the capability to perform the evaluation to determine if a defect exists, so we are informing the purchaser of this determination so that they may evaluate the deviation or failure to comply, pursuant to 10CFR 21.21(a). "ABB recommends that the affected licensee evaluate their specific application and determine whether the deviation described in this notice affects their design basis. If the licensee determines that it does, the licensee should contact ABB to determine appropriate corrective action. "If you have any questions regarding this notice, please contact ABB Technical Support at 954-752-6700." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-04-01
48871 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-11 | 2013-04-01 09:52 | 2013-04-01 | INSTRUMENTATION LINES NOT INSPECTED COMPLETELY FOR PROPER SLOPE "WBN [Watts Bar Nuclear] Unit 2 (under construction) determined that a portion of a number of instrumentation lines within multiple systems may have not been inspected completely for proper slope. This condition may have resulted in sense lines being installed with less than the 1/4" per foot minimum slope. No confirmed examples have been identified that would have created a substantial safety hazard at this time. However, walkdowns and evaluations are still underway to confirm that no substantial safety hazards exist. If any examples are found, they will be corrected prior to system turnover to Plant Operations. Therefore, at this time, the safety significance remains indeterminate. This issue has been documented in TVA's corrective action program as Problem Evaluation Report 680826 and is being conservatively reported as a programmatic breakdown by WBN Unit 2 under 10 CFR 50.55(e)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 50.55(e) |  |  |  | 0 | 2013-04-01
48870 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-03-30 23:44 | 2013-03-31 15:07 | 2013-05-13 | BOTH TRAINS OF AUXILIARY BUILDING SPECIAL VENTILATION SYSTEM DECLARED INOPERABLE "During testing of the Auxiliary Building Ventilation System it was discovered that the outlet damper of one of the normal make-up fans did not close. This created a non-closable opening in the Auxiliary Bldg Special Vent System (ABSVS) boundary of greater than 10 square feet and required entry into TS [Technical Specification] 3.7.12, Condition B, for two ABSVS trains inoperable due to inoperable ABSVS boundary. This is considered a potential loss of safety function to control the release of material." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MARK LOOSBROCK TO PETE SNYDER ON 5/13/13 AT 1639 EDT * * * "This notification is being made to retract Event Notification (EN) #48870, which reported a non-closeable opening in the Auxiliary Building Special Vent System (ABSVS) boundary of greater than 10 square feet. This required entry into TS 3.7.12 Condition B for two ABSVS trains inoperable due to an inoperable ABSVS boundary. This was considered a potential loss of safety function to control the release of radioactive material. "Engineering evaluation and analysis identified that there was not a loss of safety function because the ABSVS started on demand during the performance of SP 1172 and that the ABSVS Boundary never exceeded the Tech Spec value of 10 square feet per TS 3.7.12. Review of the work order for CD-34042 validated that the system would have performed its safety function during the failure of CD-34042. In the event of a Design Basis Accident the ABSVS would have received a signal to actuate, the system would have performed as designed and drawn a negative differential pressure in the Aux Bldg within 6 minutes with the identified opening of 9.62 square feet that was observed during the failure of CD-34042." The licensee notified the NRC Resident Inspector. Notified R3DO (Riemer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-03-31
48869 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2013-03-31 10:33 | 2013-03-31 11:57 | 2013-04-02 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO A BREAKER EXPLOSION IN THE PROTECTED AREA "At 0750 [CDT] on 3/31/2013, during movement of the Unit 1 Main Turbine Generator Stator (~500 tons), the Unit 1 turbine temporary lift device failed. This caused a loss of all off-site power on Unit 1. The ANO Unit 1 #1 and #2 EDG [Emergency Diesel Generator] have started and are supplying A-3 4160V switchgear and A-4 4160V switchgear. P-4A Service Water pump and P-4C Service Water pump has been verified running. Unit 1 has entered [procedures] 1202.007 - Degraded Power, 1203.028 - Loss of Decay Heat, and 1203.050 - Spent Fuel Emergencies. Unit 1 is in MODE 6. "ANO-1 entered TS 3.8.2 A, 'One Required Offsite Circuit Inoperable'. All required actions are complete. The event caused a loss of decay heat removal on ANO Unit 1 which was restored in 3 minutes and 50 seconds. "Unit 2 tripped and is in MODE 3. Emergency Feed Water was initiated on Unit 2 and Unit 2 was in [Technical Specification] 3.0.3 from 0817 [CDT] to 0848 [CDT] due to Emergency Feedwater. Unit 2 is being powered by off-site. Unit 2 Startup 3 [transformer] lock out at 0921 [CDT]. [Bus] 2A1 is on Start up 2 [transformer] and [bus] 2A3 is on #2 EDG. "10CFR50.72 (b)(3)(iv)(A) - 4-hr. notification due to the ES [Engineered Safeguard Feature] actuation on both Unit 1 and Unit 2. 10CFR50 72 (b)(2)(iv)(B) - 4-hr. notification due to RPS [Reactor Protection System] actuation on Unit 2. 10CFR50.72 (b)(2)(xi) - 4-hr. notification due to Government Notification. 29CFR1904.39a - [OSHA] 8-hr. notification due to death on site. "At 1033 [CDT] on 3/31/2013, Unit 2 entered a Notification of Unusual Event based on EAL HU4 due to damage in 2A1 switchgear. Notification of the NUE will be made lAW Emergency Plan requirements. Follow-up notifications will be made as appropriate." At this time, the full extent of structural damage on Unit 1 is not known. There was one known fatality and 4 known serious injuries to workers. The local coroner is on site for the fatality and the injured personnel have been transported offsite to local hospitals. Investigation into the cause of the failure and extent of damage is ongoing. On Unit 2, all rods inserted during the trip. The core is being cooled via natural circulation. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. The licensee has notified the State of Arkansas, local authorities, OSHA and the NRC Resident Inspector. Notified DHS SWO, DHS NICC, FEMA and Nuclear NSSA (via email). * * * UPDATE FROM DAVID THOMPSON TO HOWIE CROUCH AT 1934 EDT ON 3/31/13 * * * The licensee terminated the NOUE at 1821 CDT. The basis for termination was that the affected bus (2A2) is de-energized and no other equipment on Unit 2 was damaged. The licensee has notified the state and local authorities and will be notifying the NRC Resident Inspector. Notified R4DO (Pick), NRR EO (Howe), IRD (Gott), DHS SWO, DHS NICC, FEMA and Nuclear SSA (via email). * * * UPDATE FROM STEVE COFFMAN TO HOWIE CROUCH AT 1054 EDT ON 4/2/13 * * * The licensee made the following edits to the third paragraph of their original report (edits in quotes): Unit 2 tripped and is in MODE 3. Emergency Feed Water initiated on Unit 2. Unit 2 was in [Technical Specification] 3.0.3 from 0817 [CDT] to 0848 [CDT] due to Emergency Feedwater "being procedurally overridden." Unit 2 "was initially" being powered by off-site. Unit 2 Startup 3 Lock out occurred at 0921. 2A1 is now on Startup 2, and "2A4" is on #2 EDG. Notified R4DO (Kellar) via email. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | Refueling | Power Operation |  | Refueling | Hot Standby |  | UNUSUAL EVENT | 4 | AR | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2013-03-31
48868 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-03-31 04:14 | 2013-03-31 09:08 | 2013-03-31 | RCS FLOW INSTRUMENT LINE THROUGH WALL WELD DEFECT "On 3/31/13 at 0414 EDT, dye penetrant testing identified a 10mm long relevant linear indication on a 3/4 inch RCS flow instrument line weld, between the RCS loop piping and the instrument isolation valve. This constitutes a weld defect in the primary coolant system that cannot be found acceptable per ASME Section XI. This section of piping is unisolable from the Reactor Coolant System. There is no evidence of active leakage currently or during the previous operating cycle, however, based on the dye penetrant testing this is considered a through wall leak. "This event notification is being made in accordance with 10CFR50.72(b)(3)(ii)(A), as a condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. "Unit 1 is currently in a scheduled refueling outage in Mode 5 making preparations to transition to Mode 6. The plant is evaluating the appropriate repair method for this condition. The condition will be corrected during the current refueling outage. Unit 2 is in Mode 1 at 100% power and is unaffected by this condition. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-03-31
48867 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2013-03-29 08:30 | 2013-03-29 17:22 | 2013-04-08 | AGREEMENT STATE REPORT - DENSITY GAUGE FOUND An auction lot of industrial equipment was purchased by West Tech, Inc., an electronics recycling company, at an auction in Milpitas, California. The auction lot was subsequently delivered to West Tech, Inc. in Sparks, Nevada. A CPN density gauge, s/n M17031878, manufactured 1/1/1976, originally containing 50 mCi Americium-241/Be and 10 mCi Cs-137, was found in the auction lot. After discovering the gauge, West Tech, Inc. notified InstroTek, Inc. (parent company of CPN) which notified the State of Nevada Radiation Control Program. The State of Nevada Radiation Control Program dispatched inspectors. The gauge was found to be in its shipping container. The gauge appeared to be undamaged and intact. Swipes were taken and no contamination was found. The State of Nevada Radiation Control Program has impounded the gauge. The State of Nevada will provide more information as it becomes available. * * * UPDATE AT 1601 EDT ON 04/08/13 FROM GENE FORRER (STATE OF CALIFORNIA) TO S. SANDIN * * * The State of Nevada informed the State of California that after checking with the manufacturer, the recovered CPN Moisture Density gauge, S/N M17031878 was registered to American Soil Testing, Licensee # CA5059-43. The gauge will be returned to the manufacturer for disposal. HOO Note: See EN #48895 for report of stolen gauges. Notified R4DO (Deese), FSME Events Resource via email and Mexico via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2013-04-08
48866 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-03-29 | 2013-03-29 13:46 | 2013-03-29 | AGREEMENT STATE REPORT - VETERINARY TECHNICIAN POSSIBLE OVEREXPOSURE The following information was received via facsimile: "The Radiation Safety Officer (RSO) called to report that the quarterly whole body dosimeter for her technician recorded 993 mrem deep, 21,900 mrem to the lens, and 58,000 mrem shallow dose. The technician's finger ring dose was negligible. "The technician & RSO have worked for years injecting three to ten cats with I-131 on a monthly basis (approximately 3 mCi per cat) and neither have ever approached such high radiation doses. "It is suspected that the dosimeter has malfunctioned or was inadvertently contaminated with I-131. The licensee has requested that the dosimeter manufacturer re-analyze the dosimeter. "The Massachusetts Radiation Control Program is investigating." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-04-08
48865 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2013-03-13 17:26 | 2013-03-28 18:39 | 2013-05-10 | LOSS OF REASONABLE ASSURANCE OF OPERABILITY FOR STANDBY LIQUID CONTROL TANK "Information Notice IN 2012-01 on seismic qualification of Standby Liquid Control (SLC) tanks was evaluated in 2012 to assess immediate operability of the SLC system based on SLC Test Tank and Mixing Tank not being qualified to Seismic Class 1S. Based on calculation NEDC 12-015 in response to IN 2012-01, [Cooper Nuclear Station] CNS concluded that SLC was still operable with the test tank full. Long-term actions from the 2012 condition were completed by issuance of calculation NEDC 13-010 and evaluation EE 13-009. NEDC 13-010 concludes that the SLC storage tank is qualified when full and the test tank and mixing tank are qualified when empty. "No procedure step existed in the SLC surveillances to ensure the test tank is drained prior to restoration of SLC to an operable status to ensure it remained fully qualified to its NEDC 13-010 design. Further, no Caution Order or Standing Order existed to ensure short-term control until a procedure change could be implemented. So, as a short-term action, CNS implemented a Standing Order to establish positive control of the test tank. The Standing Order directs that SLC be declared INOPERABLE if the Test Tank is filled. "Initially, this was thought to be a conservative measure only, because CNS judged that reasonable assurance of OPERABILITY remained due to conservative assumptions in NEDC 13-010. However, on 3/19/13 at 2146 CDT, the Prompt Operability Determination was changed to credit the Standing Order as a compensatory measure needed to maintain or enhance OPERABILITY of SLC. Therefore, CNS had lost reasonable assurance of OPERABILITY as of 03/13/2013 at 1726 CDT when the Control Room was notified that NEDC 13-010 concluded the test tank and mixing tank had to be empty to preserve the required seismic qualification, and an 8-hour report should have been made prior to 0126 CDT on 03/14/2013. "Currently the SLC Test Tank is drained and SLC is OPERABLE." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM DAVID MADSEN TO JOHN SHOEMAKER ON 5/10/2013 AT 1436 EDT * * * "This notification is being made to retract Event Notification EN #48865 which was reported on March 28, 2013 for an event occurring on March 13, 2013. This EN identified Cooper Nuclear Station had lost reasonable assurance of OPERABILITY of the Standby Liquid Control (SLC) system based on a CNS design calculation which supported that the SLC test tank was not seismically qualified when full of water. "Subsequently, this calculation was re-evaluated specifically in support of determining OPERABILITY. This re-evaluation determined the SLC system remained OPERABLE when the consideration of nozzle loads is removed. The ability of Class IIS [ASME American Society Mechanical Engineering] seismic components to meet Class II/I [ASME] does not require the consideration of nozzle loads. The SLC test tank, which is a Class IIS [ASME] component, does not fail when filled if no nozzle loads are considered. As such, there was no loss of safety function for SLC." The licensee will notify the NRC Resident Inspector. Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-03-28
48864 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-03-27 | 2013-03-28 17:58 | 2013-05-17 | AGREEMENT STATE REPORT - UNDER DOSE IN BRACHYTHERAPY TREATMENT DUE TO USE OF WRONG LENGTH GUIDE WIRE The following information was provided by the State of Texas via email: "On March 28, 2013, the Agency [Texas Department of Health] was notified by the licensee that a medical event occurred on March 27, 2013. The licensee stated that the wrong length guide wire was used during 3 of 4 HDR [High-Dose Rate Brachytherapy] treatments. The error was discovered after the third treatment. The Radiation Safety Officer (RSO) stated the desired area of treatment was under dosed by more than 50 percent. The treatment plan prescribed 2400 cGy over 4 treatments. He stated that the patient and their physician were notified as soon as the error was discovered. The RSO is not at the facility and is trying to gather the information on the event over his phone. The licensee has suspended all HDR treatments until their process and procedures have been reviewed. Additional information will be provided as it is received in accordance with SA - 300. "Texas Incident #: I-9059" * * * UPDATE ON 4/11/13 AT 2126 EDT FROM ART TUCKER TO DONG PARK * * * The following information was provided by the State of Texas via email: "On April, 9, 2013, the licensee provided the following information: The Physicist of record retrieved tube connectors from the HDR supplies on shelves in the dosimetry area. The tube/connectors were stored, coiled in Ziploc bags. The Physicist selected green tubes when he saw the black tubes used previously were not on the shelf. He was unaware that there were two sets, each a different length when he selected the green set. The black tubes measure 120cm in length and the green tubes measure 132cm. The Senior Physicist, who was on vacation during the first two out of the four treatments, stored the black tube set in a drawer across the room. Physicist selected tubes which attached to the patient's treatment device. The Physicist planned the patient's treatment with the treatment lengths (119.9 cm) stated in our facility's HDR tandem and ring treatment planning procedure and forms but used the 132cm tube for the treatment delivery for three out of four fractions. Only the black tubes were used historically in tandem and ring HDR procedures and since their given length were known, they were not measured at the time of treatment delivery. The green tubes were also not measured prior to treatment delivery. The Physician of record saw the green tubes and believed their use was intentional. This medical event meant the patient's tissue to be treated (cervix) received less total radiation dose than that prescribed: 1,390 cGy (mean dose delivered) vs. the 5,139 cGy the cervix would have received over the four treatments. This is more than a 50 cGy (50 rem) effective dose equivalent difference to the cervix. In addition, the mean total dose delivered to the cervix over the four treatments differed from the prescribed dose by more than 20% (42.1% is the actual variance) and the delivered dose for at least one of the fractions differed by more than 50% from the prescribed dose (fraction #1 cervix mean dose delivered was 42.5 cGy vs. the 1,192.4 cGy expected) (fraction #2 cervix mean dose delivered was 34.6 cGy vs. the 1,416.3 cGy expected) and (fraction #3 cervix mean dose delivered was 45.2 cGy vs. the 1,262.2 cGy expected). The patient's urethra received a mean dose of 1,607 cGy for the four fractions. The maximum dose to 1 cc of the urethra for the four fractions was 1,849 cGy. The patient's anterior vagina received a mean dose from the four fractions of 1,549 cGy. The maximum dose to 1 cc of the anterior vagina for the four fractions was 3,049 cGy. The Agency [Texas Department of Health] has requested additional information from the licensee. Additional information will be provided in accordance with SA 300." Notified R4DO (Deese) and FSME Events Resource via email. * * * UPDATE AT 1107 EDT ON 5/17/2013 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The reference to a guide "wire" in the initial report was incorrect. An incorrect guide "tube" was used. Additionally, the title should have stated "GUIDE TUBE." Notified the R4DO (Walker). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-04-17
48863 | 0 | INTEGRATED RESOURCES, INC. |  |  |  |  | 2013-03-27 15:30 | 2013-03-28 15:53 | 2013-08-21 | PART 21 REPORT - FOXBORO POWER SUPPLY POTENTIAL FAILURES DUE TO DEFECTIVE TIE WRAPS AND HOLDERS Mr. John F. Brosemer, President of Integrated Resources, Inc., reported discovery of repeated defects in Foxboro Meter Company's N-2ARPS-A6, Style D power supplies. When manufactured, the power supplies utilized Thomas and Betts TC105A aluminum wire tie holders in random numbers and placements. As the power supplies age, the tie wrap holder adhesive degrades and the tie wraps embrittle resulting in the separation of the tie wraps and loss of holder adhesion to the power supply enclosure. This causes the wraps and holders to fall to the bottom of the enclosure which could result in shorts when the aluminum comes in contact with electronic components. In one particular power supply, all tie wrap holders in use failed and separated from the enclosure. The power supplies are used in Foxboro SPEC-200 cabinetry that are used throughout the industry. At the time of this notification, Integrated Resources has one power supply from Three Mile Island and two power supplies from Ft. Calhoun undergoing refurbishment. Integrated Resources will be following up this telephonic notification with a written report once their internal investigation is done. Recommended corrective actions are for affected facilities to open and inspect all power supplies and remove the aluminum tie wrap holders and replace the tie wraps and holders with Teflon types. * * * UPDATE FROM BROSEMER TO SNYDER AT 1530 EDT ON 4/1/13 * * * "Suspecting this to be a common mode failure IRI [Integrated Resources, Inc.] opened and inspected two Foxboro N-2ARPS-A6 power supplies which were sent to IRI for refurbishment by Fort Calhoun Nuclear Station. Examination revealed that both of the power supplies have the same failures of the tie wrap aluminum mounting plates adhesive with the majority of the plates being held on the wire bundles by age embrittled nylon wire ties. "Confirmation of the common mode failure by inspection of the Fort Calhoun Nuclear Stations was on or about 1530 CDT on March 27, 2013. "IRI is not the OEM or Original supplier for this power supply and cannot provide the number nor locations of these components. However, by searching the RAPID database IRI has found the power supplies at the following: "Arizona Public Service - Palo Verde Nuclear Generating Station; Constellation Energy - Nine Mile Point Nuclear Power Plant; Detroit Edison - Fermi 2 Nuclear Power Plant; Dominion Nuclear - Millstone Nuclear Power Plant; Dominion Nuclear - Kewaunee Nuclear Power Plant; Eletronnuclear - Angra Nuclear Power Plant; Entergy Nuclear - Arkansas Nuclear One; Entergy Nuclear - Indian Point Energy Center; Entergy Nuclear - Pilgrim Nuclear Power Plant; Entergy Nuclear - J. A. Fitzpatrick Nuclear Power Plant; Exelon Corporation - Three Mile Island Nuclear Plant; Exelon Corporation - Peach Bottom Atomic Power Station; NextEra Energy - Point Beach Nuclear Power Plant; Progress Energy Florida - Crystal River Nuclear Power Plant; Southern California Edison - San Onofre Nuclear Generating Station. "IRI suspects several other utilities and units are affected by this report. Corrective action taken: "IRI's preliminary suggestion is inspection and removal of failed tie wrap mounting plates which are being held on to wire bundles by aging nylon tie wraps. IRI also suggests replacement of age embrittled nylon tie wraps with Tefzel tie wraps." Contact Information: John F. Brosemer; President Integrated Resources, Inc. 113 South 9th Street Nebraska City, NE 68410 Notified R1DO (Dwyer), R2DO (Seymour), R3DO (Daley), R4DO (Kellar) and Part 21 Reactors (Email). * * * UPDATE FROM JOHN BROSEMER (VIA EMAIL) ON 8/21/13 AT 1628 EDT * * * "IRI's final recommendations are to remove all Thomas and Betts Co. model TC105A wire tie holders and to replace any embrittled wire ties with TEFZEL wire ties in all of the affected Foxboro Co. power supplies. "IRI also discovered during the course of the investigation that Thomas and Betts Co. supplied these wire tie holders through normal distribution to all of the manufacturers. IRI recommends that the industry, during normal inspections, inspect for the these types of wire tie holders in all other installed equipment and to remove the failed wire tie holders." Notified R1DO (Schmidt), R2DO (Haag), R3DO (Kozak), R4DO (Werner) and Part 21 Reactors (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-28
48862 | -1 | ATC NUCLEAR |  |  |  |  | 2013-01-21 | 2013-03-28 15:29 | 2013-06-05 | INTERIM PART 21 REPORT INVOLVING REVIEW OF SEISMIC TESTING METHODOLOGY The following information was received via fax: "ATC Nuclear in Oak Ridge, TN is making an initial notification of a Potential Part 21 Defect in accordance with 10 CFR 21.21(a)(2). "A recent review performed January 21, 2013 of seismic Test Response Spectra (TRS) for seismic qualification activities identified that Required Response Spectra (RRS) may not have been completely enveloped for portions of the required frequency range during test performance of the Operational Basis Events (OBE's) and the Safe Shutdown Earthquake(s) (SSEs) for some customers. Specifically, some TRS results may have been below the provided RRS in the 10-25 Hz range in certain circumstances and thus not fully meeting the RRS and required acceptance criteria of IEEE 344 1975/1987/2004. The condition is the result of the instrumentation methodology and inherent tri-axial table characteristics where vibrational energy is not fully transmitted to the unit under test in all test conditions. The safety significance is that the Basic Component may not perform its intended safety function during or following a seismic event exceeding the as-tested vibration frequencies. ATC has demonstrated through actual testing to date that this probability is very low. Many customers provide RRS that include conservatism; however, this also has not been credited in the ATC Nuclear evaluation methodology discussed below. The affected customers, purchase orders, and relevant information have been provided as Attachment 1 [not attached to this report - customers notified were XCEL Energy, Bechtel Power Corporation, TVA for Watts Bar 2 (Projected Operation 12/2015) and Preferred Metal Technologies, Inc.] to this interim notification. "ATC Nuclear developed a systematic evaluation methodology which has been independently corroborated by industry experts to evaluate the seismic tri-axial test programs of concern conducted by ATC Nuclear. The systematic evaluation involves review of the TRS to determine if adequate test margin exists within the test data when compared to the RRS, evaluation of the table test acceleration versus fixture acceleration as necessary, and when required, retesting of the component. For all program reviews completed to date (~70% of all programs) for operating licensees, all re-evaluation and re-testing has resulted in no reduction in seismic withstand capabilities and no failures. The evaluation included prioritization of operating reactors early in the process to the extent possible to ensure minimal impact to those facilities. "Based on the successful completion of evaluations to date, ATC Nuclear is confident this issue will be resolved through the methodology established and worst-case may result in the submittal of an addenda to existing qualification reports in situations where retesting has been required for a basic component. "ATC Nuclear will need until May 15, 2013 to conclude the evaluation process. Should, during any re-testing, a condition arise warranting notification, that notification will be immediately made at the time of discovery to the affected customer. All orders since the point of discovery have been addressed through corrective actions to prevent recurrence and are unaffected. "The below contact information should be utilized regarding any questions. R.A. Chalifoux Vice-President QA, ATC Nuclear Tel: (865) 384-0124 email: rchalifoux@argoturbo.com" * * * RETRACTION FROM R.A. CHALIFOUX VIA FAX AT 0957 EDT ON 6/5/13 * * * The following information was obtained from ATC Nuclear via facsimile: "ATC Nuclear in Oak Ridge, TN has concluded the evaluation of a potential Part 21 defect in accordance with 10 CFR 21.21(a) (2). The evaluation for reportability with respect to the remaining licensees in Attachment 1 of the original NRC Interim Report (ML1309/ML13091A388) determined, as anticipated, no safety degradation exists. Based on the results of the evaluation, reportability under 10 CFR Part 21 is not required for this issue. Affected customers will be receiving revised documentation as appropriate. "The [above] contact information should be utilized regarding any questions." Notified R1DO (Burritt), R2DO (McCoy), R3DO (Lipa), R4DO (Spitzberg) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-03-28
48861 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-03-28 08:04 | 2013-03-28 10:15 | 2013-03-29 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the Oyster Creek Generating Station has removed the Technical Support Center (TSC) ventilation system from service. The TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately fourteen hours and will return to service at approximately 2200 [EDT] March 28, 2013. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM ERIC SWAIN TO HOWIE CROUCH AT 1245 EDT ON 3/29/13 * * * The TSC ventilation system was returned to service at 1240 EDT. The licensee has notified the NRC Resident Inspector. Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-28
48860 | -1 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-03-27 22:45 | 2013-03-28 00:43 | 2013-04-02 | ONE EMERGENCY WARNING SIREN ENERGIZED FOR A SHORT TIME "At 2245 [EDT] on 3/27/2013, Surry Power Station (SPS) Operations Department received a report from Virginia State Emergency Operations Center (VEOC) that a concerned citizen had called James City County (JCC) law enforcement to report that an Early Warning System (EWS) siren, #62 in James City County NW side of Route 682, was sounding. VEOC reported JCC police received call at 2240 [EDT] from a concerned citizen that an EWS siren was sounding. SPS Security contacted JCC police and subsequently reported that JCC police responded approximately 10 minutes later to the site of the siren, but the siren was no longer sounding. Maintenance will investigate in the morning. All plant conditions/parameters are normal and no releases to the environment have occurred. "The site NRC Resident Inspectors have been notified. "This notification is being transmitted due to notification of other Government Agencies in accordance with 10CFR50.72(b)(2)(xi)." The licensee also notified the state and local governments. * * * UPDATE FROM JASON SWEATMAN TO STEVE SANDIN ON 4/2/2013 AT 1710 HOURS * * * "This report is being retracted based upon the following: "On 3/28/13, an activation verification test was performed. The results of the test indicated EWS siren #62 did not activate. In addition, when a siren activates, the battery voltage decreases. A review of the battery voltage trend for siren #62 found no such decrease, verifying no activation occurred. Maintenance staff reported to the siren location and confirmed the siren did not activate. They also found no indication of tampering or intrusion. Three local homeowners were interviewed and stated they did not hear any siren activation. "By all available indications, EWS siren #62 was functional and did not activate on 03/27/13. "NRC Site Resident Inspectors have been notified of the retraction." Notified R2DO (McCoy). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-03-28
48859 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-01-16 | 2013-03-27 17:02 | 2013-04-29 | DISCOVERY OF TWO RADIOACTIVE GAUGES IN LOCKED STORAGE The following information was obtained from the Commonwealth of Massachusetts via email: "[On approximately] 1/16/13, two surface gauges [manufactured in 1961 were] found in locked storage within [a] remote airfield facilities building at Worcester Regional Airport, Worcester, MA. Third-party waste brokers [were] contacted to bid on proper removal. Wipe tests by a third-party waste broker indicate no leakage of radioactive contamination from [the] gauge sources. [The Massachusetts Radiation Control Program (the Agency) received the information via email] on 3/19/13. The Agency conducted a site visit to confirm device identifications on 3/26/13. A waste brokers' bid [was] accepted [and] packaging and removal [is] scheduled for 4/17/13. Gauges [are being] held in locked storage until removal by [the] waste broker. "[The] items [are] described as one Nuclear-Chicago Corporation Model P21 Surface Moisture Probe, SN 136, containing 5 mCi Ra-Be, date stamped 5/2/61; and one Nuclear-Chicago Corporation Model P22A Surface Density Probe, SN 139, containing 3 mCi Cs-137, date stamped 5/23/61. "The Agency considers this matter to be open until [the] items [are] confirmed removed on 4/17/13." * * * UPDATE FROM ANTHONY CARPENITO TO CHARLES TEAL ON 4/19/13 AT 1132 EDT * * * "4/19/13 UPDATE - The Agency [Massachusetts Radiation Control Program] considers this matter to be OPEN until items confirmed removed for disposal. "Agency [Massachusetts Radiation Control Program] regulation 105 CMR 120.281 (A)(1) and USNRC regulation 20.2201 (a)(1)(i) requires 'immediate' telephone reporting of stolen, lost or missing licensed radioactive material in specified quantities under circumstances that it appears an exposure could result to individuals in unrestricted areas. The situation in this case involved 'found' radioactive material, devices already wipe tested to confirm no leakage of radioactive contamination and stored in a 'secure' location to prevent exposure to individuals until such time that scheduled packaging and removal by a waste broker is completed, and therefore, did not warrant immediate notification. This case was determined to be included in the 30-day notification category. The written report to NMED was issued one day after the Agency [Massachusetts Radiation Control Program] confirmatory site visit of 3/26/13." NMED Report #: 130149 Notified R1DO (Cook) and FSME Event Resource via email. * * * UPDATE ON 4/29/2013 AT 1142 EDT FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * "The gauges were removed and shipped for disposal on 4/24/13. The Agency (Massachusetts Radiation Control Program) considers this matter to be closed." Notified the R1DO (Hunegs) and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-04-04
48858 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2013-03-27 12:48 | 2013-03-27 16:06 | 2013-03-27 | SURFACE CONTAMINATION ON OUTSIDE OF PACKAGE EXCEEDING NRC REPORTING LIMITS "Per 10 CFR 20.1906(d)(1), [the Veterans Health Administration (VHA) is] reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received today (March 27, 2013) around 12:48 PM CDT by South Texas Veterans Health Care System, San Antonio, Texas. This medical center holds permit number 42-15881-01 under the VHA master materials license. "Wipe tests performed on the external surface of the package indicated a removable contamination level of 993 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. "The package contained one 30-millicurie dosage of Technetium-99m and was shipped and delivered by Cardinal Health in San Antonio, Texas. The inner packaging materials were slightly contaminated but the dosage itself was not impacted and was able to be used. "The VA facility Nuclear Medicine Technologist immediately notified, by telephone, the Radiation Safety Officer at Cardinal Health about the contaminated package. "As corrective actions: the packaging materials were bagged and set aside in a restricted area at the medical center for decay; staff with access to the area were notified about the contaminated packaging materials; and surveys were performed in the package receipt area to ensure that contamination was not spread beyond the area. "[Veterans Health Administration] notified NRC Region III (K. Null) by telephone of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2013-04-04
48857 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-03-26 | 2013-03-27 11:47 | 2013-03-27 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE DUE TO DAMAGED GUIDE TUBE The following information was obtained from the State of Texas via email: "On March 27, 2013, the Agency [Texas Bureau of Radiation Health] was notified by the licensee that a radiography [camera] guide tube at a temporary field site had suffered damage, causing the source to become unretractable. The source was recovered by the licensee according to the terms of the license. The source was part of a GRP model 880D Sentinel radiography camera, S/N 9185. The source was a 51 Ci Ir-192 sealed source, S/N 91313B. Initial dose estimates show 1.4R exposure to whole body and 2R exposure to the hand by the retrieval worker. The work site was closed so no dose was received by members of the public. More information will be provided as needed per SA300." Texas Incident # I-9060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-04-04
48856 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-01-29 | 2013-03-26 15:23 | 2013-03-27 | AGREEMENT STATE REPORT - CATHETER LEAKAGE DURING TREATMENT "The Division of Radiological Health was notified on Tuesday March 26, 2013, by a representative from Vanderbilt [University], of a misadministration. A patient was treated January 29, 2013, with Iodine 131-MIBG [metaiodobenzylguanidine]. The patient stayed in the hospital for 4 days until February 2, 2013. Foley catheter leakage occurred during this interval, but not recognized as a misadministration because there was no visible effect. "The patient returned for a second treatment on March 19, 2013, at that time a rash was noted and attributed to the catheter leakage during the initial treatment in January. "Inspectors from the Nashville Field Office will [request additional information and] follow-up and keep NRC informed of the status of our investigation." Tennessee Division of Radiological Health Report Number: TN-13-044 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-04-04
48855 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2013-03-27 08:00 | 2013-03-27 09:14 | 2013-03-27 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR MAINTENANCE "This is a non-emergency eight hour notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of a emergency response facility. "Planned maintenance activities are being performed today (March 27, 2013) to the Technical Support Center (TSC) HVAC. The work includes both corrective and preventive maintenance to the TSC HVAC system. This work activity is planned to be performed and completed expeditiously within about 14 hours. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC concurrent with this work activity as long as habitability conditions allow. Additionally, plans are in place to expedite the return of the system should an emergency condition occur. The emergency response organization duty team members will be relocated to an alternate location if required by habitability conditions in accordance with emergency implementing procedures. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM DAVE LEWIS TO HOWIE CROUCH AT 1511 EDT ON 3/27/13 * * * The Technical Support Center has been returned to service. The licensee has notified the NRC Resident Inspector. Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-27
48854 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2013-03-27 06:01 | 2013-03-27 07:30 | 2013-03-27 | SAFETY INJECTION ACTUATION DURING TESTING "On March 27, 2013 at 0601 EDT, the Safety Injection System automatically actuated while in Mode 3 during performance of I&C [Instrument and Control] testing due to faulty test equipment. All plant equipment responded normally to the safety injection. This is reportable under 10 CFR 50.72(b)(2)(iv)(A). The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the safety injection signal as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at 1140 psig and 395 degrees F with decay heat removal using auxiliary feedwater to the steam generators and normal heat removal through the atmospheric steam dumps. There was no radiation released. "Indian Point Unit Two was not affected by this event and remains at 100% power. "Notified NRC Resident Inspector. Notified NRC Emergency Operations Center Duty Officer." The Safety Injection was reset and all plant equipment was restored to normal alignment. Pressurizer level remained in the indication range during the Safety Injection. The cause of the Safety Injection is still under investigation, but appears to be related to a faulty jumper necessary for the test. * * * UPDATE FROM MICHAEL McCARTHY TO DONALD NORWOOD AT 1335 EDT ON 3/27/2013 * * * "The event reported above resulted in additional reportable actuations under 10 CFR 50.72(b)(3)(iv)(A). These were: 1) RPS actuation, 2) Phase A containment isolation, 3) Containment fan cooler unit actuation, and 4) Emergency Diesel Generator actuation (start but did not load). "The licensee notified the NRC Resident Inspector of the 1335 EDT update." Notified R1DO (Krohn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-03-27
48853 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2013-03-27 02:45 | 2013-03-27 04:21 | 2013-03-27 | REACTOR PRESSURE BOUNDARY LEAKAGE "On March 26, 2013, at 1635 [CDT], with Unit 1 shutdown for refueling, leakage was identified from the 2-inch reactor head vent line during a Reactor Pressure Vessel (RPV) pressure test. The leakage was approximately 20 drops per minute. The RPV pressure test was stopped and the reactor vessel depressurized to facilitate examination of the piping and associated flange connections. At 0245 hours on March 27, 2013, the leak was confirmed to be through-wall originating from a socket weld (i.e., pipe elbow). The cause and resolution are under evaluation. The condition is being reported under 50.72(b)(3)(ii)(A) given the defect was associated with the primary coolant system pressure boundary." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-03-27
48852 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2013-03-26 06:20 | 2013-03-26 19:06 | 2013-03-26 | TSC EMERGENCY VENTILATION SYSTEM CONTROL SWITCH DISCOVERED IN THE OFF POSITION "This is a non-emergency notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(xiii), Loss of Emergency Preparedness Capabilities. "On 3/26/13 at 0620 EDT, during a routine surveillance of the Technical Support Center (TSC), the TSC emergency ventilation system control switch was discovered in the off position (vs. auto). The Operations department was notified and the TSC emergency system ventilation was returned to normal alignment (auto) at 0644 EDT. "The switch normally operates in the 'auto' position, so that TSC emergency ventilation system can be automatically initiated from a control room isolation signal. In accordance with station operating procedures, upon initial responder activation to the TSC, the TSC ventilation system is also manually placed in service. The TSC emergency ventilation system was capable of manual initiation and was not out of service for repair or maintenance. "An investigation is underway to understand the circumstances associated with the control switch misalignment." The licensee notified the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-26
48851 | 0 | ELECTROSWITCH |  |  |  |  | 2013-03-26 | 2013-03-26 09:01 | 2013-03-26 | PART 21 - SERIES 24 CSR RELAYS WITH OVERSIZED CAM DRIVE COMPONENTS The following is a summary of a Part 21 report received from Electroswitch, via facsimile: "The root cause has been determined to be oversized OD dimension on the drive cam. This tight fit in the nylon bushing and mounting plate did not allow the drive cam to close when deenergized. "NOTE: Any switches that have passed the bench test and/or are in operation will not degrade nor have the condition as found with the returned switches." Affected Facilities: Waterford, Surry, and Harris. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-26
48850 | 0 | FAIRBANKS MORSE |  |  |  |  | 2013-01-28 | 2013-03-25 19:10 | 2013-03-25 | PART 21 REPORT - FOREIGN MATERIAL INSIDE EDG AIR START PIPING Facility Affected: Xcel Energy - Prairie Island Nuclear Generating Plant (PINGP). Component Affected: OP Engine- Air Start Piping Assemble (p/n 11879060*00) shipped after October 23, 2012. Supplier: Fairbanks Morse Engine, 701 White Ave., Beloit, WI 53511. Nature of Defect: During a routine emergency diesel generator (EDG) test on 1/28/2013, one of the two redundant air start systems was isolated from the other and the single air start system failed to start the EDG due to the foreign material in the solenoid valve. The foreign material removed from the solenoid valve during failure analysis appears to be liquid pipe sealant used to seal threaded pipe joints during assembly. Safety Hazard Which Could Be Created By Such Defect: Foreign material within both of the redundant air start piping systems could become lodged in both of the solenoid valves. Simultaneous failure of the two solenoid valves would prevent the emergency diesel generator from starting. Corrective Action: PINGP has completed disassembly and cleaning of both piping systems to ensure no foreign material remains within the piping system. FM will create a workmanship standard for pipe sealing, hydrostatic testing, and pressure testing that will include a foreign material exclusion program to ensure cleanliness of assemblies. This will be completed by June 30, 2013. FM has issued Corrective Action No. 2609 in its Quality Assurance Program. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-25
48849 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-03-25 10:30 | 2013-03-25 19:21 | 2013-03-25 | ONE ALERT NOTIFICATION SIREN REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 25, 2013, at 10:30, Mountain Standard Time, Palo Verde Nuclear Generating Station (PVNGS) removed Alert Notification System (ANS) Siren 22 from service for planned maintenance. Siren 22 provides notification to approximately 1455 members of the public within five miles of PVNGS. "Siren 22 is expected to be returned to service on March 27, 2013. "County authorities have been notified of this planned maintenance activity and appropriate contingency measures have been established to compensate for the non-functional siren. The PVNGS Emergency Plan contains contingencies for notification of members of the public within the affected area during an emergency when a siren is out of service. "There are no events in progress that require ANS operation. The NRC Resident Inspector and the Maricopa County Sheriff's Office have been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-25
48848 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2013-03-25 08:20 | 2013-03-25 12:05 | 2013-03-25 | AGREEMENT STATE REPORT - INTERNAL LEAD SHIELDING OF GAUGE SOURCE HOLDERS MELTED The following information was received via facsimile: "The Alabama Office of Radiation Control received a call at 0820 CDT on 3/25/13 from Dr. Michael Hensley of RSO Services (AL license No. 1482), a gauge service company. He had been contacted by IIG, MinWool, LLC in Phenix City, AL (AL license No. 986) to assist them with an issue. The licensee melts rock in a cupola to make insulation. The cupola has two Ohmart Model SR-A devices, one at the top and one at the bottom of the cupola, each containing a 100 mCi Cesium-137 source. The cupola was superheated to about 3,500 degrees Fahrenheit above the operating limits for the Model SR-A devices. It is believed the lead shielding in the devices liquefied, but because the source holders are sealed, the lead was contained inside the devices and did not leak out. "Dr. Hensley surveyed the devices and found a maximum reading of 2.5 mR/hr at 12 inches from the back of the device which was located at the top of the cupola. This is lower than the design maximum exposure of 4.8 mR/hr with a 100 mCi source per the SSDR. The shutters on both devices were still operable, and were closed and locked. Dr. Hensley will remove the devices and prepare them for shipment to Ohmart." Alabama Incident No.: 13-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2013-04-02
48847 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2013-03-23 23:18 | 2013-03-24 13:16 | 2013-03-28 | SWITCHGEAR ROOM DEGRADED FLOOD SEALS "On 3/23/13 it was identified that a conduit flood seal between an outside manhole and the switchgear rooms is displaced. This degraded flood seal compromises the flooding design of both the East and West Switchgear Rooms. "Compensatory measures were implemented for the flood seal in accordance with the plants barrier control process. Repairs of the seal are in progress." Per the licensee these switchgear rooms contain both normal and safety related 4kV and 480 V electrical boards. Compensatory measures implemented include: Plant Maintenance personnel will take actions to seal any leak within 24 hours of a flooding event and also provide sump pumps to remove any water that has leaked in. The licensee notified the NRC Resident Inspector and the Vermont State Liaison. * * * UPDATE AT 2000 EDT ON 03/28/13 FROM BOB VITA TO S. SANDIN * * * "This is an update to NRC Event No. 48847 reported on 3/24/13 at 1316 [EDT]. "On 3/27/2013 the extent of condition review identified two additional possible water intrusion paths from the outside to the switchgear rooms. "Compensatory measures were implemented for these paths in accordance with plant procedures. Efforts to seal these paths are in progress." This is an on-going extent of condition assessment. The licensee will inform the NRC Resident Inspector and the Vermont State Liaison. Notified R1DO (Krohn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2013-03-24
48846 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2013-03-24 04:58 | 2013-03-24 09:54 | 2013-03-24 | AUTOMATIC START OF AN EMERGENCY DIESEL GENERATOR DUE TO A LIGHTNING STRIKE "At 0458 [EDT], a lightning strike caused a voltage disturbance on the 115 KV offsite power source and resulted in the automatic start of the 'A' emergency diesel generator on an undervoltage relay actuation. The 'A' emergency diesel generator came up to rated frequency and voltage. The voltage disturbance [duration] was not long enough to cause the normal incoming breaker to the 'A' train 7.2 KV safety related bus (XSW1DA) to open or the 'A' emergency diesel generator output breaker to close. "The voltage disturbance caused the 'A' safety related chiller and some ventilation fans to trip. These loads were subsequently restarted with no issue. "The 'A' emergency diesel generator was secured and made ready for autostart at 0520 [EDT]. "The station is in Mode 5 for a mid cycle outage to repair a reactor coolant pump seal. "This notification is being made per 10CFR50.72(b)(3)(iv)(A) as a valid actuation of an emergency diesel generator." The unit is in a normal electrical shutdown plant configuration. The licensee notified the NRC Resident Inspector and will notify the State and Local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-03-24
48845 | -1 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-11-19 19:00 | 2013-03-22 19:58 | 2013-05-20 | CONTROL ROD DRIVE CHECK VALVE IN SERVICE LEAK TEST FAILURE "Control Rod Drive (CRD) Check valves 3-0399-593 and 3-0399-594 are installed on the CRD supply header inside the reactor building to prevent unfiltered radiological release from primary containment past secondary containment through the CRD supply header. The [Design Basis Accident] DBA [Loss of Coolant Accident] LOCA dose analysis does not postulate the CRD supply piping as a release path. These valves were added in response to NRC IN 90-78. Their function is described in the Dresden UFSAR section 4.6.4.6. "CRD check valves 3-0399-593 and 3-0399-594 failed their as found In Service Testing (IST) seat leakage test during refuel outage D3R22. "Based on the condition of as-found failed seat leakage tests, Engineering determined that CRD check valves 3-0399-593 and 3-0399-594 would not have been able to perform their design functions as described in the UFSAR to maintain the offsite dose and control room dose within regulatory limits. "The valves were repaired in D3R22 and successfully retested." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RILEY RUFFIN TO HOWIE CROUCH ON 5/20/13 AT 1140 EDT * * * "Based on an evaluation of the current plant design and the overly conservative assumptions made in the 1996 dose estimate, the dose that would be experienced as a result of a DBA LOCA with LOOP [Loss of Offsite Power] due to back leakage through the control rod drive system to the condensate storage tanks [CST] has been reassessed. The initial estimations of dose did not consider the as-built piping configuration of the CRD system. The backflow would be greatly reduced due to the lower differential pressure between the Drywell and CSTs that would exist following a DBA-LOOP. This differential pressure experienced following a DBA-LOOP would not result in a significant backflow due to excess flow check valves and restricting orifices in the current CRD piping configuration. Additionally, in the event that any backflow did occur, the volume of water in the CST would provide a high decontamination factor and dilution. Therefore backflows that could be experienced following a DBA-LOOP would not produce doses that would exceed current limits. "Based on this assessment, the unanalyzed condition that was reported on March 22 (EN 48845) is being retracted." The Licensee has notified the NRC Resident Inspector. Notified R3DO (Kozak). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-03-22
48844 | 0 | TENNESSEE VALEY AUTHORITY |  |  |  |  | 2013-03-22 | 2013-03-22 17:06 | 2013-03-22 | DIESEL FUEL INJECTORS FAILED A PRESSURE TEST "The Tennessee Valley Authority (TVA) recently identified that three (3) fuel injectors that were to be used on the 3A Emergency Diesel Generator failed a pressure test. Corrective Action Program documents were written to document the failure of the fuel injectors to pass a pressure test and to require performance of an engineering evaluation of the condition. It was concluded that this condition has the potential to constitute a reportable condition pursuant to Title 10 of the Code of Federal Regulations (CFR), 10 CFR 21, 'Reporting of Defects and Noncompliance,' and, as such, requires additional evaluation. "The TVA is working with Engine Systems, Inc., to determine the cause of failure of the fuel injectors. At this time, the evaluation is not expected to be complete until May 31, 2013. Pursuant to the reporting requirements of 10 CFR 21.21(a)(2), if the evaluation of the deviation or failure to comply potentially associated with a substantial safety hazard cannot be completed within 60 days (i.e. by March 23, 2013), an interim report must be submitted to the NRC. "Name and Address of the Individual Making the Interim Report: Mr. K. J. Polson Vice President Browns Ferry Nuclear Plant Tennessee Valley Authority Post Office Box 2000 Decatur, Alabama 35609-2000. "Identification of the firm supplying the basic component which fails to comply or contains a defect (under evaluation): Engine Systems, Inc (ESI) 175 Freight Road Rocky Mount, North Carolina 27804." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-03-22
48843 | 0 | TOPWORX EMERSON PROCESS MANAGEMENT |  |  |  |  | 2013-03-22 | 2013-03-22 16:29 | 2013-03-22 | INCORRECT INSTALLATION INSTRUCTIONS FOR TOPWORX GO SWITCH "Applicability: This notice applies only to TopWorx GO switch models C7, C8, H7, H8, M7, M8, R7, and SV7. "Purpose: The purpose on this TopWorx Information Notice (TIN) is to alert users of the GO Switch models listed above, that TopWorx was made aware of a situation which may affect the performance of the aforementioned equipment. "We are informing you of this circumstance in accordance with Sections 21.21(b) and 50.55 (e) of 10CFR21. "Discussion: Recently TopWorx has discovered that an incorrect 10M (Instructions & Operations Manual) for the above mentioned switches was available on the TopWorx website. Within that IOM it stated: 'Do not to use excessive force on external threads when installing, (36 in.-Ibs. max).' The correct value is 35 Ibs.-ft. max as stated in the current IOM. "Actions Required: Verify the torque value used to install the switches is adequate for the application. "10CFR21 Implications: TopWorx requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21. "From: Brian Hampton Vice President, Global Operations TopWorx 3300 Fern Valley Road Louisville, KY 40213 Fax: (502) 969-7315." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-22
48842 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-03-21 22:40 | 2013-03-22 06:10 | 2013-03-25 | MOMENTARY INNER AND OUTER REACTOR BUILDING ACCESS DOORS OPEN SIMULTANEOUSLY "During performance of surveillance OSP-CONT-M102, secondary containment had been declared inoperable and Technical Specification 3.6.4.1.A had been entered. "Operations personnel performing the surveillance were holding the inner door open and testing the outer door interlock. When the individual presented his badge to the badge reader and attempted to open the outer door, the door opened. Per the surveillance contingency actions, the individual immediately shut the door. Momentarily, both the inner and outer reactor building access doors were open. "The surveillance was completed with no further issues. Technical Specification 3.6.4.1.A was exited and secondary containment was declared operable. "There were no radiological releases associated with this event. "No safety system actuations or isolations occurred." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DIEGO SUAREZ TO DONALD NORWOOD AT 17:55 EDT ON 3/25/2013 * * * "The licensee is retracting this event based on the following: During subsequent evaluation for reportability, guidance in NUREG-1022 was reviewed. NUREG-1022 provides that removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function) is generally not reportable. "In the case of this event, the secondary containment system was removed from service as part of a planned surveillance test. TS Action 3.6.4.1.A was entered as directed by the governing surveillance procedure in anticipation of the airlock interlock testing which, by the very nature of the test, could result in both doors in a given airlock being open simultaneously. "The event described above should not have been reported in consideration of the guidance provided in NUREG-1022 and did not constitute a reportable event as a condition that could have prevented the fulfillment of a safety function under 10CFR50.72(b)(3)(v)." The licensee will notify the NRC Resident Inspector. Notified R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-03-22
48841 | 0 | EI DUPONT DE NEMOURS, PENCADER SITE |  |  |  |  | 2013-03-21 | 2013-03-21 16:25 | 2013-03-21 | MISSING TRITIUM EXIT SIGN EI DuPont de Nemours and Company Inc.(DuPont) during a routine periodic audit identified that one tritium exit sign was missing from a doorway at their Pencader Site. It is believed that the sign was misplaced during recent remodeling/construction in the area. A thorough search has been conducted by both the demolition vendor and DuPont and the sign is presumed lost. The missing sign was a Betalux E-Series, Model 171, Serial Number C090859 with a manufacture date of 7/2012. There was 21.6 curies of tritium gas in the sign at the date of manufacture. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-03-29
48840 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-03-21 05:07 | 2013-03-21 10:09 | 2013-03-21 | RADIATION MONITORS INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At approximately 0507 EDT on March 18, 2013, radiation monitor RM-01TV-3536-1, Turbine Vent Stack Wide Range Gas Monitor (WRGM) was declared inoperable for pre-planned corrective maintenance. Compensatory actions were put in place to sample per the requirements of the Offsite Dose Calculation Manual (ODCM) and the duration of the maintenance was originally not expected to take longer than 72 hours. This event is now reportable because the planned equipment outage exceeded 72 hours. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health or safety of the public or the operation of the facility. Compensatory actions remain in place to sample per requirements of ODCM. "The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-21
48839 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-03-19 | 2013-03-21 09:13 | 2013-03-21 | AGREEMENT STATE REPORT - Y-90 SIR-SPHERE UNDER DOSE OF 87% "The licensee notified the Department [Ohio Department of Health] on March 20, 2013 of a medical event that occurred on March 19, 2013 involving a Y-90 SIR-Sphere patient treatment. The delivery system became clogged and delivered only 3.2 mCi (13%) of the 24.3 mCi prescribed activity. The cause of the event is under investigation. The licensee plans on retreating the patient." Ohio Item Number: OH130002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2013-03-29
48838 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-03-20 19:51 | 2013-03-20 22:41 | 2013-03-20 | MANUAL REACTOR TRIP DUE TO LOSS OF GENERATOR STATOR COOLING WATER "At 1951 CDT on March 20, 2013, Byron Unit 2 Reactor was manually tripped due to the loss of all Generator Stator Cooling Water. 2BEP-0, 'Reactor Trip or Safety Injection Unit 2' was entered and a transition was made to 2BEPES 0.1, 'Reactor Trip Response Unit 2.' The auxiliary feedwater pumps automatically actuated upon the expected low steam generator level. Upon the trip, it was noted that a Digital Rod Position Indication System Urgent Failure occurred with a General Warning on Control Rod position M12. Indication for the Train 'B' Reactor Trip breaker was lost. All Control Rods inserted upon Reactor trip and the Train 'B' Reactor trip breaker was locally verified open." The plant is in its normal shutdown electrical lineup. No safeties or reliefs lifted during the event. There was no impact on unit-1. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-03-20
48837 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-03-20 14:47 | 2013-03-20 20:52 | 2013-03-21 | HIGH PRESSURE COOLANT INJECTION (HPCI) TURBINE OIL LEAK "After securing the Unit 1 HPCI turbine from service following a planned pump, valve, and flow surveillance test an oil leak of approximately 1 pint per minute developed. The oil leak was stopped by securing the auxiliary oil pump for the HPCI system. "There was no loss of oil pressure while the HPCI turbine was operating. This issue has caused the Unit 1 HPCI system to be declared inoperable and unavailable. Per LGS [Limerick Generating Station] Unit 1 Technical Specifications section 3.5.1, the HPCI system must be restored to operable status within 14 days. "The cause of the oil leak is being investigated." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DANIEL WILLIAMSON TO DONALD NORWOOD AT 1510 EDT ON MARCH 21, 2013 * * * "UNIT 1 HPCI has been restored to operable status following repairs and post-maintenance testing at 1300 EDT on March 21, 2013." The licensee changed the reporting requirement from 10CFR50.72(b)(3)(ii)(A) to 10CFR50.72(b)(3)(v((D). The licensee will notify the NRC Resident Inspector. Notified R1DO (Trapp). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-03-20
48836 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-03-20 | 2013-03-20 16:20 | 2013-03-20 | AGREEMENT STATE REPORT - RADIOGRAPHER OVEREXPOSURE The following report was received via e-mail: "[The Oklahoma Department of Environmental Quality was] informed of an over-exposure of a radiographer employed by Tulsa Gamma Ray (OK-17178-02). The dose involved is 6700 mR, but it isn't clear if this is the dose from just this exposure or if that is for the year to date. We [Oklahoma] will provide more details as they become available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 0 |  | OTH | AGR |  |  |  |  | 0 | 2013-03-28
48835 | -1 | US ARMY |  |  |  |  | 2013-03-19 | 2013-03-20 10:08 | 2013-03-22 | SENSITIVE INFORMATION - FOR INTERNAL NRC RELEASE ONLY EVENT RETRACTED BEFORE RELEASE POTENTIALLY DAMAGED MORTAR SIGHTING SYSTEM CONTAINING TRITIUM The radiation safety program manager for the US Army TACOM Lifecycle Management Command reported that a 60 mm Mortar Sighting System containing approximately 29 Curies of tritium may have been damaged or destroyed in an explosion at the Hawthorne Army Depot in Hawthorne, Nevada. At this time, the area of the explosion has been isolated and the investigation into the explosion is underway. The Army representative stated that it is possible that this system was being used in the mortar training when the explosion occurred. There is no other information at this time on the condition of the tritium mortar system. * * * RETRACTION FROM KAREN MCGUIRE TO VINCE KLCO ON 3/22/13 AT 0918 EDT * * * Notified by the US Army TACOM Lifecycle Management Command radiation safety program manager that the event should be retracted. An investigation revealed that there was no source damage from the explosion. The Army representative requested that the event not be released. Notified R3DO (Passehl) and FSME Events Resource via email. * * * UPDATE OF RETRACTION FROM KAREN MCGUIRE TO DONALD NORWOOD AT 1223 EDT ON 3/22/13 * * * "In accordance with our phone conversation today at 0918 eastern time, there was no release of radioactive material (Tritium), therefore this is a non-event which does not require reporting. "The item containing tritium was not damaged in the incident. Due to the fact, that there was no radioactive material (Tritium) release, the Army is requesting that the event notification be retracted without public notification of the reporting of the event and of the retraction. "The reasons for this are: (1) No release of the radioactive material (Tritium) and (2) The sensitive nature of the event where there were non-radiation caused fatalities and this could create additional unneeded stresses for the parties involved in the event, which is not justified due to the non-release of the radioactive material." This retraction was discussed with the FSME DEO (McIntosh). It was agreed that this event would not be released to the public web site but would be released for internal NRC distribution only. Notified R3DO (Passehl), FSME DEO (McIntosh), and FSME Events Resource via email. SENSITIVE INFORMATION - FOR INTERNAL NRC RELEASE ONLY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 1 | 2013-03-19
48834 | 0 | ASCO VALVE INCORPORATED |  |  |  |  | 2013-03-20 08:38 | 2013-03-20 10:41 | 2013-03-20 | PART 21 - ASCO DIRECT ACTING 3-WAY SOLENOID VALVE FAILURE The following is a summary of a Part 21 report received from ASCO Valves Inc., via facsimile: ASCO received a failed solenoid actuated valve from its distributor (Areva). The valve has been qualified for 1-E nuclear use and is referred to as a NP8320 direct acting 3-way valve. The valve that failed would not shift when de-energized. Information accompanying the valve identified that it was operating for approximately three months since August 2012. The valve was manufactured in May 2010. "The valve was disassembled and the spring was observed to be not on the core completely. The valve was re-assembled with the spring properly on the core and subjected to cycling. During cycle testing the second turn of the spring was shown to completely overlap the first turn coming over the edge of the core, pulling the first turn off of the core. The spring came completely off the core in 97 cycles. ASCO identified that the spring was not properly manufactured as the beginning of the second turn was not wound to the same diameter of the first turn. "ASCO and the spring supplier identified the manufacturing lot that was the source of the spring for serial number A483456-001. ASCO identified 10 nuclear valves manufactured with this manufacturing lot. The remaining 3990 springs from this lot were used in commercial valves. ASCO uses this same spring in approximately 40,000+ commercial valves per year and no commercial returns have been found with the same condition of this spring coming off the core. "Neither ASCO's incoming inspection nor the spring manufacturer detected the nonconformance for this manufacturing lot. "ASCO evaluated other valves that used this same spring manufactured from other lots received in 2010. These valves represent a time period shortly before and shortly after the manufacture of the above valve. ASCO's investigation concluded that these springs are conforming. "This condition may cause the spring to work itself off the core and present a situation where the valve would not shift to its de-energized position. ASCO believes the condition would present itself relatively early into its cycle life. "ASCO has contacted the customer, AREVA, who received the 10 valves in question. ASCO has implemented corrective actions to include inspection of the spring assembled to the core at nuclear dedication inspection to verify that the spring is properly seated and the second turn does not overlap the first at the springs working length. "ASCO does not have adequate knowledge of the actual installation and operating conditions of these valves to determine whether their malfunction could create a 'substantial safety hazard' as defined in 10 CFR 21.3. We are providing this information to inform you of our investigation results, corrective action and customer notification. "If you have any questions, you can contact Bob Amone at 803-641-9395." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-20
48833 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2005-03-01 | 2013-03-20 08:17 | 2013-03-20 | AGREEMENT STATE REPORT - LOST GAUGE CONTAINING RADIOACTIVE MATERIAL The following report was received from the State of Alabama Department of Public Health via facsimile: "On March 19, 2013, the Environmental Health & Services [representative] for International Paper of Pine Hill, Alabama notified the Alabama Office of Radiation Control that they had lost accountability of a fixed gauge. The gauge is a Kay Ray model 7062BP serial 27137, containing 100 mCi of Cs-137. "During a routine inspection on February 7, 2013, it was noticed by the inspector that the device had been missing since the March 2005 inventory. The inspector requested that [the] Radiation Safety Officer investigate the incident due to several changes within the department and inconsistencies in record keeping. The licensee was issued two violations, one involving the loss of the accountability of radioactive material. "The [licensee's response to the] notification [of violation] letter included both the response to the violations and a attachment. The attachment was a memorandum dated September 12, 2010, referencing losing the gauge, and indicating the loss had been discussed with the [Alabama of Public Health] Director of Licensing. This was discussed with [Director] and he does not recall this conversation nor could this memorandum be found in any of the [Alabama of Public Health] International Paper files. Due to this, the [Alabama of Public Health] considers the response letter the notification of the device being lost. "As of today [March 20, 2013], at 7:15 AM CDT, the device containing radioactive material has not been recovered. This incident remains open until further investigation can be completed." Alabama Incident 13-06 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2013-03-28
48832 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-03-20 02:46 | 2013-03-20 03:15 | 2013-03-20 | UNUSUAL EVENT DECLARED BASED ON INDICATION OF FIRE WITHIN PROTECTED AREA The licensee declared a Unusual Event based on EAL HU-2 due to indication of a fire in the Protected Area for greater than 15 minutes. The licensee received initial indication of a fire alarm and startup of fire water pumps. The alarm was located in the vicinity of the Auxiliary Building Unit 2 HVAC supply unit. The licensee declared an unusual event at 0246 EDT. Upon investigation, it was determined that the heater strips in an HVAC unit were overheated and caused a fire alarm and no fire actually existed. The licensee notified state and local agencies and will notify the NRC Resident Inspector. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). * * * UPDATE AT 0409 EDT ON 3/20/13 FROM BISHOP TO CROUCH * * * The licensee terminated its unusual event at 0341 EDT on 3/20/13 after confirming there was no fire within the Unit 2 Auxiliary Building HVAC supply unit. The licensee notified state and local agencies and will notify the NRC Resident Inspector. R2DO (Rich) and NRR EO (Lund) notified. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Defueled; FMode2: Defueled | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-03-20
48831 | 0 | BIOCOMPATIBLES INC. |  |  |  |  | 2013-02-26 09:00 | 2013-03-19 14:45 | 2013-03-20 | POTENTIAL LOSS OF BRACHYTHERAPY SEEDS On 2/25/2013, four Mick applicator kits with fifteen I-125 seeds in each applicator kit (60 seeds total) were shipped to the Dameron Hospital in Stockton, CA. Each seed contained 0.45 milliCuries. On 2/26/2013, 49 seeds were implanted with one seed jamming in the applicator. After the medical procedure, the radiologist stated that only 50 seeds were in the applicators i.e. ten missing. Surveys were performed but the missing seeds could not be found. The jammed seed is being returned to Biocompatibles. * * * UPDATE AT 0748 EDT ON 3/20/13 FROM RICHARDSON TO HUFFMAN VIA FACSIMILE * * * The following detailed event text was received from the licensee (Biocompatibles, Inc.) via fax: "Biocompatibles, Inc. ('Biocompatibles') has investigated a report that ten (10) I-125 sources (0.450 mCi each Ref date 2/26/13) that Biocompatibles sent to Dameron Hospital in Stockton CA (the 'Hospital') are unaccounted for. "On February 26, 2013, Biocompatibles received a report that at the end of an implant procedure for which Biocompatibles provided (60) sealed sources in four (4) Mick magazines of fifteen (15) sources each that: * Forty-nine (49) sources were implanted in the patient * One (1) source had jammed in the Mick Applicator and had been retained by the Hospital * Ten (10) sources were unaccounted for at the end of the procedure "A Biocompatibles sales representative was present during most of the procedure performed on February 26, 2013 and reported that there was no indication that there were not four (4) full magazines of (15) sources each at the start of the procedure. In addition, the Hospital has confirmed that the decision to implant forty-nine (49) sources was made by the operating physician at the time of the surgery. "Several communications led Biocompatibles to believe that the sources were accounted for at the Hospital, but on March 13, 2013, a conversation with relevant personnel confirmed that the Hospital did not have the sources. "Biocompatibles received the sources from its Supplier on February 19, 2013, and loaded all sources received into four (4) magazines on the same day. Biocompatibles' production records confirm that Biocompatibles received sixty (60) sources from its Supplier (OPSRAD SOP09-01), and subsequently confirmed with its Supplier that exactly sixty (60) sources were sent to Biocompatibles. Biocompatibles verified the source counts at magazine loading. Biocompatibles also performed Ludlum meter surveys for line clearance after both the assay (OPSRAD SOP09-02) and loading operations (OPSRAD SOP09-03) to ensure that no sources had been left behind. A final inspection (OPSRAD SOP09-04), performed by the Biocompatibles Quality Department, verified that the magazine plunger heights on the four (4) full magazines were identical, indicating fifteen (15) sources per magazine. After all of these quality control measures took place, all sixty (60) sources were sent to the Hospital. "Biocompatibles delivered a sterile Applicator Kit (Case 75152), containing four (4) Mick magazines of fifteen (15) sources each, for a total of sixty (60) sources, to the Hospital on February 25, 2013. The lot number for the I-125 sealed sources was Lot 2013-24638. "When first notified by the Hospital on February 26, 2013 of the possible issue, the Biocompatibles Radiation Lab performed additional meter surveys. Biocompatibles performs production station surveys at the completion of each production operation, and performs meter surveys of the entire facility at shift end. All surveys performed on February 26, 2013 through March 13, 2013 have not identified any misplaced seeds. "The empty Supplier vial and pig used to deliver the sources to Biocompatibles was shipped to the Hospital with the case in question. Biocompatibles has requested all empty packing associated with the case to be returned to Biocompatibles for further investigation." Notified R1DO (Trapp) and R4DO (Werner). ILTAB and FSME Events Resource notified via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-03-27
48830 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2013-03-19 08:30 | 2013-03-19 10:00 | 2013-03-19 | TSC VENTILATION REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On March 19, 2013, at 0830 hours [CDT], the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned TSC ventilation system maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service for approximately 5 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-19
48829 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-03-19 04:02 | 2013-03-19 08:37 | 2013-03-19 | MANUAL REACTOR SCRAM DUE TO LOWERING CONDENSER VACUUM "At 0402 [CDT] on 03/19/2013, the Unit 1 reactor was manually scrammed due to lowering main condenser vacuum. The cause of the loss of vacuum was a significant leak on the 1C feedwater heater level control line. The leak appeared as a steam/water leak near the penetration to the main condenser. As extraction steam was isolated, condenser vacuum deteriorated and was approaching the turbine trip setpoint, at which time the reactor was manually scrammed. Condenser vacuum recovered following the scram. MSIVs [Main Steam Isolation Valves] are open, main turbine bypass valves are controlling reactor pressure and reactor feedwater pumps are being used to control reactor water level. "All expected containment isolation and initiation signals (Groups 2, 3, 6, and 8) were received. Upon receipt of these signals all required components actuated as required. In response to the scram, all plant equipment responded as designed. The reactor had been operating near 95% power for several hours due to the 1C3 heater isolating at 2334 [hrs. CDT] on 3/18/13. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) `any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR50.73(a)(2)(iv)(A)." All rods inserted into the core during the scram. No safety relief valves lifted during the transient. The plant is in its normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-03-19
48828 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2013-03-18 16:05 | 2013-03-18 18:00 | 2013-03-18 | OFFSITE NOTIFICATION DUE TO RADIOACTIVE RELEASE ONSITE "On March 18, 2013, at approximately 1605 CDT, the station commenced notification of the Louisiana Department of Environmental Quality and other offsite governmental agencies that traces of radioactive contaminants were found at the site of an underground pipe leak on station property. This leak could potentially contain tritium and cobalt-60, and is believed to have been contained on the plant site. The leakage path has been isolated. The station is currently starting up following a refueling outage. "In October 2012, water was found leaking from the ground and accumulating in a ditch near the station's sewage treatment plant. The initial investigation concluded that the source of the leak was domestic water, based on pH sample results, known buried piping in the area, and the fact that the sewage treatment plant operates intermittently. During the recent refueling outage, which started on February 16, it was noted that the leak had stopped. Testing of the potentially affected piping found that the leak was not domestic water, but was actually coming from the sewage treatment plant effluent line. It was determined that the constant leakage seen in October 2012 was due to a failed check valve in the effluent line. This check valve is designed to prevent backflow from the main condenser circulating water system blow-down line. The failed check valve was allowing water from the blow-down line to flow backwards into the sewage plant effluent line and out of the breach. The leak had stopped because the circulating water system blow-down line was shut down at the start of the refueling outage. "Discharges from the liquid radwaste system also flow into the blow-down line at a point upstream of the connection to the sewage plant effluent line. During planned discharge of liquid radwaste, some of the diluted radioactive water was thus able to leak out on the ground. Samples of the dirt in the area of the leak obtained on March 17 found detectable levels of cobalt 60. No water is available to perform tritium analysis. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as a condition requiring notifications to local and state governmental agencies in accordance with the NEI 07-07 Industry Ground Water Protection Initiative." The leak path has been isolated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-03-18
48827 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-03-18 09:10 | 2013-03-18 16:50 | 2013-03-18 | HIGH PRESSURE COOLANT INJECTION INOPERABLE FOLLOWING REFUELING OUTAGE "On 3/18/2013, with the Unit 2 reactor at approximately 165 psig while in Mode 2 (Startup) following a refueling outage, the high pressure coolant injection (HPCI) system was undergoing post-maintenance testing to demonstrate operability of the system following the performance of major system maintenance. The provision allowed by the Technical Specifications was being used to increase reactor pressure above 150 psig for the purpose of performing operability testing and there was reasonable assurance that the HPCI system had been restored to support successful test results. [However, the HPCI system failed to pass operability testing and] as a result of the inability of the HPCI system to function as required during this testing while above 150 psig, HPCI was not capable of performing its safety function. Reactor pressure was decreased below the Technical Specification 3.5.1 LCO Applicability Requirement of 150 psig and work is in progress to make the needed repairs to support returning HPCI to an operable condition." The licensee notified the NRC Resident Inspector. | 0 | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-03-18
48826 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-03-15 | 2013-03-18 14:31 | 2013-03-18 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following information was received via fax: "On March 15, 2013, a patient was treated with Y-90 microspheres (Sirtex SIR-Spheres) for a liver lesion. The prescribed activity was 35.8 millicuries. Measurements of the residual activity in the delivery system indicated 24.6 millicuries was delivered to the patient. Because of this, the total dose to the treatment site differed from the prescribed dose by 31.3 percent. The need for additional treatment is being evaluated. The licensee will submit a written report within 15 days." Virginia Event ID: VA-13-0004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-03-26
48825 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-03-06 | 2013-03-15 20:43 | 2013-03-15 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGN The following information was received from the California Radiologic Health Branch via e-mail: "[The Radiation Safety Officer] RSO reported that a tritium exit sign (approximately 20 Ci of H-3) was broken when a forklift hit the sign on 3/6/13. The forklift driver did not report the damaged sign to the RSO until 3/13/13. Initial wipe surveys showed contamination up to 130,000 dpm. The area is not routinely occupied and, since being reported, access has been restricted. The forklift is also secured. A consultant will be used to decontaminate the area and the forklift. A urine sample was collected of the forklift driver on 3/14/13." California Report 031513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-03-25
48824 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-21 10:12 | 2013-03-15 17:23 | 2013-03-15 | PART 21 REPORT - INITIAL NOTIFICATION FOR FLOWSERVE MODEL 28KXL PUMP IMPELLER DEFECT "This Part 21 initial notification addresses a pump impeller defect that resulted in a post maintenance test (PMT) failure. The 0C RHR Service Water Pump was being replaced due to degraded performance which caused an In-Service Test (IST) failure. The replacement pump impeller received from the supplier had not been machined to the purchase order specifications. The IST of the new pump could not be completed since the required test conditions could not be established. The pump was later replaced and the IST was completed successfully. The pump was declared operable on March 2, 2013. "This Part 21 Initial Notification is being submitted pursuant to the requirements of 10CFR21.21 (d)(3)(i)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-15
48823 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-03-14 18:00 | 2013-03-15 01:48 | 2013-03-15 | PARTIAL LOSS OF OFFSITE COMMUNICATIONS "On 03/14/2013 at 1800 CDT, Browns Ferry Nuclear Plant experienced a partial loss of offsite communication to include the Emergency Notification System to the NRC and normal phone communication to offsite. This loss of communications appears to be the result of an unplanned degraded voltage condition on the 48VDC Telephone Battery supplying power to the communications network. Main Control Room indications and assessment capability were not affected. The Nextel cellular phone system, the satellite phones in the Control Rooms, and the Health Physics Radio Network were available onsite to communicate offsite. The plant radio system was also unaffected. Required corrective maintenance is being evaluated. Communication capability is being periodically restored during maintenance troubleshooting, but has not yet been permanently corrected. Operation of Unit 1, Unit 2, and Unit 3 was not affected by the event. "At 2145 CDT, the NRC Operations Center was notified of alternate contact numbers for [Browns Ferry] until the Telephone Battery is fully restored. "The NRC Senior Resident Inspector has been notified. "This event is reportable under 10CFR50.72(b)(3)(xiii)." * * * UPDATE FROM CHRISTMAN TO KLCO ON 3/15/13 AT 0330EDT * * * A spare battery charger was aligned to the 48 VDC Telephone Battery and offsite communications was restored. The licensee notified the NRC Resident Inspector. Notified the R2DO (O'Donohue). | 100 | 23 | 100 | 100 | 23 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-15
48822 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-03-14 08:00 | 2013-03-14 09:50 | 2013-03-14 | UNIT 2 SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE RCIC "At 0300 [CDT] on 3/02/2013, radiography results for the U2 [Unit 2] RCIC [Reactor Core Isolation Cooling] system stop-check valve 2-HCV-71-14 showed this valve to be in the fully open position thus, not meeting the acceptance criteria of 2-SI-3.2.3 (Testing ASME Section XI Check Valves). This valve is the RCIC turbine exhaust stop-check valve. It is one of two PCIVs [Primary Containment Isolation Valves] connecting RCIC directly to primary containment. TS [Technical Specification] 3.6.1.3 (PCIVs) Condition 'A' was entered. In order to comply with TS 3.6.1.3 Condition 'A', the RCIC system was required to be isolated to prevent flow through the RCIC turbine exhaust check valve 2-CKV-71-0580. This valve is the upstream RCIC turbine exhaust line PCIV. 2-FCV-71-003, RCIC Steam Line Outboard Isolation valve, was closed and deactivated to meet TS 3.6.1.3 (PCIV) Condition 'A' at 0525 [CDT] on 03/02/2013. This resulted in RCIC being unable to auto initiate and required U2 to enter TS 3.5.3 (RCIC System) Condition 'A', which requires RCIC to be returned to service within 14 days. Because valve 2-HCV-71-14 is unisolable to primary containment, a unit S/D [Shutdown] is required to perform repairs. The RCIC TS LCO [Limiting Condition for Operation] 3.5.3 requires that U2 be in MODE 3 by 1725 [CDT] on 03/16/2013 and <150psig by 1725 [CDT] on 03/17/2013. "Action to initiate Reactor S/D was taken on 03/14/2013 at 0800 [CDT]." The licensee informed the NRC Resident Inspector. | 0 | 80 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-03-14
48821 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-03-13 11:20 | 2013-03-13 19:01 | 2013-03-13 | AFW ACTUATION DUE TO TRIP OF 3B FEEDWATER PUMP "This is a non-emergency event notification to the NRCOC [NRC Operations Center] in accordance with 10 CFR 50.72(b)(3)(iv)(A) for valid Engineered Safeguards (ESF) actuations of the Auxiliary Feedwater System (AFW). "On 3/13/2013 at 1120 EDT, Unit 3 experienced an automatic initiation of AFW due to a trip of the 3B Steam Generator Feedwater Pump while shutdown with Rod Banks withdrawn in preparation for startup. Subsequently, at 1131 EDT, Rx Trip Breakers were opened due to a lowering Reactor Coolant System average temperature resulting from AFW operation. Unit 3 remains stable in Mode 3. The initiation of AFW is currently under investigation." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-03-13
48820 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-03-13 01:49 | 2013-03-13 03:11 | 2013-03-14 | UNUSUAL EVENT DECLARED DUE TO INOPERABLE EMERGENCY DIESEL GENERATORS At 0149 CDT on 3/13/2013, Wolf Creek declared an Unusual Event due to inoperability of both on-site emergency diesel generators. While the A-EDG (Emergency Diesel Generator) was out of service due to planned maintenance, the B-EDG experienced a loss of control power. The cause is currently under investigation. Offsite power is available and providing electrical power to the Unit. The licensee notified state and local agencies and the NRC Resident Inspector. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). * * * UPDATE FROM MARTINSON TO KLCO ON 3/14/13 AT 0407 EDT * * * "Repairs are complete on the 'B' EDG (Emergency Diesel Generator). The 'B' EDG has been tested and restored to operable status at 0221 [CDT] on 03/14/2013. The 'A' EDG remains out of service for scheduled maintenance. NUE (Notification of Unusual Event) terminated at 0239 CDT on 03/14/2013." The licensee notified state and local agencies and will notify the NRC Resident Inspector. Notified the R4DO (Powers), IRD (Grant) and NRR (Lubinski). Notified DHS, FEMA, DHS NICC and Nuclear SSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Defueled; FMode1: Defueled | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-03-13
48819 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-03-12 17:06 | 2013-03-13 00:58 | 2013-03-13 | UNIT 2 LOSS OF SHUTDOWN MONITORING INSTRUMENTATION SYSTEM "On March 12, 2013, at 1706 PDT, with the reactor coolant system not intact, plant operators identified [an] unexpected increase in nuclear reactivity count rate as indicated by source range instrumentation channel N-32. This increase was NOT indicated on redundant wide range instrumentation channels N-51 and N-52. Operators identified that technicians working in the area of the N-32 cable routing had bumped the cabling, resulting in the false increase in the count rate. The source range channel N-32 was subsequently declared inoperable. Prior to this event the other source range channel N-31 had been declared inoperable. "The above event resulted in loss of control room audible indication required by DCPP [Diablo Canyon Power Plant] technical specification to monitor the core reactivity condition and consequently caused loss of the monitoring system. Operators retained capability of monitoring core reactivity conditions through use of the two wide range nuclear instrumentation channels N-51 and N-52. "In response to this concern, plant operators verified all core alterations were suspended, verified boron concentration was within acceptable limits for current conditions, suspended operations that could dilute the boron concentration, verified reactor trip breakers were open and control rods incapable of withdrawal, and initiated actions to restore to service one of the source range instrumentation channels with its associated control room audible count rate indication. "NRC Resident Inspectors have been notified." * * * UPDATE AT 0848 EDT ON 3/13/13 FROM MICHAEL QUITTER TO DONG PARK * * * "This is an update to EN #48819 reported on March 12, 2013 at 2158 PDT. "This update informs the NRC that PG&E, in accordance with provisions of TS 3.0.4b, will be restoring the source range instrumentation channel N-32 to service in Mode 5, maintaining the availability and monitoring of the wide range instrumentation channels while in Mode 5 until the source range channel is returned to service." The licensee has notified the NRC Resident Inspector. Notified R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2013-03-13
48818 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2013-03-12 14:51 | 2013-03-12 18:01 | 2013-03-12 | AUTOMATIC REACTOR TRIP ON THERMAL MARGIN/LOW PRESSURE "On 3/12/13 at 1451 EDT, during normal full power operations, Unit 1 automatically tripped due to the Thermal Margin/ Low Pressure trip setpoint being exceeded. The trip was uncomplicated and all CEAs [control element assembly] fully inserted when the reactor was tripped. Main Steam Safety valves lifted momentarily post trip and reseated. No automatic safety system actuations were required and none occurred. The cause and details of the automatic trip are under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Main Feedwater and Atmospheric Dump Valves in operation. The operation of the Steam Bypass Control System is under review by Engineering. The Offsite power grid is available and stable." The licensee has notified the NRC Resident Inspector and there was no impact on Unit 2. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-03-12
48817 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-03-12 14:31 | 2013-03-12 17:31 | 2013-03-12 | AUTOMATIC REACTOR TRIP DUE TO TURBINE INLET PRESSURE PERTURBATION "Unit 3 experienced an automatic reactor trip from approximately 3% power. The turbine was off-line and undergoing testing following a control valve position indication repair. A turbine inlet pressure channel perturbation momentarily actuated the 'Reactor Trip by Turbine Trip' protection, causing the Unit 3 reactor to trip. Unit 3 is currently stable in Mode 3. No other complications were noted following the reactor trip. The cause of the turbine inlet pressure channel perturbation is currently under investigations." All control rods fully inserted. Normal feedwater is supplying the steam generators and decay heat removal is to atmosphere via the atmospheric steam dumps. There is no primary to secondary leakage. Unit 3 is in a normal shutdown offsite electrical power alignment. There is no impact on Unit 4. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-03-12
48816 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2013-03-08 | 2013-03-12 17:10 | 2013-03-12 | CONSTRUCTION DEFICIENCY INVOLVING LOOSE PROXIMITY SWITCH TARGET MAGNETS The following is a summary of information received from Fisher Control International, LLC. via facsimile: "Equipment Affected By This Information Notice: Items provided to Westinghouse Electric Company, LLC on purchase order 4500325241. TAG# APP-PV-20-ZOD-101, Fisher Serial numbers 19447200 and 19451246. "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert Westinghouse Electric Company, LLC (WEC) that as of 1/30/2013, Fisher Controls International, LLC. (Fisher) became aware of the possibility of a situation which may affect the performance of the aforementioned equipment, including their safety-related function. "We [Fisher] are informing WEC of this circumstance in accordance with Section 50.55(e) of 10CFR50. "Applicability: This notice applies only to the subject equipment supplied by Fisher, identified above, that was provided to WEC. "Discussion: It was determined that at least one of the proximity switch target magnet (find #203 on the drawing GE48644) installed on the subject equipment was loose when received by WEC. Therefore, the switch would not have been operable. "Action Required: Fisher will perform the repair work on-site at Dockside Logistics. In addition, a Corrective Action Request (CAR) has been initiated by Fisher to prevent reoccurrence of this issue, mandating procedures to functionally test all accessories. "10CFR50.55 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR50.55." "If there are any technical questions or concerns, please contact: George Baitinger Manager, Quality Fisher Controls International, LLC 301 South First Avenue Marshalltown, IA. 50158 Fax: (641) 754-2854 Phone: (641) 754-2026 George.Baitinger@Emerson.com" Fisher Information Notice FIN 2013-02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | CONSTRUCT DEFICIENCY | [9 empty] | NON EMERGENCY | 3 | IA | OTH | GEN | 50.55(e) |  |  |  | 0 | 2013-03-12
48815 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-02-14 | 2013-03-12 13:10 | 2013-03-12 | BLACKOUT BUTTON FOUND IN LOAD OF SCRAP METAL The following information was received by email: "On 2/4/13, a scrap metal load shipped by Southern Recycling from Millbury, MA, was rejected by Audubon Metals of Henderson, KY, for triggering the site's radiation detectors. The highest net radiation reading was 10 microR/hr. The vehicle returned to Millbury where, on 2/6/13, one device (described as a WWII "Blackout Button" measuring ~1.75 inch diameter and containing ~10 microCuries Radium-226) was located and removed from load by an independent consultant and isolated in secure storage for further processing. The remaining load re-shipped to Henderson without further incident. On 2/13/13, the device was removed, packaged and shipped to a proper disposal site by a third-party waste broker. The original owner was not determined. "The Agency [MA Radiation Control Program] considers this matter closed." SCRAP Docket #: 14-0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-03-20
48814 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2013-03-08 19:21 | 2013-03-09 04:57 | 2013-03-09 | SPENT FUEL POOL CRITICALITY ANALYSIS OF RECORD NOT REVISED FOLLOWING POWER UPRATE "During review of industry operating experience, engineering personnel determined the Palo Verde Nuclear Generating Station (PVNGS) analysis of record (AOR) for Spent Fuel Pool (SFP) criticality was not revised to support a license amendment to allow power uprate to 3990 MW thermal. The power uprate impacted the reactivity of fuel discharged to the SFP but the SFP criticality AOR was not revised to account for the impact to fuel reactivity. At 1921 [MST] on March 8, 2013, PVNGS received preliminary analysis from Westinghouse that indicates the current AOR for SFP criticality is nonconservative due to the impact of the power uprate. However, significant margin is maintained to SFP criticality at the current Technical Specification minimum SFP boron concentration requirement of 2150 parts per million (ppm) and additional margin is provided by procedure requirements which maintain SFP boron concentration greater than 4000 ppm. Margin also exists due to the maximum fuel enrichment used at PVNGS being less than the fuel enrichment assumed in the AOR. "The SFP criticality analysis supports Technical Specification (TS) LCOs 3.7.15 (Fuel Storage Pool Boron Concentration) and 3.7.17 (Spent Fuel Assembly Storage) as well as TS Design Features 4.3.1 (Fuel Storage Criticality). "This notification is being made pursuant to the reporting requirements of 10CFR50.72 (b)(3)(ii)(B) to describe an unanalyzed condition. The NRC Resident Inspector has been notified of this condition." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-03-09
48813 | 0 | NJ DEQ RADIOACTIVE MATERIALS PRGM |  |  |  |  | 2013-03-07 | 2013-03-08 12:54 | 2013-03-08 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE DUE TO EQUIPMENT FAILURE "A patient was treated with a Varian GammaMed plus iX HDR unit on March 7, 2013. The prescription dose was 700 cGy per fraction for 2 fractions, with a prescription dose of 800 cGy for a third fraction. The first two fractions were delivered to the patient as planned, the first fraction on February 26, 2013 and the second on February 28, 2013. The third fraction was to be delivered via tandem and ovoid. The planned tandem dose of 613 cGy was successfully delivered, and the source returned to its shielded position. However, prior to delivery of the ovoid dose of 187 cGy, the HDR unit displayed an error message of 'Electronics Defective error.' "The staff could not correct the error. The manufacturer was notified and a service technician arrived later in the day to correct the problem. The remaining portion of the fraction was cancelled for the day and re-scheduled. The fractionated dose delivered differed from the prescribed fraction by 23.37%. "The Varian service technician arrived later in the day and replaced the unit's indexer board, cleaned the indexer belt, tested a spring for tightness and re-set the wheel on the belt. The unit then functioned properly." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2013-03-18
48812 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-03-07 07:56 | 2013-03-07 11:52 | 2013-03-07 | AUTOMATIC REACTOR SCRAM ON GENERATOR TRIP/TURBINE TRIP "While operating at rated electrical power, a main generator trip and subsequent turbine trip resulted in a reactor scram. The cause of the generator trip is under investigation. All systems operated as expected with no complications. The plant is stable in Mode 3." The licensee notified the NRC Resident Inspector and the State of Illinois. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-03-07
48811 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-03-07 01:35 | 2013-03-07 03:36 | 2013-05-03 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 0135 EST, Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable, and LCO 3.5.1 entered, due to its turbine steam exhaust valve failing in the closed position during the quarterly valve exercising surveillance. The supply breaker tripped when the opening stroke was attempted. The valve was verified to have remained fully closed via the manual operator. HPCI will not automatically start with this valve closed. "HPCI is a single train Emergency Core Cooling Safety [ECCS] system. This event results in the loss of an entire safety function which requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v) and the guidance provided under NUREG-1022, rev. 2. "There are no other ECCS systems presently out of service." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM TODD CREASY TO PETE SNYDER ON 5/3/13 AT 1401 EDT * * * "The reported condition, described above, was further evaluated by PPL Susquehanna, LLC (PPL). The following is additional information concerning the condition: "The HPCI Turbine Exhaust valve (HV255F066): 1) is a DC motor operated valve with no design features which cause automatic valve actuation, 2) is manipulated by remote Operator action to open or close the valve, 3) is designed as a normally open valve to support the HPCI function, and 4) is manually closed for long-term containment isolation. "When the HPCI turbine exhaust valve was stroked, the valve successfully closed; however, position indication was lost when attempting to re-open the valve. Troubleshooting identified a faulty relay contact that in conjunction with the operator repositioning the key lock switch from CLOSE to OPEN caused a direct short in the circuit. "NUREG-1022, Revision 2, Section 3.2.7, provides the following example of a condition that is not reportable under 10 CFR 50.72(b)(3)(v): Removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function). "When the failure of the HV255F066 occurred, HPCI was properly removed from service for planned quarterly valve exercising in accordance with an approved surveillance procedure and LCO 3.5.1. "Since HV255F066 is a normally open valve, a failure to open does not impact the safety function to provide a flow path for HPCI exhaust since routine valve stroking or maintenance that might close the valve would not be conducted in an accident scenario where HPCI would be required to start and closure associated with long-term containment isolation would only occur after the HPCI function is complete (i.e., the failure to open was introduced by the testing activity and would not occur in a scenario in which the valve is required to perform its safety function to open). With regard to the long-term containment isolation function, the faulty relay contact failed in a manner that prevented the valve from opening but did not prevent the valve from closing. Based on closure of the valve during the test, there was no pre-existing operability issue associated with its safety function to close. Furthermore, even without credit for HV255F066, the containment isolation safety function would be maintained by Check Valve 255F049 and Drain Isolation Valve 255F013. "Based on the above additional information, PPL is retracting this report. Susquehanna was in a planned evolution and did not discover a condition that could have prevented performing a safety function." The licensee will notify the NRC Resident Inspector. Notified R1DO (Hunegs). | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-03-07
48810 | -1 | ST. JOSEPH HEALTH CENTER |  |  |  |  | 2013-03-05 | 2013-03-06 15:58 | 2013-03-13 | CONTRACT AUDIT DISCOVERED PHYSICIAN NOT LISTED ON LICENSE During an audit by Cardinal Health on behalf of St. Josephs Health Center it was discovered that a physician who was not listed on the current license has signed approximately 20 qualified medical procedures (QMP). The physician had been listed on earlier licenses but apparently was removed from the license in 2005. A technologist at St. Josephs said that at one point a number of oncologists were removed from the license. This physician may have been inadvertently removed at that time. The licensee's representative is reporting this as a violation of 10 CFR 35.300 since a physician not listed on the license signed QMP. Cardinal Health will continue to investigate. * * * RETRACTION FROM MARCIA WEST TO CHARLES TEAL ON 3/13/13 AT 1357 EDT * * * Upon further review it was determined that this was not a medical event. Notified R3DO (Dickson) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2013-03-07
48809 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-03-06 04:01 | 2013-03-06 12:52 | 2013-04-11 | MOMENTARY LOSS OF SHUTDOWN COOLING "At 0401 CST on 3/6/2013, while in RHR-High [Residual Heat Removal-High] water level the plant experienced a momentary Loss of Shutdown Cooling which resulted in a loss of safety function for Residual Heat Capability. Division 2 RHR shutdown cooling was restored within approximately 90 seconds without issue. No changes were experienced in refuel volume temperature or level during the loss of RHR shutdown cooling. This occurred shortly after a flow adjustment on the system was made utilizing the outboard valve. The inboard valve was reopened and an investigation is in progress. At the time of the valve closure, decay heat removal continued from Reactor Water Cleanup in heat reject mode and fuel pool cooling (with the fuel pool gates removed) is in service. Division 1 RHR (Shutdown Cooling) was available (not Operable) at the time of the loss. It is not currently understood why the injection valve closed. All systems functioned as required except for the spurious closing of MO-2015 (the Div 2 RHR inboard injection valve). The following make-up sources are available: Divisions 1 and 2 RHR, Divisions 1 and 2 Core Spray, CRD [Control Rod Drive], CST [Condensate Storage Tank] via a Core Spray with pressurizing station bypassed." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1419 EDT ON 4/11/2013 FROM RYAN RICHARDS TO MARK ABRAMOVITZ * * * "On March 6, 2013 (Notification No. 48809) NSPM [Northern States Power Monticello] reported in accordance with 10 CFR 50.72 (b)(3)(v)(B), a momentary closure of valve MO-2015 in the operating Residual Heat Removal (RHR) subsystem as an event or condition that at the time of discovery could have prevented the fulfillment of a safety function. Following the event, the RHR SDC [shut down cooling] subsystem was removed from operation for equipment forensics and troubleshooting. Results validated that valve MO-2015 was operable and no issues were identified with the associated electrical circuitry, or the RHR SDC subsystem. The decay heat removal requirements of LCO 3.9.7, RHR - High Water Level, were met and there was not a loss of safety function. Therefore, NSPM retracts the March 6, 2013 notification for this event." The licensee notified the NRC Resident Inspector, state and local authorities, and may make a press release. Notified the R3DO (Passehl). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2013-03-06
48808 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2013-03-06 08:45 | 2013-03-06 11:00 | 2013-03-06 | OFFSITE NOTIFICATION DUE TO OIL SHEEN ON HUDSON RIVER "Indian Point 3 is in Mode 5. At approximately 0845 [EST] on 3/6/2013, an oil sheen was observed in the discharge canal and Hudson River. Minor volume of oil is unknown at this time. The source of oil was from an overflowing barrel associated with a waste oil skimmer in the turbine building. Source of oil has been secured. There is no adverse impact on the plant. Notifications to New York State Department of Environmental Conservation, Westchester County Department of Health and U.S. Coast Guard National Response Center have been completed. "NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-03-06
48807 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2013-03-05 08:45 | 2013-03-05 09:40 | 2013-03-05 | SOLE IROFS PRESSURE MAT DID NOT FUNCTION AS DESIGNED "During a post maintenance test of a sole IROFS (Item Relied On For Safety) in the scrap press area, it was discovered that a sole IROFS of a pressure mat did not function as designed. The pressure mat is designed to ensure operator presence. The clutch that would be disengaged when the pressure switch is not active failed to do so. The press was immediately shut down. Similar presses have also been shut down. Double contingency was maintained (Moderation and Mass). The sole IROFS is designed for prevention of a fire scenario. At no time was an unsafe condition present." There were no radiological or chemical hazards resulting from this event. The licensee is conducting an investigation to determine the cause of the failure. The licensee has notified NRC R2 Inspectors and State and Local Agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2013-03-05
48806 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-03-04 14:00 | 2013-03-04 18:32 | 2013-03-04 | UNANALYZED CONDITION DUE TO MECHANICAL SEAL MATERIAL DESIGN "It has been determined that the mechanical seals used in two Low Pressure Safety Injection Pumps and three Containment Spray Pumps are made of a material that may not maintain the designed integrity of the systems under certain accident conditions. These seals have been installed since original plant construction. This issue was discovered by plant personnel while researching requirements for the replacement parts during scheduled outage activities." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-03-04
48805 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-03-04 09:27 | 2013-03-04 11:58 | 2013-03-04 | OFFSITE NOTIFICATION DUE TO A FISH KILL "At 0927 CST on March 4, 2012, XCEL Energy Environmental Services made a report to the State of Minnesota regarding 475 fish killed from the discharge canal temperature transient following reactor shutdown on March 2, 2013." Monticello was in the process of performing a planned shutdown in preparation for a refueling outage. The NRC Resident Inspector, Wright County Sheriffs Department and Sherburne County Sheriffs Department have been notified by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-03-04
48804 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-03-04 04:15 | 2013-03-04 08:59 | 2013-03-06 | RADIATION MONITOR INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. "At 0415 EST on March 4, 2013, REM-01MD-3528, Turbine Building Floor Drain Liquid Effluent Radiation Monitor, was declared inoperable for pre-planned corrective maintenance and surveillance testing. The pre-planned maintenance and surveillance testing is scheduled to take approximately 62 hours. Proceduralized compensatory measures are in place to sample and analyze for radioactivity at a lower limit of detection of no more than 10E-7 microCuries/ml at least once per 12 hours when the specific activity of the secondary coolant is greater than 0.01 microCuries/gram Dose Equivalent I-131, or at least once per 24 hours when the specific activity of the secondary coolant is less than or equal to 0.01 microCuries/gram Dose Equivalent I-131. The expected return to service and operability date is March 6, 2013. "The Liquid Effluent Radiation Monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. "The NRC Resident has been notified." * * * UPDATE FROM JOHN CAVES TO VINCE KLCO ON 3/6/13 AT 1703 EST * * * ". . . Radiation Monitor REM-01 MD-3528 would be out of service for preplanned maintenance for approximately 62 hours, and the estimated return to service date was March 6, 2013. The preplanned maintenance is taking longer than expected and the current estimate is approximately 110 hours with return to service on Friday, March 8, 2013. The compensatory measures will continue until the monitor is returned to service." The licensee notified the NRC Resident Inspector. Notified the R2DO (Nease). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-03-04
48803 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-03-02 21:56 | 2013-03-03 00:49 | 2013-03-03 | SAFEGUARDS REPORT - DISCOVERY OF AN UNCONTROLLED SECURITY WEAPON Discovery of an uncontrolled security weapon. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-03-03
48802 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-03-01 22:42 | 2013-03-02 00:25 | 2013-04-18 | UNUSUAL EVENT DUE TO LOSS OF BOTH EMERGENCY DIESEL GENERATORS On 3/1/2013 at 2242 CST, Wolf Creek Unit 1 declared a Notification of Unusual Event (NOUE) due to both Emergency Diesel Generators (EDG) being unavailable: With the 'A' EDG out of service for planned maintenance, the 'B' EDG was discovered to have high governor oil level and was declared inoperable at 2235 CST. The governor oil level was adjusted and the 'B' EDG was declared operable at 2307 CST. The NOUE was terminated on 3/21/2013 at 2321 CST. Normal offsite power was maintained to the plant and no offsite assistance was requested. The licensee notified state and local agencies and the NRC Resident Inspector. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). * * * RETRACTION FROM JIM KURAS TO JOHN SHOEMAKER ON 04/18/13 AT 1322 EDT * * * "Further evaluation by the Engineering department determined that the 'B' EDG was available with the high governor oil level. Testing was performed at an offsite facility, which confirmed that the 'B' EDG was capable of performing its specified safety function with the as-found oil level. As a result, the condition has been determined to not be reportable per 10 CFR 50.72(a)(1)(i)." The licensee will notify the NRC Resident Inspector. Notified R4DO (Drake), NRR EO (Skeen) and IRD MOC (Grant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Defueled; FMode1: Defueled | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-03-02
48801 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-03-01 10:45 | 2013-03-01 17:37 | 2013-03-01 | 24 HOUR NOTIFICATION OF INOPERABLE SCRAM DISCHARGE VOLUME VALVE BASED ON NRC BULLETIN 80-14 "Scram Discharge Volume (SDV) Valve Declared Inoperable. "On March 1, 2013 at 1045 hours, with the reactor at 94% core thermal power (CTP), a scram discharge volume valve, CV-302-22B was declared inoperable as required by station procedural direction due to an observed degradation in opening stroke timing during performance of a compensatory surveillance test of the Scram Discharge Instrument Volume Vent and Drain Valve. This report is provided consistent with NRC IE Bulletin 80-14. "Currently, station engineering is evaluating the valve stroke time trend data of CV-302-22B and plans to address this issue will be developed as part of the Corrective Action Program (CAP). Pilgrim Technical Specification (TS) 3.3.G applies due to the inoperability of CV-302-22B. "This notification is being made in accordance with the NRC IE Bulletin 80-14, 'Degradation of BWR Scram Discharge Volume Capability,' Part A.3., which states, 'By procedures, require that the SDV vent and drain valve be normally operable, open and periodically tested. If these valves are not operable or are closed for more than 1 hour in any 24 hour period during operation, the reason shall be logged and the NRC notified within 24 hours (Prompt Notification).' "A similar event report was generated for the same valve on February 18, 2013. Compensatory measures applicable to the original event report included a revised lubrication application and additional surveillance testing. Although surveillance tests subsequent to the original February 18, 2013 tested demonstrated valve operability, the initial March 1, 2013 test did not meet opening stroke time operability requirements for the valve. Subsequent stroke time testing has met the opening stroke time operability requirements for the valve. "This event has no impact on the health and safety of the public. "The USNRC Senior Resident Inspector has been informed." See similar event EN #48766. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW | [5 empty] | 0 | 2013-03-01
48800 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-02-28 23:58 | 2013-03-01 16:34 | 2013-03-01 | AGREEMENT STATE REPORT - IRRADIATOR RACK FAILED TO LOWER The following was received from the State of Texas via email: "On March 1, 2013, the Agency [State of Texas] was notified by the licensee that at 2358 hours on February 28, 2013, one of the two sources failed to full lower into its storage pool. The rack had dropped 11 of 24 feet when it became stuck. "The operator determined that the drive had failed, disengaged the motor from the drive mechanism, and the source lowered into the fully shielded position on its own. The licensee stated all alarms and interlocks functioned as designed. No exposure was received by any individual as a result of this event. "The licensee stated that on March 1, 2013, they replaced the drive motor and successfully tested it. The licensee has not determined the cause for the motor failure. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-03-11
48799 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2013-03-01 | 2013-03-01 11:36 | 2013-03-01 | AGREEMENT STATE REPORT - SHIPMENT CONTAINING CESIUM-137 FOUND The following was received from the State of New Jersey via email: "Provided below is a summary of the Bureau of Environmental Radiation (BERad) response received today. The owner of the shipment is International Forest Products Corporation (IFP) located in Massachusetts. Therefore, the State of Massachusetts Radiation Control Program was contacted. MA staff contacted IFP who determined that the shipment was originally sent to China and rejected. IFP was informed of this rejection, but was not given a reason for the rejection. The bails of paper came from Connecticut. Because Connecticut is not an Agreement State, the NRC Region 1 was contacted to determine if there was a licensee at that location. State of Connecticut radiation control staff were contacted. "The source is shielded, secure and awaiting disposition. At this time it has not been determined who will hire the licensed contractor to package and ship the material for disposal, nor who the contractor will be. "At 1453 on 2/28/13, RMP [New Jersey Radioactive Materials Program] personnel received notification from the Communication Center that an international shipping container on a truck was being held at Port Elizabeth due to elevated levels of Cs-137. The FBI, Union City Bomb Squad, Fire Department, EMS, and DEP [Department of Environmental Protection] emergency response responded. Per direction from the FBI, the truck was unloaded at the U.S. Customs East Coast Warehouse at the Port. The container was opened and the contents, which was found to be bales of paper, were unloaded and surveyed. An approximately 6 inch object wrapped in cardboard and duct tape was identified as the source of the elevated readings. The source was isolated and secured by Emergency response personnel, who placed the source in a lead pig (which was shorter than the source), then placed the pig in a 5 gallon pail filled with vermiculite. "On 3/1/13, RMP personnel responded to the U.S. Customs East Coast Warehouse to obtain readings and confirm the information that had been reported. DEP emergency response personnel were also at the site today. The highest reading on the outside of the bucket was 220 uR/hr, compared with a background of 10uR/hr. The highest reading with the lid of the bucket removed was 300 uR/hr. Emergency Response placed the bottom part of a second lead pig on top the pig they used yesterday in order to ensure the entire source was covered. The two pieces were then taped together. "The highest reading when the source was out of the pig was 2.5 mR/hr on contact. A wipe indicated that the source was not leaking. The highest reading once the source was shielding by the pigs was 20 uR/hr. The pigs were placed in the 5 gallon pail which was then placed in a 55 gallon drum filled with vermiculite. The highest reading on the 55 gallon drum was 15 uR/hr. All readings were obtained with a Victoreen Model 450P ion chamber. "A spectrum of the source, taken with an identiFinder, identified the nuclide as Cs-137." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2013-03-11
48798 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2013-03-01 | 2013-03-01 11:40 | 2015-03-20 | PART 21 - DUAL ALARM MODULES THAT MAY CONTAIN FAULTY DIODES IN SINGLE STATE RELAYS The following is excerpted from a facsimile received from Curtis Wright: "Crydom Inc., the sole supplier to Scientech of D4D07 Solid State Relays (SSRs) since before 2009, has informed Scientech that SSRs provided with date codes between 0908 (August 2009) and 1004 (April 2010) may have included faulty diodes which resulted in reduced reliability (early failure) of their SSRs. "The mode of failure is that the module output may not be able to maintain voltage sufficient to activate its external load. It appears that this failure occurs randomly after some duration of operation, typically weeks or months. No common cause has been found. "Scientech screens components for infantile failure by burning-in modules for a minimum of 48 hours prior to final test. There were no SSR failures during burn-in of potentially affected modules; therefore burn-in was not an effective screen for this issue. "Prior to January 2013, Scientech did not track SSRs by date code. In establishing conservative boundaries for product shipped with suspect SSRs, Scientech can be certain that no suspect SSRs were shipped in Scientech products prior to August 2009 (the earliest suspect date code). It was determined in September 2012 that Scientech did not have any SSRs with a date code of 2010 or earlier in inventory or work-in-progress. Scientech can therefore determine that products shipped after September 2012 do not contain suspect SSRs." Affected components: DAM801, a Dual Alarm Module, manufactured by Scientech, Model DAM801 (/1 optional), Part number EIP-E287PA-1 SAM801, a Single Alarm Module, manufactured by Scientech, Model SAM801 (11 optional), Part number EIP-E289PA-1 DAM502, a Dual Alarm Module, manufactured by Scientech, Model DAM502, Part number EIP-E297DD-1, -2, -3 SAM502, a Single Alarm Module, manufactured by Scientech, Model SAM502, Part number EIP-E297DD-4 DAM503, a Dual Alarm Module, manufactured by Scientech, Model DAM503, Part number EIP-E304DD-1, -2, -3 SAM503, a Single Alarm Module, manufactured by Scientech, Model SAM503, Part number EIP-E304DD-4, -20 DAM504, a Dual Alarm Module, manufactured by Scientech, Model DAM504, Part number NUS-A131PA Affected Facilities: Beaver Valley Farley Ginna Indian Point 2/3 Kewaunee North Anna Prairie Island Surry Turkey Point * * * UPDATE AT 1625 EDT ON 3/20/2015 FROM VINCE CHERMAK TO MARK ABRAMOVITZ * * * The following information was received via fax. Only information that has changed is being attached below. "Thirteen plants were notified during the original notification. On March 10, 2015, one affected plant reported that when one SSR failed, its output consisted of high frequency noise at a reduced duty cycle. This noise caused overheating and failure of resistors in an RC filter connected to the alarm module output. Plants experiencing SSR failures should check downstream elements for possible consequential damage. Scientec has not received any other reports of this condition. The condition was reevaluated and the Part 21 evaluation was revised. The evaluation concluded that this newly identified condition does not impact the original defect as reported." Notified the R1DO (Dental), R2DO (Desai), R3DO (Roach), and Part-21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-01
48797 | 0 | FLOWSERVE |  |  |  |  | 2012-12-29 | 2013-03-01 11:12 | 2017-07-11 | PART 21 - WEDGE PIN FAILURE IN ANCHOR DARLING MOTOR OPERATED DOUBLE DISC GATE VALVES WITH THREADED STEM TO UPPER WEDGE CONNECTIONS The following is a summary of information received from Flowserve via facsimile: "This is to notify the US Nuclear Regulatory Commission that, in accordance with the provisions of 10CFR Part 21, we have identified a potential issue and are submitting our evaluation of the event. "Flowserve has been working with the Tennessee Valley Authority's (TVA) Browns Ferry Nuclear Plant to investigate the failure of a Size 10, Class 900 Anchor/Darling motor-operated double-disc gate valve. The failure was due to the shearing of the wedge pin which serves a joint locking function at the threaded interface between the valve stem and upper wedge. The pin is designed to ensure that the joint does not loosen due to vibration and other secondary loads. On some valve designs, the pin also is used to attach the disc retainers to the upper wedge. The pin shearing allowed rotation of the stem during the closing stroke when the valve was seating and ultimately resulted in loss of the stem to upper wedge joint integrity. "Flowserve has completed an evaluation of the failure and concluded the root cause of the wedge pin failure was excessive load on the pin. The stem operating torque exceeded the torque to tighten the stem into the upper wedge before installation of the wedge pin. The additional stem torque produced a load on the wedge pin creating a stress which exceeded the pin shear strength causing the failure. The recommended assembly stem torque did not envelope the operating torque for the TVA application providing the potential for an over load situation and ultimate failure. The operating torque for the TVA valve was unusually high due to the fast closing time of the actuator and very conservative closing thrust margin. "This situation can potentially occur on any Anchor/Darling type double-disc gate valve with a threaded stem to upper wedge connection, typically size 2.5" and larger, operated by an actuator that applies torque on the stem to produce the required valve operating thrust. An operating stem torque greater than the assembly stem torque can provide the opportunity for excessive pin load and potentially failure. "We have reviewed our records, and the only similar wedge pin failure that we can identify, in addition to the Browns Ferry problems, is a sheared wedge pin at LaSalle Nuclear Station in 1993. Our investigation of the LaSalle failure concluded that the wedge pin failed due to excessive torque in the opening direction due to bonnet over pressurization. "Flowserve recommends that all critical Anchor/Darling Double-Disc Gate valves with threaded stem to upper wedge connections and actuators that produce a torque on the stem be evaluated for potential wedge pin failure. Valves with electric motor actuators which produce high output torques are the most susceptible to failure. Valves which were assembled with stem torques that exceed the operating torque are not candidates for failure. "Below is a list, based on our records, of customers, utilities and nuclear plants which were supplied with Anchor/Darling Double-Disc Gate valves with motor actuators on contracts with ASME Section III and/or 10 CFR 21 imposed. "Flowserve plans to provide each of the customers identified [below] with a copy of this notification letter." The following facilities in the United States may be affected: ANO 1, Browns Ferry, Brunswick, Callaway, Catawba, Clinton, Columbia, Cook, Cooper, Crystal River, Dresden, Diablo Canyon, Duane Arnold, Fitzpatrick, Fort Calhoun, Grand Gulf, Hatch, Indian Point, Kewaunee, LaSalle, Limerick, Maine Yankee, Millstone, Monticello, Nine Mile, North Anna, Oconee, Oyster Creek, Peach Bottom, Perry, Pilgrim, Prairie Island, Quad Cities, River Bend, Robinson, San Onofre, St. Lucie, Surry, Three Mile Island 2, Waterford, VC Summer, Vermont Yankee, Wolf Creek. See Related Part 21 EN #48650. * * * UPDATE AT 1537 EDT ON 7/11/17 FROM AMY OATHOUT TO JEFF HERRERA * * * The following is a summary of a report provided by Flowserve via email: This is to notify the US Nuclear Regulatory Commission that, in accordance with the provisions of 10 CFR Part 21, Flowserve has gained additional insight and information concerning the referenced previously reported issue based on a recent incident at the LaSalle County Station, Unit 2 involving a similar valve. Evaluation of a similar incident at LaSalle added an element not addressed in the previous evaluation regarding the limitation of a pressed-on stem collar to support the actuator thrust and maintain the stem-wedge preload. Valve evaluations and actions resulting from the previous notification are applicable and still apply. This notification includes additional information for maintaining the stem preload that was not addressed previously. The actuator thrust as well as the torque must be reviewed to insure the preload is maintained. A list of customers, utilities and nuclear plants which were supplied with Anchor/Darling DD Gate valves with motor actuators on contracts with Section 111 and/or 10CFR21 was provided. This list added a few sites not included on the list provided with the original notification. For questions or additional information please contact: Joseph Carter Manager, Quality Assurance Flowserve Corporation, FCD Raleigh, NC 919-831-3220 Notified R1DO(Dimitriadis), R2DO(Bonser), R3DO(Peterson), R4DO(Proulx), Part 21 group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-03-01
48796 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-28 21:54 | 2013-03-01 04:00 | 2013-03-01 | EMERGENCY BUS INADVERTENTLY DE-ENERGIZED WITH UNIT DEFUELED "On February 28, 2013, at 2154 PST, Unit 2 4kV ESF Bus G deenergized while attempting a repair to the bus automatic transfer circuitry. The deenergization of 4kV ESF Bus G initiated a start signal to Diesel Generator 2-1, which supplies emergency power to 4kV ESF Bus G. Diesel Generator 2-1 did not start due to being placed in manual control to prevent starting automatically during the repair. However, a valid actuation signal was generated to start Diesel Generator 2-1. As the Diesel Generator was shut down and in manual control, no actuation occurred. "This is reportable as a valid system actuation that was not part of a pre-planned sequence during testing. "Unit 2 is currently defueled, with the core offloaded into the spent fuel pool. No loss of cooling occurred as spent fuel pool cooling equipment had been selected to unaffected buses. "The NRC resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-03-01
48795 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-28 11:55 | 2013-02-28 17:13 | 2013-03-15 | CLOSED COOLING WATER ISOLATION VALVE FAILS LOCAL LEAK RATE TEST "On February 28, 2013, at 1155 EST, with the unit in Refueling Mode, a determination was made that reactor building closed cooling water (RBCCW) isolation valve (2P42-F051) exceeded its acceptance criteria for designed leakage when performing local leak rate testing. Diagnostic testing confirmed that all the leakage from its test boundary is going through this valve with an 'as found' leakage of >200,000 sccm at 32.87 psig. This valve is the outboard isolation barrier for that affected primary containment penetration with the inboard barrier being the RBCCW system itself as a 'closed' system. "Previous practice is to conservatively include any leakage through this valve when performing as found leak rate tests as part of the primary containment leakage summary or as part of 0.6La. This is considered conservative since the RBCCW system inside containment is assumed to remain intact following a design basis accident (DBA) loss of coolant accident (LOCA). If the closed system remains intact there is no path for leakage to exit primary containment through this system. "Since the past practice is to include the 'as found' leakage through this valve as part of 0.6La and since the 'as found' leakage would result in exceeding La, this condition is being considered a condition that results in the principal safety barriers being seriously degraded. This leakage would represent a loss of the containment function since the leak rate exceeded the Technical Specification limiting condition for operation (LCO) for primary containment. Further investigation is underway to determine if leakage through this single containment barrier is required to be included in the Appendix J primary containment leakage summary, since it is associated with a closed system." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 3/15/13 AT 1607 EDT FROM KENNY HUNTER TO DONG PARK * * * "Further investigation revealed an Appendix J exemption that was granted for the Hatch Unit 2 local leak rate test (LLRT) program in the 1978 time frame that specifically addressed the primary containment penetration that has primary containment isolation valve (PCIV) 2P42-F051 as its outboard barrier and the 'closed' system as its inboard barrier. The exemption recognizes that this system is designed to be intact and water filled post-LOCA, allows testing of the of the PCIV with water and states that the leakage through this PCIV is not included in the 0.6 La total. "Since the Hatch RBCCW system supplying components inside primary containment is a 'closed' system and remains intact and water filled post-LOCA, there is no leakage path from primary containment through this RBCCW penetration. Since no leakage from primary containment can occur through this penetration in its 'as found' state, this condition does not represent a condition that seriously degrades a principal safety barrier. As such this condition has been determined to no longer meet reporting requirement 10CFR50.72(b)(3) and is therefore not reportable. Based on this information the previous notification is being retracted." The licensee notified the NRC Resident Inspector. Notified R2DO (O'Donohue). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-02-28
48794 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-02-28 13:19 | 2013-02-28 17:01 | 2013-02-28 | HIGH PRESSURE CORE SPRAY PUMP FAILURE "On February 28, 2013, at 1319 EST, Nine Mile Point Unit 2 (NMP2) experienced a failure of 2CSH*P2, High Pressure Core Spray System Pressure Pump. The HPCS system was currently inoperable for planned maintenance for planned pump room unit cooler maintenance with a 14 day completion time per Technical Specification 3.5.1. "Shortly after the starting of the HPCS pump as part of routine surveillance testing, the system pressure pump failed. Initial troubleshooting has found the pump motor windings to be shorted. Initial investigation identified smoke in the HPCS pump room, no indications of fire were identified. No breaker failures were identified. All other plant systems functioned as required." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-02-28
48793 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2013-02-27 | 2013-02-28 16:22 | 2013-02-28 | PATIENT RECEIVED LESS THAN PRESCRIBED DOSE TO LIVER The following was received via fax from the Commonwealth of Virginia: "On February 27, 2013, a patient was treated with Y-90 microspheres (SIRTeX SIR-Spheres) for a liver lesion. The prescribed activity was 11.3 millicuries. Measurements of the residual activity in the delivery system indicated only 8.4 millicuries was delivered to the patient, resulting in a total dose differing from the prescribed dose by 25.9 percent. Notifications were made to the referring physician and patient. The licensee will submit a written report of the event within 15 days." VA Event Report: VA-13-0003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-03-08
48792 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-02-27 15:00 | 2013-02-28 15:34 | 2013-03-08 | TEST LAB FAILED TO IDENTIFY POSITIVE SAMPLES "Per 10 CFR 26.719 section (c)(2) the Omaha Public Power District (OPPD) is making this notification of an apparent false positive error that has occurred on a blind performance test sample submitted to the Health and Human Services (HHS)-certified laboratory used for drug testing. "On February 27, 2013, OPPD was notified that two positive drug samples that were part of a blind performance test package provided by Professional Toxicology and submitted to Clinical Reference Laboratory tested negative. Currently Professional Toxicology indicates that the two positive samples were provided with the NRC required positive levels for the drug. "OPPD will investigate the issue and report to the NRC as required by part 26.719(c)(1). Professional Toxicology and Clinical Reference Laboratory are contracted by OPPD as required by NRC regulations to provide fitness for duty services." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1640 EST ON 3/8/2013 FROM MICHAEL PEAK TO MARK ABRAMOVITZ * * * "Additional investigation has determined that the samples submitted by Professional Toxicology did not contain the required levels of the drug being tested. The analysis performed by Clinical Reference Laboratory was correct. There was not a reportable condition per 10 CFR 26.719. Therefore, this report is being retracted." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2013-02-28
48791 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2013-02-28 04:00 | 2013-02-28 09:43 | 2013-02-28 | SECONDARY CONTAINMENT DOOR INTERLOCK MALFUNCTION "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. An employee entered a secondary containment interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the main control room supervisor. Both doors in the interlock were open for approximately 10 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor building differential pressure, as observed in the main control room, has remained less than -0.25" H2O at all times. Initial investigation determined that a mechanical interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the mechanical interlock." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-02-28
48790 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-02-27 15:38 | 2013-02-27 16:08 | 2013-02-27 | PLANNED MAINTENANCE ON UNIT 2 PLANT PROCESS COMPUTER "Calvert Cliffs Nuclear Power Plant will perform planned maintenance on the Unit 2 Plant Process Computer (PPC) and associated network infrastructure starting on February 27, 2013. The maintenance will remove the Unit 2 PPC for a planned duration of 5 days and will render the Unit 2 ERDS out of service for this timeframe. The current outage schedule has power being restored on 03/04/2013. "Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment at all times. Control Room Emergency Response personnel will use emergency response procedures to disseminate plant parameter data points to the effected Emergency Response Facilities until the U-2 PPC is restored. MIDAS (Meteorological Data) transmission will remain functional during the maintenance window. The Unit 2 ERDS data will not be available during the power outage from 02/27/2013 to 03/04/2013. "All work associated with this plant data network software installation will be performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. ERDS was functionally tested before the outage and will be in service as soon as power is restored." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-27
48789 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-02-26 20:30 | 2013-02-27 14:47 | 2013-02-27 | SEWAGE SPILL IN THE TURBINE BUILDING THAT DISCHARGED TO THE KEOWEE RIVER "On 2/26/13 at 2030 hrs [EST], a four (4) inch sewage line in the Oconee Nuclear Station turbine building failed. This failure allowed sanitary wastewater to spill into the turbine building basement. An estimated 750 gallons entered into trench drains and traveled to the station sump which discharges into the conventional wastewater system. This conventional wastewater system is discharged to the Keowee River from NPDES (National Pollutant Discharge Elimination System) outfall 002. The discharge of outfall 002 is into the Keowee River below the Keowee Hydro Station. The normal discharge path for sanitary wastewater is to the City of Seneca, South Carolina (SC). South Carolina Department of Health and Environmental Control (SCDHEC) and the Oconee Joint Regional Sewer Authority (OJRSA) were notified of the spill on 2/27/13 at approximately 1358 hrs [EST]. "Note: SCDHEC requires the reporting of any overflow that reaches waters of the state, for overflows that exceed an estimated 500 gallons that don't reach water, and for any overflow that may cause a public health or environment concern. "This event was determined to be reportable pursuant to 10CFR50.72(b)(2)(xi) due to notification of the SCDHEC and OJRSA. "Initial Safety Significance: The sewage leak did not contain any plant produced radiological material and due to dilution, this event posed no safety risk with respect with respect to the health and safety of the public. "Corrective Actions: The affected portions of the sanitary sewage system has been isolated and an investigation is underway to determine the cause. There was no impact on plant operations, and the cleanup has been completed. The event was entered into the correction action program. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-27
48788 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-26 23:02 | 2013-02-27 02:07 | 2013-02-27 | MANUAL REACTOR TRIP DUE TO EXCESSIVE REACTOR COOLANT PUMP SEAL LEAKOFF FLOW "At 2302 EST, Vogtle Unit Two was manually tripped in response to excessive Reactor Coolant Pump #4, seal #1 leakoff flow. Seal leakoff flow exceeded the procedural limits for continued operation of the pump. Following the reactor trip, RCP #4 was shutdown per procedure guidance. All systems operated correctly in response to the reactor trip. All control rods fully inserted. The Auxiliary Feed Water (AFW) system automatically actuated as expected. System responses allowed for an uncomplicated reactor trip response. The plant is stable in Mode 3 during cause investigation. "The NRC Senior Resident was notified and is enroute to the plant for investigation." AFW is supplying the steam generators and decay heat removal is to the condenser via steam dumps. No safety valves or relief valves lifted during the transient. The unit is in a normal post-trip electrical line-up. There was no impact on Unit One. | 0 | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-27
48787 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-02-26 20:12 | 2013-02-27 00:55 | 2013-02-27 | RELAY BACKING PLATE FASTENERS DISCOVERED TO BE AT LESS THAN SPECIFIED TORQUE "During a follow-up review of off-site testing of a sample of General Electric model HFA relays, it was discovered that some of these relays did not pass testing for full qualification in their as-found condition. Additional torquing of the relay backing plate mounting screws was required to fully meet the required qualification. Further investigation into the as-found condition of these relays installed in the plant continues at this time. The relays in question are installed in Engineered Safeguards Features, Auxiliary Feed Water, and 4160 volt systems and are used in protective and actuation functions. " The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-27
48786 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-26 16:30 | 2013-02-26 19:20 | 2013-02-26 | LOSS OF ASSESSMENT CAPABILITY DUE TO VITAL INVERTER MAINTENANCE "At approximately 1630 PST on February 26, 2013, Pacific Gas & Electric (PG&E) will be performing repairs on a vital inverter. The clearance will remove power from various inputs to the Safety Parameter Display System (SPDS), Emergency Response Data System (ERDS), and Emergency Response Data and Recall Recorder Subsystem (ERFDS). "PG&E expects to have the equipment repaired and returned to service within 12 hours. During this time, a dedicated licensed operator will be available to provide plant data to the NRC's Emergency Operations Center. "DCPP is making this 8-hour, non-emergency notification under 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-26
48785 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2013-02-26 14:30 | 2013-02-26 16:59 | 2013-02-26 | STATE AND LOCAL AGENCIES NOTIFIED OF INADVERTENT TRITIUM RELEASE DUE TO OVERFLOWING SUMP "On February 25, 2013 at approximately 1030 CST, plant personnel discovered that a sump within a concrete berm area adjoining the condensate storage tank was overflowing. Water from the sump was entering an open excavation within the berm, and was soaking into the dirt underneath. At approximately 1400 [CST] that day, the sump level was pumped down to terminate the overflow. A portable tank has been staged in the area should any further pumping be required. "Analysis of the water within the berm found tritium activity of 1.135 million picocuries per liter. Additionally, total gamma activity of 1.145 E-6 microcuries per milliliter was present in the sample. The estimated volume of water reaching the open excavation was approximately 380 gallons. "Notification of this event has been made to local and state governmental agencies in accordance with NEI 07-07, Industry Ground Water Protection Initiative. The initial notifications were made at approximately 1430 CST today. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi) as a condition for which local and state governmental agencies have been notified. The station has also notified the NRC Resident Inspector, as well as NRC Region 4 personnel." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-26
48784 | -1 | ST JOSEPH REGIONAL MEDICAL CENTER |  |  |  |  | 2013-01-18 | 2013-02-26 12:42 | 2013-03-26 | UNPLANNED IODINE-131 DOSE TO AN EMBRYO A female patient with a previously removed thyroid, was treated for remnant thyroid cancer on January 18, 2013. She received an I-131 therapy dose of 58 mCi. On February 21, 2013, the radiation oncologist was informed by the primary physician that the patient had tested positive on a pregnancy test. The patient received an ultrasound on February 25, 2013 and the conception date was determined to be January 14, 2013. Based on the patient therapy activity received, an embryo dose of 15 Rem was calculated. Physician review of the ultrasound was determined to be normal for the embryo. The radiation oncologist is in contact with the primary physician and the patient. * * * RETRACTION FROM DOUGLAS HEIDORN TO DONALD NORWOOD AT 1324 EDT ON 3/26/2013 * * * Based on a telephone notification made by Douglas Heidorn, Radiation Safety Officer (RSO) at 1950 EDT on 3/25/2013, it was agreed that a written justification for a retraction would be submitted. The following is a synopsis of what Dr. Heidorn submitted. The Radiation Oncologist (Prescribing Physician) and RSO originally thought that the fetal dose was 14.6 rem, but upon further investigation, it was determined that the fetal dose was only 52 mrem. The discrepancy in the dose estimate was due to confusion about the exact conception date (fetal age). The Prescribing Physician has been corresponding with a Professor of Pediatrics and Radiology (Expert Physician) regarding this issue. The Expert Physician believes that conception occurred between 1/27/2013 and 1/29/2013. Another obstetrician at SJRMC and the Referring Physician concur with the Expert Physician's date range for conception. The 52 mrem fetal dose rate is based on this conception date. On 3/11/2013, a second ultrasound was performed that confirms the above information. Both ultrasound reports indicate the fetus is growing and has normal characteristics. As a corrective action, the Radiation Department will immediately adopt a policy that requires any female aged 12-60 shall receive a pregnancy test 48 hours prior to an I-131 administration. Notified R4DO (Pick) and FSME Event Resources (via E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 35.3047(a) |  |  |  | 0 | 2013-03-06
48783 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-26 09:00 | 2013-02-26 09:32 | 2013-02-26 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS LEAK "At 0900, the Brunswick Steam Electric Plant (BSEP) declared an Unusual Event due to a release of Freon from the 2A Turbine Building Chiller. The classification of the Unusual Event is based on Emergency Action Level (EAL) HU3.1, 'Toxic, corrosive, asphyxiant or flammable gases in amounts that have or could adversely affect normal plant operations.' Actions have been taken to secure the chiller and isolate the release of Freon; however, Freon continues to be released. The release is only affecting the area immediately surrounding the 2A Turbine Building Chiller. No other plant areas are being impacted. "There is no impact on the health and safety of the public." The licensee notified Brunswick Warning Point, Hanover Warning Point, State Warning Point and the NRC Resident Inspector. Notified DHS, FEMA, DHS NICC and NuclearSSA (email). * * * UPDATE AT 1555 EST ON 2/26/13 FROM ERIC WHITE TO S. SANDIN * * * At 1545 EST on 2/26/13, Brunswick terminated their Unusual Event based on the fact that the entry conditions no longer existed. A temporary patch has been installed on the 2A Turbine Building Chiller and work is in progress to evacuate residual Freon from the chiller unit. The licensee notified state and local agencies and the NRC Resident Inspector. Notified R2DO (Musser), IRD (Kozal) and NRR (Chernoff). Notified DHS, FEMA, DHS NICC and NuclearSSA (email). | 100 | 94 | 0 | 100 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2013-02-26
48782 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2013-02-25 13:13 | 2013-02-25 17:49 | 2013-02-25 | AUTOMATIC SCRAM DUE TO A TURBINE TRIP FROM A LOSS OF CONDENSER VACUUM "At 1313 [CST] on 02/25/2013, the Unit 3 reactor automatically scrammed due to actuation of the Reactor Protection System from a turbine trip. Preliminary indications show the turbine tripped on low condenser vacuum. Cause of loss of condenser vacuum has been identified as Reactor Feedwater recirculation piping separation. Main Steam Isolation Valves (MSIVs) were manually closed to isolate the leak. None of the Safety Relief Valves (SRVs) automatically cycled during the transient, and one Safety Relief Valve (SRV) was manually operated to maintain Reactor Pressure due to the Main Turbine Bypass Valves unavailability because of loss of condenser vacuum. All systems responded as expected to the turbine trip. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC), reactor water level initiation set points were reached. Reactor water level is being controlled by the RCIC system and Reactor Pressure is being controlled with the High Pressure Coolant Injection (HPCI) system. "All expected containment isolation and initiation signals (Groups 2, 3, 6, and 8) were received. Upon receipt of these signals all required components actuated, with the exception of one valve in Group 6. Drywell Continuous Air Monitor (CAM) Inboard Return Isolation Valve 3-FSV-90-257 did not have indication following isolation signal and was not able to be verified locally. Indication was subsequently restored following restoration of containment isolation signals, and the Drywell CAM was manually isolated at 1422 [CST] with positive indication of isolation, and isolation valves deactivated at time 1514 [CST] to satisfy TS LCO 3.6.1.3 required actions. "This event is reportable within 4 hours per 10CFR50.72(b)(2)( iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation'. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). "At 1415 [CST], Suppression Pool Water level exceeded -1 inch due to operation with HPCI in pressure control mode, and required entry into TS LCO 3.6.2.2 condition A to restore level within 2 hours. Efforts are being made to lower suppression pool water level within limits. At 1615 [CST], water level remains above -1 inch requiring entry into TS LCO 3.6.2.2 condition B requiring action to be in MODE 3 in 12 hours and MODE 4 within 36 hours. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector has been notified." All control rods fully inserted and electrical offsite power is in a normal shutdown configuration. Residual Heat Removal is aligned for suppression pool cooling. There was no impact on either Unit 1 or 2. | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | PLANT S/D REQD BY TS |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(i) |  | 0 | 2013-02-25
48781 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-02-24 17:00 | 2013-02-25 16:01 | 2013-02-25 | INVERTERS POTENTIALLY INOPERABLE DURING EMERGENCY DIESEL GENERATOR OPERATION "During a review of the plant inverters, it has been determined that the inverters may not have been operable. The inverters were replaced during the 2008 refueling outage. It appears that either the modification did not recognize that the diesel frequency range is wider than the new inverters, or did not recognize its consequence. Consequently, when the diesel is supplying power to the buses and loads are being sequenced onto the bus, the bus frequency exceeds the inverter frequency range. This causes inverter voltage transients. Operation of the inverters has been modified to improve plant reliability. This issue was discovered during scheduled plant testing of the electrical system." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-25
48780 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2013-01-17 | 2013-02-25 10:28 | 2013-03-04 | AGREEMENT STATE REPORT - PROSTATE SEED IMPLANT UNDERDOSE A prostate patient received a medical order for 74 I-125 seeds (144 Gray). The implantation was performed on January 17, 2013 with three seeds being recovered in the operating room and the patient passed two seeds. The post surgery CT scan was performed on February 20, 2013 and the post plan was performed on February 25, 2013. It was determined that the D90 dose was 60% of the prescribed dose. The physician and patient will be notified today, February 25, 2013. The Iowa Department of Public health is planning an on-site inspection for February 27, 2013. * * * UPDATE FROM DAHLIN TO KLCO ON 3/4/2013 AT 1257 EST * * * The following information was received from the State of Iowa by email: "...The post plan dosimetry was completed on February 25, 2013 where it was discovered that the D90 for the implant was 60%. The licensee immediately notified IDPH [Iowa Department of Public Health]. The patient and referring physician were also notified that same day. An IDPH inspector conducted an onsite investigation of the event on February 28, 2013. The inspector met with and interviewed the radiation oncologist, the medical physics staff and several hospital administrators. The inspector reviewed the patient chart including the written directive, the treatment pre-plan, the operating room notes and the treatment post plan. During the interviews and chart review it was determined that an additional nine I-125 seeds had migrated out of the prostate to an area slightly inferior to the prostate. The radiation oncologist and medical physics staff believe that the seed migration occurred along the needle path and was due to the bowel movement issues that the patient experienced post implant. Additionally, the treatment pre-plan was based on an ultrasound contoured prostate volume of 38.59 cc. The treatment post-plan was based on a CT scan contoured prostate of 21.61 cc. The urologist, radiation oncologist and medical physics staff determined that the D90 of 60% was due to the loss of the additional nine I-125 seeds that migrated out of the prostate and the shrinking of the prostate from 38.59 cc to 21.61 cc. The patient will receive an external beam boost to the prostate. In addition, the post-plan dosimetry showed that the rectum and bladder received a dose less than expected on the preplan. The radiation oncologist and urologist stated that the under dose to the prostate from the seed implant therapy will not have an adverse effect on the health of the patient. No corrective actions can be performed due to the licensee having no control over seeds that migrate out of the prostate." Iowa Item Number: IA130001 Notified the R3DO (Valos) and FSME Resources via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2013-03-05
48779 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-02-25 08:04 | 2013-02-25 08:56 | 2013-02-25 | LOSS OF ASSESSMENT CAPABILITY - RADIATION MONITOR INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At 8:04 AM EST on February 25, 2013 radiation monitor RM-21AV-3509-1, Plant Vent Stack Wide Range Gas Monitor (WRGM) was declared inoperable for pre-planned maintenance. The maintenance is scheduled to be completed around 6:00 PM EST on 02/27/2013. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. The Technical Support Center-Site Emergency Coordinator has been notified about this preplanned maintenance. "This condition does not affect the health and safety of the public or the operation of the facility. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-25
48778 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-24 12:05 | 2013-02-24 15:20 | 2013-02-24 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM INDICATION "On February 24, 2013 at 1205 [EST] with reactor power at 25% and the turbine offline, a manual reactor trip for Sequoyah Unit 2 was initiated due to loss of condenser vacuum indication causing closure of condenser steam dumps, opening of the Steam Generator Atmospheric Relief Valves, and lowering hotwell level resulting in imminent loss of hotwell pumps. The cause of the event was determined to be a faulty test connection on B Condenser vacuum pressure switch. "During the event, steam pressure rose to the setpoint for the first Steam Generator code safety valve (1064 psig). [The safety valve opened, then reseated]. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater actuated as expected on loss of the operating main feedwater pumps. The reactor trip was uncomplicated. "Unit 2 is currently being maintained in Mode 3 at NOP/NOT [Normal Pressure and Temperature], with auxiliary feedwater supplying the steam generators and maintaining level at approximately 33% narrow range. "Method of decay heat removal is via atmospheric reliefs to the atmosphere. Current RCS conditions: temperature [is] 547 degrees F and stable. Pressure [is] 2235 psig and stable. [There is] no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal and supplied from offsite power. [There is] no impact to Unit 1. Unit 1 is operating at 100% power / Mode 1. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart is 02/25/2013. [The licensee plans a press release.]" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-24
48777 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-22 14:30 | 2013-02-22 20:13 | 2013-02-22 | COMPUTER PROGRAM ERROR IDENTIFIED IN THE FITNESS FOR DUTY PROGRAM "On February 22, 2013 at approximately 1430 [EST], Susquehanna identified a computer program error that affected the Susquehanna Fitness for Duty (FFD) program. Specifically, two Behavioral Observation Program (BOP) inquiries were accepted without proper documentation of the required need to continue unescorted access authorization (UAA) and without verification of an actual observation within the required thirty day timeframe. The computer error resulted in answers for two of the three questions on the Behavior Observation Inquiry form not being recorded when the form was submitted by the supervisor. This resulted in the two security accounts being re-zeroed and allowing UAA for an additional 15 days. The BOP supervisor was contacted and verified that these individuals were intended to continue with UAA. At no time were these individuals removed from the FFD or Behavior Observation Program. "In accordance with 10 CFR 26.719(b)(4), this report is being made based on being a potential programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program. The [NRC Resident Inspector] and the Branch Chief for the Region I Division of Reactor Safety were notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FFD PROGRAMMATIC FAILURE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.417(b)(1) |  |  |  | 0 | 2013-02-22
48776 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-12-13 | 2013-02-22 09:55 | 2013-02-22 | AGREEMENT STATE REPORT - UNDERDOSE DURING MEDICAL PROCEDURE "On December 13, 2012, a patient received a permanent implant of I-125 seeds to the prostate as part of a combined external beam treatment and brachytherapy. It was determined during a post-surgical CT that the tumor may have been underdosed and a follow-up MRI was performed. As a result of the MRI, it was discovered, on February 21, 2013, that the dose received for the brachytherapy was 70 percent of the written directive. The licensee will submit a written report to the Virginia Radiation Materials Program." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-03-04
48775 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2013-02-21 09:57 | 2013-02-21 12:49 | 2013-02-21 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF BOTH MAIN FEED PUMPS At 0957 EST on 02/21/13, Unit 1 Reactor automatically tripped from 100% power, due to a turbine trip. The turbine trip was caused by a loss of both main feedwater (MFW) pumps. The 1A motor driven auxiliary feedwater (AFW) pump auto started to feed the "A" and "B" Steam Generators (S/G). The 1B motor driven AFW pump was unavailable due to planned maintenance, so the turbine driven AFW pump was manually started to feed the "C" and "D" S/Gs. The reactor trip was uncomplicated. All control rods fully inserted. Decay heat removal is to the main condenser via the turbine bypass valves. There was no primary to secondary leakage. Electrical buses are being supplied via offsite power. Steam generator levels are being returned to normal and MFW has been reset and is available. All other plant systems functioned as designed during and after the reactor trip. There is no impact on Unit 2. There is no impact on the health and safety of the public. The loss of the MFW pumps is still under investigation. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-21
48774 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-02-20 | 2013-02-20 17:01 | 2013-02-20 | AGREEMENT STATE REPORT - IRRADIATOR SOURCE RETRACTION MALFUNCTION The following report was received from the Texas Department of State Health Services, Radiation Branch, via e-mail: "The licensee RSO reported that, during securing the source rack [on a pool irradiator], a tote on the conveyor became lodged against the rack mechanism causing it to halt before being completely secured. The maintenance manager and an operation technician were able to dislodge the tote without receiving any additional exposure. They manually moved the conveyor belt dislodging the tote and allowing the rack to continue to its secure position in the irradiator pool. The licensee will submit a complete report within 30 days. "[The Texas Radiation Branch classifies this report as a] 30.50(b)(2) event type involving equipment failure or disability to function as designed when equipment is required to be available and operable and no redundant equipment is available and operable, includes source disconnection and failure to retract source." Texas Report I-9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-02-28
48773 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-02-19 | 2013-02-20 16:07 | 2013-02-20 | AGREEMENT STATE REPORT - SOURCES STUCK IN PROCESS GAUGES The following report was received from the Texas Department of State Health Services, Radiation Branch, via e-mail: "On February 20, 2013, the Agency was notified by the licensee that on February 19, 2013, during routine maintenance checks the sources on two nuclear gauges were found stuck inside the dip tubes. Both gauges are Berthold model 21357 gauges each containing a 500 millicurie (original activity) cesium - 137 source. In this type gauge, the source is moved from the source housing inside a tube to the desired location. The sources are stuck in the normal operating position and do not pose an exposure risk to any individual. The licensee has contacted the manufacturer for repairs. "[The Texas Radiation Branch classifies this report as a] 30.50(b)(2) event type involving equipment failure or disability to function as designed when equipment is required to be available and operable and no redundant equipment is available and operable, includes source disconnection and failure to retract source. "Additional information will be provided as it is received in accordance with SA - 300." Texas Report I-9043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-02-28
48772 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-20 05:28 | 2013-02-20 10:21 | 2013-02-22 | DEGRADED CONDITION - CONTAINMENT PENETRATION FAILS LOCAL LEAK RATE TESTING "On February 20, 2013, at 0538 EST, local leak rate testing (LLRT) of the 'A' feedwater check valves 2B21-F010A and 2B21-F077A revealed that neither valve would pressurize. Based on this information this line would not remain water filled post-LOCA and would result in the 'as found' minimum pathway leakage exceeding the limiting condition of operation (LCO) for Technical Specification 3.6.1.1. The cause for the LLRT failures will be determined and required corrective maintenance will be performed and valves successfully tested during the current refueling outage." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM KEN HUNTER TO VINCE KLCO ON 2/22/13 AT 1611 EST* * * "Subsequent investigation into the reported LLRT failure revealed that the initial LLRT performed on feedwater check valve 2B21-F010A was not considered an acceptable test, since that LLRT was not representative of the 'as found' condition of this check valve. The test volume for this valve had been slowly filled such that the check valve did not have the normal expected differential pressure across the valve disc to achieve normal check valve seating. After draining the test volume and refilling it by allowing the test volume to gravity fill from the reactor pressure vessel, the expected differential pressure across the valve disc occurred and seated the disc in such a way that it was more representative of the 'as found' condition for the check valve. An LLRT was then performed with a leakage of 50 accm [actual cubic centimeters per minute] against an acceptance criterion of 194 accm. No maintenance or operation of the check valve had occurred between the initial invalid test and the subsequent test performed with the disc in its 'as found' condition. An engineering evaluation was performed that documented the acceptability of using this means for establishing the test volume for feedwater check valves 2B21-F010A and 2B21-F010B for the 'A' and 'B' loops of feedwater, respectively. This engineering evaluation concluded that establishment of the required test volume in the manner described for primary containment penetration 9A satisfies the Hatch LLRT program requirements and that the leakage acceptance criterion for feedwater check valve 2B21-F010A in its 'as found' state was satisfied. The 2B21-F077A valve will be retested at a later date. "Based on this information, the LLRT of this check valve in its 'as found' state was successful which actually resulted in successful minimum pathway leak rate test results for primary containment penetration 9A. These conclusive test results clearly indicated that the initial test results were incorrect and the 'as found' condition of this penetration isolation capability did not represent a significant degradation of a principal safety barrier as described in 10CFR50.72(b)(3)(ii)(A). For these reasons Notification # 48772 is being retracted." The licensee notified the NRC Resident Inspector. Notified the R2DO (McCoy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-02-20
48771 | -1 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-20 08:00 | 2013-02-20 08:52 | 2013-02-20 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION AT 1730 EST ON 2/20/13 FROM KOTELL TO HUFFMAN * * * This event has been retracted. Contact the Headquarters Operations Officer for additional details. R2DO (McCoy) notified. 73.71 Group informed via e-mail. | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-02-20
48770 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2013-02-19 10:54 | 2013-02-19 17:45 | 2013-02-20 | OCONEE ALERT AND NOTIFICATION SYSTEM SIRENS OUT OF SERVICE "Event: At 1400 EST on 2/19/2013, Oconee Nuclear Station (ONS) Emergency Preparedness (EP) was notified that the 65 Oconee Alert and Notification System sirens (65 is the total number of sirens within the ONS 10 mile Emergency Planning Zone) were found to be non-functional at 1054 EST during weekly testing on 2/19/2013. Oconee and Pickens County Emergency Management have been notified and will conduct 'Route Alerting' should ONS experience an emergency event that would normally require siren activation for notifying the public. Route Alerting, a method of backup alerting, is an approved FEMA process and is documented in the Emergency-Plan of both counties. "Initial Safety Significance: None. A pre-planned alternate process for notifying the public was put in place immediately and will remain in place until siren repair and testing are completed. "Corrective Action(s): An investigation is in progress to determine the cause of the siren system failure. Appropriate repairs will be made and testing conducted once the cause is determined. ONS will notify the NRC when the sirens are returned to service. "The ONS NRC Resident Inspector has been notified of this issue." The licensee has also notified state authorities and the appropriate county authorities as indicated in the event description. * * * UPDATE AT 1522 EST ON 2/20/12 FROM MEIXELL TO HUFFMAN * * * "The ONS Siren control systems were recovered and the ONS Alert and Notification System was retested and fully returned to service as of 1040 EST on 2/20/2013. Oconee and Pickens County Emergency Management Division (EMD), South Carolina EMD, and the ONS NRC Senior Resident Inspector were notified of the return of the systems to service. The systems were restored after correcting issues associated with the computer system for the sirens. An investigation is in progress to determine the cause of the event." R2DO (McCoy) notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-19
48769 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-02-19 13:03 | 2013-02-19 16:39 | 2013-03-21 | TRANSPORT OF POTENTIALLY CONTAMINATED WORKER AND SUBSEQUENT FATALITY "On February 19, 2013, at approximately 1303 EST, the control room was notified that a supplemental worker (i.e., a contract individual) had fallen and was injured. The worker was in a contaminated area. "Due to the individual's condition, the individual was not surveyed by a Health Physics technician prior to being transported in their anti-contamination clothing. The individual was transported by ambulance accompanied by Health Physics personnel to the local hospital for medical treatment (i.e., TriPoint Medical Center). Subsequently, the worker was declared deceased at the hospital. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xii) and 50.72(b)(2)(xi). Additionally, OSHA was notified pursuant to the requirements of 29 CFR 1904.39. The Lake County Coroner was also notified. "Subsequent surveys found no contamination on the worker, hospital, medical personnel, or ambulance. "No press release is planned. The NRC Resident Inspector has been notified." * * * UPDATE ON 3/21/13 AT 2032 EDT FROM LLOYD ZERR TO PETE SNYDER * * * "The Lake County Coroner has determined that the individual died of natural causes." The NRC Resident Inspector has been notified. Notified R3DO (Passehl). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL | OTHER UNSPEC REQMNT |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2013-02-19
48768 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-02-18 | 2013-02-19 15:00 | 2013-02-19 | AGREEMENT STATE REPORT - BEAM IRRADIATOR EQUIPMENT FAILURE The following event notification was received from Tennessee Division of Radiological Health via e-mail: "On Monday, February 18, 2013, the Division of Radiological Health received notification regarding K&S's Eldorado 78 device, and the failure of the source drawer not moving to the ON position. After the Eldorado device was turned on, the console indicated all interlocks were clear, however, when the beam was activated the source drawer did not move to the ON position. A Foss Therapy Technician was contacted and will make a service call on Wednesday February 20, 2013. The device is identified as Foss Therapy Services, Inc., Eldorado 78 Beam Irradiation Device, containing an International Isotopes Idaho, Inc. Co-60 source. Model and Serial No., INIS-SF-X.X-YY-Z. "A written report is being prepared and will be sent to the Tennessee Division of Radiological Health." Tennessee Report: TN-13-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-02-27
48767 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-12-20 03:54 | 2013-02-19 13:31 | 2013-02-19 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 0354 CST on December 20, 2012, with the Duane Arnold Energy Center (DAEC) operating at 100% power, an invalid Group 3 isolation on the 'A' side of the Primary Containment Isolation System occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by spurious upscale spike on the 'A' Refuel Floor Exhaust Radiation Monitor. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-02-19
48766 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-02-18 05:15 | 2013-02-18 16:30 | 2013-02-18 | 24 HOUR NOTIFICATION OF INOPERABLE SCRAM DISCHARGE VOLUME VALVE BASED ON NRC BULLETIN 80-14 "On February 18, 2013 at 0515 hours, with the reactor at 100% core thermal power, a scram discharge volume valve, CV-302-22B was declared inoperable as required by station procedural direction due to an observed degradation in opening stroke time during performance of quarterly surveillance testing of the Scram Discharge Instrument Volume Vent and Drain Valves. This action was taken consistent with NRC IE Bulletin 80-14. "Currently, station engineering is evaluating the valve stroke time trend data of CV-302-22B and a plan to address this issue will be developed as part of the Corrective Action Program. Pilgrim Technical Specification 3.3.G applies due to the inoperability of CV-302-22B. "This notification is being made in accordance with NRC IE Bulletin 80-14, 'Degradation of BWR Scram Discharge Volume Capability,' Part A.3, which states, 'By procedures, require that the SDV [scram discharge volume] vent and drain valves be normally operable, open and periodically tested. If these valves are not operable or are closed for more than 1 hour in any 24 hour period during operation, the reason shall be logged and the NRC notified within 24 hours (Prompt Notification). "This event has no impact on the health and safety of the public. "The NRC Senior Resident Inspector has been informed." The licensee will inform the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW | [5 empty] | 0 | 2013-02-18
48765 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-02-18 03:18 | 2013-02-18 11:35 | 2013-02-18 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "On February 18, 2013, at 0318 hours (CST), the Main Control Room received an alarm associated with a transfer of the Division 4 Nuclear System Protection System (NSPS) inverter to the alternate source. Plant Technicians were performing a Technical Specification (TS) Surveillance, 'Average Power Range Monitor Flow Biased/Neutron Flux Response Time Test,' when a test cable connector contacted a fuse block staple jumper, causing the transfer of the Division 4 NSPS bus from normal inverter source to its alternate source. "TS 3.8.7, 'Inverters - Operating' Surveillance Requirement 3.8.7.1 is not met with the inverter on the alternate source, and Condition C, requires High Pressure Core Spray (HPCS) system to be declared inoperable immediately since the Division 4 NSPS bus was not energized from the inverter. Since HPCS is an emergency core cooling system and is a single train safety system, this is a condition that could have prevented fulfillment of a safety function and is reportable under 10 CFR 50.72(b)(3)(v)(D), system needed to mitigate the consequences of an accident. "At 0925 CST, the Division 4 NSPS bus has been restored to service on the normal source. At 0925 CST, HPCS has been declared Operable. "The NRC Resident has been notified." | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2013-02-18
48764 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-02-18 01:31 | 2013-02-18 03:19 | 2013-02-18 | MANUAL REACTOR TRIP DUE TO HIGH SEAL LEAKOFF ON REACTOR COOLANT PUMP 3A "This is an non-emergency event notification to the NRCOC in Accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation due to Auxiliary Feedwater (AFW) initiation (eight hour notification). "On 2/18/2013 at 0055 Unit 3 commenced a unit shutdown due to high # 1 seal leak-off on the 3A Reactor Coolant Pump (RCP). At 0129 3A RCP #1 seal leak-off exceeded operating limits. Unit 3 reactor was manually tripped. Auxiliary feedwater actuated as designed based on steam generator levels as a result of the trip. Unit 3 is currently in Mode 3 and stable. "No complications were noted as a result of the reactor trip. Steam generator levels are being returned to normal level following the reactor trip. All other plant systems functioned as designed during and after the reactor trip. 3A RCP high #1 seal leak-off is under investigation." All control rods fully inserted on the trip. Decay heat was removed by AFW to the steam generators out the atmospheric reliefs. There was no primary to secondary leakage. Electrical buses are being supplied via offsite power. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-18
48763 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-02-17 13:45 | 2013-02-17 15:51 | 2013-02-17 | PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING CONTAINMENT WALKDOWN "CCNPP [Calvert Cliffs Nuclear Power Plant] U-2 discovered during the Mode 3 NOP/NOT containment walkdown that 2CV-100F Pressurizer Spray valve had a pin hole leak on the leak-off welded cap. This indicates that the bellows has a leak and in addition, the packing is leaking, pressurizing the leak-off line thus the leak-off line is the pressure boundary making this pressure boundary leakage. Technical Specification 3.4.13 [Action B] requires the unit be in mode 3 in 6 hrs. Unit was in mode 3 when discovered and unit will be placed in mode 5 within 36 hrs. Currently, the plant is at 400 degrees and 950 PSIA." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2013-02-17
48762 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-02-16 | 2013-02-17 00:14 | 2013-02-19 | AGREEMENT STATE REPORT - SOURCE DISCONNECT FROM RADIOGRAPHY CAMERA The State of Texas submitted the following via email: "On February 16, 2013, the Agency [Texas Department of Health] was contacted by the Radiation Safety Officer (RSO) for QSA Global requesting reciprocity to work in the State of Texas. The RSO stated they had been contacted by a Texas licensee who requested the recovery of an iridium - 192 source at a work site near the city of Jacksonville, Texas. The source was out of a Sentinel model 880 exposure device. The RSO stated that the disconnect occurred at about 0900 hours [CST] during the first exposure of the day on February 16, 2013. The RSO stated that the dose rate at the exposure device was 5 millirem per hour leading them to believe the source was still in the collimator. At 2134 hours the RSO for QSA Global contacted the Agency and reported that the source had been recovered. The individual recovering the source received 10 millirem during the recovery. No overexposures occur due to this event. The source and exposure device will be returned to the manufacturer for inspection. Additional information will be provided as it is received in accordance with SA-300." TX Incident # I - 9060 * * * UPDATE FROM ART TUCKER TO CHARLES TEAL AT 0753 EST ON 02/19/13 * * * "The Texas incident number for this event has been changed to I-9042. The spelling of the company's name has been corrected." Notified R4DO (Hagar) and FSME Event Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-03-04
48761 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-16 14:03 | 2013-02-16 17:05 | 2013-02-16 | OFFSITE NOTIFICATION DUE TO ONSITE CONTRACTOR FATALITY "At approximately 1318 hours (EST), the Main Control Room was notified of a contract employee slumped over on a fork lift inside the protected area. First Responders were dispatched to the scene. Off-site assistance was requested and arrived on-site at approximately 1330 hrs. CPR was administered by the First Responders and Paramedics. At 1403 hrs., the paramedics determined that the efforts to revive the patient were unsuccessful. The cause of death has not yet been determined. "Unit 1 remains in Mode 1 at 100% power. Unit 2 remains in Mode 1 at 97% power. Power is limited due to end of cycle maximum core flow conditions. "A press release is not planned at this time. The Occupational Safety and Health Administration (OSHA) will be notified of the fatality. This notification is being performed in accordance with 10CFR50.72(b)(2)(xi) for notification to an off-site government agency. The NRC Resident Inspector has been notified. * * * UPDATE FROM STUART BYRD TO HOWIE CROUCH @ 1744 EST ON 2/16/13 * * * "The Occupational Safety and Health Administration was notified of the fatality on 2/16/13 at 1730 EST." The NRC Resident Inspector was notified of this update. | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-16
48760 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-16 03:10 | 2013-02-16 08:38 | 2013-02-16 | REACTOR PROTECTION SYSTEM SCRAM SIGNAL DUE TO SCRAM DISCHARGE VOLUME HIGH LEVEL "On 2/16/13, at 0310 EST, with the reactor shutdown for a refueling outage, a full RPS actuation was received on Hatch Unit 2 due to Scram Discharge Volume High level. The Operations crew placed the Unit 2 mode switch to the Start-up/Hot Standby position per approved procedure for the purpose of performing the U2 Refueling Interlock functional test. The cause of the Scram was due to a Scram Discharge Volume high level caused by a malfunctioning SDV drain valve. Hatch Condition Report 591279 has been generated to document the event." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-02-16
48759 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2013-02-15 07:00 | 2013-02-15 16:56 | 2013-02-15 | PACKAGE RECEIVED AT VA MEDICAL CENTER WITH OUTSIDE CONTAMINATION EXCEEDING LIMITS "[The Department of Veterans Affairs, Veterans Health Administration (VHA) National Health Physics Programs] has a master materials license from the Nuclear Regulatory Commission. License number is 03-23853-01VA. "Per 10 CFR 20.1906(d), [the VA] is reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received today (February 15, 2013) at around 7 AM ET by Carl Vinson VA Medical Center, Dublin, Georgia. The package was checked-in and surveyed around 8:30 AM ET. This medical center holds permit number 10-09569-01 under the VHA master materials license. "Wipe tests performed on the external surface of the package indicated a removable contamination level of 4190 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. "The package contained eight unit dosages of radiopharmaceuticals ranging between 6 and 40 millicuries each of Technetium-99m and was shipped from Cardinal Health in Augusta, Georgia. The inner packaging materials were also found to be contaminated. "The VA facility Nuclear Medicine Technologist who surveyed the packages immediately notified the vendor/shipper, who serves as the final delivery carrier, about the contaminated package at about 9 AM ET. [The VA National Programs] office was not notified until about 4 PM ET. "As corrective actions: the packaging materials were bagged and set aside in a restricted area at the VA Medical Center and were reclaimed later in the day by the radiopharmacy. [The VA has also] notified NRC Region III Project Manager (K. Null) ..." HOO Note: A similar incident at the same facility was reported on 02/11/13 - see EN #48742. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2013-02-25
48758 | 0 | PALISADES | 1 |  |  | [1] CE | 2013-02-15 13:00 | 2013-02-15 15:05 | 2013-02-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO COMPONENT COOLING WATER TRAIN OUT OF SERVICE "At 2030 hours [EST] on February 14, 2013, technical specification (TS) 3.7.7 condition A was entered due to the right train of the component cooling water (CCW) system being declared inoperable. The cause of the inoperable train was the identification of an approximate 40 gallon per hour CCW system to service water system leak inside the 'A' CCW heat exchanger. TS 3.7.7 condition A requires restoration of the inoperable train within 72 hours. If the restoration is not completed within 72 hours, the plant must be in Mode 3 within 6 hours and in Mode 5 within the subsequent 36 hours. "Due to the inability to repair the leak within the required 72 hour time frame during power operation, a plant shutdown was initiated at approximately 1300 hours on February 15, 2013. Entry into Mode 3 is expected at approximately 1700 hours on February 15, 2013. The plant will enter Mode 5 to execute leak repair. Mode 5 entry is expected at approximately 0800 hours on February 16, 2013. "This event has no impact on the health and safety of the public. The NRC Resident Inspector has been notified." | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-02-15
48757 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-02-15 13:00 | 2013-02-15 14:00 | 2013-02-15 | AGREEMENT STATE REPORT - LEAKING SEALED NI-63 SOURCE IN GAS CHROMATOGRAPH The following information was received from the Commonwealth of Massachusetts via fax: "The licensee reported to the Agency (MA Radiation Control Board) that a wipe test survey of an SVAC-G module containing a Ni-63 sealed source yielded 0.0068 microcuries. The licensee gave no further details about the sealed source or the device, and stated that a written report was mailed to the Agency. The SS&D registration certificate indicates the sealed source maximum activity is 5 millicuries. The SS&D certificate indicates the source is contained inside the 'Thermo Fisher Scientific' model SVAC-G module which is contained in a 'Thermo Fisher' model EGIS Defender gas chromatograph instrument." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-02-25
48756 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-15 20:00 | 2013-02-15 13:01 | 2013-02-18 | TECHNICAL SUPPORT CENTER TAKEN OUT OF SERVICE FOR PLANNED MAINTENANCE "This report is being submitted in accordance with the requirements of 10 CFR 50.72(b)(3)(xiii), for planned maintenance which will result in temporary power outages for the Salem Technical Support Center. "Planned maintenance will commence on the Salem 13 kV Substation 5, the normal power supply for the Salem Technical Support Center on February 15, 2013 at approximately 2000 hrs. [EST]. Normal and backup power supplies to the Salem Technical Support Center will be removed for approximately 3-4 hours during initial clearance tagging and system alignment, after which the Technical Support Center Emergency Diesel Generator will be available for manual starting to power the facility if needed while the normal power supply is unavailable. "Substation 5 maintenance is scheduled to be completed by the afternoon of February 17, 2013 when the Salem Technical Support Center Emergency Diesel Generator backup power supply will again be isolated for a period of 3-4 hours during clearance tag removals and system realignment. "While normal and backup power supplies are unavailable, Salem emergency plan procedures provide guidance for use of the Hope Creek Technical Support Center and the Emergency Operations Facility as backup facilities should activation of the Salem Technical Support Center be required. "The NRC Resident Inspector has been notified." The licensee will be notifying Lower Alloways Creek Township. * * * UPDATE FROM POWELL TO SNYDER ON 2/18/13 AT 0015 EST * * * The licensee completed work on the power supplies. Normal power was restored at 0010 EST on 12/18/13. The licensee will notify the NRC Resident Inspector. Notified R1DO (Dimitriadis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-15
48755 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-02-14 21:30 | 2013-02-14 23:58 | 2013-02-15 | HYDRAULIC OIL LEAK TO ENVIRONMENT "Approximately 15 gallons of hydraulic oil was spilled from excavation equipment onto the ground inside the protected area boundary. Notifications have been made to the National Response Center and the Kansas Department of Health and Environment. Cleanup by on-site personnel is in progress. "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-15
48754 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-02-14 17:10 | 2013-02-14 18:31 | 2013-02-15 | OFFSITE NOTIFICATION DUE TO RELEASE OF AMERTAP BALLS INTO THE MISSISSIPPI RIVER "On 2/14/2013, Xcel Energy personnel determined that approximately 44% of the Amertap balls recently used were not recovered. Monticello Nuclear Generating Plant is required to report to the Minnesota Pollution Control Agency (MPCA) when greater than 20% of the Amertap balls are not recovered. This is based on an agreement with the MPCA dated September 12, 2008. The MPCA was notified at 1710 CST on 2/14/2013." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL STIDMON TO HOWIE CROUCH AT 1352 EST ON 2/15/13 * * * "Update for 50.72 non-emergency notification number 48754: "The referenced report number was made at 1831 EST on 2/14/2013. This report stated the Minnesota Pollution Control Agency (MPCA) was notified that 44% of Amertap balls recently used were not recovered at 1710 CST on 2/14/2013. Due to a miscommunication between the Monticello Nuclear Generating Plant Chemistry Department and the Xcel Energy Corporate Environmental Services contractor, the actual MPCA notification was not made until 0930 CST on 2/15/2013. This update report is to ensure the correct time of the MPCA notification was documented." The licensee notified the NRC Resident Inspector. Notified R3DO (Pelke). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-14
48753 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2013-02-14 | 2013-02-14 18:29 | 2013-02-14 | AGREEMENT STATE REPORT - DISCOVERY OF GAS CHROMATOGRAPH IN BUILDING ATTIC The following is a synopsis of information received from the State of Oregon via email: When cleaning out an attic storage space acquired from a business partner (Philco International), an employee of the Evonik Corporation discovered a gas chromatograph containing a Ni-63 electron capture device (ECD). The ECD was manufactured in 1993 and contained 15 mCi of Ni-63 at the time of manufacture. The ECD is model number N610-0133 and serial number 1121. The chromatograph was manufactured by Perkin Elmer and was originally sold to InterMedics of Angleton, TX in October, 1993. In 1998, Guidant bought out InterMedics and eventually closed the facility in 1999. It is unknown what happened to the device after the 1999 closure. Evonik Corporation will be contracting out proper disposal of the unit and will inform the State of Oregon when it has been removed. Oregon Incident No.: 13-0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2013-02-22
48752 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-08-28 | 2013-02-14 14:28 | 2013-02-14 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING Y-90 SIR-SPHERES The following information was obtained from the Commonwealth of Pennsylvania via email and facsimile: "Notifications: On February 13, 2013 the licensee informed the Department's [Pennsylvania Department of Environmental Protection] South-central Regional Office of the medical event. The event is reportable within 24 hours per 10 CFR 35.3045(a)(1)(i). The referring physician was notified of this event but the patient passed away in November of 2012 as a result of metastatic pancreatic cancer. "Event Description: During a routine audit of the Y-90 written directive program, an error was noted in a SIR-Sphere procedure that was performed on August 28, 2012. The patient was prescribed 17.6 mCi of Y-90 SIR-Spheres. The patient actually received only 12.8 mCi. This corresponds to a dose that is 27.3% lower than the prescribed dose. "Cause of the Event: The physician recorded the wrong administered dose on the written directive form. Also a small liquid volume remained in the vial after the 'air-injection' final step. "Actions: The licensee initiated and completed an audit of all SIR-Sphere procedures and no other issues were identified in any other patients since inception of the program. The South-central Regional Office has been in discussion with the licensee regarding corrective actions that will be implemented." Pennsylvania Event Report ID No.: PA130006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-02-22
48751 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-02-13 15:45 | 2013-02-13 17:42 | 2013-02-13 | OFFSITE NOTIFICATION DUE TO TRITIUM RELEASE ONSITE "As part of routine rounds on 2/13/13, site personnel discovered an overflow condition at a collection tank containing water with low levels of tritium (approximately 6,000 pCi/L). The discharge pump for the tank was found to be nonfunctional which resulted in the overflow condition. Following discovery, a portable pump was utilized to pump the water to the normal monitored discharge path and terminate the overflow condition. The exact volume could not be determined but it is estimated that the volume of water that overflowed to the ground was greater than the 100 gallon threshold for voluntary reporting as indicated in Nuclear Energy Institute (NEI) 07-07, 'Industry Ground Water Initiative-Final Guidance Document.' A rough estimate of the release is between 100 and 300 gallons. The tritium was contained to a small area on the plant site in the vicinity of the discharge structure, and there is no significant potential for off-site impact or impact to on-site personnel. "Because the leak remained on site, there will be no offsite impact to drinking water sources. Furthermore, the release posed no threat to employees or the public. Southern Nuclear [SNC] will continue to monitor the affected area as required. "In accordance with SNC's groundwater protection procedures and the NEI guidance, a voluntary notification of this discovery will be made to the State of Georgia Environmental Protection Division and other agencies to inform them of this matter. The NRC Region II Resident Inspector was also notified. "Reference: Condition Report 589402. Event occurred at 1111 EST, decision to make offsite notifications authorized at 1545 EST." The tank was the outfall collection tank. Environmental Protection Agency limit for tritium in drinking water is 20,000 pCi/l. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-13
48750 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2013-02-13 13:55 | 2013-02-13 16:41 | 2013-02-13 | MANUAL REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "At 1352 [hrs. EST], the Unit 2 CCR [Central Control Room] noted a trip of both heater drain tank pumps and entered Abnormal Operating Procedure 2-AOP-FW-1, 'Loss of Feedwater'. Prior to the event, Instrumentation and Controls personnel were performing testing on the heater drain tank level control system. Turbine load was reduced per plant procedures, however a manual reactor trip was initiated at 1355 due to an inability to maintain steam generator water levels. The team subsequently entered E-0, 'Reactor Trip or Safety Injection'. All control rods fully inserted. All safety systems responded as expected with the exception of source range detector N-31 and intermediate range detector N-35. N-31 and N-35 were declared inoperable. The auxiliary feedwater system actuated as expected and provided feedwater to maintain steam generator water level. Decay heat removal is via the steam generators to the main condensers. Offsite power and plant electrical lineups are normal. No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. Unit 3 was unaffected and remains at 100% power. An investigation is in progress." Unit 2 is currently at normal operating pressure and temperature. The licensee plans to issue a press release on this event. The licensee notified the State of New York Public Service Commission and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-13
48749 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-02-06 17:52 | 2013-02-13 14:46 | 2013-02-13 | AGREEMENT STATE REPORT - STOLEN SENORX GAMMA FINDER II SURVEY METER RECOVERED The following information is a synopsis of information received from the State of Louisiana: On 2/6/2013 at 1752 CST, the Iberia Parish Sheriff's Office (IPSO) notified the Louisiana Department of Environmental Quality (LDEQ) that radioactive material had been found in a vehicle which had been towed and impounded by IPSO. LDEQ personnel conducted an investigation on 2/8/2013 at the IPSO. A metal briefcase containing a SenoRx Gamma Finder II survey meter and two calibration sources was found in the impounded vehicle by the IPSO. Survey readings done at a local hospital before LDEQ was called read 0.008 mR/hr for the two calibration sources. The briefcase containing the survey meter and calibration sources was then taken to the IPSO. Description of the first source: Co-57, serial number D-138-21, last calibration date 10/21/2008, activity 11.5242 microCuries. Description of the second source: Co-57, serial number D-139-6, last calibration date 10/22/2008, activity 1.1419 microCuries. The IPSO traced the serial numbers and found that the survey meter and calibration sources belonged to Bard Biopsy Systems in Philadelphia, Pennsylvania. The IPSO confirmed that Bard Biopsy Systems had reported the survey meter and calibration sources stolen from their location in Philadelphia, Pennsylvania in 2009. A report had been filed with the Philadelphia Police Department, District 26, at that time. LDEQ personnel performed a survey on both calibration sources using a Ludlum 14C survey meter. The first source read 0.05mR/hr on the surface and the second source read 0.03 mR/hr on the surface. A background reading of 0 mR/hr was noted during these readings. The Philadelphia PD, District 26 is following up on the stolen equipment. The IPSO will ship the survey meter and sources to the Philadelphia PD. Philadelphia PD will return the survey meter and calibration sources to the owner. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-02-21
48748 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2013-02-12 19:23 | 2013-02-13 15:42 | 2013-02-15 | INITIATION OF MATERIAL CONTROL AND ACCOUNTABILITY ALARM RESOLUTION PROCEDURE "10CFR74.57(f)(2) requires notification within 24 hours that a Material Control and Accountability (MC&A) alarm resolution procedure has been initiated. In the Oxide Dissolution Area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure has been initiated, this notification is being made. An action plan has been developed and actions are underway to resolve the alarm per the criteria in the NFS Fundamental Nuclear Material Control Plan. "There were no actual or potential safety consequences to workers, the public, or the environment. "The licensee notified the NRC Resident Inspector." Per the licensee, processes in this area have been shutdown until the investigation is complete. * * * UPDATE FROM RANDY SHACKELFORD TO HOWIE CROUCH AT 1538 EST ON 2/15/13 * * * "The abrupt alarm has been reconciled." Notified R2DO (King), NMSS EO (Habighorst) and Fuel OUO Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2012-02-14
48747 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-12 15:30 | 2013-02-12 18:01 | 2013-02-15 | NOTIFICATION OF OFFSITE AGENCIES DUE TO DISCOVERY OF POTENTIAL HUMAN REMAINS "At 1530 EST on February 12, 2013, bones were discovered in the debris removal baskets in the Screen House at the Cook Nuclear Plant. These bones have the potential to be human remains. "Local law enforcement agencies have been notified and the remains were removed by law enforcement personnel. "The NRC Senior Resident Inspector was notified. Plant operations was not impacted by the event. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies and potential for media involvement related to the discovery." * * * UPDATE FROM GREG KANDA TO CHARLES TEAL ON 2/15/13 AT 1045 EST * * * "After analysis by the Berrien County Sheriff's Department, it was determined that the bones discovered in the debris removal baskets in the screenhouse at the Cook Nuclear Plant on February 12, 2013 at 1530 EST were not of human origin, but most likely from a deer or other animal." The licensee has notified the NRC Resident Inspector. Notified the R3DO (Pelke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-12
48746 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2013-02-12 09:07 | 2013-02-12 17:53 | 2013-02-12 | MEDICAL TREATMENT OF CONTAMINATED INDIVIDUAL "An employee reported to the dispensary this morning with a laceration to the middle finger on his left hand at approximately 0907 CDT. The plant nurse administered first aid and decided to transport the employee to a local medical facility. A whole body survey of the employee in his plant clothing was performed. The maximum amount of contamination present was found on his left boot which read 19,575 dpm/100cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was re-surveyed. The employee was free of contamination upon release." The licensee plans to notify its NRC Regional contact (Bob Prince) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2013-02-12
48745 | 0 | DRESSER-RAND |  |  |  |  | 2013-02-01 | 2013-02-12 16:52 | 2014-04-01 | PART 21 REPORT - DEFECTIVE RAW MATERIAL USED TO MANUFACTURE VALVE STEMS Dresser-Rand is reporting that one of its vendors supplied annealed material instead of the specified heat-treated material. Dresser-Rand used the defective raw material to manufacture valve stems for Terry Type Emergency Feedwater pump drive turbines. Dresser-Rand has verified that the annealed material is not acceptable for the finished product. The two customers (Wolf Creek Nuclear Plant and Callaway Nuclear Plant) that received the affected parts have been notified of this issue and have confirmed that the components in question are not in service at their facilities. The remaining material and affected parts have been quarantined at the Dresser-Rand plant in Wellsville, NY. All questions should be addressed to: Joe Menichino Manager, Navy/Nuclear Product Engineering 37 Coat Street Wellsville, New York, 14895 Phone: (585) 596-3406 jamenichino@dresser-rand.com * * * UPDATE FROM JOE MENICHINO TO CHARLES TEAL ON 3/11/13 AT 1614 EDT * * * The following was excerpted from a facsimile received from Dresser-Rand: "DESCRIPTION OF DEFECT OR NON-COMPLIANCE "Specific designs of steam turbine control valve stems are made from heat treated ASM 5663M Inconel Bar raw material. Certifications associated with heat numbers of certain inventory of this material indicate that the material vendor incorrectly supplied material in an annealed condition (AMS 5662M). "POTENTIAL SAFETY HAZARD OR NON-COMPLIANCE "Valve stems are used to control steam turbine speed and power. The valve stems must be free to move within the guiding assembly during operation. Stems are made using materials that have the correct material properties to reduce the risk of failure. The use of inconel raw stock in an annealed condition is unacceptable for steam turbine valve stems due to the risk of unacceptable wear and strength characteristics which could lead to sticking or tensile failure in the mating guide bushings within the valve assembly. "ADVICE TO EFFECTED CLIENT RELATED TO THIS REPORT "For those affected sites identified, locate and return the material to Dresser-Rand immediately." Affected facilities include Point Beach, Clinton, Wolf Creek, Cooper, Callaway, San Onofre, and Prairie Island. Notified R1DO (Dentel), R3DO (Dickson), R4DO (Powers), and the Part 21 Group via email. * * * UPDATE FROM ED GRANDUSKY TO CHARLES TEAL AT 1510 EST ON 2/28/14 * * * The following was excerpted from a facsimile received from Dresser-Rand: "DESCRIPTION OF DEFECT: "This is an addendum to Part 21 Reports Log# 2013-008-00 and Log# 2013-008-01. Another Vendor certification has been discovered for valve stem material that indicates the annealed condition-lnconel was supplied in lieu of the heat treated that is specified. "ENGINEERING EVALUATION & RECOMMENDATIONS: "1- Complete review of all Vendor certification for this material to make certain no more. Discrepant material was used in the manufacture of these stems. "2- Identify all DR part numbers that were made using the affected heat numbers. "3- Notify affected customers and recall non-compliant parts. "Potential Affected Part Numbers: "800777-001 Rev. NA "800768-701 Rev. A "800768-702 Rev. A "800858-001 Rev. E "800740-701 Rev. A "800746-001 Rev. B "800739-001 Rev. NA "800743-001 Rev. A "801061-701 Rev. A "800741-701 Rev. B "800744-001 Rev. NA "800745-001 Rev. NA "800748-001 Rev. A "800742-001 Rev. B" Notified R1DO (DeFrancisco), R3DO (Kunowski), R4DO (Hagar), and the Part 21 Group via email. * * *UPDATE FROM ED GRANDUSKY TO JEFF ROTTON AT 1520 EDT ON 04/01/2014 * * * The following information is excepted from a facsimile provided by Dresser-Rand: Specifications for valve stems provided to Palo Verde (Part Number W800743-001), Tihange 2 (Part Number W800746-001), Catawba (Part Number W800746-001), and Davis Besse (Part Number (W800746-001) call for the material to be heat treated AMS 5663M Inconel Bar. Certifications associated with another heat number of material indicate that the vendor supplied material in an annealed condition (AMS 5662M). The lower mechanical properties of the AMS 5662M could lead to shorter operating life for these stems. The material certification for all Inconel valve stems has been reviewed back to the first Inconel stem made by Dresser-Rand. No new corrective actions were deemed necessary. The four sites listed above should locate and return the valve stems immediately to Dresser-Rand for evaluation. Notified R2DO (Vias), R3DO (Passehl), R4DO (Gepford), and the 10CFR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-02-12
48744 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2013-02-11 22:36 | 2013-02-12 00:45 | 2013-02-12 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON LOSS OF CONDENSER VACUUM "This is a non-emergency event notification to the NRCOC [Nuclear Regulatory Commission Operations Center] in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation due to Auxiliary Feedwater (AFW) initiation (eight hour notification). "On 2/11/2013 at 2236 EST Unit 3 experienced a loss of condenser vacuum. An automatic Turbine Trip signal was generated which initiated a Reactor Trip signal. The reactor tripped as required on the automatic trip signal. Auxiliary feedwater water actuated automatically based on low steam generator levels following the trip. Unit 3 is currently in Mode 3 and stable. Steam generator levels have been returned to normal levels . The loss of vacuum is under investigation at this time. All other plant systems are working as designed." The reactor trip was uncomplicated. All control rods fully inserted. The plant is stable at normal temperature and pressure. AFW has been secured and main feedwater is being used for Steam Generator water level control. The main condenser is unavailable and decay heat removal is to atmosphere via the atmospheric steam dumps. There are no indications of primary to secondary leakage. Unit 3 is in a normal offsite power electrical alignment. There is no impact on Unit 4. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-12
48743 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-02-11 14:35 | 2013-02-11 20:34 | 2013-02-12 | LOSS OF EMERGENCY RESPONSE CAPABILITY - JOINT INFORMATION CENTER (JIC) UNAVAILABLE "On Monday, February 11, 2013 at 1435 EST with Pilgrim Nuclear Power Station (PNPS) at 0% core thermal power, the Joint Information Center (JIC) was determined to be unavailable and was declared non-operational. [Power was lost] to the facility [due] to winter storm Nemo. This facility serves as the Joint Information Center for Entergy, State, and Federal organizations during an emergency response. "Existing emergency procedures direct the responsible Emergency Plant Manager to relocate the JIC staff to the designated alternate location (Bridgewater State University) as required. It has been confirmed that the alternate location is available for use. "The Emergency Response Organization has been informed to establish the JIC at the Moakley Center at Bridgewater State University in the event of a declared emergency classification requiring activation of this Emergency Response Facility. "The licensee has notified the NRC Senior Resident Inspector and the Commonwealth of Massachusetts. "This eight-hour notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency offsite response facility. "An update will be provided when power has been restored to the JIC and the facility is available to be activated if called upon." * * * UPDATE FROM DAVID NOYES TO DONALD NORWOOD AT 1616 ON 2/12/2013 * * * "Power has been restored to the Joint Information Center (JIC). At approximately 1000 on 2/12/13 the JIC was deemed to be available for activation if called upon by the Emergency Preparedness Department. The Emergency Response Organization has been informed to establish the primary JIC in the event of a declared emergency classification requiring activation of this Emergency Response Facility. "The licensee has notified the NRC Senior Resident Inspector and the Commonwealth of Massachusetts." Notified R1DO (Dimitriadis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-11
48742 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2013-02-11 14:00 | 2013-02-11 18:01 | 2013-02-18 | PACKAGE RECEIVED AT VA MEDICAL CENTER WITH OUTSIDE CONTAMINATION EXCEEDING LIMITS "[The Department of Veterans Affairs, Veterans Health Administration (VHA) National Health Physics Programs] has a master materials license from Nuclear Regulatory Commission. License number is 03-23853-01VA. "Per 10 CFR 20.1906(d), [the VHA] is reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received today (February 11, 2013) at around 2:00 PM ET by Carl Vinson VA Medical Center, Dublin, Georgia. This medical center holds permit number 10-09569-01 under the VHA master materials license. "Wipe tests performed on the external surface of the package indicated a removable contamination level of 561 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. "The package contained two radiopharmaceuticals dosages of Technetium-99m and two doses of Thallium-201 and was shipped from Cardinal Health in Augusta, Georgia. The inner packaging materials were not contaminated, and the four dosages were able to be used. "The VA facility Nuclear Medicine Technologist immediately notified the vendor/shipper, who serves as the final delivery carrier, about the contaminated package at about 2:30 PM ET. "As corrective actions: the packaging materials were set aside in a restricted area at the VA Medical Center for decay; staff with access to the area were notified about the contaminated packaging materials; and surveys were performed to ensure that contamination did not spread beyond the immediate area where the package was received and checked in. "[The VHA has also] notified NRC Region III (P. Pelke) of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2013-02-19
48741 | 0 | TOPWORX |  |  |  |  | 2012-10-12 | 2013-02-11 15:26 | 2013-02-11 | PART 21 REPORT - SWITCHES BUILT WITH ADHESIVE BEYOND ITS EXPIRATION DATE TopWorx discovered that switches were built and shipped using adhesive G909 that was beyond its manufacturer's recommended expiration date. Adhesion properties of the expired adhesive cannot be guaranteed against the deleterious effects of seismic events, thermal aging, and high dose radiation. The switches involved were TopWorx M8-24521-P4 shipped on 12 October 2012 and TopWorx M8-2352T-P4 shipped on 8 November 2012. Both shipments were sent to PGS Enrique Maria Hierro S.L. in Spain. If the units mentioned above are found to be installed in an environment that may expose them to the conditions of seismic events, thermal aging, and/or high dose radiation, then the units should be replaced. Per TopWorx, there were 13 switches shipped. All switches were shipped to Spain. No switches were shipped to US licensees. Technical questions or concerns should be addressed to Alex Murphy, Manager, Quality, (502) 873-4602. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-02-11
48740 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2013-02-11 07:56 | 2013-02-11 12:59 | 2013-02-11 | FITNESS FOR DUTY - CONFIRMED POSITIVE FFD TEST A non-licensed, supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been restricted. The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2013-02-11
48739 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-02-10 14:05 | 2013-02-10 20:20 | 2013-02-10 | LOSS OF OFFSITE POWER AND SUBSEQUENT PRESS RELEASE "On Sunday, February 10, 2013 at 1405 [EST], with the reactor at 0% core thermal power, all control rods fully inserted, and in cold shutdown conditions, the plant experienced a loss of off-site power. With Pilgrim Station aligned to off-site power via the start-up transformer (SUT), a fault on the 'B' phase of the SUT was experienced due to suspected falling ice striking the phase's insulator. This resulted in the tripping of the feeder breaker, ACB-102, and the loss of power to 4160 KV buses A1 through A4. Emergency Diesel Generators (EDGs) 'A' and 'B' auto-started as designed and are powering emergency buses. "The loss of off-site power resulted in de-energization of both Reactor Protection System (RPS) channels resulting in a reactor scram signal and isolation of shutdown cooling. At 1418, shutdown cooling was returned to service. All other plant systems responded as designed. Station personnel are in the process of establishing back-up power in accordance with plant procedures. "The following press release was made at 1715 hours: 'Offsite power to Pilgrim station was interrupted this afternoon. The plant is in a cold shutdown condition and Pilgrim's diesel generators are providing power to the site. There is no worker or public safety concern. Plant personnel are troubleshooting the cause of the interruption.' "This event had no impact on the health and/or safety of the public. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | POT RHR INOP |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2013-02-10
48738 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2013-02-10 07:00 | 2013-02-10 09:11 | 2013-02-10 | MANUAL REACTOR SCRAM INSERTED DUE TO DEGRADING REACTOR WATER CHEMISTRY "During normal power operations, the crew observed condensate/feedwater conductivity begin to increase at approximately 0530 EST on 02/10/13. The crew responded to the associated alarm response procedures and entered abnormal operating procedure 34AB-N61-001-1 due to degrading reactor water chemistry parameters. A power reduction [from 100%] was initiated at 0555 EST in accordance with station procedures for responding to a suspected condenser tube leak. At 0700 EST, a manual reactor SCRAM [from approximately 47%] was inserted due to the elevated reactor water conductivity in accordance with station abnormal operating procedures. All rods inserted completely and no complications were encountered following the reactor SCRAM, normal feedwater injection remained available. Following the SCRAM, a Group 2 Primary Containment Isolation Signal (PCIS} was received as a result of reactor water level lowering below +3 inches. The lowest reactor water level observed was [minus] 2 inches and was restored to normal operating levels utilizing normal feedwater injection. Following restoration of reactor water level to the normal operating level, the Group 2 PCIS signal was reset. No ECCS injection systems actuated as a result of the reactor SCRAM." The SCRAM was uncomplicated and the plant is stable. Decay heat removal is to the main condenser via the turbine bypass valves. The plant is in a normal offsite electrical power shutdown alignment. Efforts are in progress to isolate the condenser in-leakage. There was no impact on Unit 2. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-10
48737 | 0 | MILLSTONE | 1 | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-02-09 14:30 | 2013-02-09 14:42 | 2013-02-10 | SAFEGUARDS REPORT CONCERNING PROTECTIVE ACTIONS TAKEN DUE TO WEATHER CONDITIONS Certain site security measures taken due to severe weather conditions. The licensee notified local law enforcement and the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 2045 EST ON 2/10/13 FROM TODD BERGER TO HUFFMAN * * * The licensee returned to a normal security posture at 1852 EST on 2/10/13 based on recovery from weather conditions. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-02-09
48736 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-02-08 22:00 | 2013-02-08 22:50 | 2013-02-10 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER "Pilgrim Station scrammed on a loss of offsite power. All systems performed as designed. Groups I, II, VI went to completion. Reactor Core Isolation Cooling (RCIC) is injecting to the vessel controlling level. High Pressure Coolant Injection is in pressure control and slowly cooling down. Offsite power was lost multiple times. The Startup Transformer has been declared inoperable. The Unusual Event was declared under EAL SU 1.1 based on loss of offsite power greater than 15 minutes [at 2200 EST]." The licensee originally experienced an automatic reactor scram at 2117 EST due to a load reject with a turbine trip/reactor scram due to loss of power. Offsite power availability has been fluctuating in and out to the site. The licensee states that all systems are functioning as required. All rods fully inserted and the reactor is stable in Mode 3. Both Emergency Diesel Generators are providing power to the safety related buses. The loss of offsite power is believed to be weather related. The licensee has notified the State and local authorities and the NRC Resident Inspector. Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email. * * * UPDATE FROM PAUL GALLANT TO VINCE KLCO AT 2/10/13 AT 1108 EST* * * Pilgrim terminated the Unusual Event and has transitioned to recovery effective at 10:55 AM on 02/10/2013. Offsite power has been restored to safety-related and non-safety-related electrical buses through the station Startup Transformer via a single 345 KV line. The other two offsite power sources remain out of service. The emergency diesel generators have been secured and are in standby. Residual heat removal is in shutdown cooling mode maintaining the reactor in cold shutdown. Fuel Pool Cooling is in service with fuel pool coolant temperatures trending down. The licensee notified State, local authorities and the NRC Resident Inspector. Notified R1 RA (Dean), R1DO (Powell), NRR DIR(Leeds) NRR EO (Evans) and NSIR IRD (Marshall). Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email. | 0 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2013-02-08
48735 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2013-02-08 | 2013-02-08 16:32 | 2013-02-08 | PART 21 - COMPLETED EVALUATION FOR POTENTIAL ERROR IN MAIN STEAM LINE HIGH FLOW CALCULATIONAL METHODOLOGY "GEH recently discovered that some calculations of the choked flow rate in the Main Steam Lines (MSLs) of GEH BWRs were non-conservative, with potential effects on margins between choked flow conditions and existing MSL high-flow Nominal Trip Setpoints (NTSPs), Allowable Values (AVs), and Analytical Limits (ALs). "GEH has now completed the evaluation of this condition and has determined this condition is not reportable under 10 CFR 21 for all U.S. BWR/2-6 plants. The effect of the discovered non-conservatisms in choked flow rate values was offset by unintended conservatisms in the GEH recommended formulation for calculating pressure drop across the MSL flow restrictor. As a result, GEH has determined that the flow-instrument pressure remain at conservative values (which would ensure that the associated NTSPs and AVs expressed in psid also remain at conservative values), and the MSL high-flow trip will function as designed. This update to the 60-day Interim Notification issued on December 12, 2012 (MFN 12-111 R1) will be sent to all US BWR/2-6 plants licensed using the GEH design basis and safety analysis." See previous NRC Event Report 48350. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-02-08
48734 | 0 | AVERILL ENVIRONMENTAL LABS |  |  |  |  | 2013-02-08 | 2013-02-08 14:10 | 2013-02-08 | MISSING NICKEL-63 SOURCE USED FOR ELECTRON CAPTURE DETECTOR The licensee called to report a missing 15 millicurie Nickel-63 source (serial #5404) used in a gas chromatograph electron capture detector. The licensee is in the process of moving their business location and discovered that this specific source was missing. It was last inventoried 29 days ago. All other sources possessed by the licensee have been accounted for. The licensee is still searching for the source which may have been misplaced in the move. However, there is a possibility that the source may have been inadvertently disposed. The licensee has notified NRC Region 1 (Jackson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-02-18
48733 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-02-08 09:45 | 2013-02-08 11:50 | 2013-02-08 | MINOR HYDRAULIC OIL SPILL ONSITE "A hydraulic oil line break occurred on a crane inside of the protected area. The break resulted in a 2-gallon spill of hydraulic oil. "Wolf Creek has notified the National Response Center and Kansas Department of Health and Environment. The oil spill is being cleaned up by our environmental group." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-08
48732 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2013-02-07 15:53 | 2013-02-07 19:34 | 2013-02-07 | INADVERTENT EMERGENCY SIREN ACTUATION "At 1553 CST on 02/07/2013, River Bend Station emergency preparedness personnel were notified by a dispatcher at the Pointe Coupee Parish Sheriff's Office that several calls had been received regarding one or more River Bend emergency sirens sounding in the vicinity of the city of New Roads, Louisiana. The siren(s) sounded at least twice. Emergency Preparedness personnel notified the caller that no emergency condition existed at the station and made other notifications in accordance with River Bend procedure EPP-2-401 for inadvertent siren sounding. Notifications included the governors office of homeland security to notify the public that the sounding is inadvertent and that no emergency exists at the station. Additionally, the Emergency Alert System local station (WJBO/WFMF) was directly notified to broadcast the notification. The cause of the siren sounding is currently being investigated. "The Senior Resident NRC Inspector has also been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-07
48731 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-07 17:35 | 2013-02-07 18:37 | 2013-02-07 | OFFSITE NOTIFICATION RELATED TO DEATH OF CONTRACTOR ONSITE "At 1620 EST on 2/7/2013 an emergency medical report was received in Unit 1 Control Room that an individual was reported to have collapsed and was lying unconscious outside of the protected area. Fire protection and Emergency Medical personnel were dispatched to the scene. The individual was unresponsive, without a pulse and not breathing. Off-site medical assistance was immediately requested. CPR was commenced and continued until transfer of the individual to off-site medical ambulance service Medic 1. An Automatic External Defibrillator (AED) was used once, as allowed by the AED. "Confirmation of the fatality was received at 1735 EST on 2/7/2013. The individual was pronounced dead at 1712 EST on 2/7/2013. "Both Units remain at 100% power. This Event notification is being made due to the onsite fatality. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-07
48730 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-02-07 14:30 | 2013-02-07 18:21 | 2013-02-07 | UNANALYZED CONDITION DUE TO POSSIBLE RUN-OUT OF HIGH PRESSURE SAFETY INJECTION PUMP "Current design basis calculations indicate the high pressure safety injection (HPSI) pumps could potentially operate in a run-out condition under certain worst case design basis conditions. The calculated flow is beyond the pump curves. The HPSI pumps could operate in a run-out condition for an extended period following a design basis accident. The pump vendor indicates that long term operation in this condition could not be supported due to accelerated wear of pump internal components. This represents a reportable unanalyzed condition." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-07
48729 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-02-07 | 2013-02-07 15:13 | 2013-02-07 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK OPEN The following report was received from State of Texas Radiation Branch via e-mail: "On February 7, 2013, the Agency [State of Texas Radiation Branch] was notified by the licensee that the shutter on an Ohmart model SH-F1A nuclear gauge was stuck in the open position. The gauge contains a 50 millicurie cesium - 137 source. Open is the normal operating position for this gauge. The licensee has notified their personnel that no entry into the vessel the gauge is mounted on is allowed until the gauge is repaired. The manufacturer has been contacted and arrangements to repair the gauge are being completed. The failure does not create an exposure risk to any individual. This gauge had previously failed in February of 2012 (EN47691). Additional information will be provided as it is received in accordance with SA - 300." Texas Report: I-9039. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-02-15
48728 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2013-01-28 | 2013-02-07 14:10 | 2013-02-07 | AGREEMENT STATE REPORT - SMOKE DETECTORS FOUND AT SCRAP METAL RECYCLING FACILITY The following report was received from the Commonwealth of Massachusetts Radiation Control Program via facsimile: "On 1/28/13, the radiation monitors at `Schnitzer Steel', a scrap metal dealer, detected radiation coming from an incoming truck loaded with scrap metal for disposal. The measured radiation level was 5.3 uR/hr with a background of 3.1 uR/hr. The load was rejected. The MA Radiation Control Program issued a 'DOT-SP 10656 shipment approval form' in order for the truck to return to 'Testa Corporation' [originator of the scrap shipment] of Maynard, MA. At the Maynard site, a consultant unloaded the scrap onto the ground and discovered 21 old smoke detectors. The smoke detector label identified the manufacturer as `Kiddie Corporation, Ashland, MA' and stated the smoke detector contained 1 uCi of Ra-226. The consultant secured all of the smoke detectors from unauthorized removal and is arranging for disposal via a licensed radioactive materials (RAM) waste broker." Massachusetts Report Number: 13-0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-02-15
48727 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-02-06 14:00 | 2013-02-07 12:16 | 2013-02-07 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED The following information was received from the California Radiologic Health Branch via e-mail: "On February 6, 2013, the licensee notified the California Department of Public Health that one of their moisture density gauges (CPN MC-1DRP, 10 mCi Cs-137, 50 mCi Am:Be-241, S/N MD00605734) was struck by a small bobcat tractor at a construction site at approximately 2:00 P.M. The gauge user had placed the gauge on the ground by the back bumper as he went to retrieve something from the cab of this truck. He no sooner started walking from the back of the truck to the side of the truck when the bobcat ran over the gauge. "The RSO reported that although the gauge's guide tube was broken off, the body of the gauge itself was not damaged and the Cs-137 and Am-241:Be sources remained fully shielded. The external shutter, however, was slightly open. The gauge was returned to the transport case and was transported back to the licensee's facility. The RSO then contacted the manufacturer, InstroTek who instructed the RSO on how to close the shutter safely. There was no additional exposure through the external shutter even though it was slightly open because the internal shutter had remained closed during the entire event as the source rod was in the 'safe' position. "The gauge user was wearing a whole body dosimeter which was immediately sent in for immediate processing. On February 7, 2013, [representatives from] the California Department of Public Health met with the licensee. All survey measurements were as expected for this type of gauge and there was no removable contamination found. An additional piece of lead was taped to the external shutter as a precaution during transit. The dose to any individual from this incident is estimated to be less than 0.5 millirem. The gauge is being shipped to InstroTek later today for repair." California Report 020613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-02-15
48726 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-06 15:24 | 2013-02-06 21:23 | 2013-02-28 | UNANALYZED CONDITION FOR CONTROL ROOM VENTILATION "On February 06, 2012, at 1524 PST, engineers reviewing dose analyses for non-LOCA, non-fuel handling accident analyses identified deficiencies in the analyses. The analyses of concern include a locked reactor coolant pump rotor, a control rod ejection accident, main steam line break, and steam generator tube rupture. These deficiencies brought into question whether the 30 day control room operator dose received following one of these accidents would meet the station licensing basis limits of up to 5 rem whole body or its equivalent. "In response to this concern, plant operators placed the control room ventilation system in its safeguards alignment, thereby ensuring the events would continue to be bounded by the analysis of the large break loss of coolant accident. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM DAVID BAHNER TO CHARLES TEAL ON 02/28/13 AT 1815 EST * * * "Pacific Gas and Electric Company (PG&E) is correcting the event date in the above Description to February 06, 2013, and is retracting EN 48726 based on the results from reanalysis of each affected non-loss-of-coolant accident (LOCA) event (i.e., steam generator tube rupture, main steam line break, control rod ejection, and reactor coolant pump locked rotor) for potential impact on control room operator dose. The new dose assessment determined that control room dose consequences from a large-break LOCA bound the non-LOCA events as assumed in the original analyses. Accordingly, PG&E concludes the Diablo Canyon Power Plant control room ventilation system remains capable of maintaining control room dose limits within General Design Criteria-19. "Plant personnel notified the NRC resident inspector." Notified R4DO (Allen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-06
48725 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-07-28 | 2013-02-06 17:10 | 2013-02-06 | UNANALYZED CONDITION THAT COULD HAVE RESULTED IN AN INCREASED MAXIMUM FLOOD LEVEL "On July 28, 2009, TVA identified, in the Corrective Action Program, the potential to overtop and fail earthen embankments at Cherokee, Fort Loudoun, Tellico, and Watts Bar Dams. This condition could have resulted in an increase in the probable maximum flood (PMF) level at Sequoyah Nuclear (SQN) Units 1 & 2. TVA initiated immediate actions to address the condition by conducting additional analyses and developing contingent actions. Additional actions were developed including the installation of modular flood barriers [which were] completed in December 2009. The barriers increase the effective height of the affected embankments preventing their overtopping and failure. The increase in PMF could have affected plant equipment including the emergency diesel generator system and the essential raw cooling water system. "Additional details regarding the modular flood barriers and the results of TVA's subsequent hydrologic analyses for SQN were discussed in public meetings between TVA and the NRC staff on July 7, 2010 and May 31, 2012, and provided in TVA letters to the NRC dated August 10, 2012, October 30, 2012, and January 18, 2013. "This report addresses a condition as described in 10 CFR 50.72 (b)(3)(ii)(B). Affected safety-related equipment is currently operable. "The NRC Resident Inspector has been notified of this condition." See related event notifications from Watts Bar (EN #48723) and Browns Ferry (EN #48724). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-06
48724 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2009-07-28 | 2013-02-06 16:31 | 2013-02-06 | UNANALYZED CONDITION THAT COULD HAVE RESULTED IN AN INCREASED MAXIMUM FLOOD LEVEL "On July 28, 2009, TVA identified, in the Corrective Action Program, the potential to overtop and fail earthen embankments at Cherokee, Fort Loudoun, Tellico, and Watts Bar Dams. Prior Browns Ferry Nuclear (BFN) analysis did not consider the potential to overtop and fail the earthen embankments at Cherokee Dam. This condition could have resulted in an increase in the probable maximum flood (PMF) level at Browns Ferry Nuclear Plant Units 1, 2 and 3. TVA initiated immediate actions to address the condition by conducting additional analyses and developing contingent actions. Additional actions were developed including the installation of modular flood barriers [which were] completed in December 2009. The barriers increase the effective height of the affected embankments preventing their overtopping and failure. "Additional details regarding the modular flood barriers and the results of TVA's subsequent hydrologic analyses were discussed in a public meeting between TVA and the NRC staff on July 7, 2010. "This report addresses a condition as described in 10 CFR 50.72(b)(3)(ii)(B). Subsequent analyses, completed in November 2012, determined that there are no past operability concerns with this condition at BFN. "The NRC Resident inspector has been notified of this condition." See related event notifications from Watts Bar (EN #48723) and Sequoyah (EN #48725). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-06
48723 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2009-07-28 | 2013-02-06 16:00 | 2013-02-06 | UNANALYZED CONDITION THAT COULD HAVE RESULTED IN AN INCREASED MAXIMUM FLOOD LEVEL "On July 28, 2009, TVA identified, in the Corrective Action Program, the potential to overtop and fail earthen embankments at Cherokee, Fort Loudoun, Tellico, and Watts Bar Dams. This condition could have resulted in an increase in the probable maximum flood (PMF) level at Watts Bar Unit 1. TVA initiated immediate actions to address the condition by conducting additional analyses and the development of contingent actions. Additional actions were developed including the installation of modular flood barriers [which were] completed in December 2009. The barriers increase the effective height of the affected embankments preventing their overtopping and failure. The increase in PMF could have affected plant equipment including the emergency diesel generator system, the essential raw cooling water system, the thermal barrier booster pumps and the control room chillers. "Additional details regarding the modular flood barriers and the results of TVA's subsequent hydrologic analyses for Watts Bar were discussed in public meetings between TVA and the NRC staff on July 7, 2010 and May 31, 2012, and provided in TVA letters to the NRC dated July 19, 2012, October 30, 2012 and January 18, 2013. "This report addresses a condition as described in 10 CFR 50.72(b)(3)(ii)(B). Affected safety related equipment is currently operable. "The NRC Resident Inspector has been notified of this condition." See related event notifications from Browns Ferry (EN #48724) and Sequoyah (EN #48725). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2013-02-06
48722 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2013-02-06 11:43 | 2013-02-06 13:27 | 2013-02-06 | UNUSUAL EVENT - LOSS OF OFFSITE POWER TO ESSENTIAL BUSES FOR GREATER THAN 15 MINUTES "At 1132 CST on 2/6/13, Point Beach Unit 1 experienced a loss of all offsite power due to the loss of 1X-03 High Voltage Station Aux Transformer. The high side circuit switcher opened. However, the 1X-03 transformer did not lock out resulting in G-01 and G-03 Emergency Diesels energizing the 1A-05 and 1A-06 4160 VAC busses (safety related)." The cause of the loss of offsite power is being investigated. In order to exit the event, the plant requires either 345 kV power to be restored or cross-tie plant power between the units. If cross-tied, Technical Specifications require the gas turbine to be placed on the cross-tie within 24 hours. The plant remained at 100% power and there was no effect on Unit 2. The licensee notified the NRC Resident Inspector. Notified the DHS SWO, FEMA, DHS NICC, and the Nuclear SSA (via e-mail). * * * UPDATE AT 1500 ON 2/6/2013 FROM JAMIE WEIGANDT TO MARK ABRAMOVITZ * * * "There were specified system actuations with the original event. Emergency diesel generators [EDG] G-01, 2, 3, and 4 started on the undervoltage conditions with G-01 and G-03 loading onto their respective buses. 1P-53, motor driven aux feed pump started as designed on the EDG breaker closures. Offsite power has been restored to safeguards buses and the EDGs have been removed from the buses. Troubleshooting continues on the initial fault. All other systems functioned as designed. The unusual event has been terminated as of 1340 CST on 2/6/13." The safeguards buses are being powered from Unit 2 through the electrical cross-tie. The licensee notified the NRC Resident Inspector. Notified the R3DO (Kunowsky), NRR EO (Evans), IRD (Marshall), DHS SWO, FEMA, DHS NICC, and the Nuclear SSA (via e-mail). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-02-06
48721 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-12-08 01:16 | 2013-02-06 11:39 | 2013-02-06 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION OF INVALID SYSTEM ACTUATION "On December 8, 2012, at 0116 EST, with Unit 1 operating near 100 percent rated thermal power (RTP), annunciator 601-135 'Torus Level High' was received in the main control room and immediately cleared. Torus water level was reading between 148.1 inches and 148.8 inches on torus water level sensors but torus water level indications from the High Pressure Coolant Injection (HPCI) sensors were observed to be fluctuating between 149 inches and 150 inches immediately after the event. Technical Specification LCO 3.6.2.2 requires torus water level to remain greater than or equal to 146 inches and less than or equal to 150 inches. The Technical Specification allowable limit is 154 inches for the HPCI torus water level sensors and the actual set point for the HPCI suction swap is 152 inches. When the HPCI torus water level instruments' reference legs are not completely filled, fluctuations in indicated level occur. This was determined to be the cause for this invalid actuation. Enough fluctuation occurred such that the HPCI suction swap instruments completed the actuation logic causing the HPCI suction swap design function to occur. This resulted in HPCI automatically realigning to the torus. It had been manually aligned to the condensate storage tank (CST), which is its primary source. HPCI DID NOT realign to mitigate an event or condition nor did it realign for actuation and injection to send water to the reactor vessel. Should the automatic suction swap fail to occur, the Technical Specifications require that the suction be manually realigned to the torus in accordance with plant procedures and training. The operability of HPCI was maintained throughout the event and no HPCI system actuation signal (low reactor water level or high drywell pressure) was received during the event. "At approximately 0337 EST, Instrumentation and Controls technicians began backfilling the reference legs for sensors 1E41N062B, 1T48N010A, and 1T48N021A. This task was completed at approximately 0503 EST at which time the normal torus water level and HPCI torus water level instrument indications were in agreement. The HPCI suction source was then realigned to the CST in accordance with plant procedures at approximately 0507 EST. This report is being made as an actuation of a system named in 50.73(a)(2)(iv)(B)(4) and is being reported in accordance with 50.73(a)(2)(iv)(A) and under the provision of 50.73(a)(1) based on an NRC interpretation that this actuation within the HPCI system was considered an ECCS actuation. Since the actual torus water level never actually reached 152 inches, the automatic realignment was determined to be an invalid actuation. SNC [Southern Nuclear Company] takes exception to the NRC interpretation on reportability of this condition, but are making this 60 day phone LER notification on a voluntary basis while this issue is being pursued with the NRC. The initiating signal was invalid and this report is being made under the auspices of 10 CFR 50.73(a)(1) for invalid specified system actuations." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-02-06
48720 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2013-02-06 09:00 | 2013-02-06 11:21 | 2013-02-06 | PLANNED MAINTENANCE ON PLANT PROCESS COMPUTER "This report is being made in accordance with 10CFR50.72(b)(3)(xiii). Calvert Cliffs Nuclear Power Plant will perform planned maintenance on the Unit 2 Plant Process Computer (PPC) and associated network infrastructure on February 06, 2013. The maintenance will remove the Unit 2 PPC for a planned duration of 12 hours and will render the Unit 2 SPDS out of service for this timeframe. Once the maintenance starts, the effected equipment and functions, including SPDS, can be returned to service within five minutes, if required. "Should an emergency be declared during this period, the control room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment at all times. Control room emergency response personnel will use emergency response procedures to disseminate plant parameter data points to the affected Emergency Response Facilities until the U-2 PPC is restored. MIDAS (Meteorological Data) and Unit 2 ERDS [Emergency Response Data System] data transmission will remain functional during the maintenance window. All work associated with this plant data network software installation will be performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. Back-out criteria has been identified as part of the work package. A test of all systems will be performed at the completion of the upgrade." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1713 EST ON 2/6/2013 FROM AMY CORDNER TO MARK ABRAMOVITZ * * * The plant process computer was returned to service at 1700 EST. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Powell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-06
48719 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2013-02-05 15:00 | 2013-02-05 17:51 | 2013-02-14 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK OUTSIDE THE CAMERA The following report was submitted via e-mail: "At approximately 3:00 PM the licensee called the Agency [Arizona Radiation Regulatory Agency] to report an equipment failure of an industrial radiography exposure device, involving a QSA Model 880 Delta camera, serial # D3231. The source did not crank back into a closed and shielded position after use. After working with the crank system and not being able to return the source, the crank system was disengaged and the source was pulled manually into the closed and shielded position in the camera. The camera contained 48 Curies of Selenium-75. The licensee will perform a leak test on the camera and then send it out for repair. "The Agency continues to investigate the actions of the licensee and timeliness of reporting the incident. "The NRC and the Arizona Governor's office have been notified of this event. "Press coverage is not anticipated." Arizona Incident 13-006 * * * UPDATE FROM AUBREY GODWIN VIA EMAIL TO HOWIE CROUCH @ 1127 EST ON 2/14/13 * * * "The Licensee supplied additional information... showing the effects of heat on the equipment. The radiography was being conducted at a solar power generation site. The mirrors were rotated down so the radiography could be conducted. The guide tube appears to have partially melted. The manufacturer recommends not exceeding 200 degrees Fahrenheit for the equipment. The steering wheel of their truck was also melted. "The Licensee is now conducting their work at night." Notified R4DO (Hagar) and FSME_Events Resource (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2013-02-13
48718 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-02-05 10:05 | 2013-02-05 17:36 | 2013-02-05 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO HVAC SYSTEM MALFUNCTION "The facility Technical Support Center (TSC) was rendered non-functional due to a malfunction in the TSC HVAC system. A lugged connection on the air conditioning system control power relay became loose causing a loss of contact between the spade and the relay. Repairs have been completed and the air conditioning has been returned to service. However, the out of service time was greater than 30 minutes, which by the station's reporting procedures, is an 8 hour non-emergency report. The out of service time was from 0935 to 1342 CST. "Compensatory measures per site procedure FNP-0-EIP-6.0 (TSC Setup and Activation) for maintaining emergency assessment, off-site response, and off-site communication capabilities were available. These measures included the conditional relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC to be uninhabitable." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-05
48717 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-02-05 05:45 | 2013-02-05 12:26 | 2013-02-05 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR SCHEDULED MAINTENANCE "Technical Support Center (TSC) ventilation was removed from service on 2/5/13 at 0545 EST to complete scheduled maintenance activities. Without proper ventilation, habitability of the TSC cannot be assured. Work duration is planned to complete today. "In the event TSC activation is required, approved procedures are in place to establish an alternate location, if necessary." The licensee will make courtesy notifications to state and local agencies. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-05
48716 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2013-02-05 08:00 | 2013-02-05 10:57 | 2013-02-05 | OFFSITE NOTIFICATION DUE TO MEDIA/PRESS RELEASE "At 0800 Eastern Standard Time (EST) on 02/05/2013, Progress Energy Florida, Inc., a subsidiary of Duke Energy, announced its plan to permanently shutdown and decommission the Crystal River Unit 3 (CR3) Nuclear Plant. A media release was issued at 0800 EST on 02/05/2013. CR3 Security personnel are stationed at the Emergency Operations Facility/Training Facility located outside the Owner Controlled Area to monitor potential media coverage and public assembly. At this time, Security reports no security issues. No other media releases are planned at this time. This event is being reported under 10 CFR 50.72(b)(2)(xi) for offsite notifications based on the media release of the planned shutdown and decommissioning of CR3. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-05
48715 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2013-02-02 | 2013-02-05 10:20 | 2013-02-05 | RECOVERY OF TWO TRITIUM EXIT SIGNS "On February 2, 2013 an individual called the Wisconsin Emergency Management duty officer to report found radioactive material. The duty officer notified the State Radiological Coordinator who responded to the member of the public. The individual reported that his mother had inadvertently brought home a radioactive source that had come from a donation drop-box. The source was reportedly labeled 'Radioactive Tritium', '4 mCi' and 'Self-Powered Lighting' and dated 8-19-1992. The State Radiological Coordinator ascertained the source was safely stored in the mother's garage in a cardboard box. "State inspectors performed a site visit on February 4, 2013. The radioactive material was actually two 4 Curie tritium sources, Model CPI 300, Serial Numbers 1469 and 1470. Also, the sources were labeled NYS License Number 1406-1611 and parts P/N CAN/AC/4E. "The Radiation Protection Section contacted Self-Powered Lighting and the individual stated that this was an aircraft device and that they would accept the source back. The state inspectors surveyed, wiped, and bagged the sources. Wipes will be analyzed by the Wisconsin State Lab of Hygiene. The sources were retrieved and are currently stored at the State's orphan source storage location. If the wipes confirm no contamination, the sources will be returned to Self-Powered Lighting or an authorized recipient." Wisconsin Report No.: WI130003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2013-02-13
48714 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2013-02-05 08:00 | 2013-02-05 08:19 | 2013-02-05 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed today (February 5, 2013) to the Technical Support Center (TSC) HVAC. The work entails performance of DOP [dioctyplthalate oil smoke test] and Halide testing. This work activity is planned to be performed and completed expeditiously within about 12 hours including establishing and removing the clearance and performing post maintenance testing. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC concurrent with this work activity as long as habitability conditions allow. Additionally, plans are in place to expedite the return of the system should an emergency condition occur. The Emergency Response Organization duty team members will be relocated to alternate location if required by habitability conditions in accordance with emergency implementing procedures. "The licensee notified the NRC Resident Inspector." * * * UPDATE AT 1433 EST ON 2/5/2013 FROM JASON HARNER TO MARK ABRAMOVITZ * * * TSC ventilation has been returned to service. Notified the R1DO (Powell) via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-02-05
48713 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-02-04 13:40 | 2013-02-04 16:46 | 2013-02-04 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE IDENTIFIED ON SEAL INJECTION LINE DRAIN VALVE "Unit is shut down in Mode 4 and in process of cooling down to Mode 5 for a scheduled refueling outage. During a containment walkdown to inspect for boron leakage, personnel identified that Reactor Coolant Pump 'A' seal injection line drain valve has a crack in the socket weld on the upstream side of the valve with active leakage visible as a fine mist. This valve is part of the Reactor Coolant System pressure boundary. TS 3.4.13 requires that the unit be placed in Mode 5 prior to 0140 hours on 2/6/13. All Mode 4 required safety related equipment is operable. "The NRC Resident Inspector has been notified." The last primary leak rate test was conducted at 100% power and determined that there was 0.114 gpm of unidentified leakage. The leak location is inside the containment bio-shield and is not accessible at power. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2013-02-04
48712 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-02-03 12:45 | 2013-02-03 19:40 | 2013-02-03 | INFORMATIONAL NOTIFICATION - SAFETY RELIEF VALVE POTENTIALLY INOPERABLE "On February 3, 2013 at 1245 EST, with the reactor at 100% core thermal power (CTP) safety relief valve, RV-203-3B was declared inoperable as required by station procedural direction due to an observed reduction in first stage pilot valve temperature of greater than 35 degrees F from baseline temperatures. At 1300 EST, reactor power was lowered to approximately 80% CTP at which time the relief valve parameters returned or trended to normal steady state values. Consistent with a reactor power reduction, reactor pressure also lowered from 1035 psig to 1000 psig. This action was taken consistent with industry operating experience related to three stage target rock relief first stage pilot valve leakage. "Currently, station engineering is evaluating the operability of RV-203-3B. Additionally, the current valve performance is being closely monitored by the main control room operating crew. "Station Technical Specification 3.6.D.1 requires that the safety modes of all relief valves (four for [Pilgrim Nuclear Power Station] PNPS) shall be operable during reactor power operating conditions and prior to reactor startup from a Cold Shutdown, or whenever reactor coolant pressure is greater that 104 psig and temperature is greater than 340 degrees F. If this specification is not met, Technical Specification 3.6.D.2 requires that an orderly shutdown shall be initiated and the reactor coolant pressure shall be below 104 psig within 24 hours. "This is an informational notification at this time. PNPS has not initiated an orderly shutdown as of this notification; rather reactor power was lowered to reseat the safety relief pilot valve and there is a high degree of confidence that the high standard of operability will be restored for RV-203-3B and the associated Technical Specification will be exited. If RV-203-3B is not restored to an operable status, a formal and required notification will be completed in accordance with 10 CFR 50.72(b)(2)(i), 'Initiation of any plant shutdown required by the Technical Specifications.' "This event has no impact on the health and safety of the public. "The USNRC Senior Resident Inspector has been informed [by the Licensee]." | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW | [5 empty] | 0 | 2013-02-03
48711 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2013-02-03 12:08 | 2013-02-03 13:20 | 2013-02-03 | OFFSITE NOTIFICATION DUE TO RELEASE OF AMERTAP BALLS "At 1208 CST, Xcel Energy notified the Minnesota State Duty Officer that up to 950 Amertap Balls had been lost from the Prairie Island Nuclear Generating Plant Unit 2 Condenser Tube Cleaning System. Since the Minnesota State Duty Officer for the Division of Emergency Management was notified, this constitutes a 4 hour non-emergency notification per 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. The licensee also notified the local county sheriff's office. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-02-03
48710 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-09-10 | 2013-01-31 15:25 | 2013-01-31 | AGREEMENT STATE REPORT - GENERAL LICENSE DEVICE CONTAINING RADIOACTIVE MATERIAL MISSING The following information was received from the Massachusetts Radiation Control Program via email: "General licensee requested termination of GL registration G0038 on 9/13/12 noting that the registered material (two electron capture detectors [ECD]) had been shipped to another organization. Upon Agency [MA Radiation Control Program] inquiry, the receiving organization confirmed receiving only one ECD. The shipper stated the missing ECD had been physically removed from its original gas chromatograph several years earlier and was last known to be in a small cardboard box that was assumed to have been segregated during a lab cleanup and subsequently included in an overall lab equipment transfer to the receiving organization. Upon further investigation and review, the shipping organization stated on 12/20/12 that the ECD may have been inadvertently dispositioned during the lab cleanup. The ECD is a small metallic cylindrical object approximately less than one inch in diameter and four inches in length. "The Agency considers this event to be closed." The electron capture detector is a Hewlett Packard Model G1223A (Serial Number K0118). The source contained less than 15 mCi Ni-63. MA Event #: 130131. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2013-02-08
48709 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2013-01-30 15:30 | 2013-01-31 14:00 | 2013-01-31 | COMPLETION OF INTEGRATED SAFETY ANALYSIS ACTION PLAN BALANCE OF PLANT MILESTONE "In response to a Notice of Violation [NOV] (VIO 70-1113/2010-003), Global Nuclear Fuel Americas, LLC (GNF-A) committed to perform a review of the existing Integrated Safety Analysis (ISA). An ISA action plan and schedule for performing the ISA review was described in GNF-A's response to the NOV and the third milestone (balance of plant) was scheduled for completion by January 31, 2013. "On January 30, 2013, GNF-A completed the ISA reviews for the balance of plant and has identified an additional 110 items relied on for safety (IROFS) for these areas which were existing safety controls. Implementation of the revised safety basis, IROFS, and application of management measures to the IROFS will be completed by March 31, 2013 per the current ISA action plan schedule. "Because the revised ISA has designated existing safety controls as additional IROFS, GNF-A is making a report of this completion pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours. "There was no event or plant condition that resulted in a degraded safety condition. "Existing balance of plant area safety controls have been identified as IROFS per ISA action plan controls [continue to] perform their intended safety function. "Balance of Plant Area milestone complete per ISA action plan." The licensee will notify the R2 NRC Inspector (Thomas), North Carolina Division of Radiation Protection, and New Hanover County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2013-01-31
48708 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-01-31 02:10 | 2013-01-31 09:28 | 2013-01-31 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) "On January 31, 2013, at approximately 0210 hours [EST], the ability to transfer plant parameter data via the Emergency Response Data System (ERDS) was lost. ERDS capability was restored at 0701 hours [EST]. The cause is under investigation. "In the event of an emergency while ERDS was unavailable, contingency plans were in place to transmit plant parameter data, This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), "The NRC Resident Inspector has been notified." | 72 | 0 | 0 | 62 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-31
48707 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-01-14 | 2013-01-30 08:17 | 2013-01-30 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following was received from the Commonwealth of Pennsylvania via facsimile: "On January 15, 2013, the licensee sent notification via email to the Central Office [PA Bureau of Radiation Protection] about an event that took place on January 14, 2013. This email was received by Central Office [PA Bureau of Radiation Protection] on January 16, 2013. It is reportable within 24 hours under 10CFR30.50(b)(2). "During use of the gauge, the density readings were not as anticipated. The electronic technicians replaced the detector with no change in output. Based on the output readings, the suspicion is that the shutter is closed and cannot be opened. The gauge has been taken out of service and stored securely in their Meadville Warehouse. "The device is identified as: Manufacturer: Berthold Technologies USA, LLC Model: LB 8010 Serial #: 10185 Source Serial #: 1160/10 Isotope: Cs-137 Activity: 20 mCi "The manufacturer is being contacted to investigate and perform repairs if needed. A reactive inspection will be performed by the Department [PA Bureau of Radiation Protection]." Event Report No: PA 130002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-02-07
48706 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-12-22 01:42 | 2013-01-29 16:46 | 2013-01-29 | 60 DAY REPORT - INVALID ACTUATION OF THE AFW SYSTEM "This 60-day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Auxiliary Feedwater (AFW) system. On December 22, 2012 at 0142, with Unit 1 in Mode 4, the 1A AFW pump automatically started due to failure to reset the signal created when the 1B Feedwater Pump was tripped for testing. The 1A feedwater pump was already in the 'tripped' condition when the 1B feedwater pump was tripped, resulting in an auto start signal being generated for the AFW system. Both trains of the AFW had the auto start defeat instated at the time of the testing of the 1B Feedwater pump, blocking the start signal. During subsequent alignment of the AFW for standby readiness, the auto start defeat was removed from the 1A AFW system without resetting the system to remove the signal generated during the 1B Feedwater pump testing, resulting in the actuation of the system. The 1B Feedwater Pump had been reset and was in service therefore the signal associated with the trip of both feedwater pumps was not consistent with the actual plant conditions at the time that the auto start defeat was removed from the 1A AFW system. Following the auto start of the 1A motor driven AFW pump, operators confirmed the 1A AFW train experienced a complete actuation and that the 1A AFW Pump and its associated valves functioned as designed. The pump was subsequently secured and the AFW system was returned to standby readiness. This event was entered into the site specific correction action program for resolution." The NRC Resident Inspector has been informed. The licensee will notify the states of North Carolina and South Carolina. Additionally the licensee will notify York, Gaston, and Mecklenburg County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-01-29
48705 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-01-29 09:00 | 2013-01-29 10:10 | 2013-01-29 | ALERT NOTIFICATION SYSTEM SIRENS WILL BE DISABLED FOR PLANNED MAINTENANCE "A planned outage of all Fort Calhoun Station sirens is to occur at 0900 CST today to replace router power supplies. Based on the planned maintenance, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) will be nonfunctional. Prior notifications and coordination with Local Law Enforcement have been completed with compensatory measures established to support notification of the public in case of an actual emergency during the scheduled maintenance. "The planned maintenance is expected to take three hours with a projected completion time of 1200 CST. Contingencies have been established with the maintenance to back out if required in support of Law Enforcement activities. "This is being reported per 10 CFR 50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability.'" The licensee has notified the NRC Resident Inspector and local authorities. * * * UPDATE FROM LUKE JENSEN TO CHARLES TEAL ON 1/29/13 AT 1314 EST * * * "At 1159 CST, maintenance was completed with all sirens restored to functional status. Local Law Enforcement has been notified and relaxed required compensatory actions. " The licensee will notify the NRC Resident Inspector. Notified R4DO (Walker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-29
48704 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-12-28 15:15 | 2013-01-29 08:16 | 2013-01-29 | AGREEMENT STATE - STUCK SOURCE ON A RADIOGRAPHY CAMERA The following is a summary of a report received via email by the North Carolina Division of Radiation Protection Radioactive Material Branch concerning a source that became stuck while using a radiography camera at a Flowserve facility in Raleigh, NC. On December 28, 2012 at 3:15 pm during radiographic operations with a Co-60 projector model number 741AE s/n A218 containing a Co-60 source, a stuck source equipment incident occurred when the source failed to retract into the shielded position at the permanent radiographic facility located at Flowserve Flow Control Division in Raleigh, NC. The licensee implemented its source retrieval procedures and successfully retrieved the source back into the projector without exposure to the staff involved. Inspection of the guide tube setup identified that the connector that connected the flexible guide tubes was not fully engaged. All radiographers and assistants were briefed on the stuck source equipment incident and all conditions found. The importance of daily checks was stressed along with the need to perform an inspection of your guide tube setup when making any type of change. All radiographers and assistants were involved in the inspection of the two flexible guide tubes and comparison to our other guide tubes and nothing was identified as a potential problem. The incident was monitored by the RSO at each stage from beginning to end to ensure that all possible safety and security concerns were adequately addressed. It is the determination of the RSO that at no time was the safety of the employees, radiographers or the public at risk as a result of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-02-06
48703 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-28 16:20 | 2013-01-28 17:38 | 2013-01-28 | FIRE IN STORAGE BUILDING IN OWNER CONTROLLED AREA "A fire was reported within the Owner Controlled Area but outside the Protected Area. The fire was located in an air conditioning unit for a small building. The fire was extinguished within 15 minutes by the offsite fire department. The plant did not sustain any damage." The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-01-28
48702 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2013-01-15 | 2013-01-28 16:32 | 2013-01-28 | AGREEMENT STATE REPORT - ASSISTANT RADIOGRAPHER EXCEEDED ANNUAL EXPOSURE LIMIT The following was received from the state of Oklahoma via email: "On January 15 [the Oklahoma Department of Environmental Quality] was informed by the RSO for AIT [Advanced Inspection Technologies] that one of their radiographer assistants had exceeded the 5 R limit for exposure during calendar year 2012. This individual consistently had higher exposures than other employees at AIT and had failed to turn in his badge at the end of April, 2012, instead continuing to wear it through May. This resulted in a reading of 1075 mR on the April report, but this also included the month of May. His May badge was not used and showed a dose of only 19 mR when processed. This situation was discussed with the RSO during their routine inspection in June. At the end of October the assistant again failed to turn in his badge and wore it through November. At the beginning of October, his cumulative dose for the year was 4580 mR. The badge was sent in for processing at the end of November and Landauer contacted the licensee on January 15, 2013 to inform him that the exposure on the October badge was 1282 mR. This put his 2012 total at 5864 (the unused November badge showed 2 mR). The RSO submitted a written report of this incident to us [State of Oklahoma] on Jan. 22, 2013. "On January 23, [the Oklahoma Department of Environmental Quality] spoke with the radiographer who the assistant radiographer worked with most often. The radiographer [was asked] if there had been any incidents which might have caused the high doses the assistant radiographer had received. The radiographer replied that there had been no 'major' incidents that he was aware of. [The radiographer was] then asked about any minor incidents and the radiographer replied that 'two or three times' they had retracted the source into the exposure device, however when they approached the device, their rate alarms went off (these are required to be set to alarm at a dose rate of 500 mR/hr). They then cranked the source out again and again tried to retract it, which was successful. The fact that they got close enough to the source to encounter a 500 mR/hr radiation field indicates that they were not performing the post-exposure surveys required by 10 CFR 34.49(b). The radiographer [was then asked] if he had reported these incidents to the RSO to which he replied that in all cases he had checked the direct-reading dosimeters of he and the assistant radiographer's and found that they indicated a dose of 10 mR or less. Therefore, he decided not to report them. He also stated that the need to keep up with the work load played a role in his decision. The radiographer could not remember specific dates or locations where this had occurred. On January 28, 2013, [the Oklahoma Department of Environmental Quality] spoke with the RSO again and informed him of the conversation with the radiographer. The RSO professed to have no knowledge of the 'incidents' described by the radiographer. The RSO [was requested] to perform another investigation into this incident, specifically focusing on whether this was an isolated incident or if this was representative of the overall culture at the facility, and that enforcement action [would be deferred] pending the results of his investigation. The RSO agreed to this stipulation. It should be noted that AIT is, in general, one of [the] better licensees when it comes to compliance with [the Oklahoma Department of Environmental Quality] regulations. Investigation into this incident is continuing. As the over-exposure did not occur within a period of 24 hours as stipulated by 10 CFR 20.2202(b)(1), [the Oklahoma Department of Environmental Quality] is treating this as a reportable event under 10 CFR 20.2203(a)(2)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2013-02-05
48701 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2013-01-24 23:38 | 2013-01-25 12:38 | 2013-02-06 | RADIAC CALIBRATION SOURCE WINDOW INTERLOCK FAILURE "At 23:38 hours on January 24, 2013, while performing daily source checks on portable radiation meters, the Shepherd Model 78-2 Calibrator (Serial # 9047) failed a pre-operational source interlock check. The 130 mCi /130 Ci Cs-137 sources were able to be raised while the shield door was not fully shut. "This is reportable under 10 CFR 70.50(b)(2) since the interlock is required by license to prevent the accidental raising of the source with the door open. There is no equipment considered to be redundant to the interlock. The cause of the failure has not been determined at this time. "No personnel were exposed to the sources. Sources were returned to the shielded position, the calibrator was locked and removed from service. A survey of the calibrator after securing the sources showed dose rates within expected ranges. The affected calibrator is not part of any installed plant equipment and has no impact on plant operation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM STEVE PRUSSMAN TO CHARLES TEAL ON 2/6/13 AT 1105 EST * * * The licensee has changed the reporting criteria to 10 CFR 30.50(b)(2). The NRC Resident Inspector has been informed. Notified R1DO (Powell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFETY EQUIPMENT FAILURE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 30.50(b)(2) |  |  |  | 0 | 2013-01-25
48700 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2013-01-22 06:00 | 2013-01-25 11:02 | 2013-01-25 | AGREEMENT STATE REPORT - PROCESS METER SOURCE SUBJECTED TO INTENSE FIRE AT WELL SITE The following information was obtained from the State of Utah via facsimile: "The Utah Division of Radiation Control was notified at 3:40 p.m. MST on January 22, 2013 of a fire at a natural gas well. Notification was provided by the licensee's Radiation Safety Officer. This incident report is the initial notification to the NRC Operations Center. On January 22, 2013, a representative of Halliburton Energy Services, Inc. radiation safety called the Division to report a fire involving a natural gas well. The fire erupted about 6:00 a.m. that morning. The licensee was using a truck with a slurry densimeter (Sealed Source Device Registry Number NR-340-D-101-G) in-line after a chicksan on a down-hole pump. The truck was parked approximately 40 feet from the blowout preventer (well head). An 8.8 milliCurie cesium-137 sealed source (Gammatron GT-GHP) is contained within the slurry densimeter. As of Thursday afternoon, January 24, 2013, the fire continued to occasionally flare, but a Halliburton representative was able to gain brief access to the slurry densimeter. He reported to a Department of Environmental Quality representative (on-scene presence) that the sealed source is not leaking and the device containment housing was still intact. Fire control operations continue and efforts to drag the licensee's truck away from the drill rig may occur on Friday, January 25, 2013. Utah Report No: UT130002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2013-02-04
48699 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2013-01-16 14:00 | 2013-01-25 11:01 | 2013-01-25 | AGREEMENT STATE REPORT - DOSE DIFFERENT FROM PRESCRIBED USING YTTRIUM-90 THERASPHERE TREATMENT The following event report was received from the State of Utah Division of Radiation Control via facsimile: "The Utah Division of Radiation Control was notified at 11:45 a.m. MST on Thursday, January 17, 2013 of a medical event associated with a radioembolization brachytherapy treatment of liver cancer. Notification was provided by the licensee's Radiation Safety Officer. This incident report is the initial notification to the NRC Operations Center. "The licensee's radiation safety officer reported to the Division that the treatment plan prescribed 1.33 GBq of yttrium-90 for treatment of liver cancer. The patient received 0.798 GBq of yttrium associated with the TheraSphere product. After the administration of the dosage, a nuclear medicine technologist determined that the total prescribed dosage was not delivered to the patient, as radioactive material was found to remain in the dosage vial and the administration apparatus. The licensee is working with the manufacturer of the treatment delivery system to determine the cause of the medical event." Utah Event Report ID : UT130001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2013-02-04
48698 | 0 | PEACH BOTTOM |  |  |  |  | 2013-01-24 11:00 | 2013-01-25 09:43 | 2013-01-25 | NON-COMPLIANCE WITH STORAGE CASK TECHNICAL SPECIFICATION LIMITS "This report is being submitted pursuant to Transnuclear (TN)-68 Technical Specification (TS) Section 2.2, which requires reporting of non-compliances with the Functional and Operational limits of TS Section 2.1.1. "A recent review of historical ISFSI [Independent Spent Fuel Storage Installation] fuel characterization data found that in the ISFSI 2001 campaign, a total of four Unit 3 fuel assemblies were loaded into four dry cask storage casks (i.e., one assembly per cask) having been cooled for 9.8 years, with a decay heat value of 0.201 kW each, which is well below the 0.312 kW limit (TN-68 TS 2.1.1.). Therefore, it is not expected that there were any actual thermal related concerns with the fuel or the associated cask components. However, this was contrary to the Functional and Operational limits of TS Section 2.1.1 , Table 2.1.1-1, which requires the assemblies to have been cooled for 10 years. The decay heat of the assemblies has continued to decrease since their initial loading in 2001 and all assemblies currently meet the TS 2.2.1 limits. The fuel assemblies are in a safe condition as required by TS 2.2.1. "These casks were loaded under TN-68 Certificate of Compliance (C of C) Amendment 0 (Certificate 1027). This notification is required pursuant to TN-68 TS Section 2.2.2. This issue has been entered into the Corrective Action Program. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | PA | ISF | [5 empty] | 0 | 2013-01-25
48697 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2013-01-21 | 2013-01-24 16:07 | 2013-01-24 | AGREEMENT STATE REPORT - LOST I-125 SEED On January 21, 2013, a patient was undergoing a radioactive procedure using a 275 microCurie I-125 seed as well as a resection procedure for a breast tumor. The seed was implanted on the surface of the skin and taped into place. During post-surgical clean-up after the resection procedure was performed, the iodine seed was lost. It is believed it was removed with the tape and thrown away as medical waste. After discovery of the loss, the patient, her car, her home and her clothing were surveyed with negative results. The surgical suite and all bedding and gowns used were surveyed with negative results. The surgical waste had already been removed by the time the suite was surveyed. The licensee believes the seed is in the local landfill and has considered it to be lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2013-02-01
48696 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2013-01-23 15:16 | 2013-01-23 22:03 | 2013-01-23 | CONCURRENT LOSS OF HIGH PRESSURE REACTOR MAKEUP SYSTEMS CAPABILITY "On 1/23/2013 at 1516 [EST], Nine Mile Point 2 (NMP2) had a failure of a Reactor Building General Area temperature trip unit occur resulting in the closure of an isolation valve on the Reactor Core Isolation Cooling (RCIC) system steam supply line. Concurrent with this failure, the High Pressure Core Spray (HPCS) system was inoperable for planned surveillance testing. With both the RCIC and HPCS systems inoperable, NMP2 entered a Technical Specification Required Action to be in Mode 3 within 12 hours. At 1550, the HPCS system was restored to OPERABLE. Based on the concurrent loss of the high pressure reactor makeup capability of these two systems, it was determined that the condition is reportable under section 50.72(b)(3)(v) as the following safety functions were impacted: (A) Shutdown the reactor and maintain it in a safe shutdown condition; and (D) Mitigate the consequences of an accident. "NMP2 remains in a stable condition at rated power. The offsite grid is stable with no restrictions or warnings in effect." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-01-23
48695 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2013-01-22 15:30 | 2013-01-23 15:00 | 2013-01-23 | UNANALYZED CONDITION - BASED ON ONGOING INTEGRATED ANALYSIS REVIEW "During the ongoing Integrated Analysis (ISA) review, it was identified that a fire in labs adjacent to the Dry Scrap Recovery (DSR) area could impact the DSR. The existing masonry wall between DSR and the lab has several openings that are closed with plywood. With plywood in place, unicones (uranium storage containers) stored against the wall in DSR would not meet performance criteria for the accident sequence of a fire in the adjacent lab. The uranium containers have been removed from the storage area until the wall is upgraded to meet performance requirements. Other processes remain operational. A review has begun which will provide additional corrective actions, if required, and extent of condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2013-01-23
48694 | 0 | NASA AMES RESEARCH CENTER |  |  |  |  | 2013-01-16 12:07 | 2013-01-23 13:10 | 2013-01-23 | LEAKING NI-63 SOURCE The following was excerpted from email received from NASA Ames: "The source in question is a 5 mCi solid Ni-63 beta foil source located inside a Valco electron capture detector that was previously used for gas chromatograph. The leaking source in question was not in service at the time the contamination was found. The source was in storage awaiting disposal to a licensed facility." "The radiation safety officer identified elevated contamination results for the source mentioned above during his review of the semi-annual sealed source inventory and leak test report which was conducted by the former health physics contractor in December 2012. All contamination levels were well below the NRC contamination threshold of .005 micro Curie at that time. The RSO directed the former health physics contractor to take a follow-up survey to verify the counts begin detected were actually Ni-63, bag the source, perform a survey of the immediate area where the source was being stored awaiting disposal, and prepare a report documenting the follow-up report and isotope identification prior to his termination with the end of his company's contract on December 31, 2012. "On January 15, 2013, the new contract Health Physicist for NASA Ames Research Center, conducted a follow-up survey and leak test for the 5 mCi Ni-63 source. On January 16 the RSO confirmed that approximately 0.162 micro Curie (~36,000 dpm) beta contamination was distributed on the exterior surface of the electron capture detector. This value is in excess of the allowable leakage of 0.005 micro Curie (11,100 dpm) of contamination. The cause of the leaking source is not certain at this time. The source is approximately 23 years old so its possible age played a factor. The source has been in storage for a researcher who no longer had funding to continue using them in his research. It is stored in the RSO's radioactive materials storage facility for the last 6 years. During storage, the leak tests for the source continued to be conducted and all semi-annual leak tests never revealed any leaking contamination from the internal source. "No persons are expected to have received any dose or exposure to radioactive materials as a result of this event. Ni-63 is a weak beta emitter and not capable of penetrating the dead layer of skin if in contact with the skin and is thus not an external radiation hazard. A general area contamination survey was also conducted in the immediate vicinity of where the source was stored. Contamination levels were all found to be near background levels in all locations confirming that there is no contamination event for the storage facility. The device has been in storage in a locked cabinet with access only to the RSO and Health Physics contractor during the period in which the leaking occurred so this makes the possibility of inadvertent personnel contamination remote. Required procedure for performing sealed source leak tests is to always wear disposable impermeable gloves. This would have prevented any personnel contamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2013-01-23
48693 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-01-22 | 2013-01-23 12:31 | 2013-01-25 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was provided by the State of Texas via email: "On January 22, 2013, the Agency [State of Texas] was notified by the licensee's Radiation Safety Officer (RSO) that a radiography crew performing radiography operations at a field location experienced a source disconnect. The crew was using an INC IR 100 exposure device containing a iridium - 192 source. The crew had performed nine or ten exposures and was moving the camera to the next location when they discovered the source was still in the guide tube. A source recovery team was sent to the location and the source was returned to the exposure device and locked in the fully shielded position. The RSO did not know how the crew discovered the source was still in the guide tube. The RSO stated that the self reading dosimeter of the radiographer who moved the exposure device was reading off scale and that his personnel dosimeter was being sent to the dosimetry processor for immediate processing. The RSO stated that the radiographer did not perform a post exposure radiation survey prior to moving the camera and that the radiographer stated that their alarming dosimeter did not alarm. The RSO stated that he did not know how long or how close the radiographer was to the source while they were moving the exposure device. The RSO stated that the radiographer has been removed from all duties involving exposure to radiation. The RSO stated that no other individual received an exposure of concern. The RSO stated that the device would be returned to the manufacturer for inspection. The licensee is conducting an investigation into the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-9035 * * * UPDATE ON 1/25/2013 AT 1305 EST FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via fax: "On January 25, 2013, the RSO stated the dosimetry processor reported the dose received by the individual who relocated the exposure device was 791 millirem DDE [deep dose equivalent]. The RSO stated that their investigation into the event is ongoing. Additional information will be provided as it is received in accordance with SA - 300." Notified the R4DO (Okeefe) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-01-31
48692 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2013-01-23 06:22 | 2013-01-23 11:00 | 2013-01-23 | AGREEMENT STATE REPORT - VEHICLE ACCIDENT DURING TRANSPORT OF RADIOPHARMACEUTICALS The following preliminary information was provided by the State of Kansas via fax: "Rollover accident involving transport of radiopharmaceuticals. Initial report received at 06:22 A.M. [CST]. Condition of driver unknown. Accident location: 2.5 miles north of US 69 and 47 junction, close to Arma, KS. Preliminary information indicates shipment was Tc-99m. Max contact 0.04 mR/h, no damage to packages. Personnel from St. Francis are on site. Driver was taken to the hospital." Kansas Item Number: KS130001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2013-01-31
48691 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2013-01-21 | 2013-01-22 13:10 | 2013-01-22 | AGREEMENT STATE REPORT- PHARMACEUTICAL DISTRIBUTION FAILED QUALITY CONTROL TESTING The following information was received by email: "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation, and is basically all that is known by the [Arizona Radiation Regulatory] Agency Staff at this time. "At approximately 0830 [MST on 1/22/13], the Agency was notified by PCI [Patient Care Infusion], the Licensee, that yesterday [1/21/13] they distributed a pharmaceutical that failed the quality control testing. Several licensees reported to them they were receiving improper data from patients injected with the material. A total of 9 licensees were shipped the radiopharmaceutical and the licensee estimates as many as 13 patients may have received the deficient material. Additionally, a like number were scheduled to receive the material but did not receive the material. "The Licensee is preparing the 30 day written report of this event. "The Agency continues to investigate this event." Arizona First Notice: 13-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2013-01-30
48690 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-11-23 04:35 | 2013-01-22 12:45 | 2013-01-22 | PRIMARY CONTAINMENT ISOLATION ACTUATION SIGNAL DURING SURVEILLANCE "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting multiple Main Steam Isolation Valves (MSIVs). "On November 23, 2012 at 0435 Central Standard Time, during performance of Surveillance Instruction 1-SI-3.3.1.A, ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping, as the Residual Heat Removal Loop II Shutdown Cooling was being placed in service, Group 1, Division II Primary Containment Isolation System (PCIS) logic groups A2 and B2 actuated resulting in an unanticipated Division II, Group 1 Complete Isolation and subsequent Inboard MSIV closure. The Outboard MSIVs had been previously tagged closed. "Plant conditions which initiate Group 1 actuations are Reactor Vessel Low-Low-Low Water Level, Main Steamline Break, and Low Main Steamline Pressure at the Inlet to the Turbine. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The affected equipment responded as designed. "This condition was the result of the reactor vessel water level being within two inches of the reactor head vent when Shutdown Cooling was placed into service, causing pressure perturbations. When these perturbations occurred, they gave an indication of low water level, causing the isolation and MSIV closure. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the [Browns Ferry Nuclear Plant] Corrective Action Program as Problem Evaluation Report 646607. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-01-22
48689 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2013-01-22 01:13 | 2013-01-22 08:38 | 2013-01-22 | SECONDARY CONTAINMENT PRESSURE POSITIVE FOR 12 SECONDS "On 01/22/2013 at 00:30 Reactor building HVAC tripped due to low outside air temperature and Standby Gas Treatment system was manually started and maintained Reactor Building differential pressure negative. At 01:13 secondary containment pressure went positive during restart of the Center Reactor Building HVAC Train. This is a loss of secondary containment function. In a 12 second time span secondary containment pressure went above 0 inches WC [Water Column] to +0.17 inches WC and then decreased to < 0 inches WC remaining stable during the Reactor Building HVAC restart. The Center Reactor Building HVAC Exhaust Fan Discharge Damper opened after the Supply Fan discharge damper; this condition would produce the indications noted. "The System was returned to normal with two Reactor Building HVAC trains running and the Standby Gas Treatment System shutdown and in standby. Reactor building pressure is stable with differential pressure negative < - 0.30 inches WC. "The loss of Secondary Containment function is reportable under 10 CFR 50.72 (b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material." The licensee notified the NRC Resident Inspector. | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2013-01-22
48688 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-01-22 03:32 | 2013-01-22 06:57 | 2013-01-22 | AUTOMATIC REACTOR PROTECTION SYSTEM ACTUATION "On January 22, 2013, at approximately 0332 hours [EDT], an automatic Reactor Protection System (RPS) actuation occurred at the Perry Nuclear Power Plant, Unit 1. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the reactor core and the plant is currently stable in Mode 3 (Hot Shutdown) with reactor pressure and level being maintained in the normal shutdown range. "The RPS actuation was initiated by a low reactor water level (Level 3 - 178") signal. In response to the RPS actuation and subsequent reactor Level 2 (130") signal, the High Pressure Core Spray (HPCS) system and Reactor Core Isolation Cooling (RCIC) system both actuated and injected to maintain reactor coolant level. The reactor level is currently being maintained in its normal band by the feedwater system and decay heat is being removed by [turbine bypass valves to] the condenser (both HPCS and RCIC have been returned to standby). The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available, if needed. The Containment Isolation Valves (responded to the Level 2 and 3) isolation signals as designed. "The cause of the RPS actuation is under investigation. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2013-01-22
48687 | 0 | WATERFORD | 3 |  |  | [3] CE | 2013-01-21 15:51 | 2013-01-21 19:55 | 2013-03-07 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 15:51 CST, Waterford 3 experienced an uncomplicated automatic reactor trip from 84.5% reactor power. The actuations of the Reactor Protection System (RPS) and the Emergency Feedwater Actuation System (EFAS) resulted from Steam Generator #1 Low Level, which is at a nominal 27.4% narrow range setpoint. Safety systems responded as expected. "All three (3) Emergency Feedwater Pumps started and injected into Steam Generator #1. Auxiliary Feedwater pump has been started, feeding both Steam Generators (#1 and #2) at levels above the EFAS low level setpoint. All control rods inserted by the automatic RPS actuation. Electrical power is being supplied from normal off-site power and condenser vacuum is available for Steam Generator heat removal via the Steam Dump Bypass Control system. There are no safety systems out of service or inoperable, nor any safety system TS [Technical Specification] LCO [Limiting Condition for Operation] actions entered. "The cause of the Steam Generator #1 Low Level condition, and associated Reactor Trip, is under investigation. This event occurred during the initial power escalation from refuel outage RF18, after attempting to place C Heater Drain Pump (HDP), the first of three, into service. After starting, C HDP tripped for a reason not yet verified. Subsequently, based on initial Control Room operator observations, the Steam Generator #1 Main Feedwater control valve position was observed to be at 10-20% open, but with an open position demand signal of 100%. Main Feedwater response to the reactor trip (Reactor Trip Override) was as expected." The NRC Resident Inspector has been informed. * * * UPDATE FROM WILLIAM HARDIN TO PETE SNYDER AT 1645 EST ON 3/7/13 * * * The original reactor power level stated in the report should be 91% in lieu of 84.5%. This information has been changed in the event heading. The licensee notified the NRC Resident Inspector. Notified R4DO (Werner). | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-01-21
48686 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-01-21 13:00 | 2013-01-21 11:32 | 2013-01-21 | LOSS OF RESPONSE CAPABILITY - TECHNICAL SUPPORT CENTER AH-17 SUPPLY FAN NON-FUNCTIONAL FOR PREPLANNED MAINTENANCE "This is a non-emergency notification. At approximately 1300 [EST] on January 21, 2013 preplanned maintenance will be performed which will remove AH-17, one of three Technical Support Center (TSC) Supply Fans from service. The scope of the maintenance is to replace and align the fan's sheave with a contingency to replace its drive belt. This maintenance is expected to be performed and completed within approximately 7 hours. If an emergency condition should occur, the ventilation system will be restored, but potentially not within the time required for activation of the TSC. In addition, the ventilation system will be restored, but potentially not within the time required for activation of the TSC. In addition, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location in the event the TSC is not habitable. The on-call TSC Site Emergency Coordinator and Emergency Response Manager have been notified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-21
48685 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-01-20 20:50 | 2013-01-20 23:30 | 2013-01-20 | TECHNICAL SPECIFICATION (TS) REQUIRED SHUTDOWN - SAFETY RELIEF VALVE DECLARED INOPERABLE "On Sunday, January 20, 2013, at 2050 hours, with the reactor at 100% core thermal power, the station entered a 24-hour action statement to initiate a controlled shutdown and be less than 104 psig reactor pressure due to suspected leakage across the first stage pilot of safety relief valve (SRV) RV-203-3B and subsequent declaration of the SRV inoperable due to criteria specified in Pilgrim plant procedure 2.2.23. "As background, the pressure relief system includes four (4) SRVs and two (2) spring safety valves (SSVs). The SRVs discharge through their individual discharge piping, terminating below the minimum suppression pool (torus) water level. The four SRVs are installed on the main steam piping in containment between the reactor pressure vessel and the flow restrictors. "While at full power, indication of a steam leak across the first stage pilot of RV-203-3B was determined in accordance with criteria specified in procedure 2.2.23. Specifically, the SRV is inoperable if the pilot stage thermocouple temperature is 35 degrees F below its baseline temperature (with a lower decrease at the 2nd stage thermocouple) and cannot be explained by a corresponding downpower. The safety relief valve was subsequently declared inoperable and the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.6.D was entered. Due to the valve being declared inoperable the station is required to be shutdown and reactor coolant pressure below 104 psig within 24 hours per TS 3.6.D.2. "Currently a reactor shutdown is in progress to initiate safety relief valve repairs. "This event has no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2013-01-20
48684 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-01-20 16:41 | 2013-01-20 20:50 | 2013-01-20 | TECHNICAL SUPPORT CENTER VENTILATION DISABLED "At 1641 on January 20, 2013, the Technical Support Center (TSC) became non-functional when the ventilation system was secured and disabled by a fire alarm. Investigation of the alarm condition determined the fire alarm was not valid and would not reset. At 1830, Technical Support Center ventilation was restored by disabling the deficient fire alarm by using guidance in alarm response procedure APP-FP-KBLDG. The Technical Support Center was restored to functional status at 1830 on January 20, 2013. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this condition affected an emergency response facility for greater than facility activation time (one hour). "The NRC Resident Inspector has been informed" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-20
48683 | 0 | TEXAS DEPARTMENT OF STATE HEALTH |  |  |  |  | 2013-01-19 | 2013-01-19 10:11 | 2013-01-22 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received from the State of Texas via email. "On January 17, 2013, the licensee notified the Agency [Texas Department of State Health Services] that while performing preparations for maintenance the shutter on a Ronan model SH1 nuclear gauge was found stuck in the open position. The gauge contains 1,000 millicuries of cesium-137. The licensee stated that open is the normal operating position for the shutter and the gauge does not pose an exposure risk to any individual. The licensee stated that a service provider will remove the gauge and the manufacturer will be contacted to repair the gauge. Additional information will be provided as it is received in accordance with [Reporting Materials Events] SA-300." Texas incident # I-9033. * * * UPDATE FROM TUCKER TO KLCO ON 1/22/13 AT 1615 EST * * * The following information was received by email: "On January 22, 2013, the Agency was informed by the service provider that on January 14, 2013, they were able to get the shutter to close. The shutter is operating normally. The licensee has contacted the manufacturer to perform preventive maintenance on the gauge. Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (OKeefe) and FSME Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-01-28
48682 | 0 | NORTH CAROLINA RADIATION PROTECTION |  |  |  |  | 2012-03-05 | 2013-01-18 15:34 | 2013-01-18 | AGREEMENT STATE REPORT - POTENTIAL EXPOSURE TO AN EMBRYO/FETUS The following was received from the State of North Carolina via email: "Vidant Medical Center, NC Radioactive Materials License 1457-1, has reported a possible dose to an embryo/fetus in excess of 5 rem (15A NCAC 11.0365(a)) and has made notification to the NC Radiation Protection Section within 24 hours of discovery of the event as required by 15A NCAC 11.0365(c)." "The possible event is under investigation at this time and more information will be provided as it is discovered. The RSO, made the telephone notification at approximately 14:30 EST today, of the event discovered this morning. "PRELIMINARY/TENTATIVE DETAILS (to be fully investigated): A female with a child reported for renal scan at Vidant Medical Center recently and complained that she thought that radiation she received from hypothyroid treatment in the Spring of last year (2012) had adversely affected her child. Attending Nuclear Medicine Tech notified the Nuclear Medicine supervisor, and the female patient's chart was reviewed and indicated that she had had approximately 19 mCi radioiodine administered in March 2012. Pregnancy test was reported as negative at time of administration and the woman answered that she had not had sex within ten (10) days prior to therapy. However, based upon the reported age of the child, it is possible that the female may have been newly pregnant at the time of administration." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2013-01-28
48681 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2013-01-18 12:40 | 2013-01-18 15:37 | 2013-01-18 | PANS SYSTEM FALSE ACTIVATION OF 58 SIRENS There was a false activation signal applied for 3 seconds to site emergency sirens. The licensee notified the State of Minnesota and local government agencies. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-01-18
48680 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-12-22 23:20 | 2013-01-17 17:00 | 2013-01-17 | MINOR INCIDENTAL URANIUM HEXAFLUORIDE RELEASE "Note this is a late report (1/17/2013). "During December 2012, the C-360 Toll Transfer and Sample building experienced three incidents where the Laboratory Process Gas Leak Detection (PGLD) system was actuated. No visible smoke was ever seen. Subsequent bioassay samples of personnel in the area confirmed that minor exposures did occur, although no work restrictions were required. The exposures confirm that the PGLD actuations were due to actual minor incidental uranium hexafluoride releases. Investigation and testing found that the first two incidents were caused by a small pinhole leak in instrument tubing and the third incident was caused by slight leakage around the stem of a small instrument valve. These three events were evaluated for reportability at the time they occurred, but it was determined they did not meet our reporting criteria. However, after further evaluation and discussion with NRC staff, USEC is conservatively reporting the incidents. "The actuations occurred on December 22, 23, and 29, 2012. Upon each actuation, the system automatically closed the appropriate valves as designed. Response to each leak consisted of atmospheric sampling for HF and radiological swipes per procedure along with precautionary bioassay samples. The atmospheric sampling and radiological swipes on the first release were negative and the system was returned to service. The second incident the next day was similar to the first and again the immediate samples were negative. Bioassay results were then obtained from the previous night and showed a detectable exposure. With confirmation of a small leak, helium leak detection was utilized to find the small pinhole leak. The third incident was due to slight leakage around a valve stem that was discovered by soap testing the valve and evidence of some visible oxides on the valve stem. "These types of releases are incidental and do not have the potential for impact on the health and safety of personnel or the public. "These incidents are being conservatively reported as a 24-hour event based on SAR 6.9 Table 1, J.2 as an Unplanned Actuation of a Q Safety System." An automatic or manual actuation of a Q safety system that results from an event or condition that has the potential for significant impact on the health or safety of personnel. Events having the potential for significant Impact are those events where actual plant conditions existed that the system was designed to protect against." "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2013-01-17
48679 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-17 14:25 | 2013-01-17 16:27 | 2013-01-17 | FIRE IN SWITCHYARD CIRCUIT BREAKER "Failure of Unit 2 McGuire switchyard Power Circuit Breaker (PCB) 55 resulted in a fire and damage to the PCB. PCB 55 and the McGuire switchyard are located outside of the protected area. The fire was confined to the PCB only and extinguished by offsite municipal fire department in 33 minutes. This breaker affects the offsite transmission supply to Rock Springs and South Mountain. The Unit 2 plant breakers connecting offsite to onsite power were not affected and remain in service. The failure of PCB 55 did not damage any plant equipment nor did this event cause a plant transient. An estimated 50 gallons of oil has spilled from the damaged equipment which is contained to the immediate area. The spilled oil cleanup efforts are underway at this time." The NRC Resident Inspector will be informed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-01-17
48678 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-01-15 | 2013-01-16 16:46 | 2013-01-16 | AGREEMENT STATE REPORT - MISPLACEMENT OF BRACHYTHERAPY SOURCE DURING MEDICAL TREATMENT The following information was provided by the State of Ohio: "The Ohio Department of Health Bureau of Radiation Protection was notified by the licensee RSO of a potential medical event. A patient was planned for a vaginal cylinder (HDR) procedure. Approved plan prescribed 4 Gy to target organ (vaginal canal) and 4.61 Gy to rectum. On the first of three fractions, the cylinder was inserted by the Authorized User (AU) in the rectum instead of the vaginal canal. The AU reviewed the film and approved the position for treatment. The physicist determined that the rectum received approximately 6.1 Gy (132% of the prescribed dose). At the time of this report it appears that the intended treatment target received less than 2 Gy (less than 50% of prescribed dose)." The device used is a remote afterloader HDR manufactured by Nucletron, Model Microselectron S/N 31472, containing a single sealed source of 4.15 Ci Ir-192. The cause is identified as human error. Item Number: OH130001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2013-01-24
48677 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2013-01-16 12:45 | 2013-01-16 13:43 | 2013-01-16 | SECURITY REPORT INVOLVING MISDELIVERED SHIPMENT OF SNM "Loss of a shipment of Special Nuclear Material. A shipment of Special Nuclear Material was to be delivered to Perry Nuclear Power Plant in Perry, Ohio. It has been reported that the shipment was delivered to FirstSolar in Perrysburg, Ohio instead." The shipment has been recovered by the common carrier. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1751 EST ON 01/16/13 FROM RICHARD O'CONNOR TO S. SANDIN * * * "NUCLEAR INSTRUMENTATION SHIPMENT RECOVERED AND ACCOUNTED FOR "EN Notification 48677 reported that a shipment of Special Nuclear Material (SNM) to the Perry Nuclear Power Plant in North Perry, Ohio was delivered to FirstSolar in Perrysburg, Ohio. This event was reported in accordance with 10 CFR 73.71(a)(1). The reporting requirements of 10 CFR 20.2201(a)(1) and 10 CFR 74.11(a) also apply. "The SNM consisted of 34 new, unirradiated local power range monitor (LPRM) in-core detectors. Site personnel identified the shipping carrier and verified the package location. The package was delivered to FirstSolar and remained there for approximately 20 minutes before the shipping carrier returned and picked up the package for transport back to the manufacturer's facility. At approximately 1620 hours, the package arrived at the manufacturer's facility. The package was offloaded and inspected. The security tamper seals were found to be broken. An inventory of the package was subsequently performed. All LPRM detectors were accounted for at 1704 hours. "NRC Resident Inspector has been notified." Notified R3DO (Bloomer) and NMSS (Hsia). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST SNM OR SPENT FUEL SHIPMENT | LOST/STOLEN LNM>1000X | LOST/STOLEN SNM |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(a)(1) | 20.2201(a)(1)(i) | 74.11(a) |  | 1 | 2013-01-24
48676 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-01-15 21:12 | 2013-01-16 04:43 | 2013-01-16 | LOSS OF A 4160 VOLT BUS WHILE PERFORMING TESTING "On January 15, 2013 at 2112 EST while performing testing associated with the remote shutdown system at the James A. FitzPatrick Nuclear Power Plant, an unexpected loss of the 10600 bus 'B' division AC vital power system occurred. This loss of power to the 10600 bus resulted in an automatic actuation of the 'B' and 'D' Emergency Diesel Generators. The diesel generators started as expected, but did not close in to energize the 10600 Bus due to the configuration at the time of the event. As a result of the loss of the 10600 bus, the 'B' Reactor Protection System (RPS) lost power resulting in a half scram signal and a Group II Primary Containment Isolation System (PCIS) actuation. This actuation resulted in closing containment isolation valves in multiple systems and isolating Reactor Water Clean-Up (RWCU). Based on these system actuations, the event is reportable under criterion 10 CFR 50.72(b)(3)(iv). "Power to the 10600 Bus was restored January 16, 2013 at 0400 EST, and the half scram and isolation signals have been reset. Additional actions to restore systems to a normal operating line-up are on-going. Investigation into the cause of the unexpected power loss is on-going and will be addressed through the corrective action program. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2013-01-16
48675 | 0 | DEFENSE LOGISTICS AGENCY |  |  |  |  | 2013-01-14 | 2013-01-15 17:54 | 2013-01-15 | POTENTIAL THEFT OF PRESSURE INDICATOR CONTAINING SR-90 SOURCE "An item was processed for shipment [from Norfolk, VA] to the manufacturer for repair and was delivered to a contracted carrier on 9 January 2013. The carrier notified the government representative on Monday, 14 January 2013, reporting that the subject material was involved in a police investigation for a potential theft in Riverside, CA. The government contractor reported the loss of freight to the depot who reported the incident to the DLA [Defense Logistics Agency] Distribution Radiation Safety Officer at 1503 hrs on 15 January 2013. "DLA Distribution [Norfolk, VA] will work with all parties to obtain further information related to this incident and update the NRC as information becomes available." The shipped item is a pressure indicator [NSN#6620-01-125-8904] containing a Sr-90 source (500 microCuries). DLA Incident Number: 2013-DLA-001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2013-01-23
48674 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-01-14 12:15 | 2013-01-15 12:45 | 2013-01-15 | AGREEMENT STATE REPORT- SOURCE STUCK IN A TRANSFER TUBE The following information was received by email: "On Monday, January 14, 2013, the [State of Tennessee] Division of Radiological Health received a report from Methodist University Hospital regarding a stuck HDR source. A patient was to be treated with the high dose rate remote afterloader (Nucletron model 105.999) on January 14th. The radiation source became stuck in the applicator/transfer tube at the beginning of treatment before reaching the patient. The physicists and physician followed the policy and procedure for removal of the source and tubing. The source was placed in a shielded container. A Nucletron engineer was notified by phone and arrived at 1600 CST, but was unable to dislodge the source from the transfer tube. The source and transfer tube will be sent back to Nucletron and replacements have been ordered. A written report is being prepared and will be sent to the Division of Radiological Health. Inspectors from the Memphis field office will follow-up on this incident and will continue to keep NRC informed of the status of our investigation." Tennessee Event: TN-13-013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2013-01-23
48673 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-01-14 18:05 | 2013-01-14 22:04 | 2013-01-14 | AUTOMATIC REACTOR SCRAM FROM 100% POWER DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS [Reactor Protection System] with reactor critical. The Reactor Scram occurred at 1805 [CST] 01/14/13 from 100% CTP [Core Thermal Power]. The cause of scram appears to be a Turbine Generator Trip. "05-S-01-EP-2 RPV Control, Reactor Scram ONEP [Off Normal Event Procedure] 05-1-02-I-1, and Turbine and Generator Trips ONEP 05-1-02-1-2 were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "All control rods are fully inserted. MSIVs remained open and SRVs lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in the normal band and reactor pressure is being controlled via Main Turbine Bypass valves to the main condenser. There are no challenges to Primary or Secondary Containment at this time." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-01-14
48672 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-01-14 12:55 | 2013-01-14 17:52 | 2013-01-14 | TECHNICAL SUPPORT CENTER OUT-OF-SERVICE DUE TO FAILED AIR CONDITIONING BELT "The facility Technical Support Center (TSC) was rendered non-functional due to a malfunctioning TSC ventilation system. The TSC HVAC Air Handling Unit fan belt broke rendering the air conditioning non functional. Repairs have been completed and the unit has been returned to service however, the out of service time was greater than 30 minutes which by the station's reporting procedures is an 8 hour non-emergency report. The out of service time was from 1225 to 1630 [CST]. "Compensatory measures per site procedure FNP-0-EIP-6.0 (TSC Setup and Activation) for maintaining emergency assessment, off-site response, and off-site communication capabilities were immediately put in place. These measures include the conditional relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC to be uninhabitable." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-14
48671 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2013-01-11 | 2013-01-14 14:53 | 2013-01-14 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING PROSTATE BRACHYTHERAPY IMPLANT The following information was obtained from the Commonwealth of Pennsylvania Department of Environmental Protection via e-mail: "On January 11, 2013 the licensee informed the Department's Southeastern Regional Office of the Medical Event. The event is reportable within 24 hours per 10CFR 35.3045(a)(1)(i). Both the patient and referring physician were notified. "On December 4, 2012 the patient received an iodine-125 prostate seed implant. The patient returned for the 30 day post-treatment follow-up CT scan on January 9, 2013. Upon review of the CT results on January 10, 2013, it was discovered that the prostate received approximately 60% of the intended dose. The D90 was determined to be 56 Gy out of a prescribed dose of 110 Gy. "The potential cause of the event was noted as possible organ shift or incorrect depth placement of needles. "The licensee plans to compensate for the undertreated area with follow-up external beam therapy. They will provide the Department a written report in 15 days. The Southeastern Regional Office plans to follow up with a reactive inspection." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2013-01-22
48670 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2013-01-14 08:40 | 2013-01-14 08:44 | 2013-01-14 | LOSS OF ASSESSMENT CAPABILITY - RADIATION MONITORS INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At approximately 08:40 EST on January 14, 2013, radiation monitor RM-01TV-3547-1, Waste Processing Building Vent Stack 5A Wide Range Gas Monitor (WRGM) will be declared inoperable for pre-planned maintenance. MST-I0377, WPB Stack 5A Accident Monitor Channel Calibration will be performed. The maintenance activity is expected to complete January 15, 2013. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health of safety of the public or the operation of the facility. "The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-14
48669 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-01-12 09:50 | 2013-01-12 10:21 | 2013-01-25 | UNUSUAL EVENT DECLARED DUE TO POTENTIAL SECURITY EVENT "On Saturday, January 12, 2013 at 0925 hours [EST], with the reactor shutdown at 0% core thermal power, a security threat was reported. Security personnel took action to investigate the threat and implemented appropriate protective actions as required per security procedures. "Based on this security event, the Shift Manager activated the Emergency Plan and made notification of an Unusual Event at 0950 hours. As a result, the Emergency Response organization was notified and activated. At 1001 hours, the NRC and applicable state and local authorities were notified via the Emergency Notification System (ENS). "At 1050 hours, Security and applicable local law enforcement agency officials completed immediate investigations and determined that the security threat was not credible and was the result of local duck hunters on a small watercraft near the plant site. At 1105 hours, the Emergency Director terminated the Unusual Event. "The Senior Resident Inspector was on-site and has been informed of this event and associated offsite notification. The licensee has notified appropriate state and local authorities as required per Emergency Planning and other site specific procedures. A press release was also issued. "This notification is being made in accordance with 10CFR50.72(b)(2)(xi)." Notified the DHS SWO, FEMA and DHS NICC. * * * UPDATE FROM HETTWER TO S. SANDIN ON 01/25/13 AT 1101 EST * * * "This is an informational update to notification EN# 48669 based on completion of the post event Emergency Planning review. "Our initial notification contained the following documentation error: At 1001 hours, the NRC and applicable State and Local authorities were notified via the Emergency Notification System (ENS). This statement is corrected as follows: 'At 1001 hours, State and Local authorities were notified via the Dedicated Notification Network (DNN). At 1025 hours, the NRC was notified via the Emergency Notification System (ENS).' "The Resident Inspector has been informed of this event update." Notified R1DO (Ferdas). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2013-01-12
48668 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2013-01-11 09:20 | 2013-01-11 17:12 | 2013-01-11 | FITNESS FOR DUTY - ACCESS TERMINATED During a random screening, a non-licensed contract supervisor tested positive for a controlled substance. The individual's unescorted access has been terminated. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2013-01-11
48667 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-14 15:58 | 2013-01-11 16:45 | 2013-01-11 | 60 DAY TELEPHONE NOTIFICATION OF AN INVALID REACTOR TRIP ACTUATION IN MODE 4 "This 60-day telephone notification is being made in accordance with the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of a reactor trip while subcritical. "On November 14, 2012 Salem Unit 2 was in Mode 4 performing unit startup activities during its 2012 Refueling outage. Rod Control system and Individual Rod Position Indication testing was in progress with the Reactor Trip breakers closed. Control Rod Banks were being withdrawn from the core in accordance with a testing procedure. "At 1558 hours [EST], an Instrument and Controls technician removed control power fuses from the Nuclear Instrumentation System Intermediate Range Drawer 2N36, generating an invalid reactor trip. Affected equipment responded as designed. Both reactor trip breakers opened and all control rods dropped into the core. "2N36 troubleshooting had been in progress. Repair or replacement options for a broken connector had been discussed between the technician and his supervisor. Concerned for his personal safety, the technician pulled the 2N36 control power fuses in order to perform a wiring inspection. The technician failed to apply human performance standards including written directions, pre-job briefing, and notifying control room personnel and supervision prior to work. The technician failed to recognize that he was working outside of the expectations of normal work processes and failed to properly evaluate the full consequences of his actions. "There were no safety consequences or impact to the health and safety of the public as a result of this event." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A/R | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-01-11
48666 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2013-01-11 | 2013-01-11 12:27 | 2013-01-11 | PART 21 REPORT INVOLVING TYPE 546NS TRANSDUCERS The following report was received via fax: "Fisher Information Notice: FIN 2013-01; 9 January 2013 "Subject: Type 546NS Transducers "Equipment Affected By This Information Notice: Type 546NS Transducers shipped prior to 19 December 2012. "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert users of the Type 546 and 546NS Transducers, shipped prior to 19 December 2012, that Fisher Controls International LLC (Fisher) was made aware of a situation which may affect the performance of the aforementioned equipment. We are informing you of this circumstance in accordance with Sections 21.21(b) and 50.55 (e) of 10CFR21. "Applicability: This notice applies only to Fisher Type 546 and 546NS Transducers shipped prior to 19 December 2012 that are not in operation, installed or in service. "Discussion: Recently, while a Fisher maintenance engineer was installing a Type 546NS Transducer in a non US customer's plant, the instrument did not perform as expected. Upon investigation of the unit, it was determined that the vent hole to the relay was plugged which resulted in the build up of pressure inside the housing. This increased pressure will cause the output pressure to ramp up to supply pressure. In the event the relay is plugged, users will easily detect ramping up of the output pressure immediately after the sealed unit is put in service, which is why this FIN applies to units that are not yet in service. "Action Required: All Type 546 and 546NS Transducer units shipped to customers prior to 19 December 2012 and not already-in-service should be checked for this restriction of the case vent. Units in-service with the cover installed and properly working will not have a plugged case vent. "10CFR21 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21. If there are any technical questions or concerns, please contact: George Baitinger Manager; Quality Fisher Controls International LLC 205 South Center Street Marshalltown. IA 50158 Fax; (641) 754-2854 Phone: (641) 754-2026 George.Baitinger@Emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2013-01-11
48665 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-01-11 06:55 | 2013-01-11 10:16 | 2013-01-11 | OFFSITE NOTIFICATION REGARDING MANUAL REACTOR SCRAM "At 1534 EST on Thursday, January 10, Pilgrim Station operators initiated a manual shutdown of the power plant following a trip of the plant's recirculation pumps. "The plant is in a safe condition and plant personnel are investigating the cause. "The plant will be restarted after a thorough evaluation and any necessary repairs are completed. The plant had been online continuously for 230 days at the time of the shutdown. "The NRC Resident Inspector staff has been informed of this press release and notification. "This informational notification is being made in accordance with 10CFR50.72(b)(2)(xi). "The licensee will notify the Massachusetts Emergency Management Agency (MEMA)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-01-11
48664 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2013-01-10 15:34 | 2013-01-10 19:05 | 2013-01-10 | REACTOR PROTECTION ACTUATION (SCRAM) - RECIRCULATION PUMP TRIP "On Thursday, January 10, 2013 at 1534 hour [EST], with the reactor at 100% core thermal power, both recirculation pumps spuriously tripped and a manual reactor scram was inserted as required by station procedures. The cause of the recirculation pump trip is under investigation. "Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All other plant systems responded as designed. "Currently reactor pressure is being maintained between 900 and 1050 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). The Reactor Protection System has been reset; Reactor Water Cleanup System and normal reactor building ventilation have been restored. Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations) and the switchyard ring bus has been restored. "This event had no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector is on-site and has been notified. "This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(B)." The scram was uncomplicated and decay heat is being released to the main condenser via the turbine by-pass valves. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-01-10
48663 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-01-10 16:42 | 2013-01-10 17:43 | 2013-03-11 | UNAUTHORIZED ACCESS INTO THE PROTECTED AREA Actual entry of an unauthorized individual into the protected area. The individual's unescorted access was administratively withdrawn. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 0131 EST ON MARCH 9, 2013, FROM ALEX McLELLAN TO HUFFMAN * * * This event is being retracted based on the licensee's detailed review of the event timeline which determined that an unauthorized entry did not occur. The licensee will notify the NRC Resident Inspector. R1DO (Welling) notified and the 73.71 Group informed via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2013-01-10
48662 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-11-29 22:00 | 2013-01-10 11:04 | 2013-01-10 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SYSTEM ACTUATION "This telephone notification is being made for an invalid actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A) following the reporting guidance of 10 CFR 50.73(a)(1) and is not considered a Licensee Event Report. "With Unit 2 at Cold Shutdown (about 105?F and depressurized), an invalid actuation of the Main Feedwater (FW) isolation occurred at 2200 [EST] during removal of the 'A' Train Hi Consequence Limiting Safeguards (CLS) fuses. This action caused the 'A' train FW isolation relay to actuate and, as designed, tripped the operating 'B' Main Feed Pump (MFP) and the Main Turbine, which was latched for testing. The 'A' MFP was not in operation at the time of the event. "This was a partial actuation of the SI system. SI signals were inhibited prior to removal of the Hi CLS fuses by the tagging of the lead connecting the Hi CLS relay to the SI master relay. Although FW isolation occurs with SI actuation, the relay associated with the FW isolation circuitry is separately actuated and had not been tagged out. When the Hi CLS fuses were removed, the FW isolation relay was energized. "Plant systems and components responding to the signal started and functioned as designed with the exception of those inhibited by tag out. The affected components were restored to their pre-event configuration, The action to determine and initiate corrective actions is complete, and the necessary procedures are under revision." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-01-10
48661 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-11-28 23:05 | 2013-01-10 10:58 | 2013-01-10 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SYSTEM ACTUATION "This telephone notification is being made for an invalid actuation under 10 CFR 50.73(a)(2)(iv)(A) following the reporting guidance of 10 CFR 50.73(a)(1) and is not considered a Licensee Event Report. "With Unit 2 at Cold Shutdown (about 105?F and depressurized), an invalid actuation of the Unit 2 'A' train of the High High Consequence Limiting Safeguards (Hi-Hi CLS) system occurred at 2305 [EST] during reinstallation of fuses in preparation for return to service testing. The fuses were pulled to implement a design modification to replace existing relays with a new design. The 'A' train of the High High CLS actuated as soon as the fuses were installed. Plant systems and components responding to the Hi-Hi CLS 'A' train signals started and functioned successfully as designed with the exception of those systems and components procedurally rendered inoperable due to the RCS being below 350?F and 450 psig. Shutdown cooling was not lost due to safety injection leads being tagged out. "The signal could not be reset from the Main Control Room due to system design in this configuration requiring manual local manipulations to address affected components. The relays on both trains were replaced with the original design and the fuses reinstalled. The affected systems were restored to their pre-event configuration. "Specific trains and systems that actuated as a result of the "A" train of Hi-Hi CLS signal are described below: -- Component Cooling from the A Reactor Coolant Pump isolated. -- Containment Spray realigned and gravity flowed the Refueling Water Storage Tank and Caustic Addition Tank to the Containment Sump. The level did not reach the point where any components in the containment basement were affected. -- Service Water flowed to the A and C Recirculation Spray Heat Exchangers. -- Containment Instrument Air isolated. -- Emergency Diesel Generator (EDG) No.2 started but did not load since its associated Emergency Bus remained energized by offsite power. The EDG was stopped and returned to automatic. "A root cause evaluation is in progress." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2013-01-10
48660 | 0 | MPR ASSOCIATES, INC ENGINEERS |  |  |  |  | 2012-10-27 | 2013-01-09 18:09 | 2013-03-29 | PART 21 INTERIM REPORT ON THE FAILURE OF AN EMERGENCY DIESEL GENERATOR EXCITATION SYSTEM The following report was received from MPR Associates via facsimile: "MPR Associates (MPR) is investigating the failure of a replacement emergency diesel generator excitation system that MPR supplied to Cooper Nuclear Station. The root cause investigation is still in-process and will not be completed within 60 days of discovery as defined by 10 CFR Part 21. "The 10 CFR Part 21 Interim Report [below] provides the information known at this time. An updated report will be provided once the root cause investigation is completed. IDENTIFICATION OF THE BASIC COMPONENT THAT FAILED "The basic component is a Basler Electric SBSR emergency diesel generator (EDG) excitation system that was supplied as a replacement system to Cooper Nuclear Station (CNS). The replacement system included design changes relative to the original CNS excitation system, which is also a Basler Electric SBSR design. The design changes included larger magnetic components, which were intended to allow for continuous operation of the new exciter at the EDG overload rating. IDENTIFICATION OF THE SUPPLIER "The excitation system was supplied by MPR Associates (headquarters in Alexandria, VA). "Basler Electric (headquarters in Highland, IL) designed and fabricated the system under a commercial grade program certified to ISO 9001:2008. MPR Associates dedicated the commercial grade item for nuclear use under the MPR Nuclear QA Program, which complies with 10 CFR 50 Appendix B and ASME NQA-1. NATURE OF THE FAILURE "CNS installed the replacement excitation system in the Division 1 EDG system during refueling outage RE27. Prior to declaring the EDG operable, CNS manually terminated an EDG maintenance run due to erratic EDG reactive power indication, which was followed by a sudden drop of EDG reactive load and an indication of negative reactive power. "Several rounds of troubleshooting and surveillance testing were performed unsuccessfully. The surveillance testing resulted in faults to ground and overheating and failure of components in the excitation system. Some of the failed equipment included the automatic voltage regulator (AVR), manual voltage control autotransformer (T60), rectifier power diode failure indication resistors and light-emitting diodes (LEDs), insulation on the control windings of two saturable transformers, and elements of the data acquisition equipment used to record data during the testing. "The root cause of the failure has not yet been determined. However, on-site troubleshooting efforts at CNS by MPR and Basler Electric identified unexpected high voltages across the direct current (DC) control winding of the saturable transformers. These voltages are likely the cause of the failures experienced in-situ at CNS. "Follow-up tests at Basler Electric on a similar replacement system designed for the Hatch Plant (but not yet installed in the plant) also identified higher than expected voltages across the DC control windings of the saturable transformers. MPR and Basler Electric recommended postponement of the Hatch Plant installation until the impact of this condition (i.e., the higher than expected voltages) is evaluated. Note that the testing on the Hatch replacement system to date did not result in failure of the system or abnormal function of components external to the saturable transformers. NATURE OF THE FAILURE "Testing of the replacement excitation system began on October 27, 2012. The maintenance run resulting in erratic EDG reactive power indication was performed on October 30, 2012. CNS, MPR, and Basler Electric discontinued troubleshooting efforts for the replacement excitation system on November 9, 2012. "The replacement system was removed, and the original Basler Electric SBSR excitation system was re-installed. CNS declared the re-installed system operable on November 14, 2012. "MPR formally documented the issue in the MPR corrective action program on November 13, 2012. NUMBER AND LOCATION OF THE AFFECTED BASIC COMPONENTS "Based on the information known to date, this 10 CFR Part 21 Interim Report affects the following SBSR type excitation systems that were dedicated and supplied by MPR. Nuclear Plant Date Equipment Provided Items Supplied Cooper Nuclear 2012 1 Systems (failed during installation) Hatch 2012 5 Systems (not yet installed) CORRECTIVE ACTION PLAN "MPR is performing a failure analysis and root cause investigation to determine the extent of the condition, corrective actions, and actions to prevent recurrence. The root cause investigation is scheduled for completion by March 29, 2013. ADVICE GIVEN TO PURCHASERS OR LICENSEES "There are numerous Basler Electric SBSR type excitation systems in service at multiple plants throughout the nuclear industry. In addition to CNS and Hatch, MPR has dedicated and supplied SBSR excitation systems to the Beaver Valley, Davis-Besse, and Robinson plants. Each system supplied is custom designed for the generator that it is slated to control. Basler Electric SBSR excitation systems have demonstrated reliable service for many years. "The replacement SBSR excitation system supplied to CNS was not identical to the original system. Specifically, there were design differences in some of the components, including larger transformers, which were intended to allow for continuous operation of the new exciter at the EDG overload rating. Although it was not foreseen (and not revealed by factory acceptance testing), it seems that the design changes in the replacement system led to its maloperation and failure when it was initially installed at CNS. This faulty operation and failure were readily observed as part of normal EDG surveillance testing. Upon re-installation, the original SBSR excitation system functioned properly. Hence, it appears that: " - Differences between the replacement system and original system lead to the problem, and " - The problem is readily detectable in normal surveillance testing. "For these reasons, SBSR excitation systems installed at plants that have shown reliable operation during surveillance testing are in a satisfactory state and condition. MPR has no evidence that the mechanism or conditions that led to the failure at CNS will lead to failures at other installations. Therefore, plants with SBSR excitation systems installed should continue to use them and conduct normal surveillance testing." * * * UPDATE FROM PAUL DAMERELL (VIA FAX) TO HOWIE CROUCH AT 1830 EDT ON 3/29/13 * * * Reporting Individual: Paul Damerell, Principal Officer, MPR Associates, Inc., 320 King Street Alexandria, VA 22314. As indicated in the interim report, the EDG excitation system supplied to Cooper Nuclear Station failed. The root cause analysis identified a manufacturing defect induced design error in the saturable transformers supplied with the excitation system. The manufacturing error allowed the transformer control winding coils to shift which weakened the dielectric strength of the transformer control winding insulation system such that it could not withstand the voltage induced in the control windings. Testing and analysis estimated induced voltages exceeded 10 kV peak at motor start. MPR Associates also determined that H.B. Robinson has 6 saturable transformers installed with 4 spares and Farley has 3 spares with potential manufacturing defects. They noted that all installed transformers that have passed installation and surveillance testing to date have no immediate concerns but could have long-term reliability issues, if the manufacturing deficiency is present. MPR and Basler are coordinating with Cooper and Hatch to replace saturable transformers supplied by MPR. Cooper has 3 and Hatch has 15 of the devices. Additionally, they will coordinate with Robinson and Farley to test their transformers to determine if the manufacturing defects exist. All affected licensees have been notified by MPR Associates. Notified R1DO (Krohn), R2DO (Seymour), R3DO (Lara), R4DO (Pick) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2013-01-09
48659 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-08 16:40 | 2013-01-08 18:15 | 2013-01-08 | UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER FIRE "Fire in Unit 2 main transformer 2A. Reactor trip. Two train of offsite power lost to Unit 2." "An Unusual Event was declared based on EAL HU-2 - Fire or explosion in protected area or switchyard which affects normal plant operations." At 1655 CST, South Texas Unit 2 declared an Unusual Event due to a main transformer fire. Unit 2 tripped from 100% power and is currently at 0% power in Mode 3. The transformer fire is out. In addition to the loss of the main transformer, several safety related electrical busses and non-safety electrical busses lost offsite power. The appropriate emergency diesel generators started and powered the safety related busses. Unit 2 is currently stable and on natural circulation due to the loss of power to the reactor coolant pumps. Auxiliary feedwater is functioning as required and decay heat is being removed through the steam generator atmospheric relief valves. Unit 1 was unaffected by the event. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE FROM RICK NANCE TO BILL HUFFMAN AT 2055 EST ON 1/8/2013 * * * "On January 8, 2013, at 1640 CST, a failure of the Unit 2 Main Transformer occurred which resulted in a Unit 2 automatic trip. The failure of the main transformer resulted in a fire and damage to the transformer. The onsite fire brigade responded to the fire. The fire was declared under control at 1649 CST and declared out at 1656 CST. No offsite assistance was required. "An Unusual Event was declared at 1655 CST for initiating condition HU-2 (Fire or explosion in protected area or switchyard which affects normal plant operations) due to the main transformer fire. "Due to the site electrical lineup at the time, the loss of the main transformer resulted in a loss of power to 4160 ESF buses 2A and 2C, and associated Standby Diesel Generators 21 and 23 started as required and loaded on to their respective buses. 4160 ESF bus 2B remained energized from offsite power during this event and Standby Diesel Generator 22 did not start since an undervoltage condition did not exist on its ESF bus. "All three (3) motor-driven and the steam-driven Auxiliary Feedwater Pumps started as required. The Main Steam Isolation Valves were closed in accordance with procedure to limit plant cooldown. Decay heat is being removed via Auxiliary Feedwater with Steam Generator Power Operated Relief Valves. "Following the reactor trip, Pressurizer Power Operated Relief Valve 656A momentarily lifted and re-closed. "There were no personnel injuries and no radiological release as a result of this event. A press release has been issued. "The plant is currently stable in Mode 3 and the cause of the event is under investigation. "The Unusual Event was terminated at 1947 CST on 1/8/2013." The licensee notified the NRC Resident Inspector. Notified R4DO (Gaddy), NRR (Leeds), R4 (Reynolds), IRD (Gott), NRR EO (Hiland). Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and NuclearSSA via email. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2013-01-08
48658 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2013-01-08 14:32 | 2013-01-08 15:26 | 2013-01-08 | OFFSITE NOTIFICATION OF OIL FOUND IN SOIL ON PROPERTY ADJACENT TO BEAVER VALLEY "During excavation activities at the site of the former Shippingport Atomic Power Station (SAPS) which is located on company property outside the protected area but adjacent to Beaver Valley Power Station (BVPS), BVPS found soil with evidence of a historical oil leak. The area was underneath a concrete pad for a removed fuel oil storage tank at SAPS. Actions to remove the soil with oil residue have been initiated and are in progress. Decommissioning of SAPS was completed in 1989. "BVPS has notified the Pennsylvania Department of Environmental Protection of the condition and the activities being taken on 01-08-13 at 1432 EST. "This event is reportable under 10 CFR 50.72(b)(2)(xi) based on a notification to another government agency that has been made. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2013-01-08
48657 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2013-01-08 05:05 | 2013-01-08 07:05 | 2013-01-09 | PLANNED TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "A planned maintenance evolution at the Oyster Creek Nuclear Generating Station has removed the Technical Support Center (TSC) ventilation system from service. The TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately thirty six hours from 0505 [EST] to 1700, tomorrow, Jan 9, 2013. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 5O.72(b)(3)(xiii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC resident has been notified." * * * UPDATE AT 0258 ON 1/9/2013 FROM JIM RITCHIE TO MARK ABRAMOVITZ * * * TSC ventilation was returned to service at 0230 EST. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Newport). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-08
48656 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2013-01-07 14:27 | 2013-01-07 19:29 | 2013-01-07 | SECONDARY CONTAINMENT MOMENTARILY INOPERABLE "Technical Specification 3.6.4.1 (Secondary Containment) requires that the secondary containment be operable. Surveillance requirement 3.6.4.1.3 requires verifying each secondary containment access inner door or each secondary containment access outer door in each access opening is closed. "Maintenance personnel were moving scaffolding through Reactor Building outer security door (R-304) when an equipment operator opened inner door (R-305) to exit the Reactor Building. This resulted in both the Reactor Building inner and outer access doors being simultaneously open for a short duration. Normally, the doors are interlocked in which the inner door would not be able to be opened prior to the outer security door being closed. "The equipment operator immediately closed the door and notified the Main Control Room. The outer security door (R-304) has been key-locked closed, until corrective actions can be determined. "Columbia Generating Station is investigating why the interlock feature failed. "There were no radiological releases associated with this event. "No safety system actuations or isolations occurred." The licensee has notified the NRC Resident Inspector. Note: See similar event reported by licensee on 12/30/12, EN #48639, involving containment door interlock failure on doors R-204 and R-205. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-01-07
48655 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-11-13 13:00 | 2013-01-07 15:27 | 2013-01-07 | AGREEMENT STATE REPORT - DAMAGE TO AM-241 SPECTROSCOPY SOURCE The State of California Radiologic Health Branch forwarded the following report via e-mail: "(1) A description of the event, including the probable cause and the manufacturer and model number (if applicable) of any equipment that failed or malfunctioned; "A small alpha spectroscopy style source was damaged by a researcher who placed adhesive tape on the active source area. The source appears similar to an Isotope Products A-2 type. "Removal of the tape lifted the active material and transferred it to the tape. "Records of the source manufacturer were not available. "(2) The exact location of the event; "Room 369 GLAST Laboratory, Natural Sciences II Building, UC Santa Cruz campus. "(3) The isotopes, quantities, and chemical and physical form of the licensed material involved; "Am-241 solid, ~1 micro curie total, plated metal "(4) Dale and time of the event; "Occurrence on 11-13-2012 about 1:00 pm "(5) Corrective actions taken or planned and the results of any evaluation or assessment; "a. Suspend individual involved and laboratory supervisor until re-qualified by radiation safety on proper techniques for source handling. (Completed) "b. Laboratory supervisor to retrain all users in specific laboratory on proper source handling. (Scheduled to be completed by 3-15-2013) "c. Update online training materials to include information about fragility of certain types of sources. (Scheduled for 2-1-2013) "d. Include information on the event in the next radiation safety newsletter. (Scheduled for 3-1-2013) "e. Remove obviously damaged source from service. (Completed) "f. Re-inspect similar sources and remove any damaged or suspect sources from service. (Scheduled for 2-15-2013) "(6) The extent of exposure of individuals to radiation or to radioactive materials without identification of individuals by name. "No exposure or contamination was identified in surveys conducted the day of the event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2013-01-15
48654 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2013-01-08 04:00 | 2013-01-07 14:59 | 2013-01-08 | TECHNICAL SUPPORT CENTER VENTILATION WILL BE RENDERED NON-FUNCTIONAL FOR PLANNED MAINTENANCE "A planned work package (52232185-01) at the James A. FitzPatrick (JAF) Nuclear Power Plant will be performed for inspection and verification of 72AOD-171 (Admin Building Ventilation AHU-4 Fresh Air Supply Isolation Damper). The isolations necessary to perform this evolution will require tagging out 72AHU-4 (Admin Building Office Area Air Handling Unit) and breaking the boundary into the Technical Support Center (TSC) ventilation system. Therefore, the TSC ventilation system will be rendered non-functional during the duration of this work activity. The TSC ventilation is expected to be out of service for approximately 10 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE ON 01/08/13 AT 1654 EST FROM BOB WISE TO HUFFMAN * * * The TSC ventilation system was returned to service at 1650 EST. The NRC Resident Inspector has been notified. R1DO (Newport) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-07
48653 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2013-01-06 20:00 | 2013-01-06 13:32 | 2013-01-10 | PLANNED CORRECTIVE MAINTENANCE ON THE TECHNICAL SUPPORT CENTER (TSC) HVAC POWER SUPPLY "This ENS [report] is being issued in advance of planned corrective maintenance on a TSC HVAC power supply. "On 1/6/13 at 2000 [EST], the Technical Support Center Emergency Ventilation system will be removed from service to perform corrective maintenance on the load center that supplies power to the TSC HVAC system. The emergency ventilation system will not be available and cannot be restored within the time period required to staff and activate the Emergency Response Organization (ERO). The work is scheduled to complete on Friday 1/11/13 at 1500 [EST]. "If an emergency is declared and the TSC activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological or other conditions. The Station Emergency Director would assess habitability in accordance with station procedures. TSC relocation of personnel would be directed as required until such time that the TSC ventilation system is returned to service. "An update will be sent upon TSC HVAC restoration." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM WILLIAMSON TO KLCO ON 1/10/13 AT 2209 EST* * * The TSC emergency ventilation system was restored to normal at 2200 EST on 1/10/13. The licensee notified the NRC Resident Inspector. Notified the R1DO (Newport). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-06
48652 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2013-01-04 23:37 | 2013-01-05 03:09 | 2013-01-05 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS with reactor critical. Reactor Scram occurred at 2337 CST 01/04/13 from 94% CTP (Core Thermal Power). The cause of the scram appears to be a Generator/Turbine trip. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "MSIVs remained open and SRVs lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band and reactor pressure is being controlled via bypass valves to the condenser." The NRC Resident Inspector has been informed. See similar EN #48637. | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2013-01-05
48651 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-04 09:41 | 2013-01-04 14:19 | 2013-01-04 | UNIT 2 MANUALLY TRIPPED AFTER TWO SHUTDOWN CONTROL RODS UNEXPECTEDLY DROPPED DURING SURVEILLANCE TESTING "On January 4, 2013, at 0941 hours [CST], Unit 2 was manually tripped after 2 shutdown rods unexpectedly dropped during monthly control rod surveillance testing. Shutdown Bank C rods were being inserted in accordance with the surveillance procedure, when 2 rods in Shutdown Bank E (D-8 and M-8) unexpectedly dropped. This met the criteria for a manual reactor trip, which was immediately performed. "The appropriate procedures were entered to mitigate the transient and all systems responded as designed. "Unit 2 is currently in Mode 3 and the cause of the 2 dropped rods is under investigation." All three (3) motor-driven and the steam-driven Auxiliary Feedwater Pumps started as required and have since been secured. Decay heat is being removed using normal startup feedwater with steam discharge to the main condenser via the bypass valves. Unit 2 is in a normal post trip electrical lineup. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2013-01-04
48650 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-12-29 | 2013-01-04 13:20 | 2013-01-04 | PART 21 - ANTI-ROTATION PIN FAILURE IN 10-INCH ANCHOR DARLING (FLOWSERVE) DOUBLE DISC GATE VALVE The following is a summary of the information received from TVA - Browns Ferry via facsimile: On December 29, 2012 it was determined that sufficient data existed to determine a defect existed in a 10-inch Anchor Darling double disc gate valve installed in Browns Ferry Unit 1. In November, 2012 during a scheduled refueling, the High Pressure Coolant Injection valve, 1-FCV-073-0002 failed its local leak rate test with gross leakage identified on the upstream (reactor side) disc. The downstream side of the discs showed acceptable leakage. When maintenance was performed on the valve, the disc retainer bolt was found sheared. Further investigation revealed that the anti-rotation pin had failed. A review of work order history determined that this valve was installed during the Unit 1 recovery in 2007. The cause of the anti-rotation pin failure was determined to be that the stem was not adequately torqued to the upper wedge at the manufacturing plant. This cause was confirmed by internal inspections of the valve that were performed at Browns Ferry. Flowserve Corporation is also conducting an investigation. The licensee identified 15 other applications of this particular 10-inch valve in all three Browns Ferry units. For all those valves except 2-FCV-073-0002, documentation exists demonstrating that the stem to upper wedge was torqued to manufacturer requirements, determined through MOVATS [Motor-Operated Valve Analysis and Test System] testing that the anti-rotation pin is not sheared, or determined through visual inspection that the anti-rotation pin remains intact. 2-FCV-073-0002 is considered to be non-conforming and will be inspected during the next scheduled Unit 2 refueling. The licensee has notified the NRC Resident Inspector of this notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2013-01-04
48649 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2013-01-03 06:04 | 2013-01-03 17:32 | 2013-01-03 | LOSS OF SAFTEY PARAMETER DISPLAY SYSTEM (SPDS) "On 01/03/13 at 0604 CST, the Wolf Creek Generating Station Nuclear Plant Information System (NPIS) computer was removed from service for scheduled maintenance. "The NPIS computer being removed from service results in a loss of functionality of the SPDS. Due to SPDS being lost for longer than a short period of time, Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria of 10 CFR 50.72(b)(3)(xiii). There was no other loss of emergency assessment capability concurrent with the ongoing loss of SPDS. When the equipment was removed from service, plant personnel entered the appropriate Off-Normal procedure and obtained local readings for the equipment that is normally monitored by SPDS and NPIS during the loss of the plant computer. "NPIS computer was restored to service and declared functional at 1541 CST. The return of the NPIS computer to a functional condition restored the SPDS assessment capability function. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-03
48648 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2013-01-03 09:30 | 2013-01-03 15:03 | 2013-01-28 | LOSS OF ERDS CAPABILITY "At 0930 [CST] on January 03, 2013 NextEra Energy Duane Arnold discovered that the Emergency Response Data System (ERDS) was no longer capable of transmitting plant data to the NRC. The loss of ERDS is reportable per 50.72(b)(3)(xiii). "At 1151 [CST] on January 03, 2013 Information Management personnel restored ERDS to working status. "The NRC Resident [Inspector] has been notified." The licensee has the cause under investigation. * * * UPDATE AT 2136 EST ON 01/03/13 FROM STEPHEN SPEIRS TO S. SANDIN * * * "At 1725 [CST] on January 03, 2013 NextEra Energy Duane Arnold experienced a four minute interruption of the Emergency Response Data System (ERDS). During this time, ERDS was not capable of transmitting plant data to the NRC. The loss of ERDS is reportable per 10 CFR 50.72(b)(3)(xiii). "The interruption of ERDS is related to a previous problem with the system reported under EN #48648. Troubleshooting of ERDS continues to ensure long-term reliability. Additional interruptions of ERDS are possible during this troubleshooting, and a follow-up notification will be made when ERDS reliability is assured." The licensee informed the NRC Resident Inspector. Notified R3DO (Skokowski), ERDS Group and CAT Group via email. * * * UPDATE FROM ROB SPADING TO CHARLES TEAL ON 1/28/13 AT 1436 EST * * * Maintenance is complete on the ERDS system. It was tested satisfactorily on 01/15/13 at 1130 CST and returned to fully functional status. The NRC Resident Inspector has been informed. Notified R3DO (Stone), ERDS Group and CAT Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-03
48647 | -1 | RESEARCH MEDICAL CENTER |  |  |  |  | 2013-01-02 11:47 | 2013-01-03 10:22 | 2013-01-03 | RADIOISOTOPE ADMINISTERED TO THE INCORRECT PATIENT While conducting a radiopharmaceutical stress test the dose was administered to the incorrect patient. The isotope was 11 mCi of Tc-99m. The patient is not expected to experience any adverse effects as a result of this treatment. * * * UPDATE AT 1440 EST ON 01/03/13 FROM STEPHEN SLACK TO S. SANDIN * * * The licensee is retracting this report after a discussion with NRC Region III (Gattone) which concluded that the event did not meet the reporting criteria as a medical event. Notified R3DO (Skokowski) and FSME Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2013-01-11
48646 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-03 09:00 | 2013-01-03 09:28 | 2013-01-03 | COMMERCIAL GRADE DEDICATION PROGRAM DEGRADED "WBN [Watts Bar Nuclear] Unit 2 (under construction) has determined that certain equipment components have been installed that may not meet the requirements of the commercial grade dedication process. This condition has the potential to create a substantial safety hazard had it remained uncorrected. Evaluations are being performed to determine if the installed equipment would have still performed their safety functions. No specific cases of a substantial safety hazard have been found to date, but until evaluations are completed, the safety significance of this condition remains indeterminate. Therefore, this condition is conservatively being reported by WBN Unit 2 under 10 CFR 50.55(e)." This programmatic issue encompasses approximately 500 evaluations. The licensee will contact the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 50.55(e) |  |  |  | 0 | 2013-01-03
48645 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2013-01-03 03:00 | 2013-01-03 02:01 | 2013-01-03 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0300 EST on Thursday, January 3, 2013, the DC Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 2200 EST on January 3, 2013. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM GREGORY KANDA TO S. SANDIN ON 1/3/13 AT 2202 EST * * * "The TSC ventilation system maintenance and testing was completed satisfactorily and the system was restored to service at 2115 EST on 1/3/13. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Skokowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2013-01-03
48644 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2013-01-02 13:08 | 2013-01-02 18:42 | 2013-01-02 | INADVERTENT ACTUATION OF SAFETY INJECTION, CONTAINMENT COOLING AND CONTAINMENT ISOLATION SIGNALS "At 1308 hours [CST] on January 2, 2013, Arkansas Nuclear One Unit 2 (ANO-2) experienced an inadvertent safety injection actuation signal (SIAS), containment cooling actuation signal (CCAS) and containment isolation actuation signal (CIAS) during matrix testing on 'C' channel plant protective system (PPS). All components actuated as designed for the stated actuation signals. "After verification that the actuation signal was not valid the high pressure safety injection (HPSI) pumps and low pressure safety injection (LPSI) pumps were secured and their hand switches placed in pull-to-lock as directed by the abnormal operating procedure for inadvertent SIAS at 1312 hours. The HPSI and LPSI pumps were the restored to normal standby condition and available for automatic operation at 1352 hours. "The unit did down power to approximately 87% power when all three coolant charging pumps ran with suction aligned to the boric acid makeup tanks. The unit currently remains in mode 1. SIAS, CCAS, and CIAS have been reset. The cause of the inadvertent actuation signals is under investigation. The NRC Resident Inspector has been informed." Unit 2 entered Technical Specification 3.0.3 for approximately 40 minutes while the LPSI and HPSI pumps were in pull-to-lock. | 0 | 87 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2013-01-02
48643 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2013-01-02 | 2013-01-02 17:46 | 2013-01-02 | AGREEMENT STATE REPORT - MISSING TROXLER The following was received from the State of Texas via email: "On January 2, 2013, the Agency [State of Texas] was notified by the licensee's Radiation Safety Officer (RSO) that a Troxler model 3430 containing an 8 millicurie cesium - 137 source and a 40 millicurie americium - 241/beryllium source could not be located. The licensee's records indicated that the gauge had been returned by their technician and locked in the storage area on December 31, 2012. The licensee's tracking system, which tracks the location of their vehicles, confirmed that the truck used by the technician had been returned to the licensee's location at the close of business on December 31. The licensee conducted an inventory of all of its gauges and this was the only gauge missing. The RSO stated that the storage area had no signs of tampering. The RSO stated that they had interviewed the technician assigned to use the gauge, but the technician did not provide any information useful to recover the gauge. The RSO stated that they were in the process of notifying the police of the theft. The RSO stated that the offering of a reward would be discussed with company management. The RSO stated that the gauge was locked inside of a transportation case and that the operating rod was locked in the shielded position. The RSO stated that he did not believe there was any risk of exposure to a member of the general public. Additional information will be provided as it is received in accordance with SA-300. "Texas Incident Number: I-9030" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-01-10
48642 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2012-12-24 | 2013-01-02 14:19 | 2013-01-02 | AGREEMENT STATE REPORT - SHUTTER MECHANISM FAILURE The following report information was received from the State of Nevada Dept of Health via e-mail: "The handle of a Berthold source, SN: 0448/09, Model No.: LB 7440, Activity: 30 mCi, Isotope: Cs-137, separated from the shutter mechanism. The shutter is closed and was verified with survey instrument RadEye B20 SN: 0515. This source will be kept in storage until the shutter can be fixed." Nevada Event Report - NV130001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2013-01-10
48641 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-11-29 | 2013-01-02 11:18 | 2013-01-02 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE "On December 26, 2012 the licensee reported that the shutter of one of its fixed gauges could not be closed as designed. The gauge is a Metso Automation, Inc., Model BWM-T (Serial Number 21136049). The gauge contains 400 mCi of Kr-85. The gauge is mounted on a scanning platform that traverses a paper web and is used as a sensor. The problem was noted by the on-site technician of Hoosier Technical Services Company, service provider on November 29, 2012. "Metso Automation, Inc. was contacted and the following actions were taken: The scanning platform containing the gauge was placed in the home position and removed from the process, power was removed from the equipment, and finally the old shutter mechanism was removed and replaced with a new part. "A radiation survey was performed and found to be within design parameters and regulatory limits. The Virginia Radioactive Material Program is not performing a site visit or follow-up as the shutter was repaired, all radiation levels are normal, and there was no public health or environmental concerns." Virginia Report: VA-13-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2013-01-10
48640 | 0 | TEXAS DEPARTMENT OF HEALTH SERVICES |  |  |  |  | 2012-12-04 | 2013-01-02 09:44 | 2013-02-21 | THERAPY SOURCE JAMMED AT THE DEVICE ENTRY PORT "On January 2, 2013, the Agency [Texas Department of State Health Services] was notified by the licensee that on December 4, 2012, a medical event had occurred. The licensee reported that while performing a therapy procedure using a Novoste Beta-Cath IVB device the last strontium-90 source in the ribbon of sources could not be retracted into the device. The source was jammed at the device entry port. All of the sources had been removed from the patient, therefore the patient did not receive any additional exposure. The device was placed into an emergency safety box designed for such events and the box was then covered with a lead apron. No one in the treatment room received any additional exposure form the event. The licensee will return the device to their supplier. Additional information will be provided as it is received in accordance with SA-300." Texas State Report # I-9029 * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 2/21/2013 AT 1526 EST * * * The following information was received by facsimile: "The Best Vascular Technical Team based in Norcross, Georgia evaluated the returned system that was involved in the subject complaint. The team confirmed the complaint based on the evidence of discoloration to the proprietary connector and acrylic body of the main chamber distal to the pin gate, indicating prolonged exposure to radiation; however upon arrival the Jacketed Radiation Source Train (JRST) was no longer stuck at the pin gate or proprietary connector of the delivery catheter. "During testing, interlocks performed as expected to provide safety in the case of a manual removal. The team was unable to duplicate the complaint after exhaustive cycle testing. Visual examination identified a kink in the tubing leading to the fluid collection bag. "A fluid sample that had been run through the transfer device and over the jacketed radioactive source train was analyzed for unsealed radiation; no radiation leakage was detected. "Due to the size of the 3.5F delivery catheter, Best Vascular utilizes tubing materials that exhibit high column strength to ensure adequate trackability of the catheter during placement. The smaller size of the catheter is a desired feature that minimizes ischemia caused by cessation of blood flow during treatment. Unimpeded hydraulic flow is essential to performance of the system and as such, it is necessary to avoid the compression that may occur to the delivery catheter due to the configuration of the system in conjunction with other interfaces (e.g., interventional tools, patient, etc.). It is also essential that the path to the fluid collection bag be maintained in an unobstructed manner in order to provide the hydraulic pressure necessary for smooth movement of the JRST through the entire system. "Additional information on this event has been provided in the Nuclear Materials Event Database in accordance with SA-300." Notified R4DO(Miller) and FSME via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2013-01-10
48639 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-12-30 05:30 | 2012-12-30 15:45 | 2012-12-30 | SECONDARY CONTAINMENT MOMENTARILY INOPERABLE "Technical Specification 3.6.4.1 (Secondary Containment) requires that the secondary containment be operable. Surveillance requirement 3.6.4.1.3 requires verifying each secondary containment access inner door or each secondary containment access outer door in each access opening is closed. "During a fire tour, a security officer proceeded through Reactor Building outer security door (R-204) and opened the inner door (R-205) prior to the outer security door completely closing. This resulted in both the Reactor Building inner and outer access doors being simultaneously open for a short duration. Normally, the doors are interlocked in which the inner door would not be able to be opened prior to the outer security door being closed. "The security officer immediately notified the Main Control Room and operations personnel verified both doors were locked and closed. The outer security door (R205) has been key-locked closed until corrective actions are determined. "Columbia Generating Station is investigating why the interlock feature failed. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-12-30
48638 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-12-29 08:03 | 2012-12-29 15:21 | 2012-12-29 | EMERGENCY DIESEL GENERATOR AUTO-START AND LOAD UPON TRIP OF RESERVE STATION TRANSFORMER "At 0803 EST on 12/29/2012 With Unit 1 and Unit 2 operating at 100%, the Supply breaker to 'B' Reserve Station Transformer (RSST), 0-EP-BKR-252 tripped on an instantaneous over current of the B-C phases due to a Pelican contacting the lines. This resulted in a lockout of the 'B' RSST and loss of power to the Unit 2 'H' Emergency Bus from its normal off site power supply. #2 Emergency Diesel Generator auto started on under voltage and loaded onto the Unit 2 'H' Emergency Bus. The Operations staff entered abnormal operating procedure 2-AP-10.07, Loss of Unit 2 Power, to recover from the electrical transient. All equipment performed as expected during the event and there were no unexplained occurrences. Maintenance has verified there is no damage to the line, breaker or 'B' RSST and at 1242 EST offsite power was restored to Unit 2 'H' Emergency Bus. At 1501, #2 Emergency Diesel Generator was secured in accordance with Station Operating procedures. "Currently Unit 1 is operating at 100%, 922 MWE. "Currently Unit 2 is operating at 100%, 915 MWE. "All electrical distribution systems were restored to a normal alignment. "No adverse radiological consequences resulted from this event. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to the auto start of #2 Emergency Diesel Generator." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-12-29
48637 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-12-29 00:18 | 2012-12-29 05:05 | 2012-12-29 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE/GENERATOR TRIP "Actuation of RPS [Reactor Protection System] with reactor critical. Reactor Scram occurred at 0018 [CST], 12/29/12, from 100% CTP [Core Thermal Power]. The cause of scram appears to be a Generator/Turbine trip. "Appropriate off normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "MSIVs [Main Steam Isolation Valves] remained open and SRVs [Safety Relief Valves] lifted. Currently, reactor water level is being maintained by the condensate and feedwater system in normal band and reactor pressure is being controlled to limit cooldown." All control rods inserted. The plant is in hot shutdown with decay heat removal to the condenser and the electrical line-up is in a normal configuration. The cause of the turbine/generator trip is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-12-29
48636 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-28 11:00 | 2012-12-29 01:20 | 2012-12-29 | COMPUTER PROGRAM ERROR IDENTIFIED IN THE FITNESS FOR DUTY PROGRAM "On December 28, 2012 at approximately 1100 [EST], Susquehanna discovered a computer program error that affected the Susquehanna Fitness for Duty (FFD) program. Specifically, thirty-nine Behavioral Observation Program (BOP) inquiries were without proper documentation of the required need to continue unescorted access (UA) and without verification of an actual observation within the required thirty day timeframe. The computer error resulted in answers for two of the three questions on the Behavior Observation Inquiry form not being recorded when the form was submitted by the supervisor. This resulted in the thirty-nine security accounts being re-zeroed and allowing UA for an additional thirty days. All thirty-nine BOP supervisors were contacted, and it was determined that thirty-six of the individuals were intended to continue with UA. The remaining three accounts should have terminated to prevent UA; however, none of these three individuals gained unauthorized access to the Protected Area after their UA should have been terminated. Seven of the thirty-six intended to continue with UA did access the Protected Area, but per follow-up with the Behavior Observation Supervisors, these individuals were in compliance with the BOP. In accordance with 10 CFR 26.719(b)(4), this report is being made based on being a potential programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program. The [NRC] Resident Inspector and the Branch Chief for the Region I Division of Reactor Safety were briefed." | 98 | 18 | 0 | 98 | 18 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2012-12-29
48635 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-12-28 14:10 | 2012-12-28 18:02 | 2012-12-28 | FITNESS FOR DUTY - ACCESS DENIED On December 28, 2012, at approximately 1410 hours CDT, Dresden Station was informed by Station Security that a Contract Supervisory (non-licensed) individual had a confirmed positive Fitness-For-Duty test for a controlled substance. This event affects both Dresden and Braidwood Stations. The individuals access to both Dresden and Braidwood Stations has been terminated. The licensee notified the NRC Resident Inspectors. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2012-12-28
48634 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2012-12-13 | 2012-12-28 17:27 | 2012-12-28 | AGREEMENT STATE REPORT - OPEN TRANSPORT VEHICLE WITH RAD LEVELS EXCEEDING LIMITS The following information was received from the Washington State Division of Radiation Protection via e-mail: "Shipment number GE-IL-120712-USEW arrived at the US Ecology waste site on the morning of December 11, 2012. The shipment manifest listed Zn-65 and Co60 as the isotopes. The material is NARM material. Total activity 3.02E6 MBq. Total volume 6.07 m3. Total weight 15,082 Kg. Waste class A- stable. The drums were accelerator targets from GE Healthcare in Illinois and New Jersey, loaded in boxes, which were again loaded in drums and cemented in place. The outer drums were DOT 7A containers. The entity signing the shippers certification on the manifest was GE Healthcare in Illinois. "US Ecology staff conducted surveys of the shipping vehicle, and reported to Washington State Department of Health that the dose rate on the bottom of the truck was greater than 200 mr/hr with a side wall GM detector. Washington State Department of Health inspector used an Eberline RO2 ion chamber to get a more accurate measurement, and found that the dose rate measured with the meter bottom flush with the bottom of the floor I beams was 250 mr/hr. "The shipment shifted in transportation, and was not braced to withstand conditions of normal transportation. The shipment contained drums strapped to small pallets. Upon inspecting the shipment, the drums were not tightly contained in the trailer, noted by gaps between the toe boards and the drums, loose straps in the rear of the drums, and large spaces between the load locks and the drums. The driver was asked if his trip was normal, without any abnormal stops, turns, stops or bumps, and he said it was a very smooth ride, all on interstate, but he picked the load up in Iowa after the 1st truck had mechanical issues. One large drum in the center of the shipment had lead shielding blankets underneath the pallet it was on, and this drum could be rocked back and forth a few inches, while it was still strapped in the truck. "A more detailed inspection of the packages occurred on the December 12th and 13th, including using the RO2 on the bottom of drums that exhibited higher than manifested dose rates. Two drums were found to have external, on contact dose rates of 1.5 R/hr. "One drum's lid was not correctly installed. While there was no evidence of leakage, nor did the lid come off, it was not properly installed. The shipment required the use of 7A containers. "One drum could not be correlated to the manifest, as there was a transposition error in the drum number. A call to the generator corrected the problem. "The dose rate at the drivers area and the outside of the shipment vehicle were within the limits for transportation. No material was detected to have leaked from the containers. There is no suspected overexposures caused by this incident." Washington State Report WA-12-081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-01-07
48633 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2012-12-04 | 2012-12-28 17:27 | 2012-12-28 | AGREEMENT STATE REPORT - OPEN TRANSPORT VEHICLE WITH RAD LEVELS EXCEEDING LIMITS The following information was received from the Washington State Division of Radiation Protection via e-mail: "A shipment of waste from the 325 building on the Hanford reservation, prepared for shipment by Pacific Northwest National Laboratories, was received at Perma-Fix Northwest waste (PFNW) -Richland. During the unloading evolution, PFNW noted that the dose rate on the bottom of 2 drums exceeded the manifested value, and one drum exceeded 200 mr/hr on contact. (See limits in 49CFR173.221 (b)). PFNW notified Washington Department of Health (WDOH). A [WDOH] inspector came to the site on December 6, 2012 and measured the dose rate with an Ludlum M-9 and measured 350 mr/hr. [WDOH] has routinely used an Eberline RO2 type of meter to determine compliance - this reading be taken again with an RO2. PFNW had an RO20 which measured 220 mr/hr. This is the reading that was used as the 'actual' dose rate. [WDOH] is attempting to get a measurement with an RO2. The dose rate value may change, as [WDOH] takes additional reading with other instruments after the new year. "The dose rate at the drivers area and the outside of the shipment vehicle were within the limits for transportation. No material was detected to have leaked from the containers. There is not expected overexposure caused by this incident. "Actions taken by State: Suspend all shipment to PFNW by PNNL "Sr90 (in drums with errant dose rates.) Total activity in 2 drums: 2.4 e 5 MBq." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2013-01-07
48632 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-11-01 | 2012-12-28 15:24 | 2012-12-28 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following information was received from the Louisiana Department of Environment Quality via facsimile: "On 11/01/2012, the RSO for Rock Tenn called to report a stuck shutter on a [density] gauge utilized on a process [line] in the paper mill refinery. There was no possible exposure to the mill workers because the gauge is installed on a process [line in a remote location] and, [consequently,] the shutter remaining [open] is not a problem. The gauge is a Berthold, Model LB 7400 Series, loaded with a 50 mCi Cs-137 [source]. The gauge has been in the elements for a prolonged period of time and the shutter malfunctioned due to corrosion in the mechanism of the source holder. All of the sources were evaluated and inspected and only one needed repair. The manufacturer stated that it appeared to be from being in the elements. The manufacturer stated that they were looking into finding a modification to shield the shutter mechanism from the elements. The Louisiana Department of Environmental Quality considers this item closed." Louisiana Incident Number: T144358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-01-07
48631 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-11-27 | 2012-12-28 15:14 | 2012-12-28 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following information was received from the Louisiana Department of Environment Quality via facsimile: "On 11/27/2012, the RSO for BASF called in a preliminary report about a shutter on a fixed level gauge utilized in their processes in the chemical plant. There is no possible exposure to the plant workers because the gauge [is] installed on a remote process [tank inaccessible by plant personnel] and, [consequently], the shutter remaining open and operating [should not be] a problem. . . . The gauge is a Berthold, model #LB-7440D loaded with 150 mCi of Cs-137. [A manufacturer service technician] has been contacted to repair the level gauge. The manufacturer's service tech stated that [the stuck shutter] appears [to be the result of exposure to] the elements. The Louisiana Department of Environmental Quality considers this item closed and the records will be reviewed during the next inspection." Louisianan Incident Number: T145017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-01-07
48630 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-11-09 | 2012-12-28 15:26 | 2012-12-28 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following information was received from the Louisiana Department of Environment Quality via facsimile: "On 11/09/2012, the RSO for Phillips 66 called in a preliminary report about [stuck] shutters on fixed level gauges utilized in their processes in the chemical plant. There was no possible exposure to the plant workers because the gauges were still installed on a process [tank in a remote location] and the shutters remaining open was not a problem. . . . The gauges are Omart and Ronan Engineering devices. [A manufacturer service technician] was contacted to evaluate the source holders and determined which devices could be repaired and which ones needed to be replaced. All of the source holders, with the exception of two were able to be freed up for continual use. . . . Two source holders were damaged during the evaluation process. . . .These two sources in their holders will be replaced during the next turn-a-round to reduce down time. . . . The gauges have been in the elements for a prolonged period of time and the shutters malfunctioned due to corrosion in the mechanism of the source holder. All of the sources were evaluated and inspected . . .. The manufacturer's service tech stated that it appears the be from being in the elements. The manufacturer stated that they were looking into finding a modification to shield the shutter mechanism from the elements. The Louisiana Department of Environmental Quality considers this item closed and the records will be reviewed during the next inspection." The gauges involved are: 1) Omart SHLG2-45 2) Omart SR 2 3) Ronan SA1-F37 Louisiana Incident Number T145023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2013-01-07
48629 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-28 03:30 | 2012-12-28 09:55 | 2012-12-28 | LOSS OF COMMUNICATIONS WITH ALL EMERGENCY PLANNING ZONE SIRENS "Limerick and associated local counties have lost communications with all Emergency Planning Zones (EPZ) sirens for greater than 1 hour. This exceeds the 25% notification threshold. The contract vendor is responding to the loss to determine repair actions and timeline. "The EPZ plan contains alternate methods of notifying the public in the event of an evacuation. "Notifications have been made to the State and local agencies regarding this loss of Emergency Preparedness capability at 0913 EST on 12/28/12, which constitutes the 'Offsite Notification' per 10CFR50.72(b)(2)(xi)." The licensee has notified Montgomery, Chester, Burkes counties, and the NRC Resident Inspector. * * * UPDATE AT 1258 EST ON 12/28/12 FROM DAN WILLIAMSON TO HUFFMAN * * * Communications with all EPZ sirens have been restored. The licensee will notify the affected counties and the NRC Resident Inspector. R1DO (Conte) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-12-28
48628 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-12-27 14:45 | 2012-12-27 15:46 | 2013-04-12 | SCHEDULED OPERATIONS SUPPORT CENTER (OSC) OUTAGE FOR EQUIPMENT UPGRADE "Fort Calhoun Station (FCS) will be implementing a scheduled modification to renovate and upgrade the interior configuration of the site's Operational Support Center (OSC). The OSC is located within the Technical Support Center (TSC). The TSC will remain fully operable. Due to the construction, beginning on December 27, 2012 with a planned completion date of February 27, 2013, the OSC will be inoperable. An alternate OSC has been established on-site and is fully operable." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0900 EST ON 03/08/13 FROM MICHAEL PEAK TO S. SANDIN * * * "This is an update to Event Notification 48628, dated December 27, 2012. "On March 8th, 2013, Fort Calhoun Station (FCS) will be entering a new phase of scheduled modifications to renovate and alter the interior configuration of its Technical Support Center (TSC). The TSC ventilation system will not be functional during this phase of modification. Combined with renovations, the primary TSC and OSC will be inoperable. An alternate OSC and TSC have been established. If the Emergency Response Organization is activated the alternate emergency facilities will be available for emergency responders per existing Emergency Plan procedures. "The project is scheduled to be completed April 12, 2013. An update to this report will be provided when the TSC renovation is complete." The licensee informed the NRC Resident Inspector. Notified R4DO (Werner). * * * UPDATE AT 1020 EDT ON 04/12/13 FROM DAVID ORTIZ TO P. SNYDER * * * "This is an update to Event Notification 48628, dated December 27, 2012. "As of April 12th, 2013 Fort Calhoun Station has completed modifications to the Technical Support Center (TSC) and Operations Support Center (OSC). The TSC ventilation system has been proved functional through required testing. The primary TSC/OSC is now fully operational." The licensee notified the NRC Resident Inspector. Notified R4DO (Deese). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-27
48627 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2012-12-25 09:37 | 2012-12-27 14:46 | 2012-12-27 | SAFEGUARDS SYSTEM DEGRADATION The licensee discovered a safeguards system degradation that could have allowed access to a controlled area for which compensatory measures were not employed. Contact the Headquarters Operations Officer for additions details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | NON-POWER REACTOR EVENT | [8 empty] | NON EMERGENCY | 1 | MA | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2012-12-27
48626 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-12-26 09:22 | 2012-12-26 15:56 | 2012-12-26 | RADIATION MONITOR USED FOR ASSESSMENT AND RESPONSE INOPERABLE DUE TO PRE-PLANNED MAINTENANCE "At 0922 on 12/26/2012, R-16, Service Water System Effluent Line Radiation Monitor (for Containment Fan Cooling service water) was removed from service for scheduled maintenance. R-16 is used for Emergency Action Level (EAL) classifications of an unplanned release of liquid radioactivity to the environment that exceeds the requirements of the Offsite Dose Calculation Manual for an Unusual Event and an Alert, and is therefore being conservatively reported under 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability. The maintenance was completed and R-16 restored at 1308 on 12/26/2012. "R-16 is also scheduled to be removed from service for calibration on 12/27/2012 from 0800 -1400 CST." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-26
48625 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-12-26 04:10 | 2012-12-26 04:13 | 2012-12-26 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed today (December 26, 2012) to the Technical Support Center (TSC) HVAC. The work entails removing power to the system fan and dampers to perform required preventative maintenance (PM) rendering the TSC HVAC non-functional during the performance of this work activity. This work activity is planned to be performed and completed expeditiously within about 16 hours including establishing and removing the clearance and performing post maintenance testing. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC concurrent with this work activity as long as habitability conditions allow. Additionally, plans are in place to expedite the return of the system should an emergency condition occur. The Emergency Response Organization duty team members will be relocated to alternate locations if required by habitability conditions in accordance with emergency implementing procedures. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM MARKO MALINEN TO CHARLES TEAL ON 12/27/12 AT 0810 EST * * * As of 2100 EST on 12/26/12 the TSC has been satisfactorily tested and returned to service. The NRC Resident Inspector has been informed. Notified the R1DO (Conte). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-26
48624 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-12-22 17:40 | 2012-12-22 20:51 | 2012-12-22 | OFFSITE NOTIFICATION DUE TO LOSS OF AMERTAP BALLS "At 1740 CST, Xcel Energy notified the Minnesota State Duty Officer that up to 1500 Amertap Balls had been lost from the Prairie Island Nuclear Generating Plant Unit 2 Condenser Tube Cleaning System. Since the Minnesota State Duty Officer for the Division of Emergency Management was notified, this constitutes a 4 hour non-emergency notification per 10CFR50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-12-22
48623 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-12-22 11:52 | 2012-12-22 16:39 | 2012-12-22 | AUTOMATIC REACTOR SCRAM DUE TO LOSS OF POWER TO THE REACTOR PROTECTION SYSTEM "On 12/22/2012 at 1152 CST, the Unit 2 reactor automatically scrammed due to actuation of the Reactor Protection System (RPS) from loss of power to RPS. At 1134 CST, the D 4kV Shutdown Board unexpectedly de-energized during performance of post-maintenance testing for the 3D Diesel Generator paralleling circuitry, resulting in loss of power to the 2B RPS subsystem. Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations were received along with automatic initiation of A, B, and C Standby Gas Treatment subsystems and A Control Room Emergency Ventilation subsystem due to loss of power to the 2B RPS subsystem. While attempting to reenergize the 2B RPS subsystem, the 2A RPS subsystem was inadvertently de-energized resulting in Unit 2 reactor automatic scram. "All affected safety systems responded as expected for the loss of RPS and reactor scram. Due to the loss of RPS, the Main Steam Isolation Valves (MSIVs) closed. Reactor pressure did not rise to the automatic initiation set point for Safety Relief Valve (SRV) actuation. Reactor Core Isolation Cooling System (RCIC) and High Pressure Coolant Injection System (HPCI) reactor water level initiation set point of -45" was reached and RCIC and HPCI automatically initiated as designed to restore water level above the initiation set point. Both Recirculation Pumps also tripped on reactor water level of -45". Reactor pressure control was established by manually operating one SRV and water level control established with RCIC. HPCI was returned to standby readiness. The scram was reset, MSIVs were opened, and the Main Condenser was established as a heat sink. "The scram event from critical is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B). It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector was notified." The 2A and 2B RPS subsystems were returned to service. The electrical grid is stable and supplying shutdown loads on Unit 2. Unit 1 and Unit 3 were unaffected and continue to operate at 100% power. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-12-22
48622 | 0 | TENNESSEE VALLEY AUTHORITY |  |  |  |  | 2012-12-20 | 2012-12-21 16:43 | 2012-12-21 | PART 21 REPORT - BELDEN WIRE USED ON ENVIRONMENTALLY QUALIFIED FORM-WOUND MOTORS NOT FULLY QUALIFIED "Potential Condition: Tennessee Valley Authority (TVA) Power Service Shops (PSS) installed Belden EPDM lead wire in the rewind of Environmentally Qualified (EQ) safety-related motors utilizing EPRI Technical Report (TR) 1003481 and TR 1001036. EPRI informed PSS that the Belden EPDM lead wire had not been fully qualified in accordance with EPRI TR 1001036. "Thirteen (13) motors are affected. Ten (10) Browns Ferry motors, one (1) Watts Bar Unit 2 motor, one (1) Progress Energy [Crystal River] and one (1) Florida Power & Light (FPL) [St. Lucie Plant] . All the customers have been notified of a potential Part 21 condition. "Recommendation: Immediate Actions: 1.) Review PSS data to determine affected motors. 2.) Establish an Equivalency Evaluation (EE) for Belden EPDM lead wire for EPRI TR 1003481/1001036 utilizing a TVA qualified winding system that included Belden EPDM lead wire (Wyle Test Report 18070-1). 3.) Review Progress Energy and FPL EQ profiles. 4.) Perform a root cause investigation to determine how this issue occurred. "Evaluation/Action Taken: 1.) Action 1 complete. 13 motors affected and all customers notified. 2.) Action 2 - EE developed and currently being reviewed by affected TVA EQ engineers for approval. 3.) Action 3 - FPL indicated that the FPL motor in question had undergone a recent rewind that replaced the lead. Progress Energy provided the EQ profile on 12/20/12 indicating a significant delta between the Wyle Test Report 18070-1 in Radiation (Normal), Radiation (Accident) and accident temperature (Max). Based on this information, the PSS determination was made that defect in a basic component existed and NRC notification was required in accordance with 10 CFR Part 21, section 21.21(d)(1) and section 21.21(d)(3)(i). "TVA PSS will provide a follow-up written notification within 30 days pursuant to Part 21.21(d)(3)(ii). "Point of Contact- Mark E. Cook, (256) 314-7595" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-12-21
48621 | 0 | ABB INC. |  |  |  |  | 2012-10-25 | 2012-12-21 16:27 | 2012-12-21 | DEFECT DISCOVERED IN COM-5 AND SSC-T PROTECTIVE RELAYS DISTRIBUTED BY ABB, INC. The following information was obtained by ABB, Inc. via fax: "ABB Coral Springs received notice from ABB Inc. in Florence, South Carolina of a return request by NextEra Energy (Point Beach Nuclear Plant) for one of [their] COM-5 relays. The customer complaint was identified as 'A pin on the telephone relay fell out'. "ABB Coral Springs received the relay on October 25, 2012 with the telephone relay armature and armature pivot pin disassembled. The assembly process for the telephone relay armature calls for the armature pivot pin to have a knurl at one end and a flare at the opposite end. The knurl and flare secures the armature to the pivot pin. [ABB's] investigation found that on this telephone relay, the pivot pin was flared on the same end as that which had the knurl. It was determined that this was due to an operator error while performing a secondary operation. "The telephone relay was stamped with a manufacturing date code 08-38, indicating the thirty-eighth week of 2008. It is important to note the date of manufacture, as in mid-2010 the supplier and the assembly manufacturing process of the pin was changed. The hole and flaring was changed such that it is performed prior to cutting the pin to length, eliminating the secondary operation and potential for error. "In addition to the change to the flaring process described above, corrective action includes the addition of an additional step to [ABB's] final Product Inspection procedure where all telephone relays are verified to have the knurl at one end of the armature pivot pin and a flare at the opposite end. "Inspection of [ABB's] stock identified no similar condition. "[ABB has] identified COM-5 and SSC-T relays which shipped that may have a telephone relay of the same vintage as that of the subject telephone relay. There were eleven orders shipped, totaling twenty-five units to three customers; ABB Inc. Florence, S.C., Exelon Business Services and WESCO Distribution, Inc.. ABB has determined that it does not have the capability to perform an evaluation to determine if a defect exists, and therefore in accordance with 10 CFR 21.21(b), [ABB is] notifying [their] affected customers so that they may evaluate the deviation or failure to comply, pursuant to 10 CFR 21(a). "A failure of the Telephone Relay to operate on either the COM-5 or SSC-T relay can result in the breaker not tripping during an overload condition. This condition could compromise the ability of the relay to perform its intended safety function. "[ABB is] providing [their] customers with the option of inspecting for evidence of the knurl and flare or returning the relays so [they] may perform the inspection." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-12-21
48620 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-12-21 07:30 | 2012-12-21 16:06 | 2012-12-21 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) "At approximately 0730 CST, Xcel Energy Prairie Island Nuclear Generating Plant was informed of a loss of internet and data services due to equipment problems with the Wide Area Network (WAN). The loss of data services resulted in the loss of ERDS communication capabilities with the NRC. "The WAN and ERDS were restored at 0921 CST." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-21
48619 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-12-21 09:00 | 2012-12-21 15:17 | 2013-01-17 | BOTH UNIT TWO AUXILIARY FEEDWATER PUMPS DECLARED INOPERABLE "21 Motor Driven and 22 Turbine Driven Auxiliary Feedwater Pumps (AFWP) were declared inoperable at 0900 CST on 12/21/2012 due to the Condensate Storage Tank (CST) temperature exceeding 92 degrees F. "In accordance with procedure C28.6, 'Condensate Storage Tank Freeze Protection System', the maximum CST temperature shall not exceed 92 degrees F. This is to ensure the maximum AFWP discharge temperature is less than 100 degrees F when an AFWP is at design flow per USAR Table 11.9-2, 'Summary of Assumptions,' used in the AFW system design verification analyses. "LCO 3.7.5 Condition D was entered for two AFW trains inoperable in Modes 1, 2 or 3. The AFWP's could start and run if required at the time of entry. "Immediate action was taken to reduce the CST temperature. At 1315 CST temperature were lowered below 92 degrees F and LCO 3.7.5 condition D was exited. "This condition is reportable per 10 CFR 50.72(b) (3) (v) (D) as an event or condition that could have prevented the fulfillment of a safety function." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM LOOSBROCK TO TEAL ON 1/17/13 AT 1412 EST * * * "This notification is being made to retract Event Notification (EN) #48619, which reported 21 Motor Driven and 22 Turbine Driven Auxiliary Feedwater Pumps (AFWP) were declared inoperable due to the Condensate Storage Tank (CST) temperature exceeding 92 degrees F. Based on engineering analysis the 92 degree F was a margin value with no formal basis or evaluation. This value was added to the C28.6 procedure in the early 1990's as a precaution to provide Operations with additional operating information. "After the 22 CST tank was found above the 92 degrees F temperature on 12/21/12, a formal engineering evaluation (EC 21354) was performed to determine CST heat values and provide an accurate number for temperature margin. The purpose of the CST tank temperature being at a specific value is to ensure that the AFWP discharge temperature stays at or under 100 degrees F to ensure the AF system can provide adequate decay heat removal if called upon during an accident. Engineering evaluation EC 21354 determined that the average CST tank temperatures could reach 96.5 degrees F before the AFWP discharge temperature could have reached 100 degrees F. Therefore, there was no loss of safety function or past operability concerns." "The NRC Resident Inspector has been informed." Notified R3DO (Bloomer). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-12-21
48618 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-12-21 07:30 | 2012-12-21 14:12 | 2012-12-21 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) "At approximately 0730 CST, Xcel Energy Monticello Nuclear Generating Plant was informed of a loss of internet and data services due to equipment problems with the Wide Area Network (WAN). The loss of data services resulted in the loss of ERDS communication capabilities with the NRC. Compensatory actions were established to communicate plant parameters verbally via the Emergency Notification System, which was verified functional at 0836 CST. "The WAN and ERDS were restored at 0921 CST and ERDS was verified functional at 0948 CST. "This issue is being reported as a loss of communications capability non-emergency event notification under 10CFR50.72(b)(3)(xiii) as defined in NUREG 1022, Rev. 2. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-21
48617 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-12-21 05:28 | 2012-12-21 07:06 | 2012-12-21 | UNIT 1 AUTOMATIC REACTOR TRIP ON TURBINE TRIP "Salem Unit 1 has experienced an automatic reactor trip at 0528 [EST] on 12/21/12. The unit tripped due to turbine trip above P-9 [Greater than 49% power]. All shutdown and control rods fully inserted on the reactor trip. Prior to the trip, the unit was operating at 100% when the crew received the OHA [Overhead Alarm] for main power transformer over excitation which actuated generator protection, which initiated the turbine trip. The auxiliary feed water (AFW) system auto started on low steam generator levels as expected on a reactor trip. Numbers 11, 12 & 13 AFW pumps all automatically started to provide feed to the steam generators. The [Operating Crew] entered EOP-Trip-1, then transitioned to EOP-Trip-2 and stabilized the plant. "The unit is currently in mode 3. The OCC [Outage Control Center] is manned and the cause of the main power transformer over excitation is under investigation at this time. RCS temperature is 547 degrees F, RCS pressure is 2235 psig. The 11-14 RCP's are in service. There is one shut down technical specification action statement in effect. Unit 1 containment APD [Containment Radiation Monitor] is inoperable for DCP [Design Change Package] work. This is a 30 day shutdown LCO that expires on 1/16/2013 at 0830. All ECCS and ESF systems are available. Decay heat removal is being provided by 11 and 12 AFW pumps and the main steam dump system. The 13 AFW pump operation is not required and has been removed from service. The plant is aligned with a normal electrical line-up from offsite power sources. There were no personnel injuries associated with this event "This event is reportable per 10CFR50.72(b)(2)(iv)(b) due to the automatic reactor trip. "This event is reportable per 10CFR50.72(b)(3)(iv)(a) due the AFW actuation on low steam generator levels." There was no lifting of PORVs or primary to secondary leakage. There was no impact on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-12-21
48616 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-12-20 16:00 | 2012-12-21 00:06 | 2013-02-07 | UNANALYZED CONDITION DUE TO AN IDENTIFIED DEGRADED FIRE BARRIER "During a walkdown on December 20, 2012 at 1600 CST, two degraded Appendix R fire barriers (walls) were identified. These barriers separate the Torus Room (Fire Area IV)/ 'A' RHR Room (Fire Area I) and the Torus Room (Fire Area IV)/ 'B' RHR Room (Fire Area II). The walls separate Appendix R fire safe shutdown divisional equipment. "A fire watch was established as a compensatory measure immediately following identification of the issue on December 20, 2012. The barrier affecting the 'B' RHR Room has been repaired on both sides. The barrier affecting the 'A' RHR Room has been repaired on the Torus Room side. The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10CFR50.72(b)(3)(ii)(B). "The fire watch remains in place until verification of the completed repair is performed." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1746 EST ON 2/07/13 FROM JACK EARSLEY TO HUFFMAN * * * "An eight hour report per 10 CFR 50.72(b)(3)(ii)(B) was conservatively reported on December 21, 2012 for degraded fire barriers between the Torus Room (Fire Area IV) and 'A' RHR Room (Fire Area I), and the Torus Room (Fire Area IV) and 'B' RHR Room (Fire Area II). Subsequent engineering analysis determined that the degraded fire barriers maintained the required degree of separation for redundant safe shutdown trains and plant safety was not significantly degraded. The 10 CFR 50.72(b)(3)(ii)(B) report is retracted." The licensee will notify the NRC Resident Inspector. Notified R3DO (Kunowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-12-21
48615 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2012-10-25 21:08 | 2012-12-20 14:07 | 2012-12-20 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID ACTUATION OF THE ESSENTIAL SPRAY POND SYSTEM "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This telephone notification is being made pursuant to the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) and 50.73(a)(1) to describe an invalid actuation of the Palo Verde Nuclear Generating Station (PVNGS) Unit 2 essential spray pond system (SP) which serves as the ultimate heat sink as described in 10 CFR 50.73(a)(2)(iv)(B)(9). "On October 25, 2012, at approximately 2108, Mountain Standard Time, during refueling outage 2R17, Unit 2 experienced an invalid actuation of the train B essential spray pond system. Testing of the train B engineered safeguards features actuation system (ESFAS) was in progress. During the test, following activities to reset the train B containment spray actuation signal (CSAS), the procedure required a check of contact status on a relay contact which provides input to the train B Load Sequencer. The guidance required the use of a digital multi-meter to perform the contact status check. When the digital multi-meter test leads were landed and removed from the circuit, the train B Load Sequencer changed output modes which resulted in automatic starting of the train B essential chilled water system, essential cooling water system, essential fuel building air filtration unit and essential spray pond system. "This was a partial actuation of the train B ESF equipment and all the affected equipment responded as designed. No equipment failures resulted from the event. The event was entered into the PVNGS corrective action program. The invalid actuation was caused by an incorrect testing methodology in the procedure instructions which resulted in the unintended interaction of the digital multi-meter and the digital train B Load Sequencer. The inadequate procedures will be revised to modify the testing methodology for verification of relay contact status." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-20
48614 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2012-12-19 15:00 | 2012-12-20 13:46 | 2012-12-20 | MARYLAND AGREEMENT STATE REPORT - IRRADIATOR SOURCE CHAIN FAILED TO FUNCTION The following information was obtained from the State of Maryland via fax: On December 19, 2012 at 1500 EST, the licensee's irradiator chain became "kinked" and failed to function as required. The sources were being raised at the time of the incident. The chain was de-kinked from around the sprocket and the elevator/sources were returned to their lowest position in the pool. The sources will remain stored at the lowest position until an internal investigation determines the cause of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2012-12-28
48613 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-12-18 | 2012-12-20 12:21 | 2012-12-20 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following information was received via email from the Illinois Emergency Management Agency: "On December 19, 2012 this general license registrant called to advise that a shutter on one of their process gauges had failed. The registrant had discovered the failure as a result of conducting their routine 6-month safety checks of the device. A makeshift shield was placed over the beam opening following the manufacturer's instructions, pending repair. Arrangements were made to have a field engineer from the company come to the site the next day to replace the shutter. No exposures to operating personnel were reported due to the circumstances of the gauge installation and low activity of the source involved. "Source/Radioactive Material: SEALED SOURCE GAUGE "Radionuclide: AM-241, 0.025 Ci, 0.925 GBq "Manufacturer: QSA GLOBAL "Model Number: AMC.P6 "Serial Number: 7734AR" Illinois Item Number: IL12018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-12-28
48612 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2012-11-27 | 2012-12-20 10:17 | 2012-12-20 | PART 21 REPORT INVOLVING PERFORMANCE OF NPT STAMPED CAVITROL III PLUGS AT CATAWBA NUCLEAR STATION The following report was received via fax: "Fisher Information Notice: FIN 2012-05 19 December, 2012 "Subject: Instrument & Valve Services Company (Columbia, South Carolina location), Job 400000838 for Duke Energy Carolinas, LLC Catawba Nuclear Station "From: Chad Engle Nuclear Business Unit Director Fisher Controls International LLC 205 South Center Street Marshalltown, IA 50158 Fax: (641) 754-2854 "Equipment Affected By This Information Notice: Items provided solely to Duke Energy Carolinas, LLC Catawba Nuclear Station per Instrument & Valve Services Company (Columbia; South Carolina location) Job 400000838 (Duke Energy Carolinas, LLC Catawba Nuclear Station PO 00161159). Specifically, the affected parts are two hard faced NPT stamped Cavitrol III plugs, piece serial numbers 400838-1-2A and 400838-1-3A (part number 24A3784X152). "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert Duke Energy Carolinas, LLC Catawba Nuclear Station (Duke) that as of 27 November 2012, Fisher Controls International LLC (Fisher) became aware of the possibility of a situation which may affect the performance of the aforementioned equipment. Out of an abundance of caution, Fisher is informing you of this situation in accordance with Section 21.21 (b) of 10CFR21. "Applicability: This FIN applies only to the subject equipment supplied by Fisher, as identified above, provided to Duke pursuant to PO 00161159 and affects no other materials provided to Duke or any other utility. "Discussion: It was determined by Fisher that two hard faced NPT stamped Cavitrol III Plugs, piece serial numbers 400838-1-2A and 400838-1-3A, were delivered to Duke after being repaired by a welder that, at the time of shipment, was not qualified in accordance with ASME B&PVC Section IX for the base metal thickness welded to affect the repair. Upon discovery, Duke was notified and segregated the affected parts for return to the Instrument & Valve Services Company's Columbia, South Carolina location. "Action Required: Duke has returned the parts to Instrument & Valve Services Company's Columbia, South Carolina location. The parts have been labeled as nonconforming and have been segregated. The welder involved has subsequently successfully completed a welding qualification test meeting the requirements of ASME B&PVC Section IX (such testing included the base metal thickness applicable to the affected equipment). The welder qualifications and the nonconformance report will be submitted to the ANI and to Duke for review and approval. Fisher is completing a Corrective Action Report to prevent a similar situation from reoccurring in the future. "10CFR21 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21. If there are any technical questions or concerns, please contact: Guy Scaggs Quality Manager Instrument & Valve Services Company 757 Old Clemson Road Columbia, SC 29229 Fax: (803) 736-3105 Phone: (803) 736-3101 Guy.Scaggs@emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-12-20
48611 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-20 07:35 | 2012-12-20 09:22 | 2012-12-20 | LOSS OF ASSESSMENT CAPABILITY - RADIATION MONITORS INOPERABLE FOR PRE- PLANNED MAINTENANCE "This is a non-emergency notification. At 0735 [EST] on December 20, 2012, radiation monitors RM-1CR-3561A, RM-1CR-3561B, RM-1CR-3561C and RM-1CR-3561D, Containment Ventilation Isolation Radiation Monitors, were declared inoperable for preplanned maintenance. These monitors are the only monitors credited in the EALs for monitoring elevated radiation levels inside containment for irradiated fuel. "These radiation monitors are necessary for accident assessment and are credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to these monitors being out of service is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health or safety of the public or the operation of the facility. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-20
48610 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-12-20 07:51 | 2012-12-20 07:51 | 2012-12-20 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT-OF-SERVICE "Computer engineering personnel will be taking the plant integrated computer system (ICS) out-of-service for planned maintenance. During the time ICS is out-of-service, the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) will be unavailable. The computer outage is scheduled for six hours. "Contingency plans have been established to transmit plant parameter data and perform the dose assessment function in the event of an emergency while ERDS is unavailable. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). A follow-up notification will be made when the maintenance activities are complete and the equipment is restored." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JIM CASE TO HOWIE CROUCH AT 1309 EST ON 12/20/12 * * * At 1300 EST, the plant integrated computer system was restored and SPDS and ERDS was returned to service. Notified R3DO (Cameron) and ERDS Group email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-20
48609 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-08-01 | 2012-12-19 11:31 | 2012-12-20 | AGREEMENT STATE REPORT- COMPOSITE LISTING OF MISSING GENERAL LICENSED DEVICES The following fifty-four (54) lost licensee tritium signs were submitted by the State of Colorado via email: 1. American Soda LLP; (2) Isolite; Model 2040; S/N A081034 and A081076; H-3; 11500 mCi/each 2. Beaudrey American Services; (2) Isolite; Model SLX60; S/N Unknown; H-3; 6200 mCi/each 3. Boulder Manor; (8) SRB Technologies; Model BR20BK; S/N 659038 to 659039 and 659066 to 659067; H-3; 17800 mCi/each 4. Carquest; (4) Best Lighting Products; Model SLXTU1RW10; S/N Unknown; H-3; 7030 mCi/each 5. GE Johnson; (1) Safety Light; Model 880-12-6; C27200; H-3; 7500 mCi 6. Grace Management; (2) Isolite Corporation; Model SLX60; S/N 14610; H-3; 3750 mCi/each 7. Hampton Inn; ; (14) SRB Technologies; Model BXU10GS; S/N Unknown; H-3; 9210 mCi/each 8. Industrialex MFG Co; (1) NRD Inc.; Model P-2021; S/N A2HL117; PO-210; 10 mCi 9. Kinder Morgan; (4) Isolite; Model SLX60; S/N Y24490-Y24493; H-3; 7500 mCi/each 10. New Belgium Brewing; (1) Shield Source Inc.; Model SLX; S/N10-29211; H-3; 6200 mCi 11. Old West Management; (1) Isolite; Model 2040; S/N Unknown; ; H-3; 7000 mCi 12. Platt River Power Authority; (4) SRB Technologies; Model BX15WH; S/N CO12440-12443; H-3; 9210 mCi/each 13. Sisters of St. Francis; (1) Isolite; Model 2040; S/N Unknown; H-3; 7500 mCi 14. Wild Oats Markets Inc.; (1) NRD Inc.; Model T-4001; S/N Unknown; H-3; 6700 mCi 15. Wynkoop Building LLC; (8) Safety Light; Model 8801206; S/N 432968 to 432975; H-3; 7500 mCi/each THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2013-01-10
48608 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-19 19:35 | 2012-12-19 20:55 | 2012-12-19 | GROUNDWATER SAMPLES INDICATE ELEVATED TRITIUM LEVELS "On December 19, 2012, results from routine monitoring of groundwater at Plant Hatch indicated tritium was detected above historical background levels at two sample points on site. Additional samples were taken from the same points and analysis confirmed that tritium was present at elevated levels in both samples and that tritium had not migrated out of the general area of initial discovery. Immediate actions are being taken to locate the source of the leak and actions are in progress to stop the leak. The investigation currently shows that the tritium is confined to a small area on the plant site in the vicinity of the Unit 1 Condensate Storage Tank (CST), and there is no significant potential for off-site impact. Additionally, there is no impact to on-site personnel. No tritium levels above background have been detected or migrated outside the area where the two sample points are located. "Southern Nuclear [SNC] will continue to sample strategic locations in the ground water monitoring network to determine if there are changes in the impacted area and beyond. SNC is confident that these levels are of low safety significance and do not pose any issues to the public health and safety. "In accordance with SNC's groundwater protection procedures and the Nuclear Energy Institute (NEI), SNC contacted the NRC Region II Resident Inspector and will be notifying the State of Georgia Environmental Protection Division and other agencies to inform them of this matter." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-12-19
48607 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-19 17:31 | 2012-12-19 20:29 | 2012-12-19 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR PRESSURE VESSEL LEVEL "At approximately 17:31 hours on December 19, 2012, Susquehanna Steam Electric Station Unit Two reactor automatically scrammed on low RPV level (Level 3, +13 inches) while transitioning the 'A' reactor feed pump from discharge pressure mode to flow control mode. "All control rods inserted and both reactor recirculation pumps tripped. Reactor water level lowered to approximately -29 inches causing Level 3 (+13 inches) isolations. An automatic trip of the reactor recirculation pumps occurred, but is not expected at this RPV level. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected. The cause of the loss of feed water flow and trip of the reactor recirculation pumps is under investigation. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a 4 hour report, and 10CFR50.72(b)(3)(iv)(A) for an 8 hour report." Decay heat is removed via steam to the main condenser using the bypass valves . On-site electrical power is in the normal configuration. The Unit 2 reactor is currently stable in Mode 3. Unit 1 was not affected and operates at 99% power. The licensee will inform the Commonwealth of Pennsylvania and make a press release. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-12-19
48606 | -1 | US GEOLOGICAL SURVEY |  |  |  |  | 2012-11-20 15:07 | 2012-12-19 14:17 | 2013-02-27 | POTENTIAL LOST OR STOLEN C-14 SOURCE The licensee is reporting approximately 1.35 mCi of C-14 in liquid form that is missing from it's Menlo Park facility. On March 18, 1991, it was reported by the licensee to the Menlo Park Radiation Safety Committee that they had in their possession 9.3 mCi of C-14 which exceeded their maximum possession limit for their permit. At the time they recorded that, they had ordered, or logged as ordered, 5 mCi and 0.25 mCi of C-14. However, the licensee could not find any records that those isotopes had been actually received. The RSO believes that the cause of the discrepancy between the quantity they actually have on-hand and the quantity that should be in inventory, as indicated by records, is due to a bookkeeping error. On November 7, 1990, the records show that they transferred 1.725 mCi which would leave a balance of 2.171 mCi. This transfer does not show up on the records until August 20, 1991. The quantity was adjusted on the record to 2.173 mCi. They believe that back in 1991 they misreported the amount of Carbon-14 that they actually had in inventory and the error was carried forward. The licensee is going to start doing physical inventories of all isotopes on a 6-month basis as a corrective action. * * * RETRACTION FROM HENDRICKSON TO SNYDER AT 1658 ON 2/27/13 * * * This report was made due to an inventory error. This is event is retracted. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2013-01-03
48605 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-12-19 08:00 | 2012-12-19 08:54 | 2012-12-19 | PLANNED MAINTENANCE AFFECTING THE ABILITY TO ASSESS AN EMERGENCY CLASSIFICATION "Voluntary ENS Notification Regarding Maintenance Affecting the Ability to Assess an EAL Classification. "Kewaunee Power Station (KPS) is preparing to perform routine planned calibrations on Wednesday, December 19, and Thursday, December 20, 2012, on the forebay level indication. This maintenance will impact the forebay level computer and Control Room indication normally used to make the Unusual Event or Alert emergency classifications in the event the lake or forebay threshold is exceeded for greater than 15 minutes. "The maintenance is planned to occur from 0800 [CST] on 12/19/12 until 1230 [CST] on 12/20/12. There are four level transmitters each with local indication. Each transmitter will be calibrated, but only one at a time, so that the capability to locally determine forebay level using the other three transmitters will remain. "This activity has been evaluated against the requirements of 10 CFR 50.72(b)(3)(xiii) and it has been determined that the condition does not rise to the significance necessitating an event notification since Kewaunee retains the capability to make the necessary emergency classifications. However, this information is being conservatively provided so that NRC may be aware of the condition should an emergency develop." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-19
48604 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-12-17 15:50 | 2012-12-18 15:54 | 2012-12-18 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION FOUND ON PACKAGE The following was received from the State of California via fax: "On December 17, 2012, UCSB (University of California, Santa Barbara) received an excepted package from Germany containing Carbon 14, 53.2 MBq in liquid form (2 vials each 1.4 mLs) which had removable contamination in excess of 49CFR, Section 173.443, on the outside of the package. The package and inner package did not show signs of damage. Wipes were taken on the outside of the box (4 sides and bottom) using filter paper and wiping 100 cm squared. Vials were placed into a 20 mL vial containing 15 mLs of liquid scintillation cocktail. Vials were then counted on a Beckman LS6000LL, liquid scintillation counter for 2 minutes. All areas of the box were found to be contaminated, with the highest removable contamination at 32,000 dpm/cm squared. The licensee reported this event via CA EMA and notified the final delivery carrier and the company that shipped the package (Sanofi, Frankfort, Germany). Of note, there was a note on the shipping paperwork that when the box arrived at LAX, it was opened by World Carrier personnel to replenish dry ice prior to then transporting it onto the UCSB." CA 5010 #: 121712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-12-26
48603 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-12-18 14:36 | 2012-12-18 14:36 | 2012-12-20 | PARTIAL LOSS OF EMERGENCY ASSESSMENT DURING PLANNED MODIFICATIONS "Calvert Cliffs Nuclear Power Plant will begin a planned modification of the Unit 1 and Unit 2 Plant Process Computers (PPC's) and associated network infrastructure on December 18, 2012. This includes the Emergency Response Data System (ERDS) communication with the NRC Operations Center. This work will require the TSC, OSC and subsequently EOF to lose data flow from the plant data network for a period of approximately 36 hours. During this time, the following systems will be impacted for the duration of maintenance: 1. ERDS will be out of service. 2. Plant Data will not reach the TSC and OSC from the plant data network. 3. TSC Computer data transfer to the EOF only will be out of service. 4. Chemistry DAS remote monitoring capability will be lost. 5. Plant parameter data will not be available on the site's LAN network. "Once the schedule maintenance starts, the systems (listed above) can be returned to service within 1 hour. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. Control Room Emergency response personnel will use emergency response procedures (ERPIP 106) to disseminate plant parameter data to the effected Emergency Response Facilities. MIDAS (Meteorological Data) will continue to be operational at the site. Compensatory measures exist within the Calvert Cliffs Emergency Response procedures to provide plant data in the event of an actual Emergency to the NRC Operations Center until the ERDS can be returned to service." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BRIAN HAYDEN TO S. SANDIN ON 12/20/2012 AT 1035 EST * * * On 12/20/2012 at 0200 EST, the plant process computer and associated network infrastructure was restored to service. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Hunegs). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-18
48602 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-12-11 | 2012-12-18 12:03 | 2012-12-18 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT The following was received from the State of Mississippi via email: "Licensee's RSO contacted DRH (Division of Radiation Health) by telephone on December 11, 2012 to inform the department that a source retrieval was done earlier that morning on exposure device S/N D2652 source S/N 88902B. This was due to a unsecured exposure device falling to the ground from a valve assembly handle it was place on while performing an exposure. When the radiographer tried to crank the source back into the exposure device he noticed a crimp in the guide tube close to the camera. The radiographer then cranked the source back out to the collimator to provide more shielding and then contacted the RSO for source retrieval. The RSO performed the source retrieval within two hours of being called. The RSO received a dose of 32 mR for the retrieval." Mississippi Report #: MS-12006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-12-26
48601 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-10-20 19:20 | 2012-12-18 11:20 | 2012-12-18 | 60 DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 1920 on October 20, 2012, with the Duane Arnold Energy Center (DAEC) shut down for a preplanned refueling outage, an invalid Group 3 isolation on the 'A' side of the Primary Containment Isolation System occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by failed components in the power supply circuitry for the 'A' Refuel Floor Exhaust Radiation Monitor. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-18
48600 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-12-17 18:04 | 2012-12-18 02:07 | 2012-12-18 | PLANT VENT CONTINUOUS RADIATION MONITORS INOPERABLE "This is a non-emergency notification. At 1804 PST on December 17, 2012, Diablo Canyon Unit 1 experienced a loss of plant vent continuous radiation monitors (RM) and redundant monitors 14/14R, 24/24R, 28/28R and 87. These radiation monitors are credited for Emergency Action Level (EAL) classification in the Diablo Canyon Emergency Plan. This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. Compensatory measures of periodic sampling have been established in accordance with plant equipment control guidelines. Event classification can be performed by means of the sampling in accordance with plant procedures. Additionally, continuous radiation monitoring of the plant vent remains via high range radiation monitor RM-29. "The cause of the loss of radiation monitors is not known at this time. "This condition does not affect the health and safety of the public or the operation of the facility. "The NRC Resident Inspector was informed." * * * UPDATE AT 0948 EST ON 12/18/12 FROM DAVE GOUVEIA TO HUFFMAN * * * The licensee determined that the flow element on the sampling pump for the radiation monitors had failed. At 0630 EST, the condition was repaired and the radiation monitors returned to service. R4DO (Whitten) notified. | 54 | 0 | 0 | 54 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-18
48599 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2012-12-14 | 2012-12-17 10:35 | 2012-12-17 | AGREEMENT STATE REPORT - MISSING CARBON-14 VIAL The following information was received via facsimile from the Maryland Department of Environment: "In compliance with COMAR 26.12.01-01 (Section D-1201.a), Wildlife International, Ltd. is reporting the loss of 1 mCi of Carbon-14 source material. As per the originator, the radioactive material was shipped to Wildlife International, Ltd. as one shipment containing two vials (each vial contained 1 mCi). However, only one vial was received in the Wildlife International, Ltd facilities, swiped and placed in the Wildlife International, Ltd. inventory. Wildlife International, Ltd. is currently investigating the circumstances of the missing/loss Carbon-14 material, coordinating documents and, shipping procedures with the originator and conducting exhaustive searches of the Wildlife International, Ltd. facilities for its recovery." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2012-12-25
48598 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-16 01:56 | 2012-12-16 04:39 | 2012-12-16 | REACTOR SCRAM FROM 98% POWER DURING TURBINE CONTROL VALVE TESTING "At approximately 01:56 hours on December 16, 2012, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed while performing testing of the number 2 control valve per the station surveillance testing program. The number 2 control valve closure initiated a 1/2 scram in the reactor protection system as designed; specifically the 'B1' channel. Evaluation of plant data indicates that an 'A' scram channel signal was activated during the time period the number 2 control valve scram signal was active, thereby causing a full reactor scram. The cause of the 'A' scram channel signal is not understood at this time and is under investigation. "A second reactor scram signal was received at approximately 02:10 hours due to reactor water level lowering to 13 inches. Reactor water level was restored above the trip setpoint. All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -48.5 inches causing Level 3 (+13 inches) and level 2 (-38 inches) isolations. "HPCI and RCIC both automatically initiated and were overridden by control room operators after water level was restored. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "This report is being made per 10 CFR 50.72(b)(2)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B) for 4 hour reports, and 10 CFR 50.72(b)(3)(iv)(A) for an 8 hour report. "The unit 2 reactor is currently stable in Mode 3. An investigation into the cause of the reactor scram is underway. "Unit 1 continued power operation. "The NRC resident inspectors were notified. A press release will occur." The licensee will be notifying the State authorities. | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2012-12-16
48597 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-15 07:34 | 2012-12-15 10:18 | 2012-12-15 | TECHNICAL SUPPORT CENTER COOLING FAN INOPERABLE "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 based on 'Loss of Response' capability. "This is a non-emergency notification. At approximately 0734 EST on 12/15/2012 AH-17, the Technical Support Center (TSC) Cooling Fan was found exhibiting no flow. The cause of the no flow condition was a broken fan belt. Repairs are being planned and will be worked immediately. "TSC functionality requires all areas of the TSC be maintained between 50 degrees F and 86 degrees F. The actual TSC area temperatures range from 59 degrees F to 67 degrees F. "Should the TSC need to be activated for an event, . . . compensatory measures are in place to consider relocating the TSC to the Alternate Emergency Facility per PEP-240. This decision would he based on the existing event conditions and coordinated with the Emergency Response Manager, SEC-MCR, and Radiological Control Manager." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-15
48596 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-14 13:06 | 2012-12-14 17:43 | 2012-12-14 | CONTROL BUILDING EMERGENCY VENTILATION SYSTEM INOPERABLE FOR TWO MINUTES "At approximately 1306 hours Eastern Standard Time (EST), Brunswick Nuclear Plant lost the operability of both trains of Control Building Emergency Ventilation (CREV) for approximately two minutes. This is reportable per 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. "At the time of the event, Brunswick was implementing a modification to upgrade its control building fire detection. In support of short duration circuitry work on the detectors, CREV train A was placed in service manually in compliance with the Technical Requirements Manual (TRM). This action prevents an auto-start of the opposite CREV train B, and thus Technical Specification (TS) 3.7.3 Condition A was entered to restore CREV train B to service within 7 days. "During work to electrically isolate ('jumper') one of the fire detectors associated with CREV train A fire protection, electrical continuity was lost. This caused the detector to fail safe, sending an internal charcoal fire signal to the CREV train A circuitry and shutting it down. With CREV train A shut down due to the signal, TS 3.7.3 Required Action C.1 applied for both CREV trains inoperable, requiring both Units to be in Mode 3 in 12 hours. Actions were taken to immediately re-establish the circuitry, which re-started CREV train A, and TS 3.7.3 Required Action C.1 was exited. "This condition did not result in any adverse impact to the health and safety of the public. "The safety significance of this event is considered minimal. The CREV function was only inoperable for approximately two minutes. Though considered inoperable, CREV train B remained available and could have been placed in service at any time by alternating the train A and train B control switches." The licensee has notified the NRC Resident Inspector. | 100 | 93 | 0 | 100 | 93 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-12-14
48595 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-12-14 13:50 | 2012-12-14 15:00 | 2012-12-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - CONTROL STRUCTURE CHILLERS INOPERABLE "At 1350 on 12/14/2012, both Control Structure Chillers at Susquehanna were rendered inoperable. This event required entry into Tech Spec 3.0.3 for both Units. Per Susquehanna procedures, after 1 hour, a power reduction must be commenced. Tech Spec 3.0.3 requires that action be taken within one hour to place the Unit in Mode 3 within 13 hours and Mode 4 within 37 hours. "Physical power reduction commenced at 1453 for Unit 1 and 1459 for Unit 2. "The 'A' Control Structure Chiller was previously inoperable for routine maintenance. The system was in service for post maintenance testing and activities were underway to swap to the opposite train to allow removal of test instrumentation and fan belt tensioning for equipment associated with the 'A' Control Structure HVAC system. At 1350, the 'B' Control Structure loop circulating pump tripped, rendering the 'B' Control Structure Chiller inoperable. "This condition requires immediate entry into Tech Spec 3.0.3. Both Control Structure Chillers are inoperable and this report is being made per 10CFR50.72(b)(2)(i) as a shutdown required by Tech Specs, and 10CFR 50.72(b)(3)(v)(D), Loss of a Safety Function required to mitigate the consequences of an accident. "Efforts are underway to restore at least one system to operable status in parallel with Unit shutdown activities." The licensee has notified the NRC Resident Inspector, and will be notifying the State of Pennsylvania. * * * UPDATE FROM ALEX MCLELLAN TO JOHN KNOKE AT 2228 EST ON 12/14/12 * * * "On 12/14/12 at 1500 EST Susquehanna Steam Electric Station reported a shutdown had been commenced at 1453 EST for Unit 1 and 1459 EST for Unit 2 due to inoperability of both Control Structure Chillers. At 1750 EST the 'A' Control Structure Chiller was declared operable and LCO 3.0.3 was exited. Power reduction for both Units was halted at 1750 and preparations for power restoration initiated. On 12/14/12 Unit 1 power was restored to 98% at 1819 EST and Unit 2 power was restored to 98% at 1943 EST, the maximum power output possible based on grid conditions for Unit 1 and thermal limits for Unit 2." The licensee has notified the NRC Resident Inspector. R1DO (Holody) notified. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-12-14
48594 | 0 | METALTEK INTERNATIONAL CARONDELET |  |  |  |  | 2012-12-14 08:45 | 2012-12-14 14:11 | 2012-12-14 | RADIOGRAPHY GUIDE TUBE DAMAGED DURING USE While performing radiography operations at the Metaltek facility, the stand that the guide tube was resting on fell over and damaged the guide tube. The source was not able to be retrieved. A licensed source retrieval contractor was utilized and the source was restored to its safe position. There were no overexposures to personnel as a result of this event. The radiography camera was a QSA Amersham model number A-424-14, serial number 39841B. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-12-24
48593 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-10-30 | 2012-12-14 12:41 | 2012-12-14 | MEDICAL EVENT INVOLVING PERMANENT PROSTATE BRACHYTHERAPY IMPLANT The following was received from the Commonwealth of Kentucky via email: "During a prostate implant the radiation oncologist and urologist encountered issues due to the prostate size, location and pubic arch. Some of the needles became bent during the procedure and the decision was made to abort the implant. While completing the procedure the radiation oncologist revised the written directive to reflect what had occurred and revised the prescribed dose based on the complications." The patient received 64.51% of the intended dose. The procedure used 14 seeds manufactured by IsoAid with an activity of 0.350 mCi of I-125. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-12-24
48592 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-11-27 | 2012-12-14 11:00 | 2012-12-14 | AGREEMENT STATE REPORT - UNDERDOSE TO PRESCRIBED TREATMENT LOCATION FOLLOWING A BRACHYTHERAPY TREATMENT The following information was provided via e-mail from the State of Ohio Bureau of Radiation Protection: "At 3:10 PM on Dec 13, 2012 the licensee RSO called the Ohio Department of Health Bureau to report a medical event involving a prostate seed underdose. "A prostate seed implant procedure performed on 11/27/2012 was found to have failed the prescribed dose-volume criteria via post-implant CT performed on 12/10/2012. The target prescription was 160 Gy to the prostate. The patient was implanted with 88 Iodine-125 seeds with a total activity of 33.44 mCi (0.38 mCi / seed). The post-implant dosimetry was shown to have a D90 of ~40% of the prescription dose with a number of seeds outside of the prostate. The actual implanted activity in the prostate gland was 27.36 mCi. Sixteen seeds were found in the perineum outside the target volume of the prostate + 1 cm as PTV. The dose to this area unintended to receive radiation was about 20Gy to the periphery of the contour volume containing all the 16 seeds. "The physician was informed of the discrepancy on 12/12/2012 and the patient was informed on 12/13/2012. There is no negative impact expected to the patient, the physician indicates. The patient will be re-implanted to correct for the D90 discrepancy. "The Bureau of Radiation Protection will be sending an inspector the week of December 17 to investigate the incident." Ohio Report Reference Number: 2012-040 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-12-24
48591 | 0 | SHAW/AREVA MOX SERVICES, LLC |  |  |  |  | 2012-10-18 | 2012-12-14 09:18 | 2016-01-07 | PART 21 REPORT INVOLVING NONCONFORMING WELDS ON A PELLET HANDLING TRANSFER GLOVE BOX The following information was provided by Shaw/AREVA via fax: (i) Name and address of the individual or individuals informing the Commission. "Kelly D. Trice President and Chief Operating Officer Shaw AREVA MOX Services Savannah River Site P.O. Box 7097 Aiken, SC 29804-7097 (ii) Identification of the facility, the activity, or the basic component supplied for such facility which fails to comply or contains a defect. "The Mixed Oxide Fuel Fabrication Facility is addressing nonconforming welds and a weld process associated with the procurement of a pellet handling transfer glove box PML*GB100C. (iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "The pellet handling glove box is being supplied to MOX Services as a basic component by Flanders CSC. (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "PML*GB100C has a total of 32 welds that will need repair which will require adding additional fillet welds on top of the current weld such that the weld is large enough to satisfy structural requirements. Each weld will have to have at least a 3mm fillet weld added. Adding these additional welds will most likely have to be applied in two or three weld passes per location to create the needed weld dimension. "The boss was attached to the glove box using a fillet weld on top (Outer) and a single bevel weld on the inside. This does not allow for complete joint penetration between the fillet and bevel welds resulting in a weld with incomplete fusion. weakening the joint significantly and creating the possibility for high stress concentration areas in the weld joint. "Furthermore, using the GMAW (Gas Metal Arc Welding) short circuit arc process in this joint design produces a joint that cannot be counted on to carry load. When the GMAW short circuit arc weld process is used on material of ¬" or less in thickness, it allows for adequate heat to be transferred into the material to provide proper fusion of the filler material into the base material. When using the GMAW short circuit arc weld process on material over ¬", the mass of the base material results in a heat sink that is too large for the process to adequately fuse the filler material with the base material creating a weld that looks acceptable but could fail under small loads. In the PML boxes, these bosses support internal equipment and also support the glove box itself. Under this condition during a seismic event, the bosses could break away from the glove box shell breaking the confinement boundary as well as the flanges on each end, possibly causing the box to fall which could affect its static confinement barrier safety function. An additional seventeen glove boxes previously received are being reviewed for similar issues. (v) The date on which the information of such defect or failure to comply was obtained. "The deviation was identified in a non-conformance report on October 18, 2012. (vi) In the case of a basic component which contains a defect or fails to comply. the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "MOX Services does not possess information as to whether other facilities have been supplied a similar basic component by Flanders CSC. (vii) The corrective action. which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "Non-Conformance Report NCR 12-4583 will disposition the repairs associated with Flanders glove box PML* GB100C. MOX Services will ensure repairs are performed by either the vendor, MOX Services or a third party. These repairs will be performed in support of the construction schedule. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "None. (ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "This is not an early site permit concern." * * * UPDATE ON 1/7/16 AT 0921 EST FROM DOUG YATES TO DONG PARK * * * The following information was provided by CB&I AREVA MOX Services via fax: (i) Name and address of the individual or individuals informing the Commission. "David Del Vecchio President and Project Manager CB&I AREVA MOX Services Savannah River Site P.O. Box 7097 Aiken, SC 29804-7097 (ii) Identification of the facility, the activity, or the basic component supplied for such facility which fails to comply or contains a defect. "The Mixed Oxide Fuel Fabrication Facility is addressing the discovery of foreign liquid within the structural tube steel frames of ball milling gloveboxes NBX*GB1000 and NBY*GB1000. (iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "Ball milling gloveboxes NBX*GB1000 and NBY*GB1000 were being supplied to MOX Services as a basic component by Flanders CSC. (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "Ball milling gloveboxes NBX*GB1000 and NBY*GB1000 were two of the seventeen additional gloveboxes that were identified in a December 14, 2012 Part 21 Report issued by MOX Services due to use of an incorrect welding process (Gas Metal Arc Welding) for certain welded connections during glovebox fabrication. "During weld repairs associated with the earlier Part 21 report, MOX Services' third party vendor discovered foreign liquid trapped within a portion of the tube steel frames of the NBX and NBY gloveboxes. The foreign liquid and dried substances (remnants of the original fabrication processes) were determined to contain contaminates not allowed to be present during welding operations. Due to the presence of contaminants potentially in the vicinity of most of the structural weld heat affected zones, MOX Engineering determined it necessary to metallurgically examine, through additional sampling, some of these welds in order to obtain reasonable assurance the welds can perform their design function. However, MOX Services has concluded that removal of these welds as part of the sampling process would damage the structure of these GBs beyond practical repair. Therefore the decision was made to rebuild these gloveboxes rather than sample the welds to determine their adequacy. "Although the NBX and NBY gloveboxes were part of the earlier 2012 Part 21 report, they are being reported as a defect herein because of the indeterminate nature of the glovebox welds and associated potential degradation of the gloveboxes confinement function. This functional degradation would not result from use of an improper weld process as identified in the earlier report but instead would result from the lack of maintaining cleanliness controls during fabrication. (v) The date on which the information of such defect or failure to comply was obtained. "Information related to the foreign liquid sampling was provided to MOX Services on November 12, 2015. (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "MOX Services does not possess information as to whether other facilities have been supplied a similar basic component by Flanders CSC. (vii) The corrective action, which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "It is anticipated that ball milling gloveboxes NBX*GB1000 and NBY*GB1000 will be rebuilt rather than continuing with repairs by MOX Services' third party vendor. MOX Services anticipates that rebuild of the NBX and NBY glove boxes will be completed during fiscal year 2018. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "None at this time. (ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "Not applicable." Notified R2DO (Masters) and Part 21 Group via Email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-12-14
48590 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-12-13 16:30 | 2012-12-13 18:36 | 2012-12-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO PRIMARY CONTAINMENT SYSTEM DECLARED INOPERABLE "An increased usage of Nitrogen to maintain Primary Containment pressure within specification was noticed during steady state operation. Investigation into the extra Nitrogen usage revealed that Primary Containment Leakage was in excess of that allowed per Technical Specification 3.3.3.a. No action statement is provided for leakage in excess of Technical Specification 3.3.3.a; therefore in accordance with Technical Specification 3.0.1, the reactor shall be placed in an operational condition in which the specification is not applicable. This requires the plant to be shutdown and cooled down to less than 216 degrees F. "Additionally, this is reportable as an event or condition that could have prevented fulfillment of a safety function of a system needed to control the release of radioactive material. "The primary containment was declared inoperable at 1630 EST and a normal orderly plant shutdown was commenced at 1645 EST and will be less than 215 degrees F within 10 hours. "Investigation of containment leakage is in progress. "An update will be provided when the plant is in an operational condition in which Technical Specification 3.3.3.a is not applicable." The licensee has notified the NRC Resident Inspector. Licensee has notified the State of New York. * * * UPDATE AT 0011 EST ON 12/14/12 FROM CHRISTOPHER GRAPES TO BILL HUFFMAN * * * "As of 2333 EST on 12/13/2012, the reactor is below 215 degrees F, and containment is no longer required to be operable by Technical Specification 3.3.3. As part of the shutdown, a manual reactor scram was initiated as part of the pre-planned shutdown sequence and the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. "HPCI is a flow control mode of the normal feedwater systems and is not an Emergency Core Cooling System. At 1913 EST, RPV level was restored above the HPCI system low level actuation set point and the HPCI system initiation signal was reset. Pressure control was established on the turbine bypass valves, the preferred system. No Electromatic Relief Valves actuated due to the scram. "Nine Mile Point Unit 1 is currently in Cold Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via shutdown cooling (SDC). The offsite grid is stable with no grid restrictions or warnings in effect." The licensee has notified the NRC Resident Inspector and State authorities. Notified R1DO (Holody) and NRR EO (Lund). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-12-13
48589 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-12-12 | 2012-12-13 17:05 | 2013-01-08 | AGREEMENT STATE - POTENTIAL CONTAMINATED SEALED SOURCE The following was received from the Commonwealth of Massachusetts via email: "On 12/13/12, licensee notified this Agency of the 12/12/12 determination of a potential leaking or contaminated sealed source that had been received from an out-of-state vendor. The source being returned to vendor for further analysis. There was no evidence of contamination beyond the source itself." "The Agency considers this matter to be OPEN pending receipt of written report." The sealed source contained 0.040 Ci of Cd-109. The manufacturer is Eckert and Zeigler, model XFB-3, with serial number TR2463. * * * UPDATE FROM TONY CARPENITO TO CHARLES TEAL ON 1/8/13 AT 1042 EDT * * * The following was received from the Commonwealth of Massachusetts via email: "The Vendor/Manufacturer reported to licensee in a letter dated 1/7/13 that, per wipe and soak tests conducted in accordance with ISO 9978:1992 (Radiation protection -- Sealed radioactive sources -- Leakage test methods) the source is not leaking and removable activity initially found originated from the capsule's surface. The vendor/manufacturer also wrote that the incident was assigned to the vendor/manufacturer's internal corrective and preventive action program." Notified R1DO (Newport) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-12-21
48588 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-13 11:00 | 2012-12-13 13:10 | 2012-12-13 | SEISMIC MONITORING SYSTEM INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At approximately 11:00 EST on December 13, 2012, the Seismic Monitoring System was declared inoperable for pre-planned preventative maintenance, MPT-10240 Triaxial Time History Accelerograph. The preventive maintenance is expected to last approximately 5 to 6 hours. "The Seismic Monitoring System is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-l022, Rev. 2. This condition does not affect the health of safety of the public or the operation of the facility. "Licensee has available redundant seismic indication and the on-site Emergency Response Organization has been notified. "The NRC Resident Inspectors have been notified." TEST2 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-13
48587 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-10-17 23:01 | 2012-12-13 10:28 | 2012-12-13 | 60-DAY TELEPHONE NOTIFICATION OF AN INVALID SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On October 17, 2012, at 2301 hours Central Daylight Time (CDT), the 3A Reactor Protection System (RPS) Motor Generator (MG) Set tripped, causing the loss of the 3A RPS Bus, resulting in a half scram. Loss of the 3A RPS Bus automatically isolated Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 which initiated 'A' Train of Control Room Emergency Ventilation (CREV) and 'A', 'B', and 'C' Trains of Standby Gas Treatment (SGT) while isolating the Reactor Water Cleanup System (RWCU). "Plant Conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level, High Drywell Pressure, or Reactor Vessel High Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level, High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The affected equipment responded as designed. "This condition was caused by the 3A RPS MG-Set motor winding's insulation failing due to age related degradation. To correct this condition, the 3A RPS MG Set was removed, rewound, refurbished, and re-installed. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 625651. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-13
48586 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-12-13 08:55 | 2012-12-13 08:58 | 2012-12-13 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM REMOVED FROM SERVICE FOR MAINTENANCE "Planned maintenance activities are being performed today (December 13, 2012) to Technical Support Center (TSC) HVAC. This work activity is planned to be performed and completed expeditiously within about 8 hours including establishing and removing the clearances, and performing post maintenance testing. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC during the time this work activity is being performed, as long as habitability conditions allow. The Emergency Response Organization duty team members will be relocated to alternate locations if required by habitability conditions in accordance with emergency implementing procedures. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JOSEPH MCKED TO JOHN KNOKE AT 2000 EST ON 12/13/12 * * * The licensee reported that the planned maintenance activities have been completed to the Technical Support Center's HVAC. The licensee has notified the NRC Resident Inspector. R2DO (Blamey) notified. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-13
48585 | -1 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2012-12-13 | 2012-12-13 08:41 | 2013-06-12 | 60-DAY INTERIM REPORT INVOLVING AN EVALUATION OF A DESIGN CHANGE TO MAGNE-BLAST CIRCUIT BREAKERS The following information was received via fax: "Summary "GE Hitachi Nuclear Energy (GEH) is investigating the adequacy of a Design Change in AM 4.16-350-2C and AM 4.16-350-2H Magne-Blast Circuit Breakers as a result of a breaker failure at a BWR Licensee. "GEH has not completed the evaluation of this condition to determine reportability under 10 CFR Part 21 and is therefore issuing this 60-day Interim Notification. GEH will close or issue an update on this matter on or before June 14, 2013. Given the early status of the evaluation, GEH has no recommended actions at this time. This 60-day Interim Notification is issued in accordance with 10 CFR Part 21.21(a)(2), and will be sent to all GE BWR/2-6 plants and all PWRs. "Recommendation "GEH advises licensees to take no action at this time. However, if licensees wish to determine if the extent of this issue is present at their respective plants, they may identify breaker models AM 4.16-350-2H/2C with a date of manufacture prior to October 6, 1971. Other AM breaker styles do not use the booster cylinder as designed in breaker model AM 4.16-350-2H/2C and are not included in this concern. Therefore the extent is limited to the AM 4.16-350-2H/2C models manufactured prior to October 6, 1971. "US Plants Potentially Affected "Nine Mile Point 1-2, Fermi 2, Columbia, Grand Gulf, River Bend, FitzPatrick, Pilgrim, Vermont Yankee, Clinton, Dresden 2-3, LaSalle 1-2, Limerick 1-2, Oyster Creek, Peach Bottom 2-3, Quad Cities 1-2, Perry 1, Duane Arnold, Cooper, Susquehanna 1-2, Brunswick 1-2, Hope Creek, Hatch 1 - 2, Browns Ferry 1-3, Monticello, Callaway, Palo Verde 1-3 , Calvert Cliffs 1-2, Ginna, Arkansas Nuclear One 1-2, Indian Point 2-3, Millstone 2, Millstone 3, North Anna 1-2, Palisades, Surry 1-2, Waterford 3, Catawba 1-2, Oconee 1-3, McGuire 1-2, Braidwood 1-2, Exelon Byron 1-2 , Three Mi le Island 1, Beaver Valley 1-2, Davis-Besse, Seabrook, St. Lucie 1-2, Turkey Point 3-4, Point Beach 1-2, DC Cook 1-2, Prairie Island 1-2, Fort Calhoun, Diablo Canyon 1-2, Crystal River 3, Robinson, Shearon Harris, Salem 1, Salem 2, Summer, South Texas Project 1-2, San Onofre 2-3, Farley 1-2, Vogtle 1-2, Sequoyah 1-2, Watts Bar 1, Comanche Peak 1-2, and Wolf Creek. "If you have an questions, please call me at (910) 819-4491. Dale E. Porter Safety Evaluation Program Manager GE-Hitachi Nuclear Energy Americas LLC" Hitachi Reference Number: MFN-128 R0 * * * RETRACTION FROM DALE PORTER TO NESTOR MAKRIS ON 6/12/13 AT 0959 EDT * * * The following information was received via fax: "[GE Hitachi Nuclear Energy] GEH has completed all testing and evaluations and has determined that the condition previously described in MFN 12-128 R0 is not a reportable condition under 10 CFR Part 21. This information will be sent to all GE BWR/2-6 plants and all PWRs that were previously notified under the 10CFR21.21(a)(2) communication." Notified R1DO (Dentel), R2DO (Ehrhardt), R3DO (Lara), R4DO (Gepford), and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-12-13
48584 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-12-12 19:14 | 2012-12-12 23:25 | 2012-12-12 | RISK OF POSSIBLE FLOODING TO ERCW BUILDING DURING DESIGN BASIS FLOOD "At 1914 EST on 12/12/12, TVA determined that Sequoyah Unit 1 and 2 were at risk of flooding into the ERCW [Emergency Raw Cooling Water] Station Building during a design basis flood due to conduit penetrations not being filled with material required to make the building water tight. The lack of a barrier would allow flood waters to enter the ERCW building at a rate greater than the sump pumps can remove creating a condition that could result in the ERCW pumps being unavailable to perform their design function during a flood event above plant grade. "This condition places both units in an unanalyzed condition that significantly degrades plant safety [10 CFR 50.72 (b)(3)(ii)(B)], and could prevent the fulfillment of the safety related function of ERCW needed to shutdown the reactor and maintain it in a safe shutdown condition [10CFR 50.72 (b)(3)(v)(A)]. "Compensatory actions are being established to be capable of removing or limiting water that could leak into the building during the event. The required safety related equipment is currently operable. There are no indications of conditions that might result in a flood in the near term." The NRC Resident Inspector has been notified of this condition. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2012-12-12
48583 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-12-12 15:27 | 2012-12-12 19:57 | 2012-12-12 | TECHNICAL SUPPORT CENTER UNAVAILABLE FOR EMERGENCY ASSESSMENT "While attempting to swap Technical Support Center (TSC) power supplies the TSC air handling unit circuit breaker tripped rendering the TSC unavailable for emergency assessment. An emergent work order has been planned to restore the TSC air handling unit to operational status." The licensee has notified the NRC Resident Inspector. Licensee also notified state, local and other government agencies. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-12
48582 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2012-12-10 09:43 | 2012-12-12 12:38 | 2012-12-12 | AGREEMENT STATE - SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA While conducting radiography operations with a Sentinel Model 880D camera, the radiographer noticed that the connection to the source was not holding. The radiographer was qualified in source retrieval. He was able to retrieve the source into its secured position. After securing the source he inspected the camera to determine if there was a mechanical problem. No problems were found. It is believed that the problem was due to ice buildup. There were no significant exposures during this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2012-12-20
48581 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-10-13 02:18 | 2012-12-12 12:30 | 2012-12-12 | 60 DAY REPORT- INVALID SPECIFIED SYSTEM ACTUATION "Event Summary: On October 13, 2012, at approximately 0218 [EST], a full reactor scram signal was received in the James A. FitzPatrick (JAF) control room. At the time of this event, the plant was in cold shutdown (Mode 4) and refueling outage 20 (R20) was in progress. The scram signal occurred because Reactor Vessel Scram & Primary Containment Isolation Level Transmitter (02-3LT-101C) and Reactor Vessel Scram & Primary Containment Isolation Level Transmitter EQ (02-3LT-101D) momentarily failed downscale, and then immediately recovered. "02-3LT-101C is an 'A' division component and 02-3LT-101D is a 'B' division component. Therefore, both the 'A' and 'B' divisions of reactor protection actuated providing a full reactor scram and outboard primary containment isolation signal. AOP-15, 'Isolation Verification and Recovery' verified that the proper containment isolation response was received. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) because it resulted in the invalid actuation of the reactor protection system while the reactor was already shut down. "Apparent Cause: A Failure Mode Analysis and Apparent Cause Evaluation were performed to determine the most likely cause of both level transmitters to momentarily spike downscale. It was concluded that the most probable cause was due to a worker inadvertently coming into contact with the level transmitters' exposed sensing lines. Contributing to this event was the misjudgment by the Operations individual reviewing the work package, on the risk significance of the instrumentation in the vicinity of the work area. As a result, the work area was not constructed in a manner to preclude interference with the level transmitters or associated sensing lines. "Corrective Actions: Immediate corrective actions were to walk down the affected instrument lines to ensure no damage had been caused. Additional corrective actions were to install signs near the level transmitters and exposed sensing lines. The signs denote that sensitive instrument lines are present. Future corrective actions include a walk down by engineering and operations to identify other areas in the plant where sensitive instrument lines are present and place additional signs or barriers as appropriate." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-12
48580 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-12-11 20:00 | 2012-12-11 21:52 | 2013-03-13 | UNACCOUNTED FOR FIREARM AT FORT CALHOUN The licensee reported a missing firearm. Compensatory actions have been taken. The licensee will notify the NRC Resident Inspector. Contact Headquarters Operations Officer for additional details. * * * UPDATE FROM JENSEN TO KLCO ON 12/11/12 2220 EST * * * Notified that the licensee has found the weapon. Contact Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. Notified the R4DO (Haire) and the 73.71 Group via email. * * * RETRACTION FROM ERICK MATZKE TO DONG PARK ON 3/13/13 1442 EDT * * * Notified that the licensee never lost the weapon. Contact Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. Notified the R4DO (Powers) and the 73.71 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-12-11
48579 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-19 23:24 | 2012-12-11 12:10 | 2012-12-11 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "In accordance with 10CFR50.73(a)(2)(iv)(A), this telephone notification reports an invalid actuation of the Unit 2 train B (2B) Emergency Diesel Generator (DG) undervoltage auxiliary relay on October 19, 2012 at 2324 hours. At the time of he event, Unit 2 was in Mode 6, Refueling. The 2B DG was undergoing the completion of a monthly surveillance and was operating in parallel with the offsite power, when the 2B DG changed from the test mode to the emergency mode. The offsite feed to the bus (ACB 2422) tripped, and the 2B DG load increased to carry the bus. Proper operation of the 2B DG was verified, and expected train equipment loaded and functioned successfully. The potential cause is attributed to a spurious actuation of the undervoltage auxiliary relay. This condition was entered into the corrective action program. "The licensee notified the NRC Resident Inspector and the Illinois Emergency Management Agency Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-11
48578 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2012-12-06 | 2012-12-11 09:31 | 2012-12-11 | AGREEMENT STATE REPORT - LEAKING SOURCE Georgia Tech was wipe testing the Ni-63 source from a gas chromatograph. The source was determined to be leaking and had contaminated an adjacent counter top. The source was last "refoiled" in May 2011. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-12-19
48577 | -1 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-12-07 | 2012-12-11 09:05 | 2013-05-07 | AGREEMENT STATE REPORT - CONTAMINATION EVENT The following information was obtained from the State of Tennessee via email: "On 12/10/12 at 4:30 pm EST, [the] RSO [at] Energy Solutions-Bear Creek called [the State of Tennessee] to report that last Friday, 12/7/12, a drum of DU shavings had been placed in Area 9 of the old ATG building and covered w/mineral oil. When [workers] came to work on 12/10/12, they noticed that the poly drum was completely gone, the shavings were on the floor, oil was on the floor and some of the shavings looked like ash. The poly drum had burned up and the drum/shavings and oil/ash/shavings were now on the concrete floor. There was no stack release. The stack samples were pulled and indicated less than MDA: < E-14 for U-238 and <E-15 for U- 235. Workers were not allowed to enter the area/bldg. A Hi-Volume sample was pulled with no detectable findings. Smear samples were taken with a maximum reading of 11,000 dpm. The pre-filter will be removed and counted. [Workers] are in the process of checking the temperature from a distance using a remote thermometer in order to determine if they can transfer the shavings from the floor into another oil filled container. There was no release into any drains, there was no release into the air, and there were no personnel involved/no personnel contamination. A written report is being prepared and will be sent to the Division [Tennessee Division of Radiological Health]." Tennessee Report No.: TN-12-305 * * * UPDATE FROM LAURA TURNER TO DONALD NORWOOD AT 1153 EDT ON 5/7/2013 * * * The following report was received via e-mail: This is a request for event notification (EN #48577) to be retracted. "The State of Tennessee Division of Radiological Health (DRH) investigation has determined, based on the information Energy Solutions (ES) supplied and the amount of DU [Depleted Uranium] lost, incident TN-12-305 did not meet the reporting requirements for the greater than five times ALI criteria. Therefore, Event Notification Report #48577 is being retracted. "It was concluded that 126 grams of DU, or less than 37 MBq (1 mCi) of activity, is unaccounted for as a result of the oxidation incident. Energy Solutions stated that the work area sample results were 0.46 uBq/ml (1.25E-11 uCi/ml) alpha and 1.85 uBq/ml (5E-11 uCi/ml) beta with field instrument checks. Results were also less than MDA alpha and 0.2 (5.46E-12) beta with laboratory equipment checks (gamma spec). Correspondingly, the field check revealed 1.79 DAC based on 0.26 uBq/ml (7E-12 uCi/ml) DAC for Pu-239. Energy Solutions concluded that an inappropriate storage vessel was used. Corrective actions included operator training, procedural revisions, and external review by proper ES personnel." Notified R1DO (Dwyer) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-12-19
48576 | -1 | HADDAM NECK |  |  |  | ISFSI | 2012-12-11 01:08 | 2012-12-11 02:05 | 2012-12-11 | SAFEGUARDS SYSTEM DEGRADATION The licensee discovered a safeguards system degradation related to the monitoring and detection of their controlled area. Compensatory actions have been taken. Contact the Headquarters Operations Officer for details. * * * RETRACTION FROM ROBERT DESMAIS TO HOWIE CROUCH AT 1152 EST ON 12/11/12 * * * After further review, the licensee determined that this event did not meet the reporting requirements of 10CFR50.72(b)(3)(xiii) and therefore is retracting the event. Notified R1DO (Holody), NMSS EO (Pstrak), CAT Team (email) and 73.71 Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | LOSS COMM/ASMT/RESPONSE | [9 empty] | NON EMERGENCY | 1 | CT | ISF |  | 50.72(b)(3)(xiii) |  |  |  | 1 | 2012-12-11
48575 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-10-13 18:41 | 2012-12-10 21:40 | 2012-12-10 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID MULTIPLE SYSTEM ACTUATIONS "On Saturday, October 13, 2012, Unit 1 was operating at 100% power. At 1841 [EDT], the 1A RPS/UPS inverter tripped and the automatic transfer of the RPS and UPS 120 VAC distribution panel (1A-Y160) loads to the primary alternate AC power source was delayed. The delay in automatic load transfer caused the RPS series breakers to trip on undervoltage. The failure caused a loss of power to Division IA and IIA RPS relays and Division IA and IIA NS4 relays. This caused primary containment isolation valves (PClVs) to automatically close on more than one system. The IB and IIB channels were unaffected. "The most probable cause for the delayed load transfer was a failed logic power supply with a momentary loss of synchronization. Troubleshooting continues [in order] to confirm the specific cause of the component failure. The distribution panel loads are currently supplied by an installed alternate AC power source. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The isolation was a partial actuation. "This 60-day ENS report is being made per 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to report invalid automatic actuations of systems listed in paragraph (a)(2)(iv)(B). The listed system that actuated was general containment isolation signals affecting containment isolation valves in more than one system. Primary containment isolation valves (PCIVs) closed on drywell chilled water (DWCW), reactor enclosure cooling water (RECW), primary containment instrument gas (PCIG), Unit 1 containment leak detector, and Unit 2 containment leak detector." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-10
48574 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-12-10 14:14 | 2012-12-10 19:24 | 2012-12-12 | LOSS OF EMERGENCY RESPONSE CAPABILITY - TSC/OSC UNAVAILABLE "Unavailability of TSC/OSC Ventilation System due to Ventilation Fan (FN-1) failure to start. "On Monday, December 10, 2012, at 1414 hours with Pilgrim Nuclear Power Station (PNPS) at 100% core thermal power, the Technical Support Center (TSC)/Operations Support Center (OSC) emergency ventilation system was declared non-functional due to the failure of a fan (FN-1) to start during a scheduled surveillance (8.B.24). The balance of the TSC/OSC ventilation is not affected by this event and remain available. "Under certain accident conditions the TSC/OSC may become unavailable due to inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC/OSC personnel to the Emergency Offsite Facility (EOF) and the Control Room. In the event of a declared emergency, all OSC personnel will report to the Control Room Annex. TSC minimum staffing will report to the Control Room and all other TSC staff will report to the EOF. "The troubleshooting is being worked as a high priority and is conservatively scheduled to be completed by 1900 hours on Wednesday, November 12, 2012. A follow-up to this notification will be made when the TSC/OSC is returned to functional status or if the maintenance effort is significantly extended. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM PROBASCO TO KLCO ON 12/12/2012 AT 1817 EST * * * "This is an informational update to notification EN# 48574 made on Monday December 10, 2012. "On Wednesday, December 12, 2012 at 1550 [EST] with Pilgrim Nuclear Power Station (PNPS) at 100% core thermal power, the Technical Support Center (TSC) / Operations Support Center (OSC) emergency ventilation system was returned to functional status following repair and successful post maintenance testing of the fan (FN- 1). Notification has been made to the Emergency Response Organization that the normal facility activation capability has been restored. "Additionally, in our initial notification there was a documentation error in that we stated November 12, 2012 as the expected return to service vice the correct date of today, December 12, 2012. "The licensee has notified the NRC Senior Resident Inspector that the TSC/OSC emergency ventilation has been restored to functional status." Notified the R1DO (Holody). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-10
48573 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-10 07:30 | 2012-12-10 07:17 | 2012-12-10 | LOSS OF ASSESSMENT CAPABILITY- RADIATION MONITORS INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At approximately 07:30 EST on December 10, 2012, radiation monitor RM-01TV-3536-1, Turbine Building Vent Stack Wide Range Gas Monitor (WRGM) will be declared inoperable for pre-planned corrective maintenance on the FT-01TV-3536-1, Turbine Bldg Vent Stack flow rate monitor. The corrective maintenance is expected to last approximately 5 to 6 hours. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health or safety of the public or the operation of the facility. "The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-10
48572 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-12-07 14:35 | 2012-12-07 18:27 | 2012-12-07 | FITNESS FOR DUTY - EMPLOYEE HAD A CONFIRMED POSITIVE FOR ALCOHOL A non-licensed, non-supervisory employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2012-12-07
48571 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-12-07 08:00 | 2012-12-07 15:50 | 2012-12-07 | TRUCK STOLEN WITH LOCKED HYDROPROBE GAUGE IN BED OF TRUCK The following information was received via E-mail: "The RSO for GeoLogic Associates notified the RHB [Radiologic Health Branch] that a CPN DR-503 hydroprobe #H330306914 (containing 1.85 GBq (50 mCi) of Am-241:Be) was found to be stolen on 12/7/2012. The hydroprobe's Type A transportation case was locked with two padlocks, out of sight in the rear bed of the employee's personal vehicle; a Honda Ridgeline. The vehicle was reported as stolen to the Riverside City Police Department, report #P12177015, on 12/7/2012. "A notice for return of the stolen hydroprobe will be placed in the local newspaper if the stolen vehicle containing the hydroprobe is not recovered within 24 hours." California Report #120712. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-12-17
48570 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-10-12 10:12 | 2012-12-07 14:49 | 2012-12-07 | TEMPERATURE SWITCH FAILURE CAUSES DIVISION I ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation signal affecting containment isolation valves in more than one system. "On October 12, 2012, Nine Mile Point Unit 2 (NMP2) received a Division I primary containment isolation signal which resulted in the closure of Group 5, 6, and 10 primary containment isolation valves (PCIVs) in the following systems: "Group 5 PCIVs: Residual Heat Removal System (RHS); Shutdown Cooling (SDC); "Group 6 PCIVs: Reactor Water Cleanup System (WCS) supply outside isolation valve; and "Group 10 PCIVs: Reactor Core Isolation Cooling (RCIC) System. "All affected PCIVs responded as designed. The Division I isolation signal was generated due to the failure of a temperature switch unit. The Division I and II temperature switch units were both reading within limits when the Division I unit failed. Since the isolation signal was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation, the isolation signal was determined to be invalid. "The event was entered into the corrective action program as Condition Report CR-2012-009380. There were no safety consequences and no impact to the health and safety of the public as a result of this event." The licensee notified the New York State Public Service Commission and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-07
48569 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2012-11-09 | 2012-12-07 09:53 | 2013-04-30 | PART 21 - BRACKETS USED PROXIMITY SWITCHES INSTALLED UPSIDE DOWN "Equipment Affected By This Fisher Information Notice: "This Fisher Information Notice (FIN) applies to equipment provided to Arizona Public Service Company-Palo Verde Nuclear Generating Station per Fisher Order Number 019-F10051845, Items 0001, 0002, 0004, and 0005 (Arizona Public Service PO# 500559374). "The affected equipment Is: "4 [inch] CL900 Fisher HPD valve assemblies with TopWorx C8-24521-E3 proximity switches. "The equipment is identified by Fisher serial numbers 20417605, 20428975, 20428977, and 20428978 respectively and Arizona Public Service Company tag numbers 1JSGEUV0169, 2JSGEUV0169, 1JSGEUV0183, and 2JSGEUV0183. "Purpose: "The purpose of this FIN is to alert Arizona Public Service Company that as of 9 November, 2012, Fisher Controls International LLC (Fisher) became aware of a situation which may potentially affect the safety-related performance of the aforementioned equipment. "Fisher is informing you of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21. "Applicability: "This FIN applies only to the aforementioned equipment supplied by Fisher to Arizona Public Service Company- Palo Verde Nuclear Generating Station. "Discussion: "Arizona Public Service Company has determined that the brackets used to install the TopWorx switches were installed improperly by Fisher. "Specifically, the mounting brackets for the switches were installed upside down. This orientation makes it impossible for the switches to operate properly and to perform their safety-related function. "While the design used for these brackets was unique and constituted a first-time installation by Fisher, Fisher is in the process of performing a root cause analysis as well as investigating why the error was not detected prior to shipment. Fisher will implement a corrective action to prevent problems like this from reoccurring in the future. "Additionally specific arrangements are being made with Arizona Public Service Company to correct the problem on the subject serial numbers, at Fisher's cost. "Action Required: "Fisher is currently working with Arizona Public Service Company to resolve the situation, including, the implementation of a bracket redesign and testing program to demonstrate the problem has been satisfactorily corrected. "10 CFR 21 Implications: "Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10 CFR 21. "If there are any technical questions or concerns, please contact: "George Baitinger; Manager, Quality; Fisher Controls International LLC; 205 South Center Street Marshalltown, IA 50158; Fax: (641) 754-2854, Phone: (641) 745-2026." * * * UPDATE AT 1634 EDT ON 4/30/2013 FROM CHAD ENGLE TO MARK ABRAMOVITZ * * * The following information was received via fax: "After the switches were properly reinstalled it was discovered that due to potential rotation of the valve stem connector when operating the hand wheel, the target magnets could, in some cases, rotate beyond the gap required for switch functionality. This additional discovery is the reason for the issue of this supplemental FIN. "Fisher is currently working with TopWorx and APS/PVNGS [Arizona Public Service / Palo Verde Nuclear Generating Station] to develop a bracket redesign with adequate guiding which will constrain the magnet/switch gap to within acceptable criteria." Notified the R4DO (Haire), R3DO (Duncan) and Part 21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-12-07
48568 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-10-09 10:50 | 2012-12-07 10:31 | 2012-12-07 | 60-DAY TELEPHONIC NOTIFICATION OF AN INVALID SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On October 9, 2012, at 1050 hours Central Daylight Time (CDT), the 2A Reactor Protection System (RPS) Motor Generator (MG) Set Voltage Regulator failed causing the 2A1 Circuit Protector to trip on undervoltage, resulting in a half scram. In addition, the loss of 2A RPS caused the isolation of Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8, which resulted in the initiation of Standby Gas Treatment (SGT) Trains 'A' and 'C' and the isolation of the 2-RM-90-256 Continuous Air Monitor (CAM), inboard valves, Drywell floor drain inboard isolation valve, and the Reactor Water Cleanup System (RWCU). "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level, High Drywell Pressure, or Reactor Vessel High Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level, High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level or High Drywell Pressure. At the time of the event, these conditions did not exist, therefore, the actuation of the PCIS was invalid. "The affected equipment responded as designed. "This condition was the result of the failure of the 2A RPS MG Set voltage regulator. To address this condition, the failed voltage regulator was replaced. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 621027. "The NRC Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-07
48567 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2012-12-06 15:00 | 2012-12-07 09:35 | 2012-12-10 | AGREEMENT STATE REPORT - STATIC ELIMINATOR MISSING The licensee reported to the State of Iowa that they could not account for one static eliminator, NRD model P-2021, which contains a nominal 10 mCi Po-210 source. The State is investigating and will update this report when more information is obtained. * * * UPDATE FROM RANDAL DAHLIN TO VINCE KLCO ON 12/10/12 AT 1527 EST * * * The following information was received by facsimile: "AGRI Industrial Plastics reported the loss of an NRD static eliminator model P-2021, serial number A2HW186 that contained a nominal activity of 0.37 GBq (10 mCi) Po-210 sealed source. The general license registrant had received seven static eliminators from NRD on October 12, 2011. The RSO for the facility discovered the device in question to be lost on December 6, 2012. The apparent cause for the lost device is human error and inattention to detail. The remaining six devices were shipped back to NRD on December 7, 2012. The corrective action for this event is that AGRI Industrial Plastics will no longer use static eliminators that contain radioactive material." Notified the R3DO (Cameron) and the FSME Resources via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-12-17
48566 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-12-07 09:20 | 2012-12-07 09:30 | 2012-12-07 | PLANNED EMERGENCY OFFSITE FACILITY/TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "On December 7, 2012, the EOF/TSC air handler chiller unit was removed from service to perform planned maintenance. This maintenance activity will not affect the air filtration portion of the system and these facilities remain available for use during an emergency. This maintenance activity will be performed in a manner to minimize the time that the air handler chiller is out of service. This maintenance activity impacts the ability to maintain ambient air temperature in the facilities. The estimated duration of this activity is planned to be 12 hours. "If an emergency condition occurs that requires activation of the emergency response facilities, the EOF and TSC will be utilized. The Emergency Response Organization team members have the ability to relocate to alternate locations in accordance with emergency implementing procedures based on conditions. Alternate emergency response facilities will remain available in the event that relocation is necessary. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update message will be provided when the emergency response facilities are restored." The licensee has notified the NRC Resident Inspector, State and local authorities. * * * UPDATE FROM STEVE HEBLER TO PETE SNYDER AT 1948 EST ON 12/7/12 * * * The licensee completed maintenance and returned the EOF/TSC air handler chiller unit to service as of 1920 EST on 12/7/12. The licensee notified the NRC Resident Inspector. Notified R2DO (Blamey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-07
48565 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-10-08 17:09 | 2012-12-06 16:34 | 2012-12-06 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SYSTEM ACTUATION "On October 8, 2012, at 1709 EDT, Unit 2 received a Reactor Auto SCRAM System 'B' Trip signal in the main control room. The power monitoring breaker in RPS panel 2C71P003D tripped, causing a half-SCRAM in conjunction with the automatic actuation of the Unit 2 standby gas treatment system (SGT) and isolation of CIVs [Containment Isolation Valves] in multiple systems, both of which are normal responses to this loss of the 'B' RPS bus. The crew entered the appropriate abnormal operating procedures and confirmed the actuations automatically occurred as required given the loss of the RPS bus. They investigated the 'B' RPS Motor/Generator (M/G) set, placed the 'B' RPS bus on its alternate supply, reset the SGT and CIV actuation logic, and returned the CIVs to their normal position. "Upon investigation, the 'B' RPS M/G set was found running with a steady output of 120 VAC. The breaker in RPS panel 2C71P003B stayed closed in. Further troubleshooting did not identify a cause for the failure of RPS breaker 2C71B003D. The breaker was replaced and the power monitoring relays were rebuilt. The 'B' MG Set was left running unloaded for 8 days with no trips observed. "On October 26, 2012, approximately 20 seconds after returning the RPS 'B' M/G Set to service, RPS breaker 2C71B003D tripped again. At this time, investigators determined that 2C71B003B had no output voltage present when load was increased to 25 amps or greater. 2C71B003D tripped because 2C71B003B was not supplying load to it. A lug mounting screw was subsequently found to be loose on 2C71B003B. After tightening the screw, maintenance personnel determined that continuity existed and the 2C71B003B indicated closed with output voltage present as expected. "Review of the six-month surveillances on 2C71B003B and the more-detailed 5-year surveillance that took place in August 2010 revealed no previous problems with the breaker. It is unknown when the lug mounting screw became loose or if repeated cycles of operation caused it to loosen. For broadness, thermography testing is being completed on 2C71P003 A, C, D, E, F and 1C71P003 A, B, C, D, E, F. "When the second trip of 2C71B003D occurred on October 26, 2012, U1 SGT trains started and CIVs in multiple systems closed. This was an expected actuation with radiation monitor 2D11K634C already out of service and in the tripped condition at the time of the RPS 'B' trip. The RPS 'B' trip caused radiation monitor 2D11K634D to also trip thereby completing the logic to start U1 SGT trains and to close associated CIVs. The second event is included in this report since the failures are related as a result of having the same general cause and since they occurred over a reasonably short period of time. "Because a malfunctioning subcomponent caused the loss of RPS 'B' rather than a valid CIV actuation signal, the resulting isolation of CIVs in multiple systems is considered an invalid actuation in both cases. Based on that information 10CFR50.73(a)(2)(iv) allows these events to be reported via a telephone notification within 60 days instead of submitting a written LER." The licensee will notify the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-06
48564 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2012-12-06 | 2012-12-06 11:01 | 2012-12-06 | ESI REFURBISHED EMERGENCY DIESEL GENERATOR CYLINDER HEAD WITH FOREIGN MATERIAL IN INTAKE PORT The following information is a summary of a Part 21 Report from Engine Systems, Inc. (ESI) concerning a condition reportable under 10 CFR 21. ESI reports that they received notification about foreign material found within a refurbished cylinder head supplied to the Cooper Nuclear Station by ESI. Specifically, Cooper discovered two hand tools (picks) within the intake port on the cylinder head. The tools were discovered by Cooper after installation of the head onto the diesel engine and while attempting to adjust the intake valve backlash. ESI supplied the refurbished cylinder head for a Cooper-Bessemer KSV engine to Cooper Nuclear Station (Part Number 13-KSV-11-6, Serial Number 6K2201) in August 2010. The refurbishment activity was performed at the Cameron Compression (OEM) facility in Casper, Wyoming. The most likely scenario is that the cylinder head was oriented with the inlet port facing up during installation of the valve spring keeper seals. After installation of the seals, the tools were placed on top of the cylinder head. It is presumed the tools fell into the inlet port and settled in the intake valve seating area. The tools are small in size (approximately 5 inches long with a 5/8 inch handle) and were not visible from the exterior of the head. ESI considers this occurrence to be an isolated incident and that Cooper Nuclear Station is the only affected customer. Previous shipments of similar cylinder heads are not suspect. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-12-06
48563 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-06 07:00 | 2012-12-06 06:51 | 2012-12-06 | RADIATION MONITOR INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At approximately 0700 EST on December 6, 2012, radiation monitor RM-01TV-3536-1, Turbine Building Vent Stack Wide Range Gas Monitor (WRGM) was declared inoperable for pre-planned maintenance to perform surveillance testing. The surveillance test is scheduled to take approximately four hours. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health or safety of the public or the operation of the facility. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-06
48562 | 0 | ARCELORMITTAL |  |  |  |  | 2012-12-05 12:00 | 2012-12-05 17:10 | 2012-12-05 | FIXED GAUGE SHUTTER FAILED TO CLOSE During a maintenance outage, the shutter on a fixed gauge failed to close. The specific gauge information is as follows: Make: Texas Nuclear Model: 5010 Source: 1000mCi Am-241/Be The gauge is used for weighing purposes. The licensee has contacted the manufacturer, Thermo Fisher, who is scheduled to arrive on-site at 1000 EST on 12/6/12. There were no personnel exposures involved and the area containing the gauge has been posted to prevent employees from entering inadvertently. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-12-13
48561 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2012-12-05 08:10 | 2012-12-05 13:03 | 2012-12-05 | OFFSITE NOTIFICATION DUE TO A NON-WORK RELATED MEDICAL EVENT "This is a non-emergency 4-hour informational notification to the NRC in accordance with the reporting requirements of 10 CFR 50.72(b)(2)(xi). "On December 5, 2012 at approximately 0810 hours EST, a contract employee within the construction area suffered a non-work related personal medical event. The individual was transported offsite and was pronounced deceased at a local hospital. "OSHA was notified at 1134 EST pursuant to the requirements of 29 CFR 1904.39. There was no radioactive contamination involved in this event. South Carolina Electric and Gas Company has not observed any heightened media interest as a result of this event. No other notifications to government agencies are expected. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-12-05
48560 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-12-05 09:21 | 2012-12-05 09:30 | 2012-12-05 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR MAINTENANCE "On December 5, 2012, at 0921 EST, the Hope Creek Technical Support Center (TSC) ventilation system was removed from service to perform planned maintenance on the system. The maintenance consists of a 54 month inspection of the feeder breaker. The removal of ventilation, potentially affects the TSC habitability during a declared emergency requiring activation. "Appropriate compensatory measures are in place while ventilation is out of service. The Emergency Response Organization duty team has been notified of the maintenance and the possible need to activate the TSC in an alternate location. The ventilation system is scheduled to be out of service for approximately 12 hours." The licensee has notified the NRC Resident Inspector and will notify the local township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-05
48559 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-12-05 08:47 | 2012-12-05 09:15 | 2012-12-05 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR MAINTENANCE "At approximately 0847 EST on December 5, 2012, maintenance [was commenced] on the Technical Support Center (TSC) ventilation system to restore automatic differential pressure control to the TSC ventilation damper D-5. Following the maintenance, a 10 hour functionality run will be performed. Following a successful 10 hour run, full functionality of the TSC ventilation system will be declared. "If an emergency requiring activation of the TSC should occur, procedural guidance exists for the Radiation Protection staff to perform continuous air monitoring of the TSC atmosphere to determine habitability conditions. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) due to the Technical Support Center ventilation support system being non-functional during the maintenance and the 10 hour run. The Site Emergency Coordinator and Emergency Response Manager have been notified. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-05
48558 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-12-05 00:31 | 2012-12-05 08:00 | 2012-12-05 | RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "This is a non-emergency eight hour notification for a loss of emergency assessment capability. On December 5, 2012, Radiation Monitor R-9, Letdown Line Radiation Monitor, was bypassed at 0031 hours as part of planned maintenance on the Chemical Volume and Control System and is not available for monitoring letdown line radiation. "This radiation monitor is used for accident assessment and is credited for Emergency Action Level (EAL) classification for an Unusual Event in the Robinson Nuclear Plant Emergency Plan. Additionally, this monitor is one of multiple indicators used to detect the loss of a fission product barrier. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. Actions are in place to restore the monitor to functional status. "The NRC Resident Inspector will be notified." * * * UPDATE AT 2028 EST ON 12/5/12 FROM GEORGE CURTIS TO S. SANDIN * * * Radiation Monitor R-9 was returned to service at 2022 EST. The licensee informed the NRC Resident Inspector. Notified R2DO (Blamey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-05
48557 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-10-24 | 2012-12-04 15:59 | 2012-12-06 | AGREEMENT STATE REPORT - RADIUM DIAL COMPASS REJECTED AT RECYCLING FACILITY The following information was received from the Commonwealth of Massachusetts via fax: "Abstract: "10/24/12 - Metal load rejected at recycling facility. Reported to CRCPD. [Conference of Radiation Control Program Directors] "11/7/12 - Compass with suspected Ra dial was recovered from trash load. "12/4/12 - Compass was identified as 13.8 microCuries Ra-226. Compass was worn on wrist and was labeled Sperio Magneto Company." * * * UPDATE VIA FAX FROM JOSH DAEHLER TO DONALD NORWOOD AT 1534 EST ON 12/6/12 * * * "The compass source is now stored in Rockland, MA, pending disposal, in accordance with Atlantic Nuclear's specific radioactive materials license No. 56-0477. The compass source is reported by Atlantic Nuclear to have passed a leak test; be of excellent condition; and to exhibit a dose rate of approximately 8 to 10 microrem/hr at one meter from the source, as measured by a calibrated ion chamber. The compass source appears to be of type that was designed to have been worn on a wrist or attached by hook to a belt or lanyard." Notified R1DO (Jackson). Notified FSME Events Resource via E-mail. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-12-12
48556 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2012-12-04 12:00 | 2012-12-04 15:48 | 2013-04-24 | TEMPORARY EMERGENCY OPERATING FACILITY ESTABLISHED FOR PLANNED OUTAGE "In support of the planned upgrades to Crystal River Unit 3's Emergency Operations Facility's (EOF) heating, ventilation and air conditioning (HVAC) system, on Dec. 4, 2012, at 1200 hours Eastern Standard Time a temporary EOF has been established and declared operational. The temporary EOF is located adjacent to the primary EOF and remains outside the 10-mile Emergency Planning Zone. The temporary EOF meets the functional requirements of the primary EOF. During the establishment of the temporary EOF, there was no loss in the functionality of the EOF. If an emergency requiring EOF activation occurs, the temporary EOF will be staffed and activated using emergency planning procedures. The Emergency Response Organization has been briefed on the use of the temporary EOF. Readiness of the temporary EOF has been confirmed by a facility walkdown using existing procedures. This condition has no adverse affect on the public's or employees' health and safety. The EOF HVAC system is scheduled to be out of service for approximately four months. "The NRC Resident Inspector has been notified." * * * UPDATE ON 4/24/13 AT 1757 EDT FROM WARREN DEAGLE TO BILL HUFFMAN * * * "Primary Emergency Operating Facility Outage completed. "This is a courtesy notification and provides an update to the information provided in Event Notification Number 48556 on December 4, 2012, Eastern Standard Time (EDT). "The primary Emergency Operations Facility (EOF) at the Crystal River Nuclear Plant has been restored on April 24, 2013, with the completion of the planned maintenance activity on the EOF heating, ventilation and air conditioning (HVAC) system that commenced on December 4, 2012, EDT. The temporary EOF established to support this planned upgrade, previously identified in Event Notification Number 48556, is no longer in use. The primary EOF is currently operational and experienced no loss in functionality during the restoration activities. The Emergency Response Organization has been briefed on the restoration of the primary EOF. This condition has no adverse affect on the public's or employees' health and safety. "NRC Region II has been notified." The Licensee has also notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-04
48555 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2012-12-04 09:42 | 2012-12-04 13:52 | 2012-12-06 | LICENSEE NO LONGER HAS CONTROL OF EMERGENCY SIRENS "At time 0942 [CST] telecommunications technicians reported to the Main Control Room that the site no longer has the ability to control offsite sirens. This was apparently caused by lightning strike in the area prohibiting the ability of the siren control computers to communicate with the sirens. This lost capability to alert a large segment of the population for one hour (by sirens and/or tone alert radios) requires a report per 10 CFR 50.72(b)(3)(xiii). "Technicians are currently attempting to repair and correct this issue by moving another computer to the affected radio repeater in an effort to reestablish control of offsite sirens. "At time 1057 the station began contacting offsite sirens agencies including the Louisiana Governor's Office of Homeland Security & Emergency Planning as well as all parishes within the 10 mile EPZ in order to initiate contingency actions for this issue. All agencies were notified as of time 1125. This constitutes a reportable notification of offsite agencies in accordance with 10 CFR 50.72(b)(2)(xi). "Plant status remains Mode 1, 100% power, with no grid restrictions to report or radiological releases in progress. A follow up notification will be made to the NRC after the ability to control offsite sirens is restored." Contingency actions are in place until the sirens are restored. The licensee notified state and local governmental agencies as well as the NRC Resident Inspector. * * * UPDATE FROM JAMES HENDERSON TO DONALD NORWOOD AT 2227 EST ON 12/6/12 * * * "On 12/6/12 at time 0200, River Bend Station was able to restore control to offsite sirens. Silent testing was performed to ensure all necessary controls were regained for all 93 sirens. This testing was performed satisfactorily. "Plant status remains Mode 1, 100% with no grid restrictions to report or radiological releases in progress." The licensee notified the NRC Resident Inspector. Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-12-04
48554 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-12-03 13:30 | 2012-12-04 13:03 | 2012-12-05 | ITEMS RELIED ON FOR SAFETY ASSOCIATED WITH THE DRY SCRAP RECYCLE FURNACE IMPROPERLY ANALYZED "During a [Global Nuclear Fuels] GNF-A review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was determined at 1:30 PM yesterday (12/3/12) that Items Relied on for Safety (IROFS) associated with the Dry Scrap Recycle furnace operation were improperly analyzed in the ISA. Although criticality controls associated with preventing moderation intrusion exist and these controls remained in place, they were not sufficiently independent to meet performance requirements. "At no time was an unsafe condition present. The affected equipment has been shut down. An investigation is continuing which will provide additional corrective actions and extent of condition. "While this did not result in an unsafe condition, this event is being reported pursuant with the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery." The licensee will notify state and local governmental agencies and has notified the onsite NRC Inspectors. * * * UPDATE FROM SCOTT MURRAY TO PETE SNYDER AT 1600 EST ON 12/5/12 * * * "An extent of condition review determined there are three more areas with IROFS that are not sufficiently independent. These areas are vaporization/conversion of the Dry Conversion Process, an area used to pack material for recovery and a hood that is used to transition to a moderation restricted area in the gadolinia shop. The affected equipment in these areas has also been shut down and the investigation continues to identify additional corrective actions." The licensee notified the onsite NRC Inspectors. Notified R2DO (Blamey) and NMSS (Rahimi). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-12-04
48553 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-11-05 | 2012-12-03 14:57 | 2012-12-03 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED TROXLER GAUGE The following information was received from the State of Ohio: "[The Ohio] BRP [Bureau of Radiation Protection] received call at approx. 3:30 PM on 11/5/12, with follow-up e-mail, that a licensee's technician had his truck stolen from a job site earlier in the day. The truck had a locked Troxler Model 3411B gauge in its locked case in the truck bed. A report was filed with the Cincinnati Police. The gauge serial # is 14560. Gauge contains 8 mCi Cs-137 and 40 mCi Am-241 sources. "At approximately 6:00 PM on 11/5/12 the licensee informed BRP that the Cincinnati Police had apprehended person driving the stolen truck. The locked nuclear density gauge was still in the vehicle and appeared undisturbed. The truck with the gauge will be stored overnight in the secure police impound lot and licensee would be able to obtain them the next morning. "At approximately 10:20 AM on 11/6/12 the licensee reported to BRP they had recovered the truck and gauge from Cincinnati Police impound lot. Gauge case and device still locked and there was no damage evident. Leak test showed no contamination. No further action required." Ohio Item Number: OH120007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-12-11
48552 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-10-02 09:37 | 2012-12-03 11:18 | 2012-12-03 | INVALID ACTUATION SIGNAL OF THE PRIMARY CONTAINMENT ISOLATION LEVEL TRANSMITTER "This 60-day telephone notification is being made in accordance with the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation signal of the primary containment isolation level transmitter (02-3LT-101A). "Status of SSC's that were inoperable and contributed to the event: "The B Reactor Protection System (RPS) was inoperable due to performance of Emergency Diesel Generator (EDG) B & D Load Sequencing test and 4KV Emergency Power System voltage relay instrument functional test. Therefore, the B RPS was deenergized and associated B RPS channels were tripped. "Narrative: "On 10/2/2012 at 09:37 hours, James A. Fitzpatrick Nuclear Station received a full reactor scram actuation from reactor vessel level transmitter 02-3LT-101A, containment Isolation. The full scram was due to an equipment malfunction, no low level condition was actually present at the time. "It was determined that the replacement of refueling water level transmitter 02-3LT-61 on 09/30/12 was incorrectly performed by not properly venting the sensing line after installation. The common sensing line contains a local high point inside the drywell. The mechanism is air displaces the water in the line causing pressure to momentarily drop which causes the instrument to trip as if reactor water level had actually dropped. Air propagation in one sensing line can have an impact on all of the instruments attached to the common sensing line. "Corrective Actions: "A back flush was performed for instrument rack 25-5. Applicable I&C Post maintenance testing procedures will be updated to include a back flush or forward flush to ensure that instrument lines are properly vented prior to returning the instrument lines to service. "The following additional information is provided: "On 10/2/2012 at 09:45 hours, shift performed OP-18 to reset the scram that occurred at 0937 EST. The procedure provided guidance to install jumpers to allow the scram discharge instrument volume (SDIV) high level scram signal to be bypassed. The jumpers were required since one channel of the RPS was inoperable due to performance of EDG B & D Load Sequencing test and 4KV Emergency Power System voltage relay instrument functional test. "On 10/2/2012 at 10:07 hours, James A. Fitzpatrick Nuclear Station received another full reactor SCRAM actuation of the SDIV B hi-level trip. The safety function of the actuation had already been completed as a result of the previous scram due to the RPS B bus being de-energized, the SDIV B could not be drained. The SDIV A was also not yet drained, and the high level signal was still technically a valid signal that was present. AOP-1 contained steps to verify that the SDIV A or B 'not drained' annunciators are clear before placing the SDIV by-pass switch to normal position. This step was not performed. It was therefore determined to be an invalid signal based on NUREG-1022 guidance: 'actuations initiated for reasons other than to mitigate an event need not be reported.' The signal was actuated during an attempt to reset the previous SCRAM per OP-18, the occurrence of the signal was due to inadequate work planning, and a procedural deficiency which caused the jumpers to be removed prior to draining the SDIV A. Therefore this event did not meet the criteria for being a valid actuation. "Additional Corrective Actions: "Revise OP-18 to provide adequate guidance how to reset a SCRAM with one RPS bus de-energized." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-03
48551 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-12-02 15:30 | 2012-12-02 17:28 | 2012-12-02 | INADEQUATE RAW WATER PUMP ANCHOR EMBEDMENT "The raw water pumps (AC-10A/B/C/D) base plate support anchors were discovered by Fort Calhoun Station personnel to have inadequate embedment to support existing analysis. Plant drawing specify a j-bolt type of anchor with a required 16 inch embedment. Actual plant configuration was found to be a j-bolt type anchor with a 9 inch embedment. Plant design analysis requirements are not being met for the existing configuration. Existing analysis requires a minimum embedment of 60 inch for a j-bolt type anchor. There are a total of 4 anchors for each raw water pump, totaling 16 anchors. The as found condition renders all four raw water pumps inoperable. "In the current plant Mode 5 (De-fueled), Shutdown Condition, the raw water pumps are considered available per the station's Shutdown Operations Protection Plan. Raw water pumps AC-10B and AC - 10D are in service providing cooling to the Component Cooling Water System. The core is offloaded and the Component Cooling Water System is maintaining Spent Fuel Pool temperature." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-12-02
48550 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-12-02 11:42 | 2012-12-02 14:06 | 2012-12-12 | 60-DAY REPORT - INVALID AUXILIARY FEEDWATER AND NUCLEAR SERVICE WATER PUMP ACTUATION "The Unit-2 AMSAC (Anticipated Transient Without Scram Mitigation Actuation Circuitry) actuation generated a Unit-2 turbine trip signal. The Unit-2 turbine was already tripped, but the 2A and 2B Auxiliary Feedwater and 2B Nuclear Service Water pump started. AMSAC actuation occurred during calibration of AMSAC actuation pressure switches." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TIM JOHNSON TO VINCE KLCO ON 12/11/12 AT 1550 EST * * * "This notification retracts an eight (8) hour notification per 10CFR50.72(b)(3)(iv)(A) which was made December 2, 2012 and documented as NRC Event Notification (EN) # 48550. The December 2, 2012 actuation of the Auxiliary Feedwater System was initially reported under 10CFR 50.72(b)(3)(iv)(A), valid actuation of the Auxiliary Feedwater system as listed in paragraph 10CFR50.72(b)(3)(iv)(B)(6). McGuire Nuclear Station (MNS) has subsequently determined that the actuation signal, which was caused by a test signal during calibration of the AMSAC (Anticipated Transient Without Scram Mitigation Actuation Circuitry) actuation pressure switches, constitutes an invalid actuation as described in Revision 2 of NUREG-1022 (Event Reporting Guidelines 10CFR50.72 and 50.73). Specifically, valid actuations result from signals initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. A test signal is not representative of an actual plant condition and was therefore an invalid actuation signal and does not meet the NRC 8-hour reporting criteria under paragraph 10 CFR50.72(b)(3)(iv)(B)(6). "In addition to retracting the 10CFR50.72(b)(3)(iv)(B)(6) notification, MNS is notifying the NRC Operations Center that the December 2, 2012 event met the reporting criteria specified in 10CFR50.73(a)(2)(iv)(A). Specifically, an invalid actuation of the auxiliary feed water system occurred while the systems was in service. The event did not involve an actuation of the reactor protection system (RPS) when the reactor was critical; therefore, MNS is opting to notify the NRC Operations Center within 60 days in lieu of a 60 day written licensee Event Report (LER), as allowed by 10CFR 50.73(a)(1) and 10CFR50.73(a)(2)(iv)(A). "This notification satisfies 10CFR50.73(a)(2)(iv)(A) reporting requirements in lieu of a written LER. The 2A and 2B trains of the auxiliary feed water were actuated by an invalid signal. Each train's actuation was complete and systems operated as designed." The licensee notified the NRC Resident Inspector. Notified the R2DO (Sykes). | 0 | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-12-02
48549 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-12-01 23:17 | 2012-12-02 03:05 | 2012-12-02 | AMSAC ACTUATED AT LOWER THAN EXPECTED TURBINE INLET PRESSURE "The Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC) caused a Unit 2 turbine trip with reactor power at 31%. The 2A and 2B Auxiliary Feedwater pumps automatically started. The 2B Nuclear Service Water pump started as a result of 2B Auxiliary Feedwater pump automatically starting. The Main Feedwater Regulating valves and the Main Feedwater Bypass valves were in the correct position for corresponding power level and turbine inlet pressure, but AMSAC actuated earlier than design (290 psig vs. 360 psig)." The licensee has notified the NRC Resident Inspector. | 0 | 14 | 0 | 0 | 31 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-12-02
48548 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2012-12-01 14:00 | 2012-12-01 16:28 | 2012-12-01 | TSC VENTILATION NOT ABLE TO DIRECT AIRFLOW TO THE CHARCOAL FILTER "The Technical Support Center (TSC) Ventilation failed to enter 'Incident Mode' as required during scheduled testing. That is, the air cannot be re-directed through the charcoal filter in an event requiring the TSC atmosphere to be filtered due to an on-site release. The TSC ventilation system remains in service providing proper temperature control to maintain the facility habitable during normal operation; however with the 'Incident Mode' being unavailable, it may not remain habitable during all postulated scenarios and is, therefore, considered non-functional." The licensee will notify the NRC Resident Inspector and the New York Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-12-01
48547 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2012-11-30 03:10 | 2012-11-30 04:54 | 2012-11-30 | OFFSITE NOTIFICATION - 40 GALLONS OF DIESEL FUEL SPILLED IN OCA "This is a 10 CFR 50.72(b)(2)(xi) notification to the NRC of an event related to the protection of the environment for which notification to other government agencies has been made. "On 11/30/12 at 0310 EST, [licensee was] notified by the site Hazardous Materials Coordinator that a diesel fuel spill occurred in the owner controlled area [OCA] that exceeded the reporting quantity (RQ) to the state and local agencies. The quantity spilled was 40 gallons, with a minor portion entering the cooling canal system. "On 11/30/12 at 0325 EST, [licensee] initiated contact with the following government agencies: 1) National Response Center (Report # 1031907), 2) Florida State Watch Office (Report # 2012-7936), and 3) South Florida Regional Planning Council (voice mail message left with contact number)." The licensee will notify the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-11-30
48546 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-11-29 | 2012-11-29 14:08 | 2012-12-11 | AGREEMENT STATE REPORT - LOST X-RAY FLUORESCENCE ANALYZER The following was submitted by the State of Texas via email: "On November 19, 2012, the Agency [State of Texas] was notified by the licensee that they could not locate a Thermo Niton model number XL-II x-ray fluorescence analyzer. The device contains a 10 millicurie cadmium - 109 source and a 20 millicurie iron - 59 source. The radiation safety officer thought the device had been shipped to the manufacturer, but after he was unable to find any shipping papers for the device, he determined the device was missing. The licensee does not believe the lost device poses an exposure hazard to members of the general public. The investigation into this event is on going. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I - 9019 * * * UPDATE AT 1513 EST ON 12/4/12 FROM ART TUCKER TO S. SANDIN * * * The following update was received from the State of Texas via email: "The Agency [State of Texas] contacted the device manufacturer and was informed that the device requires a password to operate. The Agency [State of Texas] contacted the licensee who stated the password feature was active and that the password would not have been included in the container with the device. "The device contains a 20 millicurie iron - 55 source and not a iron - 59 source as previously reported. The date of the event was November 29, 2012, not November 19, 2012 as stated in the Event Narrative." Notified R4DO (Deese) and FSME Events Resource, ILTAB and MEXICO via email/fax. * * * UPDATE FROM ART TUCKER TO CHARLES TEAL ON 12/11/12 AT 1607 EST * * * "On December 11, 2012, the Agency [State of Texas] was notified by the licensee that the source had been located at the manufacturer facility. The manufacturer provided a letter to the licensee dated March 13, 2012, stating that they had removed the two sources from the device and placed them in storage until they could be disposed of." Notified R4DO (Haire) and FSME Events Resource, ILTAB and MEXICO via email/fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-12-07
48545 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-11-27 | 2012-11-28 20:40 | 2012-11-28 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following is a summary of a report provided by the State of California: On the morning of November 27, 2012 a licensee technician was retrieving a gauge from one of its storage locations when it was noticed that the unit had been broken into and a gauge was stolen. There were six gauges at this location and five of them are accounted for. A review of the gauge locking system was checked / confirmed. The nuclear gauge had two locks with a third lock/cable around the box. The roll-up door was locked and the gate to the storage facility itself was locked. The lock latch to the storage facility was broken. This was the evidence of forced entry into the unit. The police were notified right away and came out and took a report. The licensee will also be placing a local ad, reporting the stolen gauge and offering a reward for any lead information to the finding of this gauge. The licensee was able to move to another storage unit to secure the remaining five gauges. The licensee also purchased heavy duty chains or cables to wrap through all gauges at this location and other storage locations. Gauge Manufacturer: CPN Model: MC1DR S/N: MD70108564 Source: Cs-137 10 mCi AM-241 50 mCi THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-12-06
48544 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-06-03 | 2012-11-28 19:47 | 2012-11-28 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "At 1930 [EST] on November 28, 2012, it was determined that a Notification of Unusual Event (NOUE) was not declared for an event that occurred on June 3, 2012, when an equipment failure resulted in a deposit of ion exchange resin onto the floor of the Radioactive Waste building. Subsequent radiological surveys indicated that conditions met the requirements for a NOUE in accordance with the Perry Nuclear Power Plant Emergency Plan. "This report is being provided within one hour of the recognition of the undeclared event. As discussed in NUREG 1022, Revision 2, an actual declaration of an Unusual Event is not necessary. The Initiating Conditions for the emergency classification no longer existed at the time of recognition. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2012-11-28
48543 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-11-28 18:00 | 2012-11-28 19:35 | 2012-11-28 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-11-28
48542 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-11-28 10:19 | 2012-11-28 10:50 | 2012-11-28 | NOTIFICATION OF UNUSUAL EVENT DUE TO TOXIC GAS IN RADWASTE CONTROL ROOM "Entered an Unusual Event [under Emergency Action Level] MU1, toxic gas, carbon monoxide (CO), detected in the Radwaste Control Room. Levels rose to 34 ppm and the Radwaste Control Room was evacuated prior to reaching the First Energy exposure limit of 35 ppm. The source of the CO has not been determined. There is no radiation release from this event." There were no personnel injuries and offsite assistance was not requested. There was no effect on plant operations. The licensee has notified state and local authorities and the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE AT 1504 EST ON 11/28/12 FROM MARIKIO BLOUNT TO HUFFMAN * * * " [At 1452 EST, the licensee] terminated the Unusual Event for MU1, due to toxic gas - carbon monoxide, detected in the Radwaste Control Room. The source of the carbon monoxide readings was determined to be from a leaking acetylene bottle. The acetylene bottle has been removed from the building. Carbon monoxide readings have returned to normal." The licensee noted that the acetylene is detected as carbon monoxide by the toxic gas monitoring devices. The licensee has notified State and local authorities and the NRC Resident Inspector. Notified R3DO (Stone), NRR (EO) Lubinski) , IRD (Marshall), DHS SWO, FEMA, DHS NICC and NuclearSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-11-28
48541 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-27 20:38 | 2012-11-28 02:38 | 2012-11-28 | CONTROL ROOM VENTILATION SYSTEM WILL NOT AUTOMATICALLY START IN PRESSURIZATION MODE "The control room ventilation system (CRVS) pressurization mode is required to be actuated by a safety injection signal, control room radiation atmosphere air intake, and operator manual actuation in accordance with Technical Specification (TS) 3.3.7. "On November 27, 2012 at 2038 hrs. PST, Pacific Gas and Electric Company (PG&E) identified that none of the CRVS four pressurization fans would operate continuously if they started in response to a safety injection or control room radiation atmosphere intake actuation signal. All of the pressurization fans remain capable of continuous operation via manual actuation. At 2050 PST the Unit 2 CRVS was manually placed in pressurization mode in accordance with TS 3.3.7, ACTION B.1.1. "This was determined to be caused by a recent flow balancing of the CRVS that raised the static air pressure. The increased system static pressure actuates the fan-run pressure switches for each of the four associated pressurization fans, when only a single pressurization fan is operated. This results in the system logic securing all pressurization fans started by the CRVS automatic actuation signals. If all pressure switches actuate, automatically started pressurization fans will be secured until air pressure decays below the fan-run switch setpoint, at which time the pressurization fan would restart. This would result in cyclic operation of the pressurization fan. "The fan-run pressure switches are not part of the manual actuation circuitry for the pressurization fans. "Diablo Canyon (DCPP) is making this 8-hour, non-emergency notification under 10 CFR 50.72(b)(3)(v)(D). "Plant personnel notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-11-28
48540 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-11-27 17:20 | 2012-11-27 18:40 | 2012-11-27 | OFFSITE NOTIFICATION DUE TO A FATALITY "At 1720 hours on November 27, 2012 PPL SSES [Susquehanna Steam Electric Station] notified the Occupational Safety and Health Administration that an employee had suffered a fatality. "On November 27, 2012 at 1313 hours, a PPL employee suffered an apparent heart attack while at the Luzerne County Community College (LCCC) Public Safety Training Institute while performing SCBA [Self Contained Breathing Apparatus] training. The employee was transported to the Geisinger Wyoming Valley hospital and pronounced dead. PPL was notified at 1432 of the fatality. The LCCC training facility is not located on PPL owned property. "This ENS report is being made in accordance with 50.72(b)(2)(xi). "The NRC Resident Inspector was notified." The licensee has also notified the Commonwealth. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-11-27
48539 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2012-11-27 13:15 | 2012-11-27 17:00 | 2012-11-27 | PHYSICAL SECURITY REPORT OF POTENTIAL TAMPERING INVOLVING SAFETY RELATED EQUIPMENT The licensee reported an abnormal condition involving safety related equipment that is suspected to be the result of tampering. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode3: Defueled; FMode3: Defueled | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-11-27
48538 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-11-27 09:00 | 2012-11-27 16:29 | 2012-11-27 | LOSS OF ASSESSMENT CAPABILITY- RADIATION MONITOR INOPERABLE DUE TO DATABASE ERROR "This is a non-emergency notification. At 0900 EST on November 27, 2012, it was discovered that radiation monitor RM-1WV-3546-1, Waste Processing Building Wide Range Gas Monitor was inoperable due to a database error. The database error appears to have occurred at approximately 1724 EST on November 26, 2012. The database error was corrected and the monitor returned to service at 0958 EST on November 27, 2012. This monitor is the only monitor credited in the EALs for monitoring a gaseous release from the Waste Processing Building. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health and safety of the public or the operation of the facility because no events occurred during the time the radiation monitor was out of service. "The NRC Resident Inspector has been notified." See EN #48536 for similar report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-27
48537 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-11-26 19:30 | 2012-11-27 00:02 | 2012-11-27 | DEGRADED CONDITION DUE TO PINHOLE LEAK IN REACTOR HEAD SPRAY LINE "Pinhole leak discovered on a Reactor Head Spray line weld during Nuclear Steam Supply System Leak Test. "Oyster Creek Nuclear Generating Station is currently in the Shutdown Condition executing Refueling Outage 1R24, which includes Nuclear Steam Supply System (NSSS) Leak Testing, prior to startup. "At 1930 on 11/26/2012, a pinhole leak was discovered on a Reactor Head Spray Class 1 piping weld. The leak was discovered during the NSSS Leak Test, while the Reactor was in the Shutdown Condition. The leak is on a flange to piping weld on the Reactor Head Spray system upstream of the N-7B nozzle. Water was found to be weeping from the pinhole leak (approximately 2 to 3 drops per minute). "The cause is under investigation and corrective action plans are being developed. "The leak has been evaluated by Exelon and determined to meet the criteria for reporting identified in NUREG-1022: Welding or material defects in the primary coolant system that cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws,' or ASME Section XI, Table IWB-3410-1, 'Acceptable Standards.'" The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-11-27
48536 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-11-26 10:29 | 2012-11-26 17:29 | 2012-11-26 | LOSS OF ASSESSMENT CAPABILITY- RADIATION MONITOR INOPERABLE FOR PRE-PLANNED MAINTENANCE "This is a non-emergency notification. At 1029 EST on November 26, 2012, radiation monitor RM-1 WV-3546-1, Waste Processing Building Wide Range Gas Monitor was declared inoperable for pre-planned maintenance. This monitor is the only monitor credited in the EALs for monitoring a gaseous release from the Waste Processing Building. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and Is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. This condition does not affect the health of safety of the public or the operation of the facility. An alternative method for sampling and determination of activity levels has been implemented." The licensee stated that the radiation monitor was returned to service at 1728 EST on 11/26/12. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-26
48535 | 0 | DOW CORNING |  |  |  |  | 2012-11-26 09:30 | 2012-11-26 12:50 | 2012-11-26 | PROCESS INSTRUMENT SHUTTER FAILURE During a routine semiannual periodic inspection, a process gauge with a 15 milliCurie Cs-137 source was identified to have a stuck shutter. The gauge was an Ohmart Model SHF1-A45, S/N 0923GK. The instrument is permanently installed on a distillation column about 30 - 35 ft. from the ground. The integrity of the gauge is fine. Surveys indicated that radiation levels surrounding the gauge were less than 1 millirem per hour. The same issue involving this specific gauge was reported previously in EN #46913. The licensee plans on having the gauge repaired by the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-12-04
48534 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-25 11:30 | 2012-11-25 15:13 | 2012-11-25 | AUTOMATIC REACTOR TRIP DUE TO STEAM GENERATOR FEEDWATER REGULATOR VALVE NOT RESPONDING TO DEMAND SIGNAL "This notification is being made to report that Salem Unit 2 has experienced an automatic reactor trip at 1130 EST. The reactor trip was caused by 24BF19, 24 steam generator feedwater regulation valve, not responding to demand signal that resulted in a reactor trip due to 24 steam generator lo-lo level. The cause of the 24BF19 failure to respond to demand is under investigation. "21, 22 & 23 AFW pumps all auto started as expected on the reactor trip feeding the steam generators. 23 AFW pump has been shutdown by procedure. 21 & 22 AFW pumps are maintaining steam generator levels with decay heat removal via the main steam dump system. All control & shutdown rods fully inserted on the reactor trip. "Salem Unit 2 is currently in mode 3. Reactor coolant system temperature is 547 degrees F with pressure at 2235 psig. There are no shut down technical specifications action statements in effect. "All ECCS and ESF systems are available. All safety related equipment responded as expected. There were no personnel injuries associated with this event." The licensee will inform the Lower Alloways Creek Township, the State of New Jersey, and the State of Delaware. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-11-25
48533 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2012-11-23 20:08 | 2012-11-24 03:18 | 2012-11-24 | INADVERTENT LOSS OF INSTRUMENT AIR "On 11/23/2012 at approximately 1956 CST, it was reported that the Control Room (VC) B Chiller breaker was cycling open and closed. In order to stop the cycling, Control Building Unit Sub B was manually tripped causing the following isolations/actuations: loss of power to instrument air (IA) system containment isolation valves causing the Division 2 valves to isolate; loss of power to the low pressure switch that resulted in an automatic start of Division 2 Shutdown Service Water (SX) system; and loss of power to fuel building (VF) system ventilation Division 2 dampers resulting in a trip of the VF system. High Pressure Core Spray (HPCS) became inoperable based on inoperability of the room cooler for the associated Division 4 inverter and battery charger. Operations entered the Loss of AC Power and Automatic Isolation off-normal procedures. Following the loss of power to the VF system ventilation, at 2008, secondary containment differential pressure became positive. At 2009, power was restored to Control Building Unit Sub B and HPCS was restored to operable. At 2011, the standby gas treatment system (VG) was started and at 2013, secondary containment differential pressure was restored. Following re-energization of Unit Sub B, the IA containment isolation valves were re-opened, VG was secured, VF restarted and the Division 2 SX pump was secured. "The loss of secondary containment differential pressure is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material "An unplanned inoperability of HPCS reportable under 10 CFR 50.72(b)(3)(v)(D) as HPCS is a single train safety system "The cause of the breaker cycling is unknown at this time. The NRC Resident has been informed." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-11-24
48532 | 0 | BAYOU INSPECTION SERVICES, INC. |  |  |  |  | 2012-11-22 01:00 | 2012-11-23 14:04 | 2012-11-23 | RADIOGRAPHY CAMERA SOURCE DISCONNECT DURING OFFSHORE OPERATIONS At approximately 0100 CST on 11/22/12, the RSO was informed that the Iridium source on a Spec 150 camera, S/N 1228, had disconnected during radiography on Bisso Marine's "Mighty Chief" pipe-laying barge offshore of Louisiana. The area was posted with access controlled until the RSO arrived and retrieved the disconnected source. No personnel received any unmonitored or overexposures as a result of this incident. Rad exposures for personnel involved are as follows: RSO - 50 mR (WB) [Whole Body] Assistant Radiographer (1) - 100 mR (WB) Assistant Radiographer (2) - 95 mR (WB) Assistant Radiographer (3) - 170 mR (WB) Radiographer - 85 mR (WB) The licensee will submit a written report in 30 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-11-23
48531 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-11-21 | 2012-11-21 17:50 | 2012-11-21 | AGREEMENT STATE REPORT - POTENTIAL DEFECT OF HDR UNIT "At 4:45PM on November 21, 2012 the Radiation Safety Officer of the Southern Ohio Medical Center (OH license number 02120 74 0002) located in Portsmouth, OH called the Ohio Department of Health Bureau of Radiation Protection to make a telephone notification of a potential defect with a Nucletron microselectron HDR unit (SN 10281) containing 7.02 Ci of Iridium-192. "The following event telephone report was made in accordance with OAC 3701:1-38-23(b)(2) (equivalent to NRC 10 CFR Part 21.xx). "The nature of the defect was that prior to initiation of a patient treatment today, the computer console error code indicated a communication problem between the computer console and the HDR unit. The software indicated that the computer system needed to be rebooted which the licensee did. Upon restarting the computer it indicated a delivered treatment time of 24.6 seconds without the licensee initiating the treatment. The licensee did not see the radiation monitor light up, and entered and surveyed the room and patient with a handheld survey instrument. The licensee does not believe that the source left the shielded position. "The licensee was able to complete the treatment fraction as planned, which was fraction number ten of ten fractions of 390 seconds. This did not result in a medical event. "The Radiation Safety Officer notified their management and the manufacturer." Ohio Event Report Number: 2012-033. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-11-29
48530 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-11-21 | 2012-11-21 15:09 | 2012-11-21 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the Commonwealth of Kentucky via facsimile: "Kentucky Radiation Health Branch was notified on November 21, 2012 by the [licensee's] Medical Physicist, that a medical event occurred during the final hours of a gynecological radiation implant using Cs-137. The 40 hour procedure was scheduled to end today at 0915 CST. Upon arrival at 0910 to remove the applicators, the patient stated [that] shortly after 0600 she felt something had moved or urination or gel had come out of her. As the Medical Physicist pulled back the patient's gown, she saw the packing from the implant completely out of the patient. The top of the packing was approximately 1cm from the perineum. The sources were quickly removed from the applicators and put in a shielded transport container. The Medical Physicist's initial dose estimate to the skin on the patient's thigh and surrounding area is close to 450 cGy based on the applicator being out for 3 hours. There were a total of 5 sources used, 3 in the tandem all had the same activity (96.11 cGy*cm2/hr) and one in each ovoid, both having an activity of 29.63 cGy*cm2/hr. Radiation survey measurements of the applicators, patient, and room were below background. The RSO, patient, and prescribing physician are aware of the event that occurred and a follow-up is scheduled. The State will continue to keep NRC informed of the status of our investigation." KY Event Report ID# KY120014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-11-29
48529 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-11-21 10:36 | 2012-11-21 13:01 | 2012-11-21 | OFFSITE NOTIFICATION DUE TO CHLORINE LEAK "A chlorine leak was discovered in an area near the Unit 2 cooling towers. The leak has been isolated; the amount leaked is under investigation. Sodium bisulfite has been used to neutralize the [leaked] chlorine. The Georgia Environmental Protection Division and U.S. Coast Guard have been notified." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-11-21
48528 | -1 | STAMFORD HOSPITAL |  |  |  |  | 2012-05-01 | 2012-11-21 12:31 | 2013-02-04 | MEDICAL EVENT - ACTUAL DOSE DIFFERED FROM PRESCRIBED DOSE An NRC Region I Inspector (Abogundi) performed an inspection at the licensee facility and determined that a medical event occurred and should have been reported. In May, 2011, a patient received prostate LDR (Low-Dose Rate brachytherapy) treatment using 86 Pd-103 seeds for a prescribed dose of 125 Gy. During post-treatment evaluation, it was determined that the patient received between 72% and 75% of prescribed dose. The prescribing physician was notified and will not be notifying the patient due to treatment success. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM SARAH BULL TO HOWIE CROUCH AT 1130 EST ON 2/4/13 * * * After reviewing their reporting procedures and in consultation with their Regional NRC Inspector (Abogundi), the licensee determined that this event did not meet their activity-based (versus dose-based) reporting criteria. Based on this information, the licensee has retracted this event notification. Notified R1DO (Powell) and FSME Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-11-29
48527 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2012-11-20 13:21 | 2012-11-20 18:27 | 2013-01-16 | DRYWELL RADIATION MONITOR INOPERABLE "At 1321 [CST] hours on November 20, 2012, the 1B Drywell Radiation Monitor exhibited degraded performance at the conclusion of surveillance testing. This monitor provides the input into one division of the primary containment isolation logic for a Group II isolation. As a result, the channel was placed in a tripped condition in accordance with Technical Specification 3.3.6.1, Condition B. "Given both divisions are required to complete the Group II isolation logic, this condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The station is currently taking action to troubleshoot and restore the 1B Drywell Radiation Monitor to an operable condition." "The NRC Resident Inspector has been notified." * * * UPDATE AT 1303 EST ON 01/16/13 FROM DEREK DROCKELMAN TO S. SANDIN * * * "ENS Retraction - Drywell Radiation Monitor Inoperable "The purpose of this notification is to retract the ENS Report made on November 20, 2012, at 1827 EST hours (ENS Report # 48527). "Further evaluation performed by Quad Cities Station confirms the 1B Drywell Radiation Monitor would have performed its safety function when required. Based on this subsequent evaluation, ENS Report # 48527 is being retracted. "Note: On November 21, 2012, the 1B Drywell Radiation Monitor was successfully repaired and returned to Operable status." The licensee informed the NRC Resident Inspector. Notified R3DO (Bloomer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-11-20
48526 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-11-19 20:00 | 2012-11-20 15:51 | 2012-11-20 | NON-LICENSED CONTRACTOR SUPERVISOR TESTS POSITIVE FOR ALCOHOL A non-licensed contract acting supervisor tested positive for alcohol on a random fitness for duty test. The contractor's access to the plant has been denied. The licensee has notified the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-11-20
48525 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-11-20 06:45 | 2012-11-20 12:30 | 2013-01-11 | CONDITION THAT COULD HAVE PREVENTED AUTOMATIC ISOLATION OF REACTOR WATER CLEANUP SYSTEM "Susquehanna Unit 2 discovered a condition that could have prevented the primary containment isolation valves for the reactor water cleanup (RWCU) system from automatically isolating on a high differential flow instrumentation signal. "The RWCU system high differential flow signal was found to be indicating downscale due to an instrument failure. Both divisions of the RWCU high differential flow isolation logic utilize the same differential flow instrument loop. Thus, this single instrument failure would have prevented automatic isolation of the RWCU inboard and outboard primary containment isolation valves on a high differential flow signal. "The other RWCU primary containment isolation instrumentation functions remained operable and the associated RWCU system primary containment isolation valves were capable of being remotely closed by the control room operators. "At the time of discovery, Unit 2 was in Mode 2 due to an unplanned shutdown and all control rods had already been fully inserted as part of a soft shutdown sequence." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM DUTTRY TO KLCO ON 1/11/13 AT 2155 EST * * * "Following the ENS report (EN 48525), Susquehanna determined that although the RWCU high differential flow isolation instrumentation would have prevented automatic isolation of the RWCU inboard and outboard primary containment isolation valves on a high differential flow signal, the RWCU high flow isolation instrumentation would detect a high flow condition and generate an isolation signal that would close the isolation valves. "The RWCU high differential flow instrumentation is downstream of the RWCU pumps and it calculates the difference (delta) in flow between the inlet and the outlet of the RWCU heat exchangers. The SSES [Susquehanna Steam Electric Station] Technical Specification (TS) Bases Section 3.3.6.1 states that the RWCU Differential Flow signal is to detect a break in the RWCU system (pipe severance and separation). Engineering analysis determined that the RWCU pumps would run-out if a break occurs downstream of the pumps and the RWCU system flow rate would be approximately 1000 gpm, with one RWCU pump in operation. The flow rate would be higher for two RWCU pumps in operation. "Therefore, RWCU isolation would occur from the RWCU Flow - High isolation signal due to a flow rate that is greater than 472 gpm (TS Table 3.3.6.1-1). This high flow isolation does not rely on the RWCU high differential flow instrumentation. The above analysis is consistent with the FSAR discussion in section 7.3.1.1a.2.4.1.9.3. "Based on the above, Susquehanna has determined that the RWCU isolation function would still be completed if a pipe break occurred downstream of the RWCU heat exchangers and the RWCU high differential flow instrumentation is inoperable. Since there was no loss of safety function of structures or systems that are needed to control the release of radioactive material, this ENS report is retracted." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-11-20
48524 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-11-20 04:34 | 2012-11-20 11:59 | 2012-11-20 | LOSS OF ASSESSMENT CAPABILITY - RADIATION MONITOR DECLARED INOPERABLE "This is a non-emergency notification. At approximately 0434 [EST] on November 20, 2012, radiation monitor RM-1WV-3547-1, Waste Processing Building Wide Range Gas Monitor (WRGM) was declared inoperable due to a loss of sample flow. This monitor is the only monitor credited in the Emergency Action Levels (EALs) for monitoring a gaseous release from the radiochemistry facility. "This radiation monitor is necessary for accident assessment and is credited for EAL classification in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Revision 2. This condition does not affect the health or safety the public or the operation of the facility. An alternative method for sampling and determination of activity levels has been implemented. Actions are being taken to restore the monitor functional status. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-20
48523 | 0 | U. S. ARMY |  |  |  |  | 2012-10-29 | 2012-11-20 11:41 | 2012-11-20 | MISSING IMPROVED CHEMICAL AGENT MONITOR An ICAM (Improved Chemical Agent Monitor) is missing at Fort Riley, KS. The ICAM contains a 10 mCi Nickel-63 source. The licensee has initiated a formal investigation and notified NRC Region 3 Inspector (McGraw). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-11-28
48522 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-11-19 16:25 | 2012-11-20 11:02 | 2012-11-20 | UNINTERRUPTIBLE POWER SUPPLY SAFETY EQUIPMENT FAILURE "At 1625 CST on 11-19-12, Electrical Maintenance and Power Operations were in the process of changing a circuit breaker in the C-409 facility which supplies power to the C-409 Criticality Accident Alarm System (CAAS) Uninterruptable Power Supply (UPS). This UPS supplies power to the C-409 CAAS horns. Procedure CP2-CO-ON3031 was being utilized and the CAAS Horn Power UPS was being monitored continuously to maintain the CAAS operable. As soon as the breaker was opened it was identified that the UPS failed to throw over to battery power. At that point the breaker was re-closed and AC power restored to the CAAS horns. The time that AC power was off the CAAS horns was approximately 3-5 seconds. There were no fissile material operations in progress in the C-409 facility. This event is reportable as a 24 hour event in accordance with 10CFR76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR [Technical Safety Requirements] to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2012-11-20
48521 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-05 | 2012-11-19 12:53 | 2012-11-19 | TEXAS AGREEMENT STATE REPORT - POTENTIAL PROSTATE THERAPY UNDERDOSE "On November 16, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee that a potential medical event occurred. On January 5, 2012, a patient received an Iodine-125 prostate seed implant of 63 seeds (0.475 mCi/seed). The implant was completed as planned and verification films were taken and confirmed that the implant appeared normal and no concerns were expressed during or immediately after the implant procedure. In late August or early September, a post plan was created for evaluation. 63 seeds were localized by a staff physicist and sometime after or during the post plan analysis, the staff physicist noticed the seed placement appeared inconsistent with the pre-plan. The staff physicist informally notified the Chief Physicist and a Senior Radiation Oncologist who each viewed the plan and concluded that further evaluation was needed. The implant appeared shifted inferior to the prostate. The final determination is that all of the parameters of the implant (activity per seed, total activity, seed distribution, etc.) were all consistent with the pre-plan except that the center of the seed distribution and the center of the prostate were separated by a couple of centimeters and the most inferior seed was approximately 3.5 cm inferior to the apex of the prostate. The licensee has been contacted to report prescribed dose, actual dose, and percent of dose received. Additional information will be provided IAW SA-300." Texas Incident# I-9014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-11-27
48520 | 0 | OAKWOOD MEDICAL CENTER |  |  |  |  | 2012-09-18 | 2012-11-19 13:00 | 2012-11-19 | PATIENT RECEIVED LESS THAN PRESCRIBED DOSE FOLLOWING BRACHYTHERAPY TREATMENT On 9/18/12, a patient at the Oakwood Medical Center was administered a brachytherapy treatment of the prostate. 72 Iodine-125 seeds were implanted at the time. On a post-implant study on 11/18/12, it was determined that D90 dose for the treatment was 68.3%. The study indicated that the anterior prostate was somewhat "cold". There was some evidence of seed migration. The physician has been notified. The underdose is not expected to have any significant impact on the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-11-27
48519 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-06-03 | 2012-11-19 11:03 | 2012-11-19 | AGREEMENT STATE REPORT - MEDICAL EVENTS INVOLVING PROSTATE SEED IMPLANTS The following information was obtained from the Commonwealth of Kentucky via fax: "KY RHB [Radiation Health Branch] was notified via e-mail by the Medical Physicist of the facility of two past medical events. The medical events involved two patients treated for prostate cancer with I-125 and Pd-103 seeds for which the Medical Physicist had developed the treatment plans. The Radiation Oncologist and the Urologist, who performed the procedures determined the dose delivered to the target organ based on D90 was less than 80% using the Variseed Treatment Planning software. The Radiation Oncologist who contoured the prostate and determined the post implant D90 doses, was not aware that a D90 less than 80% of the prescribed dose was a medical event that required reporting to the Radiation Health Branch. The patient treated on 6/3/11 was treated with 101 Bard STM1251, I-125 seeds (0.37 mCi/seed) monotherapy and received a D90 of 76.7%. The intended dose to the prostate was 145Gy and the administered dose was 111.2Gy. The second patient was treated on 4/12/12 with 73 seeds of Theraseed Model 200, Pd-103 (1.1 mCi/seed) as a part of a boost therapy to IMRT [Intensity Modulated Radiation Therapy]. This patient received a post implant D90 of 68.3%. The intended dose to the prostate was 90Gy and the administered dose was 61Gy. The Medical Physicist discovered these two medical events after performing an audit of the facility's permanent implant prostate brachytherapy program since its inception for a total of 71 patients. The State will continue to keep NRC informed of the status of our investigation. "KY Event Report ID No: KY120013" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-11-27
48518 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2012-11-18 11:30 | 2012-11-18 11:10 | 2012-11-19 | LOSS OF ASSESSMENT CAPABILITY DUE TO INTEGRATED PLANT COMPUTER PLANNED MAINTENANCE "On 11/18/2012 at approximately 1130 EST, the Summer Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) will be taken out of service for approximately 12 hours to support a planned maintenance on an inverter that feeds the station's Integrated Plant Computer System (lPCS). During this time frame. ERDS and SPDS will be unavailable. Should the need arise, plant status information will be communicated to the NRC using other available communication systems. SPDS and ERDS are expected to be restored on 11/18/2012 at 1800 EST. This event is reportable under 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE FROM MICHAEL MOORE TO DONALD NORWOOD AT 1003 EST ON 11/19/2012 * * * "On November 18, 2012, at approximately 1730, IPCS was returned to service. Completing this planned maintenance activity restored the VCSNS Safety Parameter Display System and the Emergency Response Data System (ERDS). ERDS was tested this morning, November 19, 2012, by VCSNS and the NRC ERDS Help Desk to verify system operability. "The NRC Resident Inspector has been notified." Notified R2DO (Widmann). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-18
48517 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-11-17 20:00 | 2012-11-17 22:16 | 2012-11-17 | AUTO-INITIATION FEATURE OF TECHNICAL SUPPORT CENTER VENTILATION IMPROPERLY INHIBITED "In anticipation of core offload, the control room emergency ventilation system was placed in recirculation mode. As a result of a deficient procedure, an automatic initiation feature to the Technical Support Center (TSC) ventilation system was inhibited from 11/16/12 at 2325 [EST] to 11/17/12 at 1419 [EST]. "The Turkey Point TSC habitability design basis assumes that upon discovery of an accident condition, an initiation signal will automatically place both control room and TSC ventilation systems in recirculation. "Contrary to the design basis, it was discovered on 11/17/12 at 2000 [EST] that when the TSC ventilation system was placed in the 'inhibited mode,' the automatic initiation feature to the TSC ventilation system recirculation mode was defeated. The TSC ventilation system otherwise remained functional and available. "Upon discovery of this condition, the TSC inhibit switch was returned to enable which would allow the TSC to automatically go on recirculation from an automatic start signal. No accident conditions occurred that warranted a need to activate any emergency operations facilities. "This notice is made in accordance with 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-17
48516 | 0 | ACUREN USA |  |  |  |  | 2012-11-16 14:00 | 2012-11-17 14:50 | 2012-11-17 | RADIOGRAPHY CAMERA SOURCE CONTROL CABLE BREAKAGE The following is a summary of a report provided by the licensee to the NRC Operations Center: The licensee could not fully retract a radiography camera source into the shielded position (Sentinel Delta 880D, Serial # 87400B). It was determined that the control assembly cable had broken approximately three inches from the source connector. The source assembly was gravity fed from the guide tube onto the ground and then shielded by reverse placement into another Sentinel exposure device. A serviceable control assembly was then connected to the original exposure device and the control cable routed through the device and guide tube, then connected to the source. The source was then retracted into the original device without incident. Corrective actions taken and planned to prevent reoccurrence: Remove 100% of control assemblies from service and complete a thorough inspection. Perform a safety stand down with all radiographers and assistants for review of daily equipment inspections. The four individuals involved in this event received exposures of 95 mR; 48 mR; 20 mR; and 20 mR respectively. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-11-26
48515 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-11-16 16:40 | 2012-11-17 13:45 | 2012-11-17 | AGREEMENT STATE REPORT - DAMAGED TROXLER DENSITY GAUGE The following information is a summary of a report received from the Ohio Bureau of Radiation Protection: A Troxler nuclear density gauge was being used on an Ohio Earthwork Project in Riley Township, Ohio. The gauge technician set the gauge on the ground and left it unattended while preparing for testing. A bulldozer moved over the location where the gauge had been set down without realizing the gauge was there. The isotopes in this unit are 8 millicuries of cesium 137 and 40 millicuries of Am-241/Be. The damaged unit was a Troxler Model Number 3430, Serial Number 21036. The source serial number for the Cs 137 is 75-2465 and the source serial number for the Am-241:Be is 47-16507 The licensee dispatched a contractor (Solutient Technologies) to the jobsite. Solutient identified that no leakage occurred, that the sources are intact and in their protective housing. The sources were placed in a 5 gallon steel drum and the remainder of the gauge was placed in a 30 gal steel drum and deemed suitable for transport. These containers were removed from the site on Saturday, November 17, 2012 and returned to the licensee's Cleveland office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-11-26
48514 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-17 10:23 | 2012-11-17 12:30 | 2012-11-17 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "At 1023 CDT Comanche Peak Unit 2 automatically tripped due to steam generator low level. The trip was uncomplicated. All control and shutdown rods fully inserted. Neither emergency diesel generator started. All safety systems functioned as designed. Both motor driven and the turbine driven AFW pumps started as required to restore steam generator level as a result of the trip. The turbine driven AFW pump was returned to auto-start status. The turbine driven AFW pump has been placed in pull-out as per procedure after verifying normal motor driven AFW pump operation. "Currently Unit 2 is in Mode 3, (no-load Tave 557 - degrees Fahrenheit) with temperature being maintained with the AFW and steam dumps to the main condenser. Recovery actions will be planned. All electrical busses are powered from offsite power and grid conditions are stable. "The initiating event appears to be a sheared instrument air tubing line that feeds the common heater drain pump discharge valve which will fail close resulting in loss of all heater drain flow." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-11-17
48513 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-11-15 | 2012-11-16 20:06 | 2012-11-26 | AGREEMENT STATE REPORT - IRIDIUM-192 SOURCE MISSING DURING SHIPMENT A representative from the Massachusetts Radiation Control Program called to report information he had received concerning a missing Iriduim-192 Category 3 source shipment that was being imported to QSA Global in Burlington, Massachusetts from Australia. The shipment had cleared customs at JFK and was being stored at a warehouse near JFK (Air Menzies Aviation). On the evening of 11/15/12, the package was scheduled to be picked up at the warehouse, however, it could not be found. At this point the shipment is considered missing. QSA currently believes that the package is simply misplaced at this time. QSA and the carrier continue to search for the package. * * * UPDATE FROM M. WHALAN TO P. SNYDER ON 11/26/12 AT 0819 EST * * * The source was found by the licensee at an alternate location. Notified R1DO (Dwyer), ILTAB (Hahn) and FSME Event Resource (Email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-11-26
48512 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-16 15:00 | 2012-11-16 15:35 | 2012-11-16 | UNUSUAL EVENT DECLARED BASED ON FIRE ALARM IN PROTECTED AREA The licensee received a fire alarm in an auxiliary building tunnel (Zone 146) that could not be verified within 15 minutes. An unusual event was declared (EAL HU2) at 1500 EST. At 1505 EST the licensee fire responders were able to reach the location of the alarm and confirmed that there was no fire. The licensee has performed inspections of the area and do not yet know the cause of the fire alarm but are certain that it was not caused by an actual fire. The cause of the fire alarm is still under investigation. No offsite assistance was summoned for this event. Following restoration of fire protection system to a normal status the licensee terminated the unusual event at 1550 EST. The licensee has notified State and local authorities and the NRC Resident Inspector. No press release is planned at this time. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-11-16
48511 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-10-01 14:03 | 2012-11-16 10:58 | 2012-11-16 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SYSTEM ACTUATION "In accordance with 10CFR50.73(a)(2(iv)(A), this telephone notification reports an invalid actuation of the Unit 1 train A (1A) Emergency Diesel Generator (DG) on October 1, 2012, at 1403 hours. At the time of the event Unit 1 was in Mode 5, Cold Shutdown. The 1A DG was undergoing a surveillance procedure that verifies a safety injection override signal when a technician actuated the incorrect under voltage relay which resulted in the inadvertent start of the 1A DG. The engine functioned successfully and ran unloaded, as expected. The cause is attributed to the technicians failing to verify they were actuating the correct relay. This condition was entered into the corrective action program." The licensee notified the NRC Resident Inspector and the Illinois Department of Nuclear Safety. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-11-16
48510 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-11-16 08:10 | 2012-11-16 09:04 | 2012-11-16 | SPDS OUT OF SERVICE DUE TO PLANNED MAINTENANCE "A planned maintenance evolution at Duane Arnold Energy Center (DAEC) to replace a hard drive in the plant process computer will result in a loss of all SPDS indication for a duration of less than six hours. "There is no planned maintenance affecting Primary Indications or Annunciators in the Control Room which would affect the plant's ability to assess or monitor an accident or transient in progress. "This notification is being made pursuant to 10CFR50.72(b)(3)(xiii)." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1433 EST ON 11/16/12 FROM MANKIN TO HUFFMAN * * * The planned maintenance has been completed and SPDS returned to service at 1431 EST. The licensee has notified the NRC Resident Inspector. R3DO(Kunowski) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-16
48509 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-11-09 | 2012-11-15 13:27 | 2012-11-15 | AGREEMENT STATE REPORT - PATIENT RECEIVED WRONG TREATMENT PLAN The following report was received from the State of Florida via facsimile: "On November 9, 2012, two patients with a different treatment plan (HDR Brachytherapy) were scheduled on the same day, patient 2 received patient 1 treatment plan. [The] error [was] found during mid treatment and stopped. Oncologist and patient informed, treatment continued under original plan, expect no adverse effects to patient Primary care physician has not been informed as of 13 November 2012, 0800 hours. A private company Radio Physics Associates (TRP-73) performs procedures involving HDR at this hospital. Investigation assigned to [State of Florida Bureau of Radiation Control] Tampa Office. No further action will be taken on this incident. "Isotope involved: Ir-192; Activity: 8.3 Ci" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-11-23
48508 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-11-14 09:27 | 2012-11-14 16:13 | 2012-11-17 | RADIATION MONITOR OUT OF SERVICE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "On November 14, 2012, Radiation Monitor R-9, Letdown Line Radiation Monitor was removed from service at 0927 [EST] hours following failure of the internal and external source checks during performance of radiation monitor source checks. Both source checks failed high. "This radiation monitor is used for accident assessment and is credited for Emergency Action Level (EAL) classification for an Unusual Event in the Robinson Nuclear Plant Emergency Plan. Additionally, this monitor is one of multiple indicators used to detect the loss of a fission product barrier. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. Actions are in place to restore the monitor to functional status. "The NRC Resident Inspector has been notified." * * * UPDATE ON 11/17/12 AT 0812 EST FROM GEORGE CURTIS TO DONG PARK * * * At 1717 EST on 11/16/12, the Letdown Line Radiation Monitor was placed back in service and is functional. The licensee has notified the NRC Resident Inspector. Notified R2DO (Widmann). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-14
48507 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-11-14 10:00 | 2012-11-14 15:43 | 2012-11-14 | LOSS OF ASSESSMENT CAPABILITY - GROSS FAILED FUEL DETECTOR "This is a non-emergency notification. At approximately 10:00 am on November 14, 2012, it was identified that on June 14, 2012 at 4:04 am, the Gross Failed Fuel Detector was not controlling flow as required and therefore would not be able to perform its function. Further investigation revealed that the monitor has been in and out of service since that time. The last time the monitor was taken out of service was November 2, 2012 at 08:40 am and currently remains out of service. This condition has not impacted the health and safety of the public as this condition is not impacting the operation of the facility. "This radiation monitor is necessary for accident assessment and is credited for Emergency Action Level (EAL) classification for an Unusual Event in the Harris Nuclear Plant Emergency Plan. Inability to classify an EAL due to an out of service monitor is considered a loss of accident assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. Actions are in place to restore the monitor to functional status." The licensee can obtain chemistry grab samples to determine if there is failed fuel though this is not as responsive. The Gross Failed Fuel Detector is planned for repair on 11/16/2012. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-14
48506 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-09-18 00:45 | 2012-11-14 15:40 | 2012-11-14 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID ACTUATION OF CONTAINMENT ISOLATION SIGNALS "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On September 18, 2012, at 0045 hours Central Daylight Time (CDT), during performance of surveillance procedure 1-SR-3.3.6.2.3(B), Reactor/Refueling Zone Ventilation Radiation Monitor 1-RM-90-141/143 Calibration and Functional Test, a Primary Containment Isolation System (PCIS) partial Group 6 isolation occurred. The partial Group 6 isolation caused the initiation of Standby Gas Treatment (SBGT) subsystems 'A' and 'B' and Control Room Emergency Ventilation (CREV) subsystem 'A', and the isolation of the Unit 1 H2O2 analyzer and the 1-RM-90-256 Continuous Air Monitor (CAM). Due to the isolation of the 1-RM-90-256 CAM, Operations personnel declared the drywall CAM inoperable and entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.5 Condition B. "Plant conditions which initiate PCIS Group 6 actuations are Reactor Vessel Low Water Level (Level 3), High Drywall Pressure, and Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). At the time of the event, these conditions did not exist, therefore, the partial actuations were invalid. "The affected equipment responded as designed. On September 18, 2012, at 0123 hours CDT, Operations personnel commenced restoring the affected systems to normal. At 0132 hours CDT, the 1-RM-90-256 CAM was returned to service, the SBGT subsystems 'A' and 'B' were secured, and TS LCO 3.4.5.B was exited. At 0133 hours CDT, the CREV subsystem 'A' was secured and at 0138 hours CDT, the Unit 1 hours analyzer was returned to service. "This condition was the result of improper test setup during performance of 1-SR-3.3.6.2.3(B). It was determined that a jumper installed during the performance of 1-SR-3.3.6.2.3(B) to prevent an invalid actuation was not installed correctly. When the detector lead was lifted, an isolation signal was received. The surveillance procedure was stopped and the equipment was restored to pre-test condition. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 611238. "The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-11-14
48505 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-09-17 03:12 | 2012-11-14 15:34 | 2012-11-14 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID ACTUATION OF CONTAINMENT ISOLATION SIGNALS "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On September 13, 2012, Browns Ferry Nuclear Plant (BFN) personnel completed the installation of three metal-oxide varistors (MOVs), MOV1, MOV2, and MOV3, on the governor of the 3C Emergency Diesel Generator (EDG) as part of a design change. On September 17, 2012, at 0312 hours Central Daylight Time (CDT), during post-modification testing of the 3C EDG, the Direct Current (DC) control circuit breaker tripped, causing a loss of governor control power for the 3C EDG. This event resulted in the loss of the 3B Reactor Protection System (RPS) Bus. In addition, Primary Containment Isolation System (PCIS) groups 3, 6, and 8 successfully isolated. The Steam Vault Booster Fan tripped and the 3B Steam Jet Air Ejector isolated. Standby Gas Treatment (SGT) Trains 'A' and 'B' and Control Room Emergency Ventilation Train 'A' initiated. The SGT Train 'C' was already in service for BFN, Unit 3, Reactor Zone Ventilation. "Plant Conditions which initiate PCIS Group 3 actuations are Reactor Vessel Low Water Level or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level, High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The affected equipment responded as designed. On September 17, 2012, at 0335 hours CDT, Operations personnel restored the 3B RPS Bus. "This condition was the result of MOV1 and MOV3 operating due to induced current in their associated ground cables. This resulted in grounds which tripped the DC control power breaker. To address this condition, MOV1 and MOV3 were permanently removed. "There were no safety consequences or impact to the health and safety of the public as a result of this event. This event was entered into the Corrective Action Program as Problem Evaluation Report 610091. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-11-14
48504 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-13 09:00 | 2012-11-13 07:49 | 2012-11-13 | PARTIAL LOSS OF EMERGENCY ASSESSMENT DURING PLANNED MODIFICATIONS "Cook Nuclear Power Plant will begin a cyber security modification of Unit 1 and Unit 2 Plant Process Computers (PPCs) and associated network infrastructure on Tuesday, November 13, 2012 at 0900 EST. This includes the Emergency Response Data System (ERDS) communication with the NRC Operations Center. "The entire PPC for each unit will be out of service and unavailable for approximately 6 hours. During that time, the PPC satellite display systems in the Control Rooms, TSC and EOF will be unavailable. After approximately 9 hours, the ERDS will be restored to service along with the satellite display systems in the Control Rooms, TSC and EOF. "Compensatory measures exist within the DC Cook Emergency Response procedures to provide plant data in the event of an actual Emergency to the NRC Operations Center until the ERDS can be returned to service. Unavailability of the ERDS and Control Room, TSC and EOF data is being reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a major loss of emergency assessment capability. The NRC Resident Inspector has been notified. A follow-up ENS communication will be made when both units ERDS are fully restored to service. "Unit 1 and Unit 2 PPC availability is expected to be restored on Tuesday, November 13, 2012 at 1500 EST. ERDS communication with the NRC Operations Center is expected to be restored on November 13, 2012 at 1800 EST." * * * UPDATE FROM BRADDOCK LEWIS TO HOWIE CROUCH @ 1559 EST ON 11/13/12 * * * The licensee notified the Operations Center that the PPC work was delayed and, as a consequence, ERDS restoration will be delayed. Work on the PPC continues. The licensee has notified the NRC Resident Inspector. Notified R3DO (Giessner) and ERDS Group (via email). * * * UPDATE AT 1908 EST ON 11/13/12 FROM GREG KANDA TO MARK ABRAMOVITZ * * * ERDS was declared operable at 1815 EST. The licensee notified the NRC Resident Inspector. Notified R3DO (Giessner) and ERDS Group (via email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-13
48503 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-11-12 15:51 | 2012-11-12 20:52 | 2012-11-12 | REACTOR BUILDING ISOLATION WITH STANDBY GAS TREATMENT SYSTEM ACTUATION DURING RADIOACTIVE MATERIAL MOVE "At 1551 EST on 11/12/12, the 'A' Refuel Floor Process Radiation Monitor reached 62 mR/hr during movement of the old steam dryer in the plant reactor building. This resulted in the isolation of the drywell containment air monitor and the oxygen analyzer primary containment isolation valves. The signal also resulted in a reactor building isolation (Secondary Containment), start of 'A' Standby Gas Treatment, and transfer of the control room ventilation to the High Radiation Mode. "All automatic isolation valves have been reset. Reactor building and control room ventilation have been reset. Standby gas treatment has been secured. There were no challenges to the health and safety of the general public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-11-12
48502 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-11-12 11:00 | 2012-11-12 14:13 | 2012-11-12 | TECHNICAL SUPPORT CENTER INOPERABLE NUMEROUS TIMES OVER PREVIOUS THREE YEARS WITHOUT PROPER REPORTING "This non-emergency event report is being made per 10CFR50.72(a)(1)(ii) which requires reporting events that occurred within three years of the date of discovery. "Based on operating experience, Engineering personnel reviewed past maintenance activities involving the Technical Support Center (TSC) ventilation system (VH system) and identified 11 occasions between September 2009 and October 2012 (3 years) where the VH system functions could not have been restored within the required facility activation time. The specific instances have been documented in our corrective action program. "If an emergency had been declared during these periods and TSC ERO activation was required, the TSC would have been staffed and activated unless the TSC became uninhabitable due to ambient temperatures, radiological or other conditions. If relocation of the TSC staff was necessary, the Station Emergency Coordinator would relocate the staff to an alternate TSC location. "Practices and processes have been revised to improve control of TSC maintenance activities and to improve facility availability going forward. In addition, site reporting guidance has been revised to assure timely reporting of these types of events if required. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2, since the maintenance activities affected an emergency response facility." The licensee will be notifying the NRC Resident Inspector and state and local authorities in North Carolina and South Carolina. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-12
48501 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-11-11 03:55 | 2012-11-11 06:08 | 2012-11-11 | REACTOR SCRAM DUE TO TURBINE TRIP FOLLOWED BY UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER AND BUS DUCT FIRE "An unplanned, automatic reactor scram occurred at 0355 EST due to a Main Turbine trip signal. All safety systems operated and actuated as expected. Both the Main Transformer, T-1A and normal station services transformer T-4 activated their respective deluge systems. On-site fire brigade and offsite fire assistance have successfully extinguished the T-1A transformer fire. There is still an active fire in the T-1A bus ductwork. The plant will be taken to cold shutdown conditions. At 0545 EST the plant entered the emergency plan at the NUE level due to inability to successfully extinguish the fire." All control rods fully inserted following the reactor scram. MSIVs remain open with decay heat being removed via steam to the main condenser using the bypass valves. All electrical buses are powered from their normal offsite reserve source. The licensee notified the NRC Resident and appropriate State and local government agencies. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE FROM JOHN WALKOWIAK TO DONALD NORWOOD AT 0642 EST ON 11/11/2012 * * * As of 0639 EST the fire in the T-1A bus ductwork has been extinguished. * * * UPDATE FROM MARK HAWES TO DONALD NORWOOD AT 0747 EST ON 11/11/2012 * * * "Local fire department is on-site. No radiological release and no protective actions required. Plant cooldown in progress." * * * UPDATE FROM MARK HAWES TO DONALD NORWOOD AT 0810 EST ON 11/11/2012 * * * "The Unusual Event (HU 6.1) has been terminated at 0801 EST. Cooldown in progress to cold condition. Reactor level at 206 inches and pressure is at 530 pounds." The licensee notified the NRC Resident and appropriate State and local government agencies. Notified R1DO (Dentel), NRR EO (McGinty), IRD (Gott). Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2012-11-11
48500 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-11-09 04:20 | 2012-11-10 16:20 | 2012-11-10 | RPS ACTUATION RESULTING FROM LOW REACTOR WATER LEVEL "At approximately 04:20 hours on November 9, 2012, Susquehanna Steam Electric Station Unit Two reactor received a subsequent scram due to low reactor water level during recovery from the scram (EN# 48496) that occurred at approximately 01:18 hours due to a loss of ICS (Integrated Control System; which controls the reactor feed and reactor recirculation systems). Reactor water level was +15 inches at the time of the trip. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "The reactor is currently stable in Mode 3. Unit One continued power operation. The NRC Resident Inspectors were notified." The licensee will notify the Pennsylvania Emergency Management Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-11-10
48499 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-11-09 15:30 | 2012-11-09 17:19 | 2012-11-15 | SAFEGUARDS REPORT - MISSING SAFEGUARDS INFORMATION The licensee has determined that some safeguards information is unaccounted for. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION AT 1520 EST ON 11/15/12 FROM BILL ARENS TO HUFFMAN * * * Upon further review, the missing safeguards information was determined to be not significant and did not meet the requirements for a 1-hour non-emergency report. Consequently the licensee has retracted this report. Contact the Headquarters Operations Officer for additional details. R2DO (Widmann) notified. The 73.71 group was informed via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-11-09
48498 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-11-07 | 2012-11-09 17:02 | 2012-11-09 | AGREEMENT STATE REPORT - DOSE TO EMBRYO/FETUS The following information was obtained from the Commonwealth of Massachusetts via facsimile: "A lung cancer patient [underwent] PET and CT [scans and received] a calculated dose of 2 Rem to [her] embryo. The patient was asked if she was pregnant and she replied no. The dose was calculated to be 8.8 mGy from CT and 11.5 mGy from PET." The patient was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-11-19
48497 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-11-09 11:00 | 2012-11-09 14:59 | 2012-11-09 | UNANALYZED CONDITION - SYSTEM AS-FOUND CONDITION NOT FULLY DESCRIBED IN ISA "As part of the ongoing GNF-A review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), an accident sequence associated with hydrogen piping in the laboratory area was being evaluated. As part of this evaluation, a configuration that had not been properly analyzed was identified. Based on a review of this as-found condition, it was determined at approximately 11 AM [EST] on November 9, 2012 that the system was not fully described in the ISA and resulted in a failure to demonstrate performance requirements were met. "Hydrogen supply to the affected piping system has been isolated. Additional corrective actions and extent of condition are being evaluated. "This event is being reported pursuant to the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery." The licensee determined the as-found condition is of minimal safety significance. The licensee will be notifying NRC Region 2, State, and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-11-09
48496 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-11-09 01:18 | 2012-11-09 03:03 | 2012-11-09 | UNIT 2 MANUAL SCRAM DUE TO LOSS OF THE INTEGRATED CONTROL SYSTEM "At approximately 0118 hours [EST] on November 9, 2012, Susquehanna Steam Electric Station Unit Two reactor was scrammed by plant operators due to a loss of ICS (Integrated Control System; which controls the reactor feed and reactor recirculation systems). The reactor operator placed the mode switch in shutdown when reactor water level reached +25 inches and lowering. All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -52 inches causing Level 3 (+13 inches) and level 2 (-38 inches) isolations. HPCI and RCIC both automatically initiated. HPCI was overridden prior to injection and RCIC was utilized to restore reactor water level to the normal band. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "The [Unit 2] reactor is currently stable in Mode 3. An investigation into the cause of the loss of ICS is underway. "Unit One continued power operation [at 78% power]. "The NRC Resident Inspectors were notified. A press release will occur." The licensee will inform the State of Pennsylvania. Decay heat removal is being maintained through the main condenser. On-site electrical power is in the normal configuration. | 0 | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ECCS INJECTION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(A) |  | 0 | 2012-11-09
48495 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-11-08 10:20 | 2012-11-08 16:55 | 2012-11-08 | LOSS OF EMERGENCY PLANNING ZONE SIRENS "Prior to 1020 EST on November 8, 2012, 4 out of 42 Emergency Planning Zone (EPZ) Sirens remained inoperable, due to issues caused by Hurricane Sandy. At 1020 on November 8, 2012, Oyster Creek was notified by ANS, the provider of Exelon siren maintenance, that due to the recent snow storm, 11 out of 42 sirens in the Oyster Creek Emergency Planning Zone were inoperable. 11 out of 42 sirens exceeds Exelon's reporting threshold of 25 percent or more sirens out of service. Therefore, an 8-hour report is required under 10 CFR 50.72(b)(3)(xiii) due to a 'Loss of Emergency Preparedness Capabilities.' "Prior to the submission of this report, Oyster Creek was notified by ANS that 4 of the 11 inoperable sirens were returned to service. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-08
48494 | 0 | SCIENTECH |  |  |  |  | 2012-10-11 | 2012-11-08 16:28 | 2012-11-08 | PART 21 - POTENTIAL GROUNDING PATHWAY BETWEEN HEAT SINK AND CHASSIS OF CONTROL MODULES The following information was obtained from the vendor via facsimile: "This report notifies the Nuclear Regulatory Commission of a defect in CMM830 and TMD830 [modules] that could result in an unintended ground loop that could lead to a low impedance connection between the module output circuitry and chassis. "There is a mechanical interference between the sheet metal housing and the heat sink for transistor Q1 on the master board assembly. The heat sink of transistor Q1 is connected to the drain of Q1, which is the output of the current loop circuit. Should the heat sink of transistor Q1 short to chassis because of the interference, then an unintended ground loop could lead to a low impedance connection between the module output circuitry and chassis. The effect of grounding Q1 to chassis will vary with the application. "If Q1 is grounded to the chassis, but no ground connection exists in the output loop, the incidental ground may produce no observable effect on the performance of the module. In that case, any subsequent independent event which introduces a ground in the output loop will cause a loop fault, potentially affecting the module output current. "Alternatively, if Q1 and chassis are initially isolated, the defect may not manifest unless vibration causes mechanical wearing of the oxide coating of the heat sink. It is possible that a seismic event could cause sufficient wearing to initiate a loop fault, again potentially affecting the module output current." The affected facilities are HB Robinson and Turkey Point. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | ID | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-11-08
48493 | 0 | ABB INC. (MEDIUM VOLTAGE SERVICE) |  |  |  |  | 2012-09-14 | 2012-11-08 14:55 | 2012-11-08 | PART 21 - AN OPERATING MECHANISM FRONT COVER FAILED DURING LICENSEE RECEIPT INSPECTION The following information was received by facsimile: "[ABB, Inc. provided] notification of a failure to comply with specifications associated with an operating mechanism front cover P/N 707939A00 used in low voltage electrically operated K-Line circuit breakers. A single occurrence of a newly manufactured circuit breaker failure to close was noted during Next Era Energy Seabrook Station receiving inspection supported by an ABB Medium Voltage Service Field Service Engineer. This circuit breaker was set up and tested satisfactorily during ABB cycle testing, inspection and commercial grade dedication prior to shipping. It was noted during the Seabrook receiving inspection that the control device plunger and secondary close latch were misaligned. Replacement of the operating mechanism front cover improved this alignment and the circuit breaker receipt inspection was completed satisfactorily. Inspection of the subject operating mechanism front cover indicates cause of the misalignment is due to incorrect hole locations for mounting the control device. This operating mechanism front cover was manufactured by Accutrex Products, Inc., an ABB approved vendor. "Identification of the Subject component: ABB part numbers 707939A00 and 707939B00 operating mechanism covers. These covers are used in operating mechanisms for the K-Line electrically operated circuit breakers rated 2000 amps and below. "Because of the large potential variety of usages of the affected circuit breakers, ABB (Medium Voltage Service) cannot determine if the potential for a substantial safety hazard exists at any licensee's facility if control device plunger and secondary close latch are misaligned. It is recommended the Licensees determine if the circuit breaker control device plunger and secondary close latch are misaligned at the next convenient maintenance opportunity defined in the ABB K-Line circuit breaker Information Bulletin." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-11-08
48492 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2012-11-07 | 2012-11-08 10:11 | 2012-11-08 | PART 21 REPORT- COMMERCIAL GRADE DEDICATION NOT PROPERLY APPLIED TO BUTTERFLY VALVES The following information was received by facsimile: "While reviewing an order for a Type 9200 Butterfly Valve, it was discovered that some parts [shipped from Marshalltown, Iowa from 2009-present] had not been identified for Commercial Grade Dedication, These parts were considered Essential-to-Function and were needed for the valve assembly to perform its safety-related function(s). "[The vendor] then extended its review to all safety-related orders going back to 2009. This review confirmed that the failure to dedicate was not confined to Type 9200 butterfly valves. The beginning of 2009 was selected because [an audit follow-up was] performed in January, 2009. A key point of emphasis during the audit was commercial grade dedication, with a recommended outcome being the addition of guidance on commercial grade dedication with all new quotations. Therefore, the 2009 audit brought clarity and consistency in approach, that was not always applied correctly between January, 2009 thru October, 2012. "It is [vendor's] opinion that while the affected equipment identified as safety-related was not properly dedicated, the failure to dedicate does not appear to pose an inherent safety risk based on currently available Information. The reason being that much of the equipment affected by [the vendor's] error were items such as mounting kits, wherein [the vendor] failed to dedicate the hardware used to mount the instrument (i.e., the bracket and screws), but did properly dedicate the instrument. Additionally, in forming this opinion, [the vendor] has taken into account that there are no known field issues with the affected equipment and all such possibly non-dedicated equipment passed the required standard testing." U.S. nuclear plants affected include the following: D.C. Cook; Millstone; Surry; McGuire; San Onofre; Indian Point; Palisades; Clinton; Peach Bottom; Beaver Valley; Cooper; Palo Verde; Brunswick; Hope Creek/Salem and Watts Bar. It is noted that numerous foreign facilities are also affected. If there are any technical question, contact the Fisher Quality Manager (George Baitinger) : Fax: (641) 754-2854 or Phone: (641) 754-2026. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-11-08
48491 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-11-07 12:40 | 2012-11-07 20:18 | 2012-11-07 | LIQUID PENETRANT SURFACE INDICATIONS FOUND ON CONTROL ROD DRIVE RETURN NOZZLE SAFE END TO PIPE WELD "Oyster Creek Nuclear Generating Station is currently in Cold Shutdown executing Refueling Outage 1R24, which includes in-service inspections. "At 1240 EST, General Electric notified Oyster Creek Management of surface indications that were detected by dye penetrant testing. The indications are in the adjacent base material area of the System Pressure Boundary weld. The indications are located Top Dead Center (TDC) of the 3 inch pipe. Indication #1 is upstream 0.7 inches away from the weld toe, the indication is 1.5" long. Indication #2 is downstream 0.2 inches away from the weld toe, the indication is 2.5" long. The depth of the indications are unknown at this time. "Initial investigation revealed that there was no moisture or leakage found in the area of the indications. Further investigation is in progress to better characterize the indications. The cause is under investigation and corrective action plans are being developed. "The surface defects have been evaluated by Exelon and determined to meet the criteria for reporting identified in NUREG-1022: Welding or material defects in the primary coolant system that cannot be found acceptable under ASME Section XI. IWB-3600, 'Analytical Evaluation of Flaws,' or ASME Section XI, Table IWB-3410-1, 'Acceptable Standards'." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-11-07
48490 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-11-07 | 2012-11-07 14:57 | 2012-11-07 | AGREEMENT STATE REPORT- DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of Texas via email: "On November 7, 2012, the Agency [State of Texas] was notified by the licensee that one of its Troxler model 3411B moisture/density gauges had been damaged. The gauge contained one 8 milliCurie cesium-137 source and one 40 milliCurie americium-241/beryllium source. The operator had stepped aside to a nearby wall to get location information. A bulldozer operator assumed that this meant that the test was finished and drove into the area, impacting the gauge. The gauge was not run over, but suffered a bent top and damaged electronics. The licensee performed a survey and determined that the integrity of the sources and shielding were not impacted. The licensee has performed a leak test and will be returning the device to the manufacturer for evaluation. The investigation into this event is ongoing." Texas Incident Number: I-9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-11-15
48489 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-10-26 | 2012-11-07 14:05 | 2012-11-07 | AGREEMENT STATE - RECOVERED LOST PORTABLE GAUGE The following was received from the Commonwealth of Pennsylvania via fax: "NOTIFICATIONS: On October 31, 2012, the PA DEP Southwest Regional Office received a call from the licensee regarding an event that took place between October 26 and October 31, 2012. "EVENT DESCRIPTION: An employee of the licensee used a portable gauge on October 26th in the south Philadelphia area. He then secured it in his car that evening. The car remained parked near his home until the morning of October 31. The licensee received a call from an unrelated construction worker who found the gauge hidden between shrubberies near a hotel in Philadelphia. The portable gauge was retrieved by Earth Engineering and was found intact but water logged. "The device is identified as: "Manufacturer: Troxler "Model #: 3440 Serial #: 21391 "Isotope: Cs-137 Activity: 8 mCi " ** Source Serial Number: 35-2906 "Isotope: Am-241 Activity: 40 mCi " **Source Serial Number: 47-16682 "CAUSE OF THE EVENT: Human error. After a reactive investigation and interview by DEP with the licensee on November 1, 2012, it was determined the gauge was not properly secured within the vehicle, and the vehicle my have been unlocked. "ACTIONS: The gauge is currently secured with the licensee and will be inspected by a vender before use." Event Report Number: PA120039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-11-15
48488 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2010-07-06 | 2012-11-07 11:38 | 2012-11-07 | AGREEMENT STATE REPORT - DELIVERED DOSE DIFFERENT THAN PRESCRIBED The following was received from the State of Georgia via email: "The Licensee reported to the Department [state of Georgia] on July 14, 2010 that a patient who received a prostate seed implant procedure on July 6, 2010 resulted in a medical incident. The patient was scheduled to receive a Cs-131 Isoray seed implantation for the prostate with a total planned activity of 194.3 mCi. During the procedure on July 6, 2010 it was noticed that many of the seeds implanted were not visible on ultrasound. Following final implantation of all the seeds, a cystoscopy was performed on the patient where it was revealed that 19 seeds were implanted in the bladder and not the prostate which was the intended implant site. All 19 seeds were removed from the bladder without difficulty. A post plan evaluation was completed the same day of the treatment. The total activity implanted (seeds implanted to the prostate) was determined to be 140 mCi with a difference of -54.3 mCi deviation from the total planned activity. Post plan D90 for the prostate was calculated to be 62.68% with a D90 deviation of 53.28 Gy from the dose prescribed of 85 Gy. An additional procedure was scheduled for the patient on July 12, 2010 where 18 seeds were implanted to bring the combined dose distribution to the prescribed amount. "The department [Georgia Radioactive Materials] reported the incident to NMED in November 2012." Georgia Incident Summary: GA-2010-07i A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-11-15
48487 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-11-07 09:21 | 2012-11-07 12:39 | 2012-11-07 | MANUAL REACTOR SHUTDOWN DUE TO HYDROGEN IN-LEAKAGE TO STATOR WATER COOLING SYSTEM "At 09:21 EST 11/7/12, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to hydrogen gas in-leakage into the stator water cooling system from the main turbine generator. The scram was uncomplicated, and all control rods, except one, fully inserted into the core. One control rod stopped at position 02 and was manually inserted. The lowest reactor vessel water level reached was 125 inches, and as expected, HPCI & RCIC did not actuate. No safety relief valves (SRV) actuated. Reactor water level is being controlled in the normal band using the control rod drive and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The cause of the increased hydrogen gas in-leakage into stator water cooling is under investigation. At the time of the manual scram, all Emergency Diesel Generators were operable. All Emergency Core Cooling Systems were available and no significant safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. The plant is in a normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-11-07
48486 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-09-01 | 2012-11-07 11:15 | 2012-11-07 | AGREEMENT STATE REPORT - MISSING PACKAGE CONTAINING GA-67 The following was received from the Commonwealth of Massachusetts via fax: "On September 1, 2012, [a common carrier] notified Lantheus that a package was missing. The Yellow III package, containing 175 mCi of Ga-67, was shipped on 8/30/12 from Lantheus and destined to Bogota, Colombia. The package was received in Miami on 8/31/12, but never scanned out of Miami. [The common carrier] believes the package shipped unmanifested to Bogota. The licensee agreed to write a follow-up report." Docket Number: 22-0446 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-11-15
48485 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-11-07 09:00 | 2012-11-07 09:39 | 2012-11-07 | PLANNED OUTAGE OF EMERGENCY SIRENS "A planned outage of all FCS [Fort Calhoun Station] sirens is to occur at 0900 CST today to replace required router power supplies. Based on the planned maintenance, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) will be nonfunctional. Prior notifications and coordination with Local Law Enforcement have been completed with compensatory measures established to support notification of the public in case of an actual emergency during the scheduled maintenance. "The planned maintenance is expected to take three hours with a projected completion time of 1200 CST. Also, contingencies have been established with the maintenance to back out if required in support of Law Enforcement activities. "This is being reported per 10CFR50.72(b)(3)(xiii) for: 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability'." The licensee notified the NRC Resident Inspector and local counties. * * * UPDATE FROM JOHN FICKLE TO CHARLES TEAL ON 11/7/12 AT 1246 EST * * * "At 1129 CST, maintenance was completed with all sirens restored to functional status. Local Law Enforcement has been notified and relaxed required compensatory actions. NRC Resident informed." Notified R4DO (Farnholtz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-07
48484 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-10-31 | 2012-11-06 13:20 | 2012-11-06 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following was received from the Commonwealth of Pennsylvania: "While performing a leak test and shutter check on October 31, 2012, it was discovered that one of the level gauges had an inoperable shutter. Because the location of the gauge was on an operating tank and inaccessible to personnel, no exposure issues were plausible. "The device is identified as: "Manufacturer: Ohmart Corp Cincinnati OH "Model: Minirad II "Source Holder Model: SHF2 "Isotope: Cs-137 "Activity: 500 mCi "The manufacturer was notified to make repairs. The licensee plans to increase shutter testing and have the manufacturer install a cover over the source holder to better protect it. DEP plans to follow up with a reactive inspection." Event Report No: PA 120038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-11-14
48483 | 0 | PINNACLE AIRLINES |  |  |  |  | 2012-11-06 | 2012-11-06 11:45 | 2012-11-06 | AIRLINE UNDERGOING RE-ORGANIZATION UNABLE TO LOCATE VARIOUS RADIOACTIVE SOURCES A representative for Pinnacle Airlines called to report that the company has records of various radioactive sources which cannot be located and are presumed lost. The airline is undergoing bankruptcy reorganization. The individual noted that the sources were previously registered under a company called Mesaba Airlines. Mesaba Airlines was at one time associated with Northwest Airlines. The individual believes that the devices were originally registered with the NRC as general licensed material. The material records indicate that the company was in the possession of 10 "Tritium Light Comparators" of approximately 1 curie each. The company has been able to locate 5 of these sources: In Knoxville TN; Memphis TN; Detroit MI; and Ft. Wayne IN. In addition, the company states that it had five explosive detector sources that are unaccounted for and (10 millicuries Nickel - 63 each) were last stored in Michigan (Esbaneba, Muskegon Kincheloe, and Gwinn MI). There may also be some missing Tritium Exit signs but the licensee has not been able to determine how many or where they were last located. At this time, the licensee believes that this material is lost and that the responsible reporting agency is the NRC. The sources are registered on the generally licensed source tracking list. The licensee has discussed this information with NRC Region 3 (Reichhold). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | TN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-11-14
48482 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-11-02 | 2012-11-06 12:10 | 2013-02-05 | AGREEMENT STATE REPORT- MISSING TROXLER The following was received from the State of Texas via email: "On November 6, 2012, the licensee notified the Agency [State of Texas] that at approximately 0820 hrs one of its employees had discovered that a Troxler Model 3411B moisture/density gauge, containing one 8 millicurie cesium-137 source and one 40 millicurie americium-241/beryllium source, had been stolen from the company-owned vehicle while it was parked at his residence in Laredo, Texas, sometime during the preceding weekend. The licensee reported that the employee had left a temporary work site on Friday, November 2, 2012, and gone to his residence due to a family emergency and had failed to return the gauge to the licensed location. While the employee was loading the vehicle to go to a temporary work site this morning, he realized he had left the gauge in the vehicle over the weekend. When he checked the vehicle, he found the chains had been cut and the gauge was gone. The licensee notified local law enforcement. More information will be provided as it is obtained per SA-300. "Gauge info: Troxler, Model 3411B, SN: 13121" Texas Incident Number: I-9007 * * * UPDATE FROM KAREN BLANCHARD TO MARK ABRAMOVITZ AT 1330 ON 2/5/2013 * * * The following information was received from the State of Texas via e-mail: "The Troxler Model 3411B moisture/density gauge that was stolen sometime between November 2-6, 2012, in Laredo, TX, was recovered by the licensee on February 2, 2013. "The licensee was contacted by an unknown person who was offering a machine for sale, no questions asked. Suspecting it was probably their gauge, the licensee made arrangements to buy it. The licensee has no information on the seller. "The licensee notified local law enforcement of the recovery." Notified the R4DO (Proulx), FSME Resources, ILTAB (Johnson), and Mexico. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-11-14
48481 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-11-06 00:06 | 2012-11-06 03:56 | 2013-04-24 | HIGH PRESSURE COOLANT INJECTION ACTUATION SIGNAL "On Tuesday, November 06, 2012, at 00:06 EST, during the application of a tag-out associated with feedwater level control, the 12 feedwater flow control valve (FCV-29-137) unexpectedly partially opened. As a result, reactor vessel water level rose to the high level turbine trip set point causing the main turbine to trip. The turbine trip signal then resulted in the initiation of High Pressure Coolant Injection (HPCI) channels 11 and 12 logic. No actual system component starts or actuations occurred as a result of the logic initiation and no actual HPCI injection occurred due to the system configuration, nor was injection required. "Actions were taken to manually isolate the 12 feedwater flow control valve and reactor vessel water level was restored to normal. "This meets NRC 8-Hour reporting criteria per 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the High Pressure Coolant Injection System." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM JERRY HELKER TO CHARLES TEAL ON 12/17/12 AT 1543 EST * * * "This notification is being made to retract Event Notification (EN) #48481, which reported an automatic actuation of the High Pressure Coolant Injection (HPCI) system initiation logic. "The HPCI system is automatically initiated based on conditions representing a small break loss of coolant accident (LOCA). The initiation signals are: - Low reactor water level - This is a direct indication of a potential loss of adequate core cooling. - Turbine trip - During a LOCA within the drywell, high drywell pressure due to the line break will cause a reactor scram, which causes a turbine trip, which then by design initiates the HPCI system. "The event occurred with the reactor in the cold shutdown condition, with the main turbine and main turbine shaft-driven feedwater pump (#13) out of service. In the cold shutdown condition, the probability of a LOCA is low and the HPCI system is not required by the Technical Specifications to be operable. Neither of the conditions requiring actuation of the safety function of the HPCI system (high drywell pressure or low reactor water level) was present. Although the turbine trip signal was in response to an actual sensed high reactor water level condition, high reactor water level is not a plant condition satisfying the requirement for actuation of the safety function of the HPCI system. With reactor vessel water level high, the safety function of the HPCI system (i.e. to provide adequate core cooling) was already completed. Thus, the HPCI initiation signal was invalid, and the event is not reportable under 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector has been informed. Notified the R1DO (Hunegs). * * * UPDATE FROM JOHN APRIL TO VINCE KLCO ON 4/24/13 AT 0158 EDT * * * "Upon further review, it has been determined the event did constitute a valid actuation of the HPCI system and is reportable per 10CFR50.72(b)(3)(4)(A)." The licensee will notify the NRC Resident Inspector. Notified the R1DO (Joustra). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-11-06
48480 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-11-01 | 2012-11-05 12:56 | 2012-11-05 | AGREEMENT STATE - DOSAGE ADMINISTERED LESS THAN PRESCRIBED The following was received from the State of California via email: "Patient was prescribed to receive 30.24 mCi of Y90 in Microsphere form (MDS Nordion, Model TheraSphere) through a catheter. The catheter became plugged during the procedure not allowing approximately 47% of the prescribed spheres to reach the treatment location. Patient received 16.2 mCi of the prescribed 30.24 mCi (53%) "The dosage to the patient was not available at the time of report, therefore RHB (Radiation Health Branch) was unable to determine whether this met all requirements to be classified as a 'Medical Event.' "The reporting requirements will be reviewed once the licensee provides RHB with the dose information. "A formal, written report will be compiled by the licensee and submitted to RHB Brea and Sacramento." California 5010 #: 110112 * * * UPDATE FROM DONALD OESTERLE TO CHARLES TEAL ON 11/5/12 AT 1428 EDT * * * "On 11/2/2012, the dosage to the patient was not available at the time of the report, therefore RHB was unable to determine whether this met all requirements to be classified as a Medical Event. The reporting requirements will be reviewed once the licensee provides RHB with the dose information. A formal, written report will be compiled by the licensee and submitted to RHB Brea and Sacramento. "At 11:00 am, 11/5/2012 RHB received additional information: The physician's written directive prescribed 130 Gy (13,000 rem) to the liver. The patient received 68.9 Gy (6,890 rem) to the intended organ. The remaining activity was contained by the microsphere delivery system. "The NRC Operation Center was updated on 11/5/2012; 11:25AM confirming this report as meeting the necessary conditions of classifying this as a Medical Event. " Notified R4DO (Farnholtz) and FSME Event Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-11-13
48479 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-11-04 21:53 | 2012-11-05 00:40 | 2012-11-05 | AUTOMATIC REACTOR SCRAM FROM FULL POWER FOLLOWING TURBINE TRIP "The reactor was scrammed on a valid reactor protection system activation caused by a main turbine trip. The cause of the main turbine trip is under investigation. All control rods fully inserted. All isolations and initiations occurred as designed. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated as expected. RCIC injected into the reactor coolant system, HPCI did not, as expected." This scram was characterized as uncomplicated and the reactor is stable in Mode 3. The plant is in a normal post shutdown electrical lineup. All systems functioned as required. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-11-05
48478 | 0 | PALISADES | 1 |  |  | [1] CE | 2012-11-04 12:30 | 2012-11-04 14:52 | 2012-11-04 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO SECONDARY SIDE STEAM LEAK "At 1115 EST on November 4, 2012, primary coolant loop #2 was declared inoperable due to a small un-isolable steam leak on a drain valve of an atmospheric steam dump valve on the secondary side of the 'B' Steam Generator. The valve is ASME Class II high energy piping and the non-conforming condition could not be evaluated with the steam generator pressurized. Based on the condition of the valve and the inability to evaluate, Technical Specification 3.4.4, PCS loops - Modes 1 and 2, Required Action A.1 was entered which requires the plant to be placed in Mode 3 in 6 hours. Repair of the valve may require cooldown to Mode 5. "At 1230 EST on November, 2012, Palisades initiated a shutdown in accordance with Technical Specification 3.4.4." The licensee has notified the NRC Resident Inspector. | 47 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-11-04
48477 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-11-03 08:23 | 2012-11-03 11:50 | 2012-11-03 | AUTOMATIC SCRAM ON LOW REACTOR WATER LEVEL "On November 3, 2012 at 0823 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram on low reactor water level. All control rods fully inserted and all plant systems responded per design following the scram. Prior to the automatic scram, an unexpected high Reactor Pressure Vessel (RPV) water level was experienced, followed by a turbine trip and subsequent lowering of RPV water level to the RPV low level scram set point. The cause of the water level transient is unknown. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0824 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Since the scram, there have been no anomalies observed with feedwater system operation. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. The unit is currently implementing post scram recovery procedures. "The licensee has notified the NRC Resident Inspector." Unit 2 was not affected during this event. | 0 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-11-03
48476 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2012-11-01 16:00 | 2012-11-02 11:33 | 2012-11-05 | FITNESS FOR DUTY - CONTRACT SUPERVISOR FOUND IN POSSESSION OF PROHIBITED SUBSTANCE A non-licensed contract supervisor was found to have in his possession a prohibited substance prior to entry into the plant protected area. The contractor's access to the plant has been terminated. This event has been re-posted after additional discussions with the licensee. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-11-02
48475 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-11-02 01:42 | 2012-11-02 03:30 | 2012-11-02 | MANUAL REACTOR TRIP DUE TO HIGH REACTOR COOLANT PUMP MOTOR BEARING TEMPERATURE "At 0142 CDT, Comanche Peak Nuclear Power Plant Unit 1 was manually tripped due to high temperature indications on the 1-04 reactor coolant pump motor radial bearing concurrent with a high / low oil reservoir level alarm. The trip was uncomplicated; all control rods and shutdown rods fully inserted; neither emergency diesel generator started; all safety systems functioned as designed. Both motor driven and the turbine driven auxiliary feed water pumps started as required to restore steam generator levels as a result of the trip. The turbine driven AFW pump was stopped per procedure and returned to auto-start status. Currently, Unit 1 is in Mode 3, no load Tave of 557 degrees F, with temperature being maintained with AFW and steam dumps to the main condenser. All electrical busses are powered from offsite and grid conditions are stable." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-11-02
48474 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-11-01 | 2012-11-01 17:46 | 2012-11-01 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was provided by the State of Texas via email: "On November 1, 2012, the licensee notified the Agency that one of its Campbell-Pacific Model MC-3 moisture/density gauges had been run over by a pickup truck at a temporary work site in Houston, Texas. The gauge contained one 10 millicurie cesium-137 source and one 50 millicurie americium-241/beryllium source. The sources were in the safe position when it was run over. The source rod was broken off at the top of the housing. The gauge was taken to a gauge service company where it was checked. There was no leakage of radiation. A determination will be made by the licensee as to whether they will have the gauge repaired or replaced. There was no exposure to any individual as a result of this incident. "Gauge Information: Mfg: Campbell-Pacific Model: MC-3 SN: M38118595 "Source Information: cesium-137 -- 10 millicuries -- SN: C8595 americium-241/beryllium -- 50 millicuries -- A8595" Texas Incident Number: I-9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-11-09
48473 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-10-02 | 2012-11-01 16:55 | 2012-11-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was provided by the State of Colorado via email: "The Colorado Department of Public Health and Environment received notification on 10-2-12 from Westin Hotel - Westminster, 10600 Westminster Blvd., Westminster, CO 80030. Phillip McDonald, Engineering Manager, reported a contractor removed and disposed of one exit sign during a remodel project when a new front entrance was completed, (no date given on project). "Maker of Sign: Isolite Model Number: SLX60 Serial Number: 12-02897 Activity (Curies of H-3): 6.2 Curies Date Manufacture Shipped: 1/31/2012 Date of Loss: No Date Reported for project. Location of Sign When Lost: Front entrance "Other Details: Per the letter submitted by Phillip McDonald, he states 'I do remember this device being installed, but I was unaware it had radioactive material inside or the responsibility of tracking this device. Our restaurant was remodeled this year and the contractor removed the device and disposed of it'." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-11-09
48472 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-10-22 | 2012-11-01 16:55 | 2012-11-01 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGN The following information was received from the State of Colorado via email: "The Colorado Department of Public Health and Environment received notification on 10-23-12 from Town of Lyons, Town Hall, 432 Fifth Avenue, Lyons, CO 80540, that a tritium exit sign was found on the floor when an employee entered the building on 10-22-2012. This exit sign was installed on 10-19-12. It is presumed the installation was incorrectly completed causing the sign to fall. An employee who entered the building picked the sign up and reported the damaged sign to the Public Works Director who contacted the Radioactive Materials Unit on 10-23-12 at 1330 PDT to report the damaged exit sign. The tube containing the Tritium is reported as damaged. "The sign was reported installed on 10-19-12. The sign fell from the ceiling during the weekend, and was found on Monday, 10-22-12 just inside the front entrance to the building. The licensee was provided documentation regarding how to package and ship the sign back to the manufacturer. The documentation emailed to him included the NRC NUREG -1556, Vol. 16 Appendix L. "Maker of the sign is Best Lighting Products. The model number is SLXTU1RB10 and serial number is 232970. The date it was reported shipped to the licensee was 12/28/10. "The activity of H-3 is 7.03 Curies." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-11-09
48471 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-11-01 12:15 | 2012-11-01 15:35 | 2012-11-01 | OFFSITE NOTIFICATION - OIL SPILL INTO NAVIGABLE WATERS "At approximately, 1215 EDT, November 1, 2012, Fermi 2 experienced an oil spill to navigable waters, requiring notification of National Response Center, Michigan Department of Environmental Quality (MDEQ) Pollution Emergency Alert System (PEAS), and Primary Public Safety Answering Point (911). The spill has not left site. A fuel oil and water mixture overflowed from a tank onto the ground during the performance of station fire header flushing. It is estimated that the volume of the overflow was less than ten gallons. A portion of the overflow entered the site storm drains. The source of the spill has been terminated. "The NRC Resident Inspector has been notified." | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-11-01
48470 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2009-08-17 | 2012-11-01 14:56 | 2013-01-30 | AGREEMENT STATE REPORT - LATE REPORTING FOR DIAGNOSTIC MISADMINISTRATION The following information was provided by the State of Georgia via email: "Licensee informed the Department [Georgia Radioactive Materials Program] via written correspondence dated 8/28/09 that a patient who underwent a nuclear cardiology treadmill stress test on 8/17/09 resulted in an embryo/fetus exposure greater than 500 mRem. Prior to treatment the patient declared to the licensee that she was not pregnant and the licensee followed in house protocols in which all female patients under the age of 55 are asked if they are currently pregnant or breastfeeding. In the event that a patient is unsure the licensee postpones testing until a negative pregnancy test can be obtained. The patient later informed the licensee of her pregnancy on 8/27/09. Isotopes and activity administered to the patient were as follows: Tc-99m 26.9 mCi & Tl-201 5.38 mCi with a Total Activity of 32.28 mCi. RSO for the licensee & consulting medical physicists conducted a dose determination and the conclusion was that the embryo/fetus did receive an effective dose equivalent in excess of 500 mRem. The results were forwarded to the patient's OBGYN." This was a diagnostic misadministration that did not involve contamination. * * * UPDATE FROM TRAVIS CARTOSKI TO VINCE KLCO ON 1/30/13 AT 0943 EST * * * The following information was excerpted from a received facsimile: "[The update is concerned with] the radiopharmaceutical dose administration that a female patient recently received at testing facility. It was subsequently determined that this patient was 9 weeks pregnant. The patient received two dose administrations, one dose of Tc-99m - Myoview for the Stress Myocardial Perfusion scan and one dose of TI-201 as Thallous Chloride for the Rest Myocardial Perfusion scan. The patient received 26.9 mCi of Tc-99m-Myoview and 5.38 mCi of TI-201. "The dose to the conceptus was approximately 2.53 Rad. Determination of dose is limited by patient habitus and physiology." Notified the R1DO(Bellamy) and FSME Resources via email. Report: GA-2009-18i NMED# 090812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-11-09