48469 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2009-08-03 | 2012-11-01 14:56 | 2013-01-30 | AGREEMENT STATE REPORT - LATE REPORTING FOR DIAGNOSTIC MISADMINISTRATION The following information was provided by the State of Georgia via email: "Licensee contacted the Department [Georgia Radioactive Materials Program] via telephone on 8/12/09 reporting that a patient who underwent a nuclear cardiology treadmill stress test on 8/3/09 resulted in an embryo/fetus exposure greater than 500 mRem. The Department received a report from the licensee on 8/14/12 describing that prior to treatment the patient declared to the licensee that she was not pregnant and the licensee followed in house protocols in which all female patients under the age of 55 are asked if they are currently pregnant or breastfeeding. In the event that a patient is unsure the licensee postpones testing until a negative pregnancy test can be obtained. The patient later informed the licensee of her pregnancy on 8/10/09. Isotopes and activity administered to the patient were as follows: Tc-99m 28.2 mCi & Tl-201 3.62 mCi with a Total Activity of 31.82 mCi. RSO for the licensee & consulting medical physicists conducted a dose determination and the conclusion was that the embryo/fetus did receive an effective dose equivalent in excess of 500 mRem. The results were forwarded to the patient's OBGYN." This was a diagnostic misadministration that did not involve contamination. * * * UPDATE FROM TRAVIS CARTOSKI TO VINCE KLCO ON 1/30/13 AT 0943 EST* * * The following information was excerpted from a received facsimile: "[The update is concerned with] the radiopharmaceutical dose administration that a female patient recently received at the testing facilities. It was subsequently determined that this patient was 4 months pregnant. The patient received two dose administrations, one dose of Tc-99m - Myoview for the Stress Myocardial Perfusion scan and one dose of Tl-201 as Thallous Chloride for the Rest Myocardial Perfusion scan. The patient received 28.2 mCi of Tc-99m-Myoview and 3.62 mCi of TI-201. "The dose to the conceptus was approximately 1.97 Rad. Determination of dose is limited by patient habitus and physiology." Notified the R1DO (Bellamy) and FSME Resources. Report: GA-2009-12i NMED# 090811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-11-09
48468 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-11-01 08:00 | 2012-11-01 08:20 | 2012-11-09 | INTEGRATED PLANT COMPUTER SYSTEM OUT-OF-SERVICE OUTSIDE THE CONTROL ROOM FOR PLANNED MAINTENANCE "Beginning November 01, 2012, at approximately 1000 [EDT], the Fermi 2 Integrated Plant Computer System (IPCS) will be removed from service outside of the Control Room to support installation of a Cyber Security Modification. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform and will be out of service when the IPCS is removed from Emergency Response Facilities (ERFs). These systems will be unavailable to all Emergency Response Facilities (ERFs) for approximately 196 hours. "By 1600 [EDT] on November 9, 2012 it is planned to restore IPCS, including SPDS and ERDS, to the Operational Support Center, the Technical Support Center, and alternate facilities. During this time dose assessment (Raddose) capability will only be available in the manual data input mode. The SPDS indications and Raddose remain available to the plant staff in the Control Room, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems as needed. A follow-up notification will be submitted when the IPCS is completely restored. "This 8-hour non-emergency notification is being made per the requirements of 10 CFR 50.72(b)(3)(xiii), as an event that results in a major loss of emergency assessment capability. ERDS previously reported out of service under event number EN 48451 ." The licensee informed the NRC Resident Inspector. * * * UPDATE ON 11/9/12 AT 2056 EST FROM BRETT JEBBIA TO DONG PARK * * * "This is a follow up to EN #48468 & EN #48451. "On October 29, 2012, Fermi experienced a failure of a data server within the process computer system which feeds data to Emergency Response Data System (ERDS), and EN #48451 was made to the NRC. "On November 1, 2012, planned maintenance for Cyber Security Modification began which removed ERDS, SPDS, and IPCS from service, and EN #48468 was made to the NRC. "On November 9, 2012, planned maintenance on ERDS, SPDS, and IPCS is complete, restoring full emergency assessment capabilities to all onsite emergency response facilities (EN #48468). The maintenance also repaired the data server within the process computer system which feeds data to ERDS (EN #48451)." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-11-01
48467 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-10-31 12:53 | 2012-10-31 21:09 | 2012-10-31 | POTENTIALLY UNABLE TO PROVIDE POWER TO SAFE SHUTDOWN EQUIPMENT DURING APPENDIX R FIRE "During BFNP [Browns Ferry Nuclear Plant] NFPA [National Fire Protection Association] 805 transition review, it was determined in the event of an Appendix R fire, the ability to provide power to equipment needed to achieve and maintain safe shutdown may be adversely impacted. In certain fire zones/areas, feeder breakers for the 480V Shutdown Boards are credited for backup control operation using the 43 emergency switches, which isolate the breaker controls from circuits going to the control bay, and allow for local operation of the breaker. Fire damage to Main Control Room 480V Shutdown Board transfer switch cables could cause the control circuit fuses for the credited breaker to clear prior to the use of the 43 emergency switch. In addition, cable fire damage in the same fire areas could also cause the normal and/or alternate feeder breakers to spuriously trip. These breakers do not have separate emergency fuses like other BFNP breakers equipped with backup controls. Therefore, Safe Shutdown Instruction (SSI) procedure steps to use 43 switches to perform local breaker operation to supply power to safe shutdown equipment may not work as written where this cable fire damage can occur. "Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the BFNP Fire Protection Report. "This condition is being reported pursuant to 10CFR50.72(b)(3)(ii)(B) and 10CFR50.72(b)(3)(v)(A),(B),(C).&(D). "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2012-10-31
48466 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-10-31 14:41 | 2012-10-31 20:12 | 2012-10-31 | BOTH TRAINS OF STANDBY GAS TREATMENT SYSTEM INOPERABLE "On Wednesday, October 31, 2012 at 1200 hours, with the reactor at approximately 100% core thermal power and steady state conditions, Standby Gas Treatment (SBGT) System Train 'B' was removed from service (made inoperable) for surveillance testing. "At 1441 hours, the control room staff declared the Standby Gas Treatment System Train 'A' inoperable as a result of an engineering analysis that determined that 480 VAC feed, Motor Control Center (MCC) B15, had the potential to exceed its trip set point under worst case bus loading. "The inoperability of both SBGT System Trains 'A' and 'B' could have prevented the fulfillment of the safety functions to 'control the release of radioactive material' and 'mitigate the consequences of an accident.' "At 1510 hours, a compensatory measure was taken to preclude the overload condition on MCC B15 and the SBGT System Train 'A' was restored to operable status. "At the time of submittal of this notification, the SBGT System Train 'B' remains inoperable for replacement of an overload relay. SBGT System Train 'B' is expected to be returned to service this evening. "This event had no impact on the health and/or safety of the Public. "The USNRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-10-31
48465 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-10-17 15:37 | 2012-10-31 18:50 | 2012-10-31 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT INVOLVING MISADMINISTRATION "On 10/17/12, the licensee notified RHB (Radiation Health Branch) of an issue related to prostate brachytherapy and questioned if this falls into the category of Medical Event (ME). RHB is currently investigating this matter to evaluate if a ME had occurred. "The RSO called RHB for guidance about three permanent prostate seed implants for which post-implant dosimetry showed less than ideal dose coverage of the gland. The RSO reiterated that none of these deviations were a surprise all were expected based on intra-operative experience. In one Iodine-125 case, poor coverage of the lateral base resulted from significant pubic arch interference. In the other two cases, both Palladium-103, poor coverage of the base occurred from vendor failure to disclose an additional unplanned spacer at the end of each seed strand. "As stated, the D90 value (minimum dose to 90% of the CT-defined prostate one month following the implant) for the I-125 case was 77% and for the two Pd-103 cases was 68% and 53% of the dose prescribed as a minimum peripheral dose to the ultrasound-defined prostate +margin prior to the implant. The RSO requested RHB read this statement carefully, as it compares apples to oranges 'The RSO will make the case that the post-plan D90 is relevant as an assessment of plan and programmatic quality but is irrelevant for definition of a medical event'. "The RSO indicated that the hospital's physicians do not prescribe by D90. What is prescribed is a minimum peripheral dose (MPD) to the ultrasound-defined prostate gland plus planning margin (PTV). A pre-plan is generated to deliver the intended MPD (145 Gy for I-125 monotherapy and 125 Gy for Pd-103 monotherapy) to the PTV. The resulting planned combination of radionuclide, source strength, and number of sources is what is approved, prescribed, ordered, and implanted. "Very often, changes are made intra-operatively to account for implantation difficulties and clinical factors (deviation of urethra from predicted path, pubic arch interference, presence of more aggressive disease in a specific part of the gland, etc). In addition, extra seeds are ordered for each case, to be implanted at the discretion of the Authorized User (AU). Extra seeds may be implanted to boost areas of sparse coverage following implantation of planned seeds. Extra seeds may also be implanted to boost areas of known aggressive disease to a dose higher than the initial MPD. It is impossible to mentally arrive at a new dose that might correlate to a D90 on post-implant dosimetry under these conditions. The AU recognizes that this will result in an increase to the D90 on the post-plan but does not alter the dose on the written directive but only the number of sources (in part to of the written directive following implant but prior to release of the patient) to reflect the intra-operative changes. This is because the prescribed dose refers to a MPD for the pre-implant ultrasound prostate volume with margin (as our policy states). It was never meant to correlate with a D90 on a CT-defined prostate volume (which volume may be double the ultrasound-defined pre-implant volume) a month after the implant. "As a result of the clinically discretional implantation of extra seeds, many of our D90 results in post-implant dosimetry actually exceed 100% of the prescribed dose. Several even exceed 120% of the 'prescribed' dose, and this is intentional. Nevertheless, the radionuclide, source strength, number of seeds, and duration of implant (permanent) indicated on part 2 of each written directive (the part completed following implantation but prior to release of the patient) correctly reflects what was done, as required by 10 CFR 35.41. The RSO called RHB about these three cases because the dose delivered to parts of these prostate glands was less than intended, an anticipated but initially unplanned result due to known but unplanned and uncontrollable outside factors. "The Authorized Users for these cases are still reviewing the clinical data to determine what, if any, additional medical actions will be taken. Note that none of these cases meet the criteria for a medical event as recommended by the Nuclear Regulatory Commission's Advisory Committee on the Medical Use of Isotopes on October 18, 2011 (see attached). These criteria analyze the spatial distribution of seeds within octants of the gland as well as the overall D90 (threshold for which is lowered to 60% of prescription dose, and only in conjunction with failure of the spatial analysis). In each of these cases (and in contrast to what happened in the VA cases), very few seeds (only a few percent) were implanted outside the planning margin of the prostate CTV. Even by the older document the state reference, the May 18, 2011 Prostate Permanent Implant Brachytherapy and Associated Medical Event Questions and Answers from Clarification of Current Guidance for Prostate Permanent Implant Brachytherapy, the hospital assert (as in Case 2) that ' in accordance with NRC regulations, a ME has not occurred, since the delivered activity is equal to the prescribed activity for the treatment site (as defined by the AU). Even though the D90 values differ by more than 20 percent; the AU does not use D90 to prescribe dose, and is therefore, not required to use D90 to perform the regulatory evaluation of the prescribed dose'." CA 5010 Number: 101712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-11-08
48464 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-10-31 14:18 | 2012-10-31 15:41 | 2012-10-31 | NOTICE OF UNUSUAL EVENT DUE TO SECURITY CONDITION The licensee declared an Unusual Event based upon a security condition at the site. Compensatory measures are being put in place. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. * * * UPDATE FROM TERRY BACON TO CHARLES TEAL ON 10/31/12 AT 1924 EDT * * * The licensee terminated the NOUE at 1754 CDT. Notified NRR EO (Nieh), IRD (Morris), and R3DO (Kozak), DHS SWO, FEMA, DHS NICC and NuclearSSA via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-10-31
48463 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-10-31 06:15 | 2012-10-31 14:09 | 2012-12-20 | SEQUENCER FAULT RESULTING IN SYSTEM ACTUATIONS "On October 31, 2012 at 0615 hours CDT, Unit 1 Train 'B' Safety Injection/Blackout Sequencer faulted resulting in a start of the Turbine Driven Auxiliary Feed Water (TDAFW) Pump and Train 'B' Emergency Diesel Generator (EDG). Reactor power was reduced to 97% rated thermal power (RTP) by an immediate load reduction of 50 MWe due to the resulting cooler Auxiliary Feed Water being injected into the Steam Generators; reactor power did not exceed 100% RTP. Train 'A' equipment was not affected by the event. "The TDAFW Pump was secured at 0628 hours by closing the Train 'B' steam supply valve from the main control board and the steam supply valve was declared operable at 0916 hours when the hand switch was returned to 'Auto' and the control switch lineup surveillance was completed. The Train 'B' EDG was loaded to 100% capacity in accordance with the operating procedure and secured at 1032 hours. The EDG is available but remains inoperable until the Sequencer is declared operable. "Efforts continue to restore the Sequencer at this time. A faulted 15 Volt power supply was identified and further investigation/calibration will determine if other conditions contributed to the fault. A final surveillance test will determine Sequencer operability. The most limiting Shutdown Technical Specification action statement is 24 hours in accordance with Safety Injection Sequencer TS 3.8.1 F. Current projections for Sequencer operability, and thus Train 'B' EDG operability, are 1800 hours. "This action appears to be an invalid actuation. However, this will be confirmed after a cause analysis and an update to this event will be provided at that time." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ROBERT CLARK TO VINCE KLCO ON 12/20/12 AT 1130 EST * * * "This is an update to Event Notification #48463. This event was initially reported on October 31, 2012 as a valid actuation per 50.72(b)(3)(iv)(A). However, further evaluation of this event has confirmed that the cause was isolated to a failed 15VDC power supply and the ESF bus voltage sensed by the Blackout Sequencer did not dip. Therefore, a valid blackout condition did not occur and the starts of the Unit 1 Turbine Driven Auxiliary Feed Water Pump (TDAFWP) and the Unit 1 Train B Emergency Diesel Generator (EDG) were both determined to be invalid. "For the EDG start, the associated electrical bus was never de-energized and the EDG output breaker did not close. Therefore, the EDG start is not reportable per 10CFR50.73(a)(2)(iv)(A) since it was an invalid actuation and the safety function (i.e. provide power to the safety related electrical bus) had already been completed at the time of the EDG actuation. "For the TDAFWP start, the AFW system safety function had not already been completed. Therefore, the TDAFWP start is reportable as an invalid actuation per 10CFR50.73(a)(2)(iv)(A) with the option to provide a telephone notification within 60 days instead of an LER per 10CFR50.73(a)(1). The following required information is being submitted per NUREG-1022, Rev. 2 for the TDAFWP start: "(a) The specific train(s) and system(s) that were actuated - Unit 1 Turbine Driven Auxiliary Feed Water Pump. "(b) Whether each train actuation was complete or partial - The train actuation was complete. "(c) Whether or not the system started and functioned successfully - The system started and functioned successfully. "The NRC Resident Inspector has been informed." Notified R4DO (Spitzberg). | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-10-31
48462 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2009-08-01 | 2012-10-31 13:34 | 2012-10-31 | HISTORICAL UNAVAILABILITY OF TECHNICAL SUPPORT CENTER VENTILATION DUE TO MAINTENANCE "This non-emergency event report is being made per 10CFR50.72(a)(1)(ii) which requires reporting events that occurred within three years of the date of discovery. "Based on operating experience, Engineering personnel reviewed past maintenance activities involving the Technical Support Center (TSC) ventilation system (VH system) and identified four (4) occasions between August 2009 and October 2012 (three years) where the VH system functions could not have been restored within the required facility activation time. The specific instances have been documented in our corrective action program. "If an emergency had been declared during these period and TSC ERO activation was required, the TSC would have been staffed and activated unless the TSC came uninhabitable due to ambient temperatures, radiological or other conditions. If relocation of the TSC staff was necessary, the Station Emergency Coordinator would relocate the staff to the alternate TSC location. "Practices and processes have been revised to improve control of TSC maintenance activities and to improve facility availability going forward. In addition, site reporting guidance has been revised to assure timely reporting for these types of events if required. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since the maintenance activities affected an Emergency Response Facility." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-31
48461 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-31 07:42 | 2012-10-31 09:06 | 2012-10-31 | TECHNICAL SUPPORT CENTER OUTAGE DUE TO PLANNED MAINTENANCE "A condition is being reported per Technical Requirements ManuaI13.13.1 Emergency Response Facilities Action B.2. The Functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54(q) Evaluation has been performed for this planned maintenance activity. "The NRC Resident Inspector has been notified." * * * UPDATE FROM ERIC TEW TO CHARLES TEAL ON 10/31/12 AT 1452 EDT * * * TSC maintenance is complete. The TSC has been returned to operable status at 1445 EDT on 10/31/12. The licensee will notify the NRC Resident Inspector. Notified R2DO (Hopper). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-31
48460 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-10-30 23:40 | 2012-10-31 00:07 | 2012-10-31 | OFFSITE NOTIFICATION TO THE NATIONAL MARINE FISHERIES SERVICE "[The licensee] notified National Marine Fisheries Service per OC-08 that Oyster Creek has been unable to use the dilution and intake trash rake for greater than 24 hours due to safety concerns and loss of power. Daily manual raking of intake and dilution is in progress." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-31
48459 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2012-10-15 14:00 | 2012-10-30 18:59 | 2012-11-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER A Troxler model 3440 portable gauging device (serial number 66163, containing approximately 8 milliCuries of cesium-137, and approximately 40 milliCuries of americium-241/beryllium) was hit by a bull dozer at a temporary jobsite. The source rod containing the Cs-137 source was not extended and remained in the shielded position. The case was cracked but the americium source was not damaged. The RSO arrived at the site and the survey results did not show evidence of contamination. The damaged gauge was placed in the transport case and removed from the jobsite. Utah Event Number: UT-120004 * * * UPDATE FROM PHILIP GRIFFIN TO JOHN KNOKE AT 1926 EDT ON 11/01/12 * * * The following information was provided by the State of Utah via email: "The licensee's RSO reported to the Division that one of the licensee's gauge operators was at a temporary job site to perform soil moisture density measurements on October 15, 2012. As the gauge operator was preparing to make the first measurement, he looked behind him and saw a bulldozer coming towards him. The gauge operator was able to avoid being run over by the bulldozer, but the portable gauge was run over and damaged. The operator informed the licensee's RSO of the incident, and the RSO went to the temporary job site to investigate the incident. According to the RSO, there were other drivers in other vehicles at the job site when the incident occurred. They had honked their horns to get the attention of the bulldozer driver, but they could not. "After clearing everyone out of the area, the RSO verified that the 8 mCi Cs-137 source was in the safe, shielded position, and that the 40 mCi Am-241:Be source was intact. The top cover of the gauge was cracked, and the source rod and depth gauge were bent approximately 15 - 20 degrees off vertical. The RSO was able to get the damaged gauge into the transportation package, and the RSO performed a survey of the area of the accident to verify that no contamination was present. Finding none, the RSO took the damaged gauge back to the licensee's facility in Richfield, Utah. "Gauge information: Troxler 3440, s/n 66163 "The portable gauge was recently purchased from Troxler in June 2012, and the sources in the gauge had been leak tested by Troxler and no leakage was found. "The incident occurred on 10/15/12 at approximately 2:00 PM. The manager got the message late in the day on 10/18/12." Notified the R4DO (Rick Deese) and FSME Event Resource | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2012-11-07
48458 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-10-18 | 2012-10-30 13:24 | 2012-10-30 | AGREEMENT STATE REPORT - RADIOGRAPHY DEVICE SOURCE DISCONNECTED The following information was received by email: "On October 18, 2012, the Agency [State of Texas Radiation Branch] received a request from an exposure device manufacturer for reciprocity to retrieve a . . . cobalt 60 source into a Spec 300 radiography device. The Agency contacted the Texas licensee and was told that the source had been retracted and that no reportable event had occurred. The licensee stated it needed assistance in disconnecting the drive cable from the source pig tail. On October 23, 2012, the Agency was informed by the manufacturer that the dose rates measured at the front of the exposure device indicated that the source may not be in the fully shielded position. On October 30, 2012, the Agency was informed by the manufacturer that the source was stuck inside the device approximately three inches from the locked and fully shielded position. The licensee has not reported this event to the Agency. The Agency will conduct an on-site investigation at the licensee's facility on November 1, 2012. There does not appear to have been any exposures to members of the general public. There were no overexposures to employees of the manufacturer. Exposures to the licensee's employees have not been determined. The investigation into this event is ongoing. Additional information will be provided as it is received in accordance with SA 300." Texas Incident: I-9000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-11-07
48457 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-10-30 01:09 | 2012-10-30 04:10 | 2012-10-30 | MANUAL REACTOR TRIP FROM 100% POWER "This report if being made under the requirements of 10 CFR 50.72(b)(2)(iv)(B), Actuation of the Reactor Protection System While Critical, except preplanned, and under the requirements of 10 CFR 50.72(b)(3)(iv)(A), Valid Actuation of Listed System, except preplanned. "Salem Unit 1 was operating at 100% reactor power when a loss of 4 condenser circulators required a manual reactor trip in accordance with station procedures. The cause of the 4 circulators being removed from service was due to a combination of high river level and detritus from Hurricane Sandy's transit. "All control rods inserted. A subsequent loss of the 2 remaining circulators required transition of decay heat removal from condenser steam dumps to the 11-14 MS10s (atmospheric steam dump). Decay heat removal is from the 11/12 Aux Feed Pumps to all 4 steam generators via the 11-14 MS10s. 11/12/13 AFW pumps started due to low level on all steam generators due to shrink from full power operation (this is a normal response). All safety related equipment functioned as expected. No one has been injured. As an additional note, Hurricane Sandy had recently moved past artificial island. Salem Unit 1 is currently in Mode 3. Salem Unit 2 reactor is currently in its 2R19 refueling outage and is shutdown and defueled with no fuel movement in progress." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 10/30/12 AT 0835 EDT FROM JOHN OSBORNE TO DAN LIVERMORE * * * "At 0513, following [a] Unit 1 manual [reactor] trip due to loss of condenser cooling, a manual steam line isolation was initiated due to a high condenser back pressure. All main steamline isolation valves responded as expected. The high condenser back pressure resulted in the #11 low pressure turbine rupture disc relieving. Unit 1 remains in mode 3 with Reactor Coolant System temperature at 549 [degrees] and stable. Reactor Coolant System pressure is 2235 psig and in automatic control. Pressurizer level is on program at 26 percent level and in automatic control. Core cooling is via aux feed water and the steam generator levels are on program. There were no [personnel] injuries." The licensee has notified the NRC Resident Inspector. Notified R1DO (Caruso). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-10-30
48456 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-10-29 21:00 | 2012-10-30 03:35 | 2012-10-30 | AUTOMATIC INITIATION OF EMERGENCY DIESEL GENERATOR DUE TO LOSS OF ONE OFF-SITE POWER SOURCE "On October 29, 2012 at 2100 EDT, Nine Mile Point Unit 2 experienced an automatic initiation of the Division 1 Emergency Diesel Generator due to a loss of line 5. Line 5 is one of the 115KV offsite power sources. Line 5 was lost due to a lightening arrestor falling onto electrical components in the Scriba switchyard during high winds. "During the electrical transient, Nine Mile Point Unit 2 also experienced a feedwater level control lockup, requiring manual control. No Emergency Core Cooling Systems actuated and feedwater level control was returned to automatic. Nine Mile Point Unit 2 remained at 100% power during the loss of line 5. "The off-site power source, line 5, was restored on October 30, 2012 at 0326 EDT." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-10-30
48455 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2012-10-30 00:30 | 2012-10-30 03:20 | 2012-10-31 | LOSS OF EMERGENCY SIRENS DUE TO IMPACTS FROM HURRICANE SANDY "Peach Bottom Atomic Power Station Control Room was notified of a loss of greater than 25% of sirens after severe storms in the area associated with Hurricane Sandy. Thirty-one (31) of 97 Emergency Planning Zone (EPZ) sirens are currently unavailable in Lancaster, York, Cecil and Harford Counties. Actions are currently being taken to restore unavailable sirens." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0515 EDT ON 10/31/12 FROM SCOTT RUCKER TO S. SANDIN * * * "Currently 12 of 97 sirens remain inoperable." The licensee will inform state and local agencies and the NRC Resident Inspector. Notified R1DO (Caruso). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-30
48454 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2012-10-29 22:41 | 2012-10-30 00:30 | 2012-10-30 | AUTOMATIC RPS ACTUATION ON GENERATOR TRIP "On October 29, 2012, at 2241EDT, the Reactor Protection System automatically actuated at 100% reactor power due to a direct electrical trip to the Unit 3 Main Turbine Generator. The generator trip resulted in a turbine/reactor trip. All control rods fully inserted on the reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators and normal heat removal through the condenser via condenser steam dumps. There was no radiation released. "Indian Point Unit 2 was not affected by this event and remains at 100% power. "A post trip investigation is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-10-30
48453 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-10-29 | 2012-10-29 21:58 | 2012-10-29 | RPS ACTUATION WHILE CRITICAL DUE TO GENERATOR LOAD REJECT On October 29, 2012 at 2100 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram due to a generator load reject. The cause of the load reject is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 2101 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. Three Electromatic Relief Valves actuated due to this scram and re-closed automatically. Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using bypass valves. Both Reserve Station Transformers are in service and being supplied by their normal power sources. Both Emergency Diesel Generators are operable and in standby. The unit is currently implementing post scram recovery procedures. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-10-29
48452 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-10-29 18:55 | 2012-10-29 19:18 | 2012-10-31 | NOTICE OF UNUSUAL EVENT DECLARED DUE TO HIGH INTAKE STRUCTURE WATER LEVEL At 1855 EDT on 10/29/2012, the licensee declared a Notice of Unusual Event (NOUE) per criteria HU4 for high water level in the station intake structure of greater than 4.5 feet. At the time of the notification, water level in the intake structure was approximate 4.8 feet and slowly rising. The cause of the increased water level was due to storm surge associated with Hurricane Sandy. No other station impacts were reported at the time. The licensee continues to monitor the intake levels and ocean tides. The licensee has notified the NRC Resident Inspector and the State of New Jersey. * * * ALERT UPDATE ON 10/29/2012 AT 2141 EDT FROM STEVE SERPE TO RYAN ALEXANDER * * * At 2044 EDT on 10/29/2012, the licensee escalated its emergency declaration to an Alert per criteria HA4 for high water level in the station intake structure of greater than 6.0 feet. At the time of the notification, water level in the intake structure was approximately 6.6 feet. The site also experienced a loss of offsite power event concurrent with the additional water level increase. Both emergency diesel generators started and are supplying power to the emergency electrical busses. Shutdown cooling and spent fuel pool cooling have been restored. Reactor pressure vessel level is steady at 584.7 inches. Intake levels continues to rise slowly and the licensee is monitoring. The licensee has notified the NRC Resident Inspector and the State of New Jersey. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC, and NuclearSSA via e-mail. * * * UPDATE on 10/30/12 at 0414 EDT FROM GILBERT DEVRIES TO RYAN ALEXANDER * * * The licensee updated this report with an 8-hour non-emergency notification of emergency diesel generator auto-actuation due to the actual loss of off-site power event [which occurred at 2018 EDT on 10/29/2012]. This event caused a valid RPS actuation with automatic containment isolations that resulted in a temporary loss of shut-down cooling to the reactor. Shutdown cooling was subsequently restored with power provided by the emergency diesel generators. The licensee has notified the NRC Resident Inspector. Notified R1DO (Caruso). * * * UPDATE AT 0357 EDT ON 10/31/12 FROM GILBERT A. DeVRIES TO S. SANDIN * * * "Termination of Alert. "The Oyster Creek Station has terminated the Alert that was declared at 2044 [EDT] on 10/29/12 due to Intake Structure high water level greater than 6.0 ft. MSL (EAL HA4). "Intake water level has returned to normal and is now below the Unusual Event EAL threshold (4.5 ft. MSL) and continues to lower." The licensee informed state and local agencies and the NRC Resident Inspector. Notified Region I IRC (Clifford), NRR (Evans), and IRD (Marshall). Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC, and NuclearSSA via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | POT RHR INOP |  | IMode1: Refueling; FMode1: Refueling | ALERT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2012-10-29
48451 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-10-29 17:00 | 2012-10-29 18:15 | 2012-11-09 | ERDS LOST DUE TO PROCESS COMPUTER SYSTEM DATA SERVER FAILURE "At 1700 EDT on October 29, 2012, Fermi 2 discovered a failure occurred with a data server within the Process Computer system at 0115 EDT on October 28, 2012. The failure of the data server affects data input to the server providing information to the Emergency Response Data System (ERDS). ERDS is currently not receiving updated information from Fermi data systems. This loss in capability is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "Indications of related plant variables are available in the Main Control Room. The Visual Annunciator System (VAS) and other portions of the Process Computer system remain functional. Meteorological and process effluent radiological monitor indications are available and dose assessment capability is available. Fermi 2 personnel will use normal phone communications to update NRC Operations Center in the case of an event declaration. Information normally provided by ERDS can be transmitted via the notification system as described in the Radiological Emergency Response Preparedness Plan. Fermi 2 will notify the NRC when ERDS is returned to service." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 11/9/12 AT 2056 EST FROM BRETT JEBBIA TO DONG PARK * * * "This is a follow up to EN #48468 & EN #48451. "On October 29, 2012, Fermi experienced a failure of a data server within the process computer system which feeds data to Emergency Response Data System (ERDS), and EN #48451 was made to the NRC. "On November 1, 2012, planned maintenance for Cyber Security Modification began which removed ERDS, SPDS, and IPCS from service, and EN #48468 was made to the NRC. "On November 9, 2012, planned maintenance on ERDS, SPDS, and IPCS is complete, restoring full emergency assessment capabilities to all onsite emergency response facilities (EN #48468). The maintenance also repaired the data server within the process computer system which feeds data to ERDS (EN #48451)." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lipa). | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-29
48450 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-10-29 15:00 | 2012-10-29 16:15 | 2012-10-30 | LOSS OF 21 EMERGENCY NOTIFICATION SIRENS On October 29, 2012, at approximately 1500 EDT, ANS, the licensee's provider of siren maintenance, reported a loss of 12 out of 43 sirens in the Oyster Creek Emergency Planning Zone, which exceeded the licensee's reporting threshold of 25 percent or more sirens out of service. At 1600 EDT, ANS, updated that the number of sirens out of service was 21 out of 43 sirens. ANS and the licensee continues to work to rectify the issue. The NRC Resident Inspector will be notified. * * * UPDATE ON 10/30/12 AT 0428 EDT FROM JOHN CLARK TO RYAN ALEXANDER * * * As of 0320 EDT on 10/30/12, it was determined that 36 of the 43 Emergency Planning Zone sirens were out of service, and the licensee continues work to rectify the issue. The NRC Resident Inspector will be notified. Notified R1DO (Caruso) and IRD (Marshall). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-29
48449 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-10-28 10:08 | 2012-10-28 16:27 | 2012-10-28 | EQUIPMENT FAILURE AFFECTING SPDS AND ERDS "At approximately 1008 EDT on October 28th, 2012, a failure between the Plant Computer and the MMI (Man Machine Interface) occurred. The cause is due to a failure of the data diode. The Plant Computer is still working however the MMI is not, therefore Safety Parameter Display System (SPDS) outside of the Control Room and the Emergency Response Data System (ERDS) is unavailable. "In the event of an emergency, plant parameter data will be communicated to the facilities through the status board ring down circuit with back-up by the Private Branch Exchange (PBX), Off Premise Exchange (OPX), and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function is maintained during this out of service time period by manual input of data into the Meteorological Information and Dose Assessment System (MIDAS). The ability to open and maintain an 'open line' using the Emergency Notification System is not affected and will be the primary means for transferring plant data to the NRC as a contingency until the ERDS can be returned to service. "At 1548 EDT on October 28th, 2012, a re-start of the data diode was successful in restoring the connection between the Plant Computer and the MMI. SPDS and the ERDS are functioning as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspector has been notified." The licensee has notified the State and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-28
48448 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-27 14:15 | 2012-10-27 17:43 | 2012-10-28 | LOSS OF OFFSITE COMMUNICATIONS "On 10/27/2012 at 1415 CDT, the control room was notified of a loss of telephone communications. Reason is unknown at this time. "Offsite communications lost includes the state and county ring down lines, the NRC ring down line. The ability to transfer information from the Emergency Response Data System (ERDS) to offsite agencies is believed not to be available. Satellite phones remain available. "At approximately 1500 CDT, the NRC Operations Center was notified via satellite communications of alternate phone numbers to contact the Unit 1 Control Room and that Unit 2 Control Room satellite phone is not available to receive calls. This is a follow up to make the notification of this event to the NRC pursuant 10 CFR 50.72(b)(3)(xiii). "The NRC Senior Resident Inspector was notified of the issue." State and local agencies were notified via alternate means. * * * UPDATE FROM CHRIS VANFLEET TO HOWIE CROUCH AT 0003 EDT ON 10/28/12 * * * Emergency Notification System has been returned to service. The cause of the loss of communications was a cut fiber optic line. Notified R4DO (Hagar). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-27
48447 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2012-10-25 | 2012-10-26 13:23 | 2012-10-26 | AGREEMENT STATE REPORT - STOLEN X-RAY FLUORESCENCE ANALYZER The following was submitted by the State of Georgia via email: "Around noon time on 10/26/12, [a licensee representative] called and notified the Department [Georgia Radioactive Material Program] that upon his arrival at work that morning around 8:30 am, he discovered that his office was vandalized, and the Niton Model # XP300A/Serial # 22283 Lead Paint Analyzer radioactive device was stolen. He indicated that his door was left unlocked that night. When he walked in the two drawer file where the gauge was stored, was opened. The intruder was able to locate the key to the cabinet and the key was still in the open drawer. The device was locked in the carrying case, and the case was also stolen. The licensee stated that the device was last used on 10/25/12, and returned to storage around 5:00 pm before leaving work on that day. The device contains a Cadmium 109, 40 mCi source, Serial # TR0380." Georgia incident ID: GA-2012-30i THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-11-05
48446 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-10-25 10:31 | 2012-10-25 17:13 | 2012-10-25 | CONFIRMED POSITIVE FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.719 |  |  |  | 0 | 2012-10-25
48445 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-10-25 | 2012-10-25 15:24 | 2012-10-25 | AGREEMENT STATE REPORT - HIGH PORTAL MONITOR READINGS AT SCRAP YARD The State of North Carolina reported the following via email: "NC Radiation Protection Section received a call from Gerdau Charlotte regarding a load of scrap tire-wire that tripped their portal monitor. [An individual] measured 10 mR/hr on contact at the rear of the truck trailer using a handheld meter (Ludlum 192, background reported at 3 mR/hr). The shipment originated from Liberty Tire in Atlanta, GA. "[The shipment] will be returned to Liberty Tire, Atlanta, GA, via CRCPD exemption NC-GA-12-01." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-11-02
48444 | 0 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2012-05-01 13:00 | 2012-10-25 15:54 | 2012-10-25 | RADIOPHARMACEUTICAL THERAPY RECORD TRANSPOSITION ERROR A doctor prescribed a patient 0.4 mCi/Kg Zevalin (a prescription medication containing Yttrium-90). The calculated dose based on the patient's weight was 44 mCi; however, the package insert for the drug says the maximum dose to be used is 32 mCi. So 32 mCi of Y-90 was to be given to the patient. A radiopharmaceutical therapy record was prepared as required at the hospital but the dose on the radiopharmaceutical therapy record was improperly copied as 23 mCi. The dose prepared at the radiopharmacy and delivered to the patient was 31.8 mCi. The dose differed from that specified on the radiopharmaceutical therapy record by more than 20%. The prescribing physician is aware and there is no significant impact to the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-11-02
48443 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-29 23:37 | 2012-10-25 14:17 | 2012-10-25 | INADVERTENT ALIGNMENT OF NUCLEAR SERVICE WATER TO STANDBY NUCLEAR SERVICE WATER POND "On September 29, 2012, McGuire Nuclear Station experienced an inadvertent alignment of the Nuclear Service Water (RN) system suction and discharge to the Standby Nuclear Service Water Pond (SNSWP). This event occurred when a Unit 2 'B' Train blackout signal was inadvertently generated as a result of a tagging restoration/coordination error. This error resulted in the Unit 2 Train 'B' load sequencer sensing an under-voltage condition on 4160V Essential Switchgear 2ETB, which was de-energized at the time for maintenance activities. Further evaluation determined that the blackout signal which automatically aligned RN to the SNSWP was not in response to actual plant conditions or parameters satisfying the requirements for initiation of a blackout signal or the SNSWP safety function. Since alignment of RN to the SNSWP was not in response to a valid signal, this represented an invalid actuation reportable per the requirements of 10 CFR 50.73(a)(2)(iv)(A). "As allowed by 10 CFR 50.73(a)(1), McGuire is providing a telephone notification of this invalid actuation in lieu of submitting a written LER. The following additional information is being provided as part of the telephone notification of this event: 'B' Train of RN actuated to align Unit 1 and Unit 2 RN to the SNSWP. 'B' Train actuation of Unit 1 and Unit 2 RN to the SNSWP functioned successfully and was complete. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-10-25
48442 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-10-25 09:30 | 2012-10-25 10:22 | 2012-10-26 | PARTIAL LOSS OF EMERGENCY ASSESSMENT DURING PLANNED MODIFICATIONS "On October 25, 2012, Callaway Plant will begin implementation of a modification to the plant computer system. The Emergency Response Data System (ERDS) and plant computer stations in the Technical Support Center (TSC) and Emergency Operations Facility (EOF) will be unavailable during the modification. Plant computer stations will remain available in the Control Room. The period of unavailability is anticipated to be approximately 12 hours on October 25, 2012, with an additional 8 hours for system testing on October 26, 2012. "During the modification process, the TSC and EOF will remain functional and available for use. Plant procedures provide guidance for manual data collection and sending ERDS data to the NRC. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE FROM SHANNON GAYDOS TO PETE SNYDER AT 2123 ON 10/25/12 * * * "Based on the current work progress on the plant computer system, the Emergency Response Data System (ERDS) and the plant computer stations in the Technical Support Center (TSC) and Emergency Operations Facility (EOF) will not be available until early evening on October 26, 2012." The NRC Resident Inspector will be notified. Notified R4DO (Hagar). * * * UPDATE FROM DAVID LANTZ TO DONG PARK AT 2033 EDT ON 10/26/12 * * * "Modification has been completed on the plant computer system. The Emergency Response Data System (ERDS) and the plant computer stations in the Technical Support Center (TSC) and Emergency Operations Facility (EOF) have been restored to normal operation." The NRC Resident Inspector will be notified. Notified R4DO (Hagar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-25
48441 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2011-05-24 | 2012-10-25 08:03 | 2012-10-25 | AGREEMENT STATE REPORT - Y-90 THERASPHERE SPILL The following information was obtained from the State of Georgia via facsimile: "Description of Event: A spill involving Y-90 microspheres (SIR-Spheres) that occurred on May 24, 2011 at Emory University Hospital [and] was reported by the Deputy Radiation Safety Officer. During an embolization treatment using Y-90 microspheres, resistance was encountered when flushing the catheter following the initial successful microsphere administration. The authorized user examined the catheter which was found to be occluded. Preparations were made to continue the administration with a second measured dose, but this was halted when further examination showed evidence of a leak between the Y-90 vial and the catheter. The procedure was postponed until contamination controls were complete. The patient received the completion of the prescribed dose pursuant to the Authorized User's written directives when the Interventional Suite was available for use on the following day. "Describe clean-up actions taken by RCP [Georgia Radiation Control Program]: No action performed by RCP but the licensee sealed the Y-90 shielding and cart and removed [them] for decay and evaluation. The floor and equipment were decontaminated by licensee radiation safety staff. "List radiation measurements taken by RCP: No measurements performed by the RCP but the licensee initiated spill containment procedures [and surveyed] the staff before allowing anyone to exit the room. Some minor contamination was discovered on staff clothing and shoes, but no contamination was detected on the skin of staff after removal of affected items. The deputy RSO surveyed the patient and had a bremsstrahlung scan of patient. No contamination was found on the patient during the scan. "List any other actions required of RCP: The licensee is storing all waste from this event for decay and subsequent investigation." Georgia Incident Summary number GA-2011-61i. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-11-02
48440 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-24 15:30 | 2012-10-24 20:09 | 2012-10-24 | TECHNICAL SUPPORT CENTER VENTILATION SUPPORT SYSTEM NON-FUNCTIONAL "At 3:30 PM EDT on October 24, 2012, Harris Operations discovered that the Technical Support Center (TSC) outside differential pressure controller (PDC-4011) was not working. This pressure controller makes the TSC non-functional due to the ventilation system not being capable of maintaining a positive pressure with respect to outside. Procedural guidance exists for the Radiation Protection staff to perform continuous air monitoring of the TSC atmosphere to determine habitability conditions. Actions are being taken to expeditiously restore the system. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) due to the Technical Support Center ventilation support system being non-functional. The on call Site Emergency Coordinator and Emergency Response Manager have been notified. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-24
48439 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-10-24 19:20 | 2012-10-24 19:23 | 2012-10-24 | PRESS RELEASE REGARDING STATUS OF ONGOING LABOR NEGOTIATIONS "On October 24, 2012, at 1920 EDT hours with the reactor at 100% core thermal power the following press release is being issued by Entergy Nuclear regarding the status of the ongoing labor negotiations. "ENTERGY NUCLEAR STATEMENT - ENTERGY AND UWUA LOCAL 369 AGREE TO TENTATIVE CONTRACT "October 24, 2012 "Plymouth, Mass. - Entergy Nuclear and the Utility Workers Union of America (UWUA) reached a tentative agreement today on a new four-year labor contract for Local 369 technical employees at Pilgrim Station, pending a ratification vote by Union membership. "Additionally, the parties have agreed to a 21-day extension that will expire at midnight on Nov. 14. The previous contract for the approximately 67 workers affected by this union contract will remain in effect during the extension. The original contract was set to expire at midnight Oct. 24. "Pilgrim's Site Vice President Robert Smith said, 'We appreciate the hard work of both parties to come to a successful outcome to this negotiation process. We believe the new proposal represents fair and equitable terms both for our employees and the Company.' "END "The Resident Inspector staff has been informed of this press release and notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-24
48438 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-09-13 | 2012-10-24 17:07 | 2012-10-24 | AGREEMENT STATE REPORT - STUCK SHUTTER ON A FIXED NUCLEAR GAUGE The following information was received from the State of Louisiana via fax: "Event date and Time: [On] 09/13/2012, the RSO for Marathon Petroleum called to be in compliance with Condition #4 of his radioactive material license. "Event Location: Production/process field at the refinery located at 4663 Airline Highway, Garyville, LA 70051 "Event type: Fixed gauge, stuck shutter "Event description: On 09/13/2012, the RSO for Marathon called to report a stuck shutter on a fixed level gauge utilized in a process in the refinery. There was no possible exposure to the plant workers because the gauge was installed on process [equipment] and the shutter remaining [open] was not a problem. [The RSO] called in the incident to comply with Condition #4 of Marathon's Radioactive Material License. The gauge is an Ohmart Vega gauge Model SHFBI, loaded with 20 mCi of Cs-137. The gauge has been [exposed to] the elements in excess of 10 years and the shutter malfunctioned due to corrosion in the mechanism. Eight [gauges] were evaluated and only one needed repair. The manufacturer stated that it appeared to be from being in the elements. The manufacturer stated that they were looking into finding a modification to shield the shutter mechanism from the elements. The Department [Louisiana Department of Environmental Quality] considers this item closed. "Event Report ID No.: LA 12-0005" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-11-01
48437 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2012-10-24 08:25 | 2012-10-24 09:31 | 2012-10-24 | TECHNICAL SUPPORT CENTER VENTILATION REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On October 24, 2012, at approximately 08:25 hrs [CDT], the Exelon LaSalle Station Technical Support Center (TSC) Ventilation system was removed from service for planned TSC ventilation system maintenance. "The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The ventilation system is expected to be out of service for approximately 21 hours. "This telephone notification is provided in accordance with Exelon Reportability Manual SAF 1.10, 'Major Loss of Emergency Preparedness Capabilities', and 10CFR50.72(b)(3)(xiii)." The licensee has notified the Senior Resident Inspector of the issue. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-24
48436 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2012-10-24 01:47 | 2012-10-24 02:40 | 2012-10-24 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "On 10/24/12 at 0147, North Anna Unit 2 reactor tripped automatically. The reactor first out is the 'C' steam generator lo-lo level. The turbine first out is reactor tripped, turbine trip. The event was apparently initiated by a loss of load on the secondary side. The cause of the loss of load is still being investigated. All systems responded as expected. This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System. "The Auxiliary Feedwater pumps received an automatic start signal due to low-low level in all steam generators at the time of the trip, Steam generator levels have been restored to normal operating level. The Auxiliary Feedwater System operated as designed with no abnormalities noted. This event is reportable per 10 CFR 50.72(b)(3)(iv)(A) due to actuation of an ESF system. "All control rods inserted into the core at the time of the trip and decay heat is being removed via the main condenser steam dumps. Several secondary [feedwater] relief valves lifted and reseated during the event. North Anna Unit 2 is currently stable at no load temperature and pressure in mode 3. "At 0147 EDT, the Unit 2 Pressurizer Power Operated Relief Valve (PORV) , 2-RC-PCV-2455C, opened during an automatic reactor trip of Unit 2. The valve indicated open for less than 1 second. During this time, the identified leakage threshold for EAL SU6.1 [25 gpm] was exceeded." The cause of the loss of secondary load, which is believed to have caused the low steam generator water level and the lifting of the pressurizer PORV, is still under investigation. The licensee is focusing on the high pressure to low pressure turbine intercept valves or reheat valves going shut for reasons unknown at this time. The licensee's data shows that a pressurizer PORV opened momentarily. The instantaneous leak rate exceeded the unusual event threshold leak rate of 25 gpm. The PORV reseated and no ongoing leakage occurred during the transient. The rest of the transient was characterized as uncomplicated. The unit is in a normal post-trip electrical configuration. All systems functioned as required. There was no impact on Unit 1. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1346 EDT ON 10/24/12 FROM PAGE KEMP TO S. SANDIN * * * The licensee is updating their report to RETRACT the portion related to the after-the-fact entry into EAL SU6. "At 0147 hours EDT on 10-24-12, a Unit 2 Pressurizer Power Operated Relief Valve, 2-RC-PCV-2455C, opened during automatic reactor trip. The valve indicated open for less than 1 second. 2-RC-PCV-2455C opened as designed in response to the plant trip and allowed a small amount of water to transfer to the Pressurizer Relief Tank, as designed. The Pressurizer Power Operated Relief Valve subsequently re-closed and remains available for automatic operation, if needed. Initially, this issue was reported to the NRC at 0240 hours on 10-24-12 as an After-The-Fact Unusual Event for EAL SU6.1. Subsequent review has determined that the Pressurizer Power Operated Relief Valve functioned as designed and the small amount of inventory was transferred to the Pressurizer Relief Tank as designed and therefore does not meet the criteria for an Unusual Event and this notification is being retracted. "NEI 99-01, Rev. 5 provides additional guidance that relief valve normal operation should be excluded from this Initiating Condition. However, a relief valve that operates and fails to close per design should be considered applicable to this Initiating Condition if the relief valve cannot be isolated. In this case, the Pressurizer Power Operated Relief Valve operated as designed and returned to automatic operation." The licensee informed state and local agencies and the NRC Resident Inspector. Notified R2DO (Musser). | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-10-24
48435 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2012-10-23 19:22 | 2012-10-23 20:59 | 2012-10-25 | DEGRADED CONDITION DUE TO REACTOR HEAD VESSEL PENETRATION INDICATIONS "On October 23, 2012, V. C. Summer Station Unit 1 (VCSNS) identified two reactor vessel head penetrations (19 and 52) that did not meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1. The station is in a refueling outage (RF20) and the plant is currently shutdown and in Mode 6. The reactor vessel head (RVH) contains a total of 66 penetrations and inspection efforts are approximately 50% percent complete. There have been no previous repairs to the reactor vessel head penetrations and/or j-groove welds. The indications are not through wall as indicated by volumetric and bare metal visual inspections. The penetrations will be repaired to meet the requirements of 10CFR50.55a prior to returning the vessel head to service. "The inspection results are reportable pursuant to 10CFR50.72(b)(3)(ii)(A). The NRC Resident Inspector has been notified." The licensee will notify the State of South Carolina and local counties. * * * UPDATE FROM BETH QUATTLEBAUM TO PETE SNYDER AT 1800 ON 10/25/12 * * * "On October 25, 2012, V. C. Summer Station Unit 1 (VCSNS) finalized our inspections of the reactor vessel head, which has identified a total of four reactor vessel head penetrations (19, 52, 31, and 37) that did not meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1. The station is in a refueling outage (RF20) and the plant is currently shutdown and defueled. The indications are not through wall as indicated from volumetric and bare metal visual inspections. The penetrations will be repaired to meet the requirements of 10CFR50.55a prior to returning the vessel head to service. "The inspection results are reportable pursuant to 10CFR50.72(b)(3)(ii)(A). The NRC Resident Inspector has been notified." Notified R2DO (Musser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-10-23
48434 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2012-10-23 09:00 | 2012-10-23 11:51 | 2012-10-23 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following report was received from the State of New York via fax: "The Radiation Safety Officer for Materials Testing Lab, Inc. (NYS license no. C2274) called to report that a moisture density gauge (Troxler Model 4640, serial no.1003) was stolen around 9 a.m. today. The New York City Police Department was immediately called but as of 10:45 a.m. they have not responded. The gauge contains 40 mCi of Am-241/Be and 8 mCi of Cs-137. Materials Testing Lab staff are canvassing the area and posting reward flyers with a picture of the gauge. [The RSO] will keep NYS DOH informed of any significant changes to the situation. No press release has been issued at this time. New York City radioactive material program has been notified. "NYS DOH Incident: #991 "Event Report ID No. NY-12-02" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2012-10-31
48433 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-10-22 19:01 | 2012-10-22 19:29 | 2012-10-22 | NOTIFICATION OF UNUSUAL EVENT DUE TO A FIRE GREATER THAN 15 MINUTES At 1846 EDT on 10/22/12, the Main Control Room received a report of an arc flash and smoke in the screen house. The fire brigade leader was dispatched and confirmed that smoke was coming from heater board H-111. The board was de-energized at 1854 EDT and smoke was observed to be reduced. The licensee declared an Unusual Event at 1901 EDT per EAL 8.2.1. The fire was out at 1908 EDT. The Unusual Event was terminated at 1932 EDT. Unit 1 continues running at full power operation and all parameters are stable. There was no impact on Unit 2. The licensee notified the NRC Resident Inspector, State of New York and Oswego County. Notified DHS SWO, FEMA, DHS NICC and NuclearSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-10-22
48432 | 0 | ANDERSON ENGINEERING INC |  |  |  |  | 2012-10-22 11:30 | 2012-10-22 16:48 | 2012-10-22 | DAMAGED NUCLEAR DENSITY GAUGE "Incident: At approximately 1130 CDT, at the new Joplin High School Construction Site in Joplin, Jasper County, Missouri, a nuclear density [gauge] was run over by a tire of a towed scraper. The damage was primarily to the housing of the meter. The technician immediately secured the area and contacted his supervisor. [The supervisor] went to the site and took readings using a TROX-A-LERT Model 3105B Radiation Survey Meter of the gauge and the soil where the gauge was run over and of the scraper which ran over the [gauge]. Readings at 1 meter from the [gauge] ranged from 0.12 to 0.20 mrem/hr. A reading of 2.5 mrem/hr [was indicated at the] housing of the [gauge] . The source did not appear to be damaged and was still encapsulated in the [gauge]. "The gauge was placed in a truck box mounted in the bed of a pickup truck and taken back to [the licensee's lab]. Once at the lab the gauge was wrapped in lead sheeting and placed in a nuclear [gauge] storage box. A reading of 0.1 mrem/hr was obtained at 1 meter with the lead sheeting wrapped around the meter." The damaged gauge is a CPN, serial number MD1205992. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-10-30
48431 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-10-22 13:39 | 2012-10-22 14:46 | 2012-10-22 | OFFSITE NOTIFICATION DUE TO PLANNED DECOMMISSIONING "At 0745 CDT on 10/22/2012, Dominion announced its plan to permanently shutdown and decommission the Kewaunee Power Station. A local press release was made at 1100 [CDT] on 10/22/2012. At 1139 [CDT], security reported that members of the local media were gathering on company property at the plants training facility which is located outside the Owner Controlled Area. At this time security reports no security issues and no other press releases are planned at this time. This event is being conservatively reported under 10 CFR 50.72(b)(2)(xi) for offsite notifications based on the press release and the notification to Midwest Independent System Operator (MISO) of the planned shutdown of the Kewaunee Power Station." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-22
48430 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-10-22 06:42 | 2012-10-22 13:28 | 2012-10-22 | PARTIAL LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 0642 [CDT] on 10/22/2012 a failure of power supply RMA-ES-53B was indicated by multiple area radiation alarms in the Control Room. This failure results in the loss of ability to remotely measure and quantify radiation levels in multiple area in the Reactor Building, Turbine Building and Main Control Room. This power supply serves 10 of 30 area radiation monitors located throughout the plant. The remaining 20 monitors remain fully functional. These radiation monitors do not cause entry to any Technical Specification conditions or required actions. "The loss of ability to monitor and quantify radiological conditions in multiple area of the plant represents a major loss of emergency assessment capability per 10CFR50.72(b)(3)(xiii). These radiation monitors are used for EAL determinations. As specified by station procedures compensatory monitoring has been implemented by use of surveys and portable monitoring devices. "Repairs are being implemented per station procedures and processes." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-22
48429 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2012-10-22 00:10 | 2012-10-22 03:49 | 2012-11-09 | POTENTIAL CONDITION COULD BYPASS FLOODING BARRIERS AND AFFECT RESIDUAL HEAT REMOVAL EQUIPMENT "During a walkdown evaluating potential for adverse consequences of site flooding, per 10CFR50.54(f) request, a condition was identified which had the potential to adversely impact the ability to address external flooding conditions. The old Emergency Offsite Facility (which currently houses information technology offices) has a drain pipe which connects to Sump AA in the Augmented Radwaste (ARW) building and bypasses the flooding barriers erected per maintenance procedure 7.0.11 in the event of site flooding. "Per the USAR, the basis for site flooding is a flood with concurrent surge effects on exposed safety related structures reaching an elevation of 905 feet. This elevation is 2.0 feet above the grade elevation of 903 feet. Flooding protection for important site facilities is provided by installing temporary barriers protecting to elevation 906 feet. Primary and Secondary Flood Barriers are installed at the ARW building external entrances on the 903 feet elevation to protect the Reactor Building from external flood water. The drain piping from the old EOF floor drain and shower is piped directly to Sump AA in the ARW building basement. This is a 3 inch pipe which drains by gravity. There are no isolation features on the pipe, and no barriers to flooding are provided for this facility, thus the potential exists to bypass the flood barriers which would be erected around the ARW Building. Flooding of the building basement could result, disabling processing equipment. If the basement fills up, flood waters could enter the Reactor Building through the internal entrance, which has no additional protection installed. Floodwaters could then affect equipment which is required to remove residual heat. "This condition has been determined to be reportable per 50.72(b)(3)(v) - Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of SSCs that are needed to remove residual heat. The potential condition was identified on 10/20/2012. Evaluation of the condition and the potential impact was completed and reportability determined on 10/22/2012. The condition has been entered into the Corrective Action Program." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2211 EDT ON 10/22/12 FROM KYLE SAYLER TO S. SANDIN * * * "During a walk down evaluating the potential for adverse consequences of site flooding per 10CFR50.54(f) request, a condition was identified which had the potential to adversely impact the ability to address external flooding conditions. The Optimum Water Chemistry (OWC) building has 5 floor drains, at ground level elevation 903 ft, which connect to a common 3 inch drain pipe which connects to a sanitary sump located in the Turbine building, at an elevation of 882 ft, and bypasses all flooding barriers erected per maintenance procedure 7.0.11 in the event of site flooding. "Per the USAR, the basis for site flooding is a flood with a concurrent surge effect on exposed safely related structures reaching an elevation of 905 ft. This elevation is 2 ft above the grade of the floor drains. Flooding protection for important site facilities is provided by installing temporary barriers which provide protection to an elevation of 906 ft. Primary and secondary barriers are installed at the Turbine building external entrances to protect the Reactor building from external flood waters. Additional secondary barriers are erected inside the Turbine building to provide additional protection to the Diesel Generator rooms. The drain piping from the OWC building floor drains is piped directly to the sanitary sump located in the Turbine building. There are no isolation features on the piping and no barriers to flooding are erected between the Turbine building and Reactor building thus the potential exists to bypass the flood barriers erected around the Turbine building. Flooding of the Turbine building could result in the accumulation of water in sufficient quantities to fill the Turbine building 882.5ft elevation to the height of the external floodwaters which would then be allowed to flow unimpeded by flooding barriers to the Reactor building through the internal entrance which has no additional barriers installed. These floodwaters could then affect equipment, located within the Reactor building, which is required to remove residual heat. "This condition has been determined to be reportable per 50.72(b)(3)(v) - Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of SSC's. that needed to remove residual heat. This condition was identified at 1550 [CDT on] 10/22/2012 and has been entered into the Corrective Action Program." The licensee informed the NRC Resident Inspector. Notified R4DO (Hagar). * * * RETRACTION FROM DAVID MADSEN TO HOWIE CROUCH AT 1228 EST ON 11/9/12 * * * "This notification is being made to retract Event Notification EN #48429 which reported a loss of safety function due to the discovery of two flow paths (one from the old Emergency Operating Facility and one from the Optimum Water Chemistry building) where an external event flood event at 905 feet would result in flooding of the Turbine and Radwaste basement and eventually the Reactor building basement. "Upon further review, the design basis Probable Maximum Flood for CNS is 903 feet. The two water entry points discussed in the Event Notification are above the 903 foot elevation. Wave energy would be dissipated before reaching any of the main buildings so there would be a minimal influx of water into the structures. As such, there is no loss of safety function for equipment in the Reactor building basement. NPPD therefore retracts Event Notification EN #48429." The NRC Resident Inspector has been notified. Notified R4DO (Farnholtz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-10-22
48428 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2012-10-21 08:05 | 2012-10-21 13:03 | 2012-10-21 | OFFSITE NOTIFICATION DUE TO HYDROGEN LEAKAGE "The control room was notified that an unknown quantity of H2 gas (classified as a minor coupling leak [identified with Snoop liquid leak detector]) is currently being released to the air from the Unit 2 Full Flow Hydrogen skid. "The Environmental Protection Group reported the leak to the California Emergency Management Agency (Cal EMA) at 0809 PDT and the San Diego Department of Environmental Health at 0812 PDT lAW [plant] procedure S0123-XV-17.3, 'Spill Contingency Plan'. The Hydrogen Gas leak is currently still in progress. There is no gas collection areas. Maintenance is in the process of taking action to terminate the leak." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-21
48427 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-21 00:09 | 2012-10-21 03:25 | 2012-10-21 | UNUSUAL EVENT DECLARED DUE TO SEISMIC EVENT "HU1.1 Seismic event identified by earthquake felt in plant and US Geological Survey (USGS)." An earthquake was felt onsite at approximately 0000 PDT. The licensee stated that two out of three methods for determining if an Unusual Event should be declared were met (i.e. the earthquake was felt in the plant and the earthquake was monitored by the USGS). The licensee characterized the earthquake as a "very mild" event. The licensee stated that, at the present time, there was no indication of damage to either unit and that both units remain at 100% power. The licensee is in the process of conducting walkdowns to confirm there was no damage to the plant. The USGS classified the magnitude of the earthquake as 5.3. The licensee notified state and local authorities and the NRC Resident Inspector. Notified other federal agencies (FEMA, DHS, DHS NICC and Nuclear SSA via email). * * * UPDATE FROM HENRY CLARDY TO VINCE KLCO ON 10/21/12 AT 1448 EDT * * * As of 1142 PDT on 10/21/12, the licensee terminated from the Unusual Event based on review of completed plant walkdowns. No damage was identified. Both Units are stable and in normal plant operations. The licensee notified state and local authorities and will notify the NRC Resident Inspector. Notified the R4DO (Pick), NRR EO (Bahadur), IRD MOC (Grant) and federal agencies (FEMA, DHS, DHS NICC and Nuclear SSA via email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-10-21
48426 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-10-20 11:00 | 2012-10-20 15:09 | 2012-10-20 | OFFSITE NOTIFICATION DUE TO A POTENTIAL INADVERTENT RELEASE OF TRITIUM "The notification is being made pursuant to 10 CFR 50.72(b )(2)(xi) due to the fact that Exelon Nuclear has informed the Illinois Emergency Management Agency (lEMA) and the Illinois Environmental Protection Agency (IEPA) of the discovery of a hole in the 'A' Waste Sample Tank resulting in a potential inadvertent release of tritium at Dresden Station. Any release is currently contained within the plant's restricted area. The notifications to lEMA and IEPA were made at 1340 hours CDT on October 20, 2012. "The tank was out of service and had been emptied for internal inspection. Therefore at the time of discovery, there was no active leak. "The IEPA/lEMA regulations require notification when newly occurring, event-related unpermitted releases of radionuclides are identified. A release has not been confirmed but is suspected. A review of the historical groundwater monitoring well data trends and trending analysis from wells in proximity to the tank indicates no impact on groundwater. Further investigation of the groundwater in the area of the tank is ongoing to determine if an actual release has occurred. The potential leak was not released to an unrestricted area; therefore there is no anticipated adverse impact to the health and safety of the public. "Since there was no release to an unrestricted area, 10 CFR Part 20 limits were not impacted. "The licensee has notified the NRC Resident Inspector." The Waste Sample Tank normally contains processed rad waste water. The hole was found at the bottom of the tank. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-20
48425 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2012-10-18 | 2012-10-19 17:34 | 2012-11-02 | AGREEMENT STATE REPORT - MEDICAL DOSAGE NOT DELIVERED AS PLANNED A patient was being treated for a liver tumor and the dosage was delivered to the wrong lobe. The physician prescribed 17 mCi of Y-90 to the left lobe of the liver. The prescribing physician was not present during the dose administration procedure. The intervention radiologist examined a fluoroscope of the patient's liver and noted a larger tumor on the right lobe. The prescribed dosage was then delivered to the right lobe of the liver, not in accordance with the prescribed dosage plan. Patient examination detected no observable impact, and the physician is developing another dosage plan for the patient. The Iowa Department of Public Health will perform an onsite investigation. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM RANDAL DAHLIN TO CHARLES TEAL ON 11/2/12 AT 1408 EDT * * * The following was received from the State of Iowa via email: "The University of Iowa nuclear medicine staff notified the Environmental Health & Safety (EHS) office on October 19, 2012 that they had discovered a reportable medical event that occurred during an October 18, 2012, therapy administration of Yttrium-90 microspheres (SIRSpheres) to a patient with liver metastases from a carcinoid tumor. "The Nuclear Medicine authorized user had prescribed for the delivery of 17 millicuries of the Y-90 microspheres to the left lobe of the patient's liver with plans to also administer 34 millicuries of the Y-90 microspheres to the right lobe of the patient's liver at a later time. Y-90 activity to be administered was calculated based on body surface area and tumor involvement. However, the interventional radiologist performing the Y-90 microsphere administration under fluoroscopic guidance noted that the angiogram of the patient's liver showed more tumor blood flow in the right lobe of the patient's liver and decided it would be medically more advantageous for the patient to treat the right lobe of the liver first. He proceeded to treat the right lobe without consulting the authorized user. "The interventional radiologist was only able to deliver 96% of the 17 millicurie Y-90 dose to the right lobe of the patient's liver before the right artery occluded. The authorized user discovered the administration discrepancy the next day when the patient was scheduled for post therapy imaging on October 19th. Both the patient and referring physician were informed of the medical event on October 19th. The physicians involved concluded that the patient's health and outcome were not affected by treating the right lobe of the liver first with only 17 millicuries of Y-90 microspheres since only 96% of activity could be injected before full embolization of the right hepatic artery occurred. "The physicians plan to treat the left lobe of the patient's liver in approximately 4 weeks. The Iowa Department of Public Health (IDPH) performed an onsite investigation of this medical event on October 23, 2012. The IDPH inspector interviewed the University Radiation Safety Officer, the Nuclear Medicine Authorized User, the Interventional Radiologist performing the Y-90 administration, the Chief Nuclear Pharmacist, the Chairman of the Medical Radiation Protection Committee, and Hospital Radiation Safety Review Group. The cause of the event was a lack of understanding of the requirements for administering radioactive material under the supervision of an authorized user. The interventional radiologist made a medical decision to alter the administration site without consulting the prescribing authorized user. "To avoid recurrence the following actions are being taken by the University of Iowa. All nuclear medicine authorized users prescribing Y-90 microsphere therapy will review the supervision requirements specified in Iowa Administrative Code 641-41.2(11) with all interventional radiologists on staff to ensure that they understand that they are required to follow the instructions of the prescribing authorized user. A roster of the individuals receiving this training will be forwarded to the IDPH upon completion. Additionally, nuclear medicine and interventional radiology will develop a written policy regarding the proper steps to be taken in the event that any deviation from the authorized user's written directive for the medical administration of radioactive materials is required. A copy of the policy will be forwarded to IDPH upon completion. "Reporting Requirement: 35.3045(a)(1(i) - Total dose delivered that differs from the prescribed dose by 20% or more; and differs from the prescribed dose by more than 0.05 Sv (50 rem) SDE." IA Report: IA120006 Notified R3DO (Kozak) and the FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-10-29
48424 | 0 | ACUREN INSPECTION |  |  |  |  | 2012-10-04 23:30 | 2012-10-19 17:08 | 2012-10-19 | RADIOGRAPHY SOURCE STUCK "A drive cable designed for 25' controls was installed in a 35' control assembly. This resulted in 15' of usable drive cable to travel through the guide tube. The radiographers were using a guide tube and extension with a total length of 17' and were unaware that there was not enough drive cable to reach the source stop. The cable was run out past the stop, and could not be retracted. "The exposure being taken at the time of the incident was a 6:00 shot on a 12" oil line. The line was 15' off the ground near an elevated platform. There was a 42" pipe running between the platform and the pipe being inspected. The exposure device was placed on the platform and an extension was added to the guide tube to route the source around the 42" pipe. The total length of the guide tube and extension was 16'11". The control cables were rerouted to take advantage of nearby shielding. The conduits were disconnected from the Pistol Grip Assembly exposing the drive cable. The source was then retracted into the fully shielded position by pulling the drive cable by hand. "The entire inventory of control assemblies were inspected to ensure the proper drive cables are installed, as will new assemblies when they are initially received. Additionally, personnel qualified to repair control assemblies will be retrained with emphasis placed on ensuring proper length of drive cable is in place. Training will be documented and filed in personnel records. "Qualifications of personnel involved in incident: 1. Radiographer, Texas Industrial Radiographer Certification holder, Dose Received, 3mR (dosimeter) 2. Radiographer, IRRSP card holder, Dose Received, 5mR (dosimeter) 3. Radiographer, Illinois Industrial Radiography Certification holder, Dose Received, 7mR (dosimeter) 4. Assistant Radiographer, Dose Received, 2mR (dosimeter) Source retrieval personnel: Site Radiation Safety Officer, IRRSP card holder, Source Retrieval trained by LAMCO & Associate February 25, 2011, Dose Received, 2mR (Dosimeter) "Equipment Involved: 7' flexible Guide Tube, serial # GT 1211 22 10' flexible Guide Tube Extension, serial # EXT 12 11 Crank Assembly serial # 11652 Exposure Device Model #: Sentinel Delta 880 Exposure Device serial #: D3534 Isotope: Iridium 192 Source serial #: 84462B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-10-29
48423 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2012-08-03 | 2012-10-19 16:25 | 2012-10-19 | AGREEMENT STATE REPORT - LOST SOURCE The licensee misplaced a static eliminator device containing 10 mCi of Po-210. The device model number is P-2021-8301; Serial number is A2HS590. The device was used to neutralize static charge on plastic parts prior to entering the paint process. The licensee considers the device as lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-10-29
48422 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-10-19 | 2012-10-19 15:51 | 2012-10-19 | AGREEMENT STATE REPORT- CONTAMINATION EVENT The following information was received by facsimile: "DRH [Tennessee Division of Radiological Health] was notified on 10/19/12 by the licensee that preliminary analytical results of a 30-gallon waste container of tritium contaminated waste oil and absorbents indicate approximately 8,600 curies of tritium. The container was manifested by the generator (SRS) [Savannah River Site] as containing 14.9 curies. Post sampling of this container, DSSI [Diversified Scientific Services, Inc.] had a controlled but elevated level of tritium contamination in the process room; this room is under negative ventilation. The room has been decontaminated back to normal processing levels. Contents of the container have been overpacked and placed in a safe state, [and] not a source of tritium contamination to the air or surface." Tennessee Event: TN-12-267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-10-29
48421 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-10-18 13:14 | 2012-10-18 18:57 | 2012-10-18 | FIRE PROTECTION REVIEW IDENTIFIES A POTENTIAL UNANALYZED CONDITION "During BFNP [Browns Ferry Nuclear Plant] NFPA [National Fire Protection Association] 805 transition review, it was determined in the event of an Appendix-R fire, fire induced circuit damage could potentially result in the Residual Heat Removal System Division II inboard isolation valve being prevented from opening or cause the valve to spuriously close on units 2 and 3. The current Appendix R safe shutdown analysis credits opening of these valves. Failure to open these valves results in loss of ability to provide long term cooling to the core. "Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the BFNP Fire Protection Report. "This condition is being reported pursuant to 10CFR50.72(b)(3)(ii)(B) and 10CFR50.72(b)(3)(v). "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2012-10-18
48420 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-10-17 | 2012-10-18 16:56 | 2012-10-18 | AGREEMENT STATE REPORT- UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was received by email: "On October 18, 2012, the Agency [Texas Radiation Branch] was notified by the licensee that on October 17, 2012, a radiographer was unable to retract a [source] into the QSA 880F exposure device. The guide tube for the device was damaged during radiography operation in the fixed facility when a part fell on it, crimping the guide tube to a point where the source could not pass through it. The licensee stated that they were able to repair the guide tube enough to retract the source and lock it in the exposure device. The licensee stated that no over exposure occurred from the event and no member of the general public received any exposure from the event. Additional information will be provided as it is received in accordance with SA 300. Texas Incident: I-8998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-10-26
48419 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-10-17 14:50 | 2012-10-18 13:34 | 2012-10-18 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed contract supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The contractor's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2012-10-18
48418 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2012-10-17 09:46 | 2012-10-17 16:05 | 2012-10-17 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive during a for-cause fitness for duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.719 |  |  |  | 0 | 2012-10-17
48417 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-10-16 | 2012-10-17 15:55 | 2012-10-17 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following report was received from the State of Texas Radiation Branch via facsimile: "On October 17, 2012, the Agency [Texas Radiation Branch] was notified by the licensee that on October 16, 2012, a radiography source had disconnected from the drive cable during radiography at a field location. The radiographers were using a SPEC 150 exposure device [redacted]. The radiographers had completed an exposure and as they were surveying the exposure device, the radiographer noted that the dose rates at the front of the device were higher than expected. The radiographers contacted their Radiation Safety Officer. A source recovery team was sent to the location and the source was recovered without incident. The licensee read the Instadose dosimeters for the individuals involved in the event and no over exposures occurred. No additional exposure to a member of the general public occurred due to this event. The licensee was not able to determine the cause for the disconnect. The exposure device and the crank-out device the radiographers were using are being sent to the manufacturer for inspection." Texas Incident #: I-8994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-10-25
48416 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-17 11:38 | 2012-10-17 13:49 | 2012-10-17 | OFFSITE NOTIFICATION OF WASTE WATER PIPE LEAK CONTAINING TRITIUM "The Harris Nuclear Plant is following the guidance in NEI 07-07 and has initiated this event notification as a result of our voluntary communication to state agencies in accordance with the Groundwater Protection Initiative. The state was notified at 1138 EDT. "On October 16, 2012 at 5:12 pm, plant personnel identified a leak from a pipe on plant property. The pipe carries secondary plant and water treatment building waste water for chemical processing. The water, containing a low level of tritium (10,760 picocuries per liter), leaked into the surrounding soil. The surrounding soil is being excavated and the leak is being repaired. The EPA Drinking Water Standard is 20,000 picocuries per liter. "The health and safety of the public are not affected by this event, based on the location of the leak and the low tritium levels. "The NRC Resident Inspector has been notified." The licensee also plans to notify local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-17
48415 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-10-17 08:00 | 2012-10-17 07:40 | 2012-10-17 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OUT OF SERVICE "At approximately 0800 hours EDT on October 17, 2012, computer engineering personnel will be taking the plant integrated computer system (ICS) out-of-service for planned maintenance. During the time ICS is out-of-service, the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) will be unavailable. The computer outage is scheduled for twelve hours. "In the event of an emergency, plant parameter data will be communicated to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, Off Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out-of-service time period by manual input of data into the Meteorological Information and Dose Assessment System (MIDAS). The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). A follow-up notification will be made when the maintenance activities are complete and the equipment is restored. The [NRC] Resident Inspector has been notified." * * * UPDATE FROM THOMAS MORSE TO VINCE KLCO ON 10/17/12 AT 2146 EDT * * * As of 2140 EDT on 10/17/12, the ERDS system was tested and restored to service. The licensee notified the NRC Resident Inspector. Notified the R3DO (Orth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-17
48414 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-10-16 23:30 | 2012-10-17 05:46 | 2012-10-17 | ALL FOUR EMERGENCY DIESEL GENERATORS AUTO-START ON VALID UNDERVOLTAGE SIGNAL "On October 16, 2012, Watts Bar Nuclear Plant Unit 1 experienced a momentary loss of power to the 1B 6.9 KV Shutdown board. This resulted in an emergency start of all 4 Emergency Diesel Generators due to actuation of the designed undervoltage EDG start signal. A manual transfer of the shutdown board from the Normal power supply to the Alternate was in progress to support maintenance. The momentary loss of power lasted approximately 2 seconds, which caused load shed and Diesel Generator start to occur. "Core cooling was maintained throughout the transient. "This condition is being reported under 10 CFR 50.72 (b)(3) (iv) (A). "All safety systems responded as designed. The unit remains stable in Mode 5. "The cause for this failure is not yet known. Investigation is in progress. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-10-17
48413 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2012-10-16 19:20 | 2012-10-16 19:56 | 2012-10-16 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE FELT ON-SITE "An Unusual Event was declared at 1920 EDT, HU1 - Earthquake felt in the plant (Control Room), and confirmed by calling the Manchester Dispatch Office. "Post event walkdowns indicate no reports of damage at the station. Walkdowns of station structures and systems continue. "Plant is stable in Mode 5 planned refueling outage. "No adverse impacts to shutdown cooling. "The station seismic monitor is currently out of service for a scheduled calibration." The licensee is exiting a refueling outage. The earthquake was felt by the site at 1914 EDT. The United States Geological Survey website indicates that an earthquake of magnitude 4.0 centered 3 miles west of Hollis Center, Maine occurred at this time. The licensee is currently in a Train 'B' system outage. All Train 'A' systems are functioning as required. The licensee has notified the NRC Resident Inspector and State authorities. No media or press release is anticipated at this time. The Headquarters Operations Officer has notified other FEDS (FEMA, DHS, DHS NICC and Nuclear SSA via email). * * * UPDATE FROM SEAN RILEY TO PETE SNYDER AT 0212 ON 10/17/12 * * * "The Unusual Event was terminated at 0149 EDT. Initiating condition was HU-1 due to the earthquake felt at the plant and confirmed by calling Manchester Dispatch Office. Information obtained by seismic monitoring system confirmed no additional escalation warranted. Site walkdown of key systems revealed no damage from the earthquake. All systems required for the current mode of operation were not adversely affected and remain in operation. " The licensee will notify the NRC Resident Inspector. Notified R1DO (Welling), NRR (Bahadur), IRD (Grant) and other FEDS (FEMA, DHS, DHS NICC and Nuclear SSA via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-10-16
48412 | 0 | HEMLOCK SEMICONDUCTOR CORPORATION |  |  |  |  | 2012-10-16 | 2012-10-16 17:32 | 2012-10-16 | PROCESS GAUGE SHUTTER STUCK OPEN The RSO reported a shutter problem on a fixed mounted process gauge manufactured by Vega Americas (Model SHF-2B) containing an 800 mCi Cs -137 source. The shutter problem was discovered during a semi-annual shutter check when it was determined that the shutter would not close. The shutter is normally always open to support the manufacturing process and the failure to close does not pose any personnel exposure risk. The RSO is following up with a vendor to repair the shutter onsite. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-10-24
48411 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2012-10-15 | 2012-10-16 17:23 | 2012-10-16 | AGREEMENT STATE REPORT - DOSE DIFFERENT FROM PRESCRIBED The following report was received from the Nevada Radiation Control Program via e-mail: "We would just like to inform you of a medical event. "Preliminary info: Yesterday (10-15-2012) we received a call from the RSO of 21st Century Oncology, regarding an incident that occurred with their HDR. Due to a faulty ruler, a parameter was entered incorrectly in the HDR control panel, resulting in a dose to the skin of the patient of around 160 centiGray. The skin area was one cubic cm. The intended dose was 160-170 cGy [to a different treatment site]. "The intended target was an almost spherical volume located in the right breast. The skin that was exposed is located in the right breast, at the entrance of the device (multi lumen mammosite) catheter. "The closest organ is the right lung. "The patient is fine and was informed of this. "The sealed source remained inside the tube. "[The event is] being reported under 10 CFR 35.3045 (a)(3): A dose to the skin or an organ or tissue other than the treatment site that exceeds by 0.5 Sv (50 rem) to an organ or tissue and 50 percent or more of the dose expected from the administration defined in the written directive (excluding, for permanent implants, seeds that were implanted in the correct site but migrated outside the treatment site)." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2012-10-24
48410 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-10-16 07:00 | 2012-10-16 13:16 | 2012-10-16 | SHUTDOWN COOLING ISOLATION CAPABILITY LOST "On October 16, 2012, at 0529 EDT, with the reactor in mode 4 and one operable channel for the Residual Heat Removal (RHR) shutdown cooling isolation function, as permitted by TS 3.3.6.1, Operators identified a rising reactor water level indication on instruments associated with the 3A reactor water level reference leg while actual level remained constant. At 0700 EDT, Operators determined this condition rendered the RHR shutdown cooling isolation function inoperable; specifically, an isolation signal for RHR shutdown cooling based on a low reactor water level. In accordance with Tech Spec 3.3.6.1 Required Action J.1, immediate action was initiated to restore isolation capability. RHR shutdown cooling isolation capability was restored at 1040 EDT by changing in-service RHR shutdown cooling systems. "This event could have prevented the fulfillment of a safety function, 10 CFR 50.72(b)(3)(v), at time of discovery to mitigate the consequences of an accident (D)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-10-16
48409 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-09-11 | 2012-10-16 11:31 | 2012-10-16 | AGREEMENT STATE- DAMAGED WATCH WITH REMOVABLE RADIUM CONTAMINATION The following report was received from the Commonwealth of Massachusetts via facsimile: "During a decommissioning survey of the Watch City Museum, the museum's consultant 'Babcock Services, Inc.' (BSI), discovered an antique radium watch with potential damage. The subject watch, marked '8-Day Watch' was missing the glass face. BSI obtained the following radiological survey results: - Maximum radiation reading on contact [was] 0.38 mR/hr and - Alpha plus beta removable contamination smear of 52,767 dpm/100 cm2. - The estimated Ra-226 activity is less than 1 microCuries "The 8-Day Watch was removed from the museum, securely wrapped, and placed in a secure container. "The owner of the 8-Day Watch, 'Charles River Museum of Industry and Innovation', was notified about the condition of the 8-Day Watch. The timepiece owner and the Watch City Museum agreed that the damaged timepiece should be properly disposed as radioactive waste. The 'Watch City Museum' arranged for the disposal of the timepiece with their decommissioning consultant, BSI. The Agency agreed with the disposition of the damaged timepiece. "The Agency conducted a confirmatory radiological survey of the timepiece display case and the adjacent museum floor. The survey included the display case glass cover (outside and inside surfaces), the display case base, the adjacent floor within 2 feet of the display case, the secured container of the 8-Day Watch, [and] the viewing surface where the timepiece was displayed. [The] inspector observed no readings above background of 10 cpm using an alpha probe. Maximum radiation level at the surface of the time piece container was 0.2 mR/hr using a gamma probe. "The Agency considers this event to be closed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-10-24
48408 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-16 08:00 | 2012-10-16 08:10 | 2012-10-16 | PLANNED TECHNICAL SUPPORT CENTER (TSC) MAINTENANCE "At approximately 0800 on October 16, 2012 pre-planned maintenance will be performed that will affect the Technical Support Center (TSC) ventilation system. The scope of the maintenance is to inspect and clean all air handler units, fans, and outside air condensing units that support TSC ventilation. This maintenance is expected to be performed and completed within approximately 13 hours. If an emergency condition should occur, the ventilation system will be restored, but potentially not within the time required for activation of the TSC. In addition, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location in the event the TSC is not habitable. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-16
48407 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-10-15 06:56 | 2012-10-15 14:37 | 2012-10-15 | AREA RADIATION MONITOR USED FOR EMERGENCY ASSESSMENT FAILED "At 0656 on 10/15/2012, the Unit 3 Control Room received indication that the area radiation monitor, 3RlA-15 for Unit 3 High Pressure Injection (HPI) Pump Room had faulted. 3RIA-15 is used in the Oconee Emergency Plan Enclosure 4.3 (Abnormal Rad Levels Radiological Effluent) and Enclosure 4.4 (Loss of Shutdown Functions) for declaration of NOUE and/or Alert. Although the loss of a single area radiation monitor is not generally reportable, the loss of 3RIA-15 is conservatively considered as a major loss of emergency assessment capability pending further review of the Oconee Emergency Plan. The loss of 3RIA-15 is being reported per 10 CFR 50.72(b)(3)(xiii). "Initial Safety Significance: None. There is no event in progress and the station has implemented an alternate means to monitor area radiation for the Unit 3 HPI Room. "Corrective Action(s): Repair and restoration of the affected radiation monitor has been initiated as a high priority work request. An alternate means to monitor Unit 3 HPI Pump Room has been established. The station will notify the appropriate Emergency Response Organization personnel of the loss of 3RIA-15. "Corrective actions are in place to review station procedures/processes for improvement relative to reporting requirements of 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been informed." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-15
48406 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2012-10-15 08:00 | 2012-10-15 09:13 | 2012-10-15 | PLANNED TECHNICAL SUPPORT CENTER (TSC) MAINTENANCE "Planned maintenance activities will commence today (October 15, 2012) on the Quad Cities Station TSC. The maintenance involves replacing a portion of the TSC roof. The roof repair work affects the TSC habitability during a declared emergency requiring activation (the roof is part of the habitability boundary). The maintenance is scheduled to be completed in approximately 48 hours. During off-hours the roof will be temporarily sealed. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Station Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This event is reportable per 10CFR50.72(b)(3)(xiii) since the scheduled maintenance affects an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-15
48405 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-10-13 03:20 | 2012-10-13 11:33 | 2012-10-13 | PORTIONS OF ONSITE TELEPHONE SYSTEMS NOT RESPONDING NORMALLY "At approximately 0320 CDT on 10/13/2012, Cooper Nuclear Station personnel identified portions of the onsite telephone system are not responding normally, following reports of a lightning strike in the vicinity of the meteorological tower. Personnel performed checks of onsite and offsite communications capability, and determined the normal method of contacting the state and local agencies would not function. Alternate methods were checked, and found to be only partially functional. This is considered to be a major loss of the offsite communications capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Alternate methods of contacting state and local agencies are available using working phones and the site cell phone system to obtain an offsite phone line and dial the direct line as listed in the emergency telephone directory. State and local agencies must be contacted individually. The capability to activate the ERO paging backup system per the implementing procedures is not affected by this condition. "Communication personnel will respond to the site to correct the condition." The licensee has notified the NRC Resident Inspector and will be notifying state and local agencies. * * * UPDATE FROM ROY GILES TO DONALD NORWOOD AT 1617 ON 10/13/2012 * * * "This is a follow-up notification to EN 48405. At 1407 CDT on 10/13/2012, the normal method of contacting state and local agencies during an emergency has been restored." The licensee has notified state and local agencies and will be notifying the NRC Resident Inspector. Notified R4DO (Hagar). | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-13
48404 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-10-12 21:00 | 2012-10-12 21:04 | 2012-10-12 | TECHNICAL SUPPORT CENTER REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On October 12, 2012, at 2100 EDT, the Hope Creek Technical Support Center (TSC) ventilation system was removed from service to perform planned preventive maintenance on the system. The maintenance consists of minor maintenance to clean the intake louvers that supply outside air to the emergency filter unit (00-VH313), the supply unit fan (00-VH314) and the remote shutdown panel (RSP) supply unit fan (00-VH316). The removal of the ventilation potentially affects the TSC habitability during a declared radiological emergency requiring activation. Appropriate compensatory measures are in place while the ventilation is out of service. The Emergency Response Organization duty team has been notified of the maintenance and the possible need to activate the TSC in an alternate location. The ventilation system is scheduled to be out of service for approximately 25 hours and the TSC Ventilation will be returned to service at 2200 on October 13, 2012. "The licensee has notified the NRC Resident Inspector. The local township will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-12
48403 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-10-12 15:35 | 2012-10-12 17:02 | 2012-10-12 | OFFSITE NOTIFICATION DUE TO LEAK FROM CONDENSATE STORAGE TANK CONTAINMENT PIT SUMP "On October 12, at 1535 CDT, Duane Arnold Energy Center made a voluntary report to the State of Iowa (Bureau of Radiological Health and Department of Natural Resources) and Linn County Public Health Department in accordance with the nuclear industry voluntary reporting criteria contained in NEI 07-07, 'Industry Ground Water Protection Initiative.' The subject of the report was a leak from the Condensate Storage Tanks' containment pit sump. The release occurred in an isolated area inside the plant property and has been terminated. Samples were taken and no regulatory limits were exceeded. During and following the leak, there was no impact to site worker or public health and safety. "This report in being made in accordance with 10 CFR 50.72(b)(2)(xi), as a result of notification to offsite agencies. "The Licensee has notified the NRC Resident Inspector." Total amount leaked was estimated to be less than 100 gallons. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-12
48402 | -1 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-10-12 04:20 | 2012-10-12 11:29 | 2012-12-04 | REACTOR POWER EXCEEDED FSAR ANALYZED VALUE "On 10/12/12 at 0420 CDT the Unit 2 Steam Generator B Atmospheric Steam Dump Valve (ADV) spuriously opened while in automatic control. This resulted in indicated reactor power exceeding the FSAR analyzed value of 1810.8 MWt. Prompt operator action was taken and reactor power was restored to within limits in approximately four minutes. The operators placed the Atmospheric Steam Dump Controller to manual and closed the ADV successfully. This event is being reported under the criteria in 10 CFR 50.72 (b)(3)(ii)(B). "All other plant systems responded as expected." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MARY SIPIORSKI TO VINCE KLCO ON 12/04/12 AT 1544 EST * * * "This notification is being made to retract Event Notification EN #48402 which reported power exceeding the FSAR analyzed value of 1810.8 MWt due to a spurious opening of an Atmospheric Steam Dump Valve. While 1810.8 MWt is the normal PBNP [Point Beach Nuclear Plant] full power value without consideration to uncertainties, subsequent reviews show that the peak power level reached during the event was bounded by FSAR analyzed events. Additionally, the opening of the valve is an Anticipated Operational Occurrence, described and analyzed in the FSAR. "The power excursion during the event was below excursions evaluated in the FSAR. The event was analyzed and plant safety was not significantly degraded. Therefore, the event does not meet the criteria of 10CFR50.72(b)(3) and NextEra Energy Point Beach retracts Event Notification EN #48402." The licensee notified the NRC Resident Inspector. Notified the R3DO (Pelke). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-10-12
48401 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-10-11 21:07 | 2012-10-12 00:55 | 2012-10-12 | OFFSITE NOTIFICATION DUE TO ONSITE SIRENS ALARMING DURING A DRILL "On 10/11/12 the Prairie Island Nuclear Generating Plant (PINGP) Security Force was conducting scheduled force on force security drills from 2000 to 2330 CDT. At 2107 CDT the Licensee was notified by the Wisconsin State Radiological Coordinator (SRC) that an intern had contacted the Wisconsin State Patrol Duty Officer to say they had taken cover at the plant and that there were sirens going off in the background. The intern did state that he did not know whether this was a real event or a drill. "The Wisconsin State Patrol contacted the office of Wisconsin Emergency Management and the SRC. The SRC then contacted the PINGP Control Room and was informed by control room personnel that this was a security force-on-force drill. Xcel Energy Communications has notified other government agencies of this event via an email. No press release is planned at this time. This event is reportable per 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-12
48400 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-11 12:08 | 2012-10-11 18:44 | 2012-10-12 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP ON A 500KV LINE DIFFERENTIAL RELAY ACTUATION "On October 11, 2012, at 1208 PDT, the Diablo Canyon Power Plant Unit 2 500kV line differential relay actuated, resulting in a unit trip. The unit trip actuated the turbine trip. With the turbine tripped and Unit 2 operating above the P-9 50% power permissive, a reactor trip was initiated from the reactor protection system. All plant equipment responded as designed. "Unit 2 is stable at normal operating temperature and pressure. All power transferred to the plant startup source without incident. Condenser vacuum was maintained. The cause of the differential relay actuation is under investigation. Based on personnel observation it appears to have been initiated due to a flashover to ground across the phase 'A' main bank transformer capacitive coupled voltage transformer. "PG&E will issue a press release regarding the Unit 2 trip. "NRC Resident Inspectors have been informed of this event." * * * UPDATE FROM DAN STERMER TO DONG PARK AT 2259 EDT ON 10/11/12 * * * "This update to clarify the status of the auxiliary feedwater system during the above noted transient. Both motor driven pumps and the steam driven pump automatically started as expected. "In addition, on October 11, 2012, at 12:26 PDT, the Diablo Canyon Power Plant Unit 2 turbine driven auxiliary feedwater pump was secured by plant operators manually closing the steam supply valve to the pump turbine. This action was performed in accordance with plant operating procedures after the operators had verified that the indicated steam generator levels were greater than the procedural requirement of 16%. However, because the steam generator low level bistables associated with the auxiliary feedwater actuation circuits had not yet cleared, the emergency safeguards actuation signal drove the steam supply valve back open, restarting the turbine driven auxiliary feedwater pump. "Operators increased steam generator levels to clear the bistables and successfully reclosed the steam supply valve. "The NRC Resident Inspector has been informed of this event." Notified R4DO (Hagar). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2012-10-11
48399 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-11 14:28 | 2012-10-11 15:00 | 2012-10-11 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO MAINTENANCE "At approximately 1428 EDT on October 11, 2012, preplanned maintenance will be performed that will affect the Technical Support Center (TSC) ventilation system. This maintenance will be performed as part of an electric heater control panel inspection (DH-1). This maintenance is expected to be performed and completed within 4 hours. If an emergency condition should occur, the power will be restored, but potentially not within the time required for activation of the TSC. In addition, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location in the event the TSC is not habitable. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-11
48398 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-10-10 13:05 | 2012-10-10 22:43 | 2012-10-10 | DOUBLE CONTINGENCY CONTROL FOR EMPTY CYLINDERS NOT MAINTAINED "At 1305 CDT, on 10-10-12 the Plant Shift Superintendent (PSS) was notified that during reviews of paperwork for a customer, it was discovered that four clean, empty cylinders used for transfer did not have a hydrocarbon test performed prior to filling, in violation of NCSA 360-005. NCSA 360-005 requires a test for never used non-USEC owned cylinders prior to filling to detect the presence of hydrocarbons. The presence of moderator in the cylinders could lead to either an 'explosion' that ruptures the cylinder and releases UF6 or criticality from moderation of greater than a safe mass of uranium. The controls ensure that double contingency exits to prevent filling a cylinder containing enough moderator to support criticality. "Cylinders affected are GE0195, GE0191, JM0226, and GE0407 and were filled on 9/16/12 and 9/22/12. "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "The NRC Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-12-2554; PGDP Event Report No. PAD-2012-06. "Responsible Division: Production Support & Product Scheduling "SAFETY SIGNIFICANCE OF EVENTS: A control relied upon for double contingency was violated. A cold pressure check and cylinder weight check performed prior to initial transfer of UF6 did not indicate the presence of moderator, and customer compliance with ANSI N14.1 also ensures that cylinders received at PGDP would not contain moderator. There was no indication of an adverse reaction noted during the filling of the cylinders. A cold pressure check performed after filling and cooldown did not indicate that an adverse reaction associated with UF6 and moderator had occurred. The introduction of UF6 eliminates the possibility of any residual moderator remaining in the cylinder; therefore, the cylinders are now in compliance with double contingency. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for criticality to be possible, sufficient undetected moderator would have to be present in the cylinder prior to the initial transfer of UF6. Although a control was violated, the cold pressure check ensured the moderation parameter was not exceeded. "CONTROLLED PARAMETERS: Double contingency for this scenario is provided by two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: 20,000 lbs. of UF6 at approximately 4.0% U235 enrichment. Plant limit is 5.5 wt.% U235 enrichment "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on cylinder compliance with ANSI N14.1 and the performance of a cold pressure check prior to initial transfer of UF6. ANSI N14.1 compliance ensures that the cylinders are clean and free of moderator. The cold pressure check provides a positive indication that no moderator is present inside the cylinder. The cold pressure check was adequately performed prior to initial UF6; therefore, this control was not violated. "The second leg of double contingency is based on performing a hydrocarbon test on the internal valve opening of the UF6 cylinder prior to initial transfer of UF6. The presence of hydrocarbon material in a UF6 cylinder could result in a cylinder rupture or criticality prior to initial transfer of UF6. The hydrocarbon test will give telltale signs that the inside of the cylinder may contain oil or other potential moderators. The hydrocarbon test was not performed; therefore, this control was violated. This leg of double contingency is considered to have been lost. "Since double contingency for this scenario is based on two controls on one parameter and a control was violated, double contingency was not maintained. "CORRECTIVE ACTIONS: None are needed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2012-10-10
48397 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-10-10 16:33 | 2012-10-10 18:34 | 2012-10-10 | REDUCED RADIATION MONITORING CAPABILITY FOR AUXILIARY BUILDING AND CONTAINMENT VENT STACKS "On October 10, 2012, at 1633 [CDT], Kewaunee Power Station staff identified (in response to concerns raised by the NRC Resident Inspector) that the Containment and Auxiliary Building SPING (Special Particulate Iodine Noble Gas) units could likely not have been relied upon to determine Emergency Classifications based on the Kewaunee Emergency Action (EAL) Level Matrix. This was due to these SPINGs having been nonfunctional during the period from 2/28/2011 at 0150 [CDT] until 3/30/2011 at 1845 [CDT]. Alternate radiation monitoring capability remained available to provide indication of radiation levels in the Auxiliary Building and Containment vent stacks; however, they would not have been sufficient to identify the upper two emergency action levels. Alternate means (e.g., grab samples) could also have been used to make the appropriate declarations. However, use of the alternate means could potentially impair the plant's ability to declare an emergency in a timely manner. "These SPING units had been returned to service on 3/30/2011 and were subsequently available for EAL classifications. However, the ramification of this condition was not fully recognized until today. "This condition is being conservatively reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-10
48396 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-09 13:00 | 2012-10-10 07:14 | 2012-10-10 | POTENTIAL FITNESS FOR DUTY VIOLATION A non-licensed employee supervisor was administered a for-cause chemical test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2012-10-10
48395 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-03 18:15 | 2012-10-10 00:32 | 2013-01-30 | UNANALYZED FIRE PROTECTION DEFICIENCIES "On 10/9/12, at 16:30 PDT control room operators were questioned whether recently identified fire protection program deficiencies should have been reported to the NRC. "On October 3 and October 8, 2012, DCPP [Diablo Canyon Power Plant] staff reviewing NFPA 805 Nuclear Safety Capability Assessment (NSCA) Variance From Deterministic Requirements (VFDRs) identified fire areas that neither conformed to Appendix R requirements nor had established, proceduralized and practiced compensatory measures in place. The issues were identified in the DCPP corrective action program and compensatory measures were established in accordance with the DCPP fire protection program requirements. "Event: 10/3/12 Fire areas containing cables associated with startup transformers 1-2 and 2-2 could result in loss of startup power and also prevent the emergency diesels from performing their Appendix R safe shutdown function. "Event: 10/8/12 Fire areas containing reactor coolant pump (RCP) breakers could result in loss of RCP seal cooling and prevent the credited local manual trip of the RCPs, contrary to the specified method of performing the Appendix R safe shutdown function. "Event: 10/8/12 Fire areas containing cables for the ventilation systems of the 480V switchgear, DC panels, and battery chargers could require unproceduralized use of portable fans to maintain adequate cooling of the electrical equipment necessary to perform the Appendix R safe shutdown function. "Operators established fire watches as compensatory measures as required by the DCPP fire protection program requirements. "The above late notification of discovery of the unanalyzed conditions has been entered into the DCPP corrective action program. "NRC Resident Inspector has been notified." *****UPDATE AT 0028 EDT ON 11/01/12 FROM GLENN GOELZER TO S. SANDIN***** "This is an update to EN #48395 reported on October 10, 2012, at 0032 EDT. "During the NRC's Fire Protection Triennial Inspection the NRC identified that several Alternate Compensatory Measures (ACMs) were not in the current post-fire procedure CP M-10. The ACMs address potential Appendix R non-conformance issues identified via the initiative to convert the DCPP fire protection program to NFPA 805. PG&E has established compensatory measures for all the identified areas in accordance with the DCPP fire protection program requirements. "[The] NRC Resident Inspector has been notified." Notified R4DO (Deese). * * * UPDATE FROM D. BAHNER TO V. KLCO ON 11/30/12 AT 1618 EST * * * "This is an update to EN #48395 reported on October 9, 2012, at 2132 PST. "During the ongoing evaluation of the issues previously identified in this event notification, PG&E [Pacific Gas & Electric] has concluded that a fire in the fire areas containing cables associated with startup transformers 1-2 and 2-2 would not result in loss of startup power or prevent the emergency diesels from performing their Appendix R safe shutdown function. This issue was reported as an unanalyzed condition. However, it is analyzed and controlled in plant procedure CP M-10, 'Fire Protection of Safe Shutdown Equipment.' PG&E retracts the initial event documented on October 3, 2012, thus making the date on which the first unanalyzed condition was discovered October 8, 2012. Therefore, PG&E will submit the 60-day Licensee Event Report by December 7, 2012. "The NRC Resident Inspector has been notified." Notified the R4DO(Whitten). * * * UPDATE AT 1944 EST ON 1/30/13 FROM KLINE TO TEAL* * * "This is an update to EN #48395 reported on October 9, 2012, at 2132 PDT. "On October 31, 2012, at 2128 PDT, PG&E provided an update to this event notification identifying that several alternate compensatory measures (ACMs) were not in plant procedure, CP M-10, 'Fire Protection of Safe Shutdown Equipment.' PG&E has evaluated this further and concluded that ACMs had been adequately implemented in CP M-10, and therefore retracts the EN update of [November 1, 2012 at 0028 EDT]. "NRC resident inspector has been notified." Notified R4DO (Walker). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-10-10
48394 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2012-10-09 21:20 | 2012-10-09 23:06 | 2012-10-16 | SAFEGUARDS REPORT - DISCOVERY OF POTENTIALLY COMPROMISED SAFEGUARDS DOCUMENT Discovery of a potentially compromised safeguards document. Compensatory actions were taken. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM DALE SHELTON TO CHARLES TEAL AT 1404 EDT ON 10/16/12 * * * This event has been retracted. Contact the Headquarters Operations Officer for additional details. R3DO (Orth) notified. 73.71 Group informed via e-mail. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-10-09
48393 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2012-08-26 12:31 | 2012-10-09 16:47 | 2012-10-09 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - UNUSUAL EVENT "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On August 26, 2012, at approximately 1231 Mountain Standard Time (MST), some Auxiliary Operators located in the Palo Verde Nuclear Generating Station (PVNGS) Operations Support Buildings reported to the control room that they had felt an earthquake. The US Geological Survey (USGS) internet web page recorded several small earthquakes in the Salton Sea area of Southern California. The earthquake was not felt by the control room staff and no Seismic Monitoring System alarms were received. The event was evaluated and a determination was made at that time that the event did not meet the classification criteria for declaration of an Unusual Event per the PVNGS Emergency Plan. Similarly, at 1358, personnel again reported they felt motion in the Operations Support Buildings and the USGS reported an aftershock in Southern California. The event was similarly determined to not meet the classification criteria for declaration of an Unusual Event. "There were no indications of any impact to plant equipment or site operations other than being felt by personnel in the Operations Support Buildings. "During post event reviews, it has been determined that these events met the classification criteria for declaration of an Unusual Event for a seismic event as specified by the PVNGS Emergency Plan. No emergency situation exists at this time. "The NRC Resident Inspector was informed of this notification." The licensee notified Maricopa County and the State of Arizona. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | UNUSUAL EVENT | 4 | AZ | POW | [5 empty] | 0 | 2012-10-09
48392 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-10-08 | 2012-10-09 16:13 | 2013-01-14 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECTED The following information was obtained from the State of Arkansas via email: "The Arkansas Department of Health [the Department] was notified on October 8, 2012 at 1345 [hrs. CDT], by the licensee, of a source disconnect. The radiography crew had completed a radiograph of a pipe weld and was unable to retract the source into the shielded position. The licensee's RSO was notified, the boundaries were verified and the radiography crew made several attempts to retract the source. The crank-out device was disassembled and the crew manually pulled the cable and discovered that the drive cable had separated. "The licensee contacted Source Production & Equipment Company (SPEC) for source retrieval. Licensee representatives remained on-site and maintained direct surveillance awaiting the arrival of the source retrieval team. SPEC personnel arrived on site on October 9, 2012 and were able to retrieve the source into the radiography camera. "The Department sent two Health Physicists to observe the source retrieval. "Equipment involved: Radiography Camera is a SPEC 150, SN # 1357, radiography source is a SPEC G-60, SN # TH0302 containing [redacted] Iridium-192. "The camera was inspected by SPEC personnel and the source leak tested. After the associated equipment (crank-out and guide tube) were replaced, the camera was returned to service. "The Department is awaiting a report from SPEC and from the licensee. "The Arkansas Department of Health, Radioactive Materials Program, Event Number is AR-2012-012" * * * UPDATE AT 1555 EDT ON 10/16/12 FROM KRIESEL TO HUFFMAN * * * The Arkansas Department of Health, Radioactive Materials Program, reported that the SPEC source retrieval crew received exposures of 12 mR for individual #1 and 10 mR for individual #2 during retrieval of the source back into the radiography camera. R4DO(Pick) notified and a copy of this update was e-mailed to FSME Events Resource. * * * UPDATE AT 1314 EST ON 01/14/13 FROM PEMBERTON TO ALEXANDER * * * The Arkansas Department of Health reported that it received the final reports from SPEC and Applied Inspections Systems (the licensee). SPEC has found that their investigation of the failure of the drive cable to be inconclusive. The Arkansas Department of Health has concluded that the root cause of this incident cannot be determined from the data available. Since the exposure device and source involved in the incident were certified for use and returned to service by SPEC personnel, the Arkansas Department of Health considers this event closed. R4DO (Vasquez) notified and a copy of this update was e-mailed to FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-10-17
48391 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2012-10-09 10:57 | 2012-10-09 16:22 | 2012-10-10 | LOSS OF ASSESSMENT CAPABILITY AT THE EMERGENCY OPERATIONS FACILITY "At approximately 0100 hours EDT, on October 9, 2012, a low voltage circuit breaker in the Crystal River Unit 3 (CR-3) Emergency Operations Facility (EOF) tripped due to an electrical fault. The associated loads were powered by backup batteries until they depleted at approximately 1057 EDT. This condition resulted in the loss of dose assessment (RASCAL) and facility cooling capability. "Dose assessment capability at the EOF was restored by 1335 EDT. During this event, RASCAL could be run from any plant computer outside of the EOF and the results conveyed back to the EOF. EOF ambient temperature is being monitored. An estimated completion time for chiller restoration has not been established. A follow-up notification will be provided when the chiller operation has been restored. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii). "At no time was the public's or plant employees' health or safety at risk. Due to numerous backup systems, alternate methods were available to calculate dose projections, if required, and communicate the information to the EOF. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DAVE MCAGY TO CHARLES TEAL AT 2001 EDT ON 10/10/12 * * * "At 1500 EDT on 10/10/12 Chiller Operations for the EOF has been restored. At 1700 EDT on 10/10/12 the EOF returned to normal office temperatures. At no time did temperatures affect the habitability or functionality of the EOF." The NRC Resident Inspector has been informed. Notified R2DO (Seymour). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-09
48390 | 0 | CONTINENTAL CEMENT |  |  |  |  | 2012-10-09 11:00 | 2012-10-09 15:25 | 2012-10-09 | SHUTTER STUCK OPEN ON FIXED VEGA AMERICAS, INC. NUCLEAR GAUGE The licensee hired VEGA Americas (formerly Ohmart/VEGA) to remove a fixed industrial gauge from their Green America Recycling facility. During removal, it was determined that the shutter was stuck in its normal operating open position. The vendor placed a temporary shutter over the source and will be shipping the gauge back to their facility for disposal. There were no personnel overexposures reported as a result of this incident. The gauge was a VEGA Americas model SHF2-0, S/N M-6997, containing 120 mCi of Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-10-17
48389 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-23 | 2012-10-09 15:15 | 2012-10-25 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT The following was received from the State of California: "During a routine inspection on Oct. 8, 2012, RHB inspectors discovered a potential medical event had occurred on May 23, 2012. A patient was admitted to the hospital for carcinoma treatment of the endometrium near both ovaries on May 22, 2012 and treatment began at 1800 PDT. The treatment plan called for 3000 cGy to each ovary, using two 18.5 mg Ra eq. CS-137 sources and an ovoid applicator. [The] dosimetrist placed one source at a time into an insert, which was to be verified by the physician, a second year medical resident, who then placed the insert into the applicator and patient. The source inserts are individually screwed into the ovoid applicator, which prevents the source from movement. The patient treatment was to take 26.5 hrs. On May 23, 2012 at 2030, [the doctor] and the dosimetrist were removing the implant from the patient, starting with the right side. That source was verified to be in the insert and then placed into the pig. The doctor then proceeded to remove the left side insert, which was handed to the dosimetrist, who found the insert to be empty. The radiation survey meter was used immediately around the patient, rolling her back and forth as it appeared the source may be on the bed somewhere. The source was found on an IV monitor stand, which was approx. 2 foot from the patients head partially blocked by a portable lead shield that had been placed the day before. The source recovery was completed around 2045. Hospital staff (supervising MD, lead dosimetrist and RSO) were notified of the event and the patient treatment of the left side was completed on May 29, 2012, after revising the original patient treatment plan. The investigation did not discover how the source ended up on the IV stand. The licensee's RSO evaluated the event and did not feel that it qualified as a medical event per 10CFR35.3045 and therefore did not inform RHB within the 24 hour timeframe." 5010 #: 052312 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-10-17
48388 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2012-10-07 21:40 | 2012-10-08 02:37 | 2012-10-08 | ESSENTIAL BUS DEENERGIZED WHILE DEFUELED "On October 7, 2012, with Unit 2 in a defueled condition, a differential current lockout occurred on the 2B3 4.16kV essential bus, causing a deenergization of the 2B3 4.16kV essential bus. At the time of the event, the 2B Emergency Diesel Generator (EDG) was loaded to the essential bus. Due to the differential current lockout, all bus loads were lost and the 2B EDG output breaker feeding the essential bus opened and the 2B EDG transferred to emergency mode. The 2A EDG is operable and in standby. All equipment responded as expected. The plant is currently being maintained in a defueled condition. Decay heat removal is being supplied by the 2A Fuel Pool Cooling train. The cause of the differential current lockout of the 2B3 4.16kv bus is under investigation. "This event is reportable pursuant to 10CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-10-08
48387 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-10-06 16:35 | 2012-10-06 17:07 | 2012-10-06 | ONE OF SIXTY SIX REACTOR VESSEL PENETRATIONS DID NOT MEET ACCEPTANCE CRITERIA "On 10/6/2012 during the Beaver Valley Power Station Unit No. 2 (BVPS-2) refueling outage, it was determined that the results of planned ultrasonic (UT) examinations performed on one of the 66 penetrations of the reactor vessel head would not meet the applicable acceptance criteria. This penetration will require repair prior to returning the vessel head to service. The indications are not through wall and there was no evidence of leakage based on inspections performed on the top of the reactor vessel head. The examinations were being performed to meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to find potential flaws/indications well before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. Currently 60 of 66 penetrations have been examined, with 59 satisfactory; all of the penetrations will be examined during the current refueling outage. "The plant is currently shutdown and in Mode 6 and the reactor vessel head is not currently installed. Repairs are currently being planned and will be completed prior to startup. "This is reportable pursuant to 10CFR50.72(b)(3)(ii)(A) since the as-found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-10-06
48386 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-10-05 13:03 | 2012-10-05 16:53 | 2012-10-06 | RPS AND PCIV ACTUATION DUE TO LOSS OF OFFSITE POWER "On October 5, 2012, at 1303 hrs. EDT James A. FitzPatrick Nuclear Power Plant (JAF) experienced a loss of offsite power during its planned refueling outage. This resulted in the Reactor Power System (RPS) receiving a valid actuation of containment isolation valves in more than one system. All control rods were fully inserted when the full scram signal occurred. In addition, the four Emergency Diesel Generators (EDG) started in response loss of power but the EDG 'A' output breaker did not automatically close. Investigations are underway. "The following systems were automatically isolated: - Reaction Water Clean-up (RWCU) - Drywell Floor Drain - Drywell Equipment Drain "The following systems were automatically actuated: - 4 Emergency Diesel Generators (EDG) "All systems functioned as required except as noted above. JAF remains in Mode 5. "In addition, a major loss of Emergency Response communication capability has occurred. Some of the systems not available include: Emergency Notification System (ENS), Health Physics Network (HPN), and commercial phone communication." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MARK HAWES TO CHARLES TEAL AT 1637 EDT ON 10/6/12 * * * "On October 5, 2012, at 2011 hrs. EDT, James A. FitzPatrick Nuclear Power Plant (JAF) restored 345 kv backfeed qualified offsite power line and restored non-vital power. One of the two newly installed 115 kv Reserve Station Transformers experienced a lockout signal for an unknown reason which caused an isolation signal disconnecting offsite power. The Emergency Diesel Generators (EDG) started in order to provide vital power to plant systems. Both 115 kv Reserve Station Transformers have been removed from service and corrective actions are resolving this issue and the failure of the EDG 'A' output breaker to close. The EDGs are in standby. The current state of JAF is normal, Refueling Outage mode 5. "In addition, Emergency Notification System (ENS), Health Physics Network (HPN), and commercial phone communication have been restored and verified functional. The Emergency Plan is functional." The NRC Resident Inspector has been informed. Notified R1DO (Trapp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-10-05
48385 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-10-05 05:14 | 2012-10-05 12:18 | 2012-10-05 | UNPLANNED AUXILIARY FEEDWATER ACTUATION "On October 5, 2012 at 05:14 EDT, restoration of steam generator narrow range level instrumentation from a bypassed condition was in progress when a valid Auxiliary Feedwater Actuation signal was received due to steam generator levels being below the Lo-Lo Level setpoint. As a result, both motor driven auxiliary feedpumps automatically started and two turbine driven auxiliary feedwater discharge valves automatically opened. The turbine driven auxiliary feedwater pump and the motor driven auxiliary feedwater discharge valves had been previously removed from service under administrative controls. The system was aligned per procedure so that water injection into the steam generators did not occur and the motor driven pumps were operated on mini-flow. Unit 1 is off line for a planned refueling and maintenance outage. There were no adverse impacts on the plant. "At the time of the event, Unit 1 was in Mode 5 with RHR in service and preparations for Mode 4 entry in progress." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-10-05
48384 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2010-04-16 | 2012-10-05 11:55 | 2012-10-05 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PORTABLE ANALYZER The following information was obtained from the State of New Hampshire: "NH Radiological Health (Agency) was contacted by NH Licensee 461R, Prolerized New England Co., LLC, a part of Schnitzer Northeast, on April 16, 2010. Their Niton Model XLp-818 XRF Analyzer, Serial No. 7170, with a 30 mCi AM-241 source, reported an error message regarding the shutter when turned on. The instrument was surveyed and a high reading of 120,000 cps was detected. When the instrument was turned off, high readings were still detected. The Agency detected 10 mR/hr at the shutter. "The instrument was leak tested and properly stored until it could be sent back to the manufacturer. The manufacturer received the instrument on May 26, 2010. The description of repairs was that they 'found large metal shavings in front end. Small shaving was jammed in the shutter motor gear causing shutter to remain opened. Removed metal shavings and tested shutter. Shutter working properly. Ran detector calibration and found resolution to be out of spec. Top and bottom housings are damaged. Strongly recommend upgrading to new LCD/Power board.' Unit required a wipe test. "The licensee turned the instrument in and purchased a new one." During a records review, it was determined that this event was not reported but should have been. No personnel overexposures occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2012-10-15
48383 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-10-04 19:21 | 2012-10-05 11:19 | 2012-10-05 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2012-10-05
48382 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2012-04-02 | 2012-10-05 10:33 | 2012-10-05 | PART 21 - TEMPERATURE SWITCH POTENTIALLY SHIPPED WITHOUT SET SCREW "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 9/18/2012 after an ESI test technician found a set screw in one of the oil bath stations of the temperature test fixture. After evaluating all components that were tested on the fixture, it was determined that this set screw is the same length, thread size and style as the set screw utilized in the EMD/Detroit temperature switches to lock the differential adjustment screw. The other components tested on the fixture did not contain such a set screw. Either an extra set screw was inside a temperature switch and it fell into the test fixture oil bath when the test technician removed the switch cover; or, the test technician dropped the set screw after removing it from a temperature switch to adjust the differential setting of the switch. If the latter occurred, then the potential exists that a temperature switch was shipped without the differential adjustment screw locked and therefore the switch settings could drift over-time from exposure to vibration on the EDG skid. ESI has identified the time period in which this could have occurred to be 4/2/2012 to 9/18/2012. The suspect temperature switches are EMD parts manufactured by Detroit Switch. These are located in the engine cooling water and lube oil systems for low standby lube oil temperature alarm, high coolant temperature alarm/shutdown and coolant immersion heater control applications. "The evaluation was concluded on 10/3/2012 and it was determined that this issue is a reportable defect as defined by 10CFR21. If a switch applied in the immersion heater control application experiences significant setpoint drift, it is possible that the standby temperatures of the lube oil and coolant systems may be degraded enough to affect the start time of the diesel generator. "All affected users should inspect the suspect switches for presence of the set screw at their earliest convenience. If the set screw is missing, the temperature switch should be returned to ESI for rework." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-10-05
48381 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-05 08:00 | 2012-10-05 07:37 | 2012-10-05 | LOSS OF EMERGENCY RESPONSE FACILITY INFORMATION SYSTEM DUE TO PLANNED MODIFICATION "At approximately 0800 EDT, on October 5, 2012, the Emergency Response Facility Information System (ERFIS) will be removed from service to perform a planned modification for the improvement of site wide data communications between various plant process computing platforms. The expected duration of ERFIS non-functionality should not exceed 24 hours and during this time would not be able to be restored within one hour. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS) and the Safety Parameter Display System (SPDS). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS computer system is non-functional. The on call Emergency Response Organization has been notified of the ERFIS outage. "This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-05
48380 | 0 | MITSUBISHI NUCLEAR ENERGY SYSTEMS |  |  |  |  | 2012-02-21 | 2012-10-05 07:17 | 2012-10-05 | STEAM GENERATOR TUBE TO TUBE WEAR The following information was received via email: "Mitsubishi Heavy Industries, LTD (MHI) has identified steam generator tube wear for San Onofre Nuclear Generating Station. "Steam Generator tube wear has been identified in areas of the U-bend between anti-vibration bars, where the tube is not supported by the anti-vibration bars. This tube wear occurred due to the contact of a tube with an adjacent tube, and resulted in a leak from a Unit 3 tube. The cause of the tube leak was determined to be the in-plane direction fluid elastic instability under high localized thermal-hydraulic conditions (steam quality (void fraction), flow velocity and hydro-dynamic pressure), and insufficient contact force of the tube to anti-vibration bar. This type Mitsubishi Heavy Industries has identified steam generator tube wear for San Onofre Nuclear Generating Station. The Steam Generator tube wear adjacent to the retainer bars was identified as creating a potential safety hazard. "The plugging of the tubes that have the possibility of the fluid elastic instability and thermal power output reductions were identified as potential corrective actions. SCE [Southern California Edison] will run Unit 2 at 70% power for a short duration as a corrective action. In addition, SCE and MHI will continue a detailed analysis and investigation to this problem. Additional corrective actions may be required as the analysis and investigation continue. MHI has recommended to the purchaser that it perform eddy current inspection of tubes after Unit 2 operation resumes." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-10-05
48379 | 0 | MITSUBISHI NUCLEAR ENERGY SYSTEMS |  |  |  |  | 2012-02-13 | 2012-10-05 07:17 | 2012-10-05 | PART 21 - STEAM GENERATOR TUBE WEAR ADJACENT TO RETAINER BARS The following information was received via email: "Mitsubishi Heavy Industries, LTD (MHI) has identified steam generator tube wear for San Onofre Nuclear Generating Station. "The Steam Generator tube wear adjacent to the retainer bars was identified as creating a potential safety hazard. The maximum wear depth is 90% of the tube thickness. The cause of the tube wear has been determined to be the retainer bars' random flow-induced vibration caused by the secondary fluid exiting the tube bundle. Since the retainer bar has a low natural frequency, the bar vibrates with a large amplitude. This type tube wear could have an adverse effect on the structural integrity of the tubes, which are part of the pressure boundary. "The plugging of the tubes that are adjacent to the retainer bars was performed. MHI has recommended to the purchaser to remove the retainer bars that would have the possibility of vibration with large amplitude or to perform the plugging and stabilizing for the associated tubes." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-10-05
48378 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-10-04 16:00 | 2012-10-04 22:29 | 2012-10-04 | PRIMARY AND BACKUP METEOROLOGICAL TOWERS OUT OF SERVICE "At 1600 CDT on 10/4/2012, it was determined that the plant backup meteorological tower was not reliable as a source of data and was declared non-functional. At the time of this determination, the primary meteorological tower was out of service for maintenance and was also non-functional. Based on both the primary and backup meteorological towers being non-functional, this is considered a loss of emergency assessment capability. The ability to assess certain Emergency Action Levels (EALs) or perform dose assessment calculations could potentially be hampered by the unavailability of the meteorological monitoring instrumentation. The alternate method per procedure is to contact the National Weather Service for information. The station implemented the alternative method for information gathering. The primary met tower was returned to service at 2011 CDT on 10/4/2012." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-04
48377 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2012-10-04 13:01 | 2012-10-04 16:52 | 2012-10-04 | INADVERTENT ACTIVATION OF ALL EMERGENCY SIRENS "At 1301 [CDT] on October 4, 2012, during the restoration of a single Farmer City owned siren, DeWitt County Emergency Dispatch Center inadvertently activated all of Clinton Power Station's emergency sirens instead of the Farmer City owned siren. A siren in the Farmer City area had fallen off a pole, and following repairs, instead of testing the individual siren, the Dispatch Center inadvertently actuated all 40 Clinton Power Station sirens. The sirens were actuated for approximately 1 minute and 14 seconds. The Clinton Power Station siren system covers parts of four surrounding counties (DeWitt, Piatt, McLean, and Macon). "A spurious actuation of one or more emergency response sirens is reportable under 10CFR50.72(b)(2)(xi) addressing a notification of a government agency related to the health and safety of the public. "The NRC Resident Inspector has been notified. All of the affected county Emergency Management Agencies have been notified. "The DeWitt County Sheriff has notified various media outlets." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-10-04
48376 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2012-10-04 09:59 | 2012-10-04 16:37 | 2012-10-04 | BOTH TRAINS OF CONTROL ROOM EMERGENCY VENTILATION SYSTEM OUT OF SERVICE "The 'A' Main Control Room Emergency Ventilation System (MCREV) fan failed to automatically start when placed in service at 0959 EDT on 10/4/12. The `B' fan was available at the time of the initiation, but was inoperable due to E-42 Emergency 4kV Bus outage. Both MCREV fans inoperable is an entry into Technical Specification 3.7.4 Condition E which requires Unit 3 to be Mode 3 in 12 hours. Unit 2 was not in a mode of applicability at the time of the event [Unit 2 is defueled]. This issue is being reported under 10 CFR 50.72(b)(3)(v)(D) for an event that could have prevented the fulfillment of a safety function - mitigate the consequences of an accident. The 'A' MCREV fan was restored to an operable status at 1237 EDT on 10/4/12 and the Technical Specification Action was exited." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-10-04
48375 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2012-10-04 10:00 | 2012-10-04 15:32 | 2012-10-04 | UNANALYZED ACCIDENT SCENARIOS FOR CERTAIN CONSEQUENCES OF CONCERN "This notification is based on 10CFR70 Appendix A (b)(1), 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis (ISA), and which results in failure to meet the performance requirements of 10CFR70.61.' "Westinghouse Columbia Fuel Fabrication Facility routinely enters external NRC event notifications and issues into the Corrective Actions Program (CAPs) for external operating experience. Westinghouse Environment, Health and Safety (EHS) staff and the Issue Review Committee evaluated the AREVA NP, Inc. Richland NRC Event Report #48366 for applicability and impact on compliance for the Columbia plant. "This evaluation identified a regulatory noncompliance. The ISA currently identifies Items Relied on for Safety (IROFS) for scenarios based on Emergency Response Planning Guidelines (ERPG) (i.e., airborne concentration criteria) for chemical consequences. However, the Process Hazards Analysis (PHA) conducted for the ISA, with minor exceptions, did not specifically identify high or intermediate events that may or may not require additional IROFS for dermal or ocular exposures from the plant's chemical processes subject to 10 CFR 70 requirements. This report is intended to cover all potential chemical dermal or ocular exposures within those systems covered by the plant's ISA. "There is no actual safety significance, and the potential safety significance of this issue is low due to the following: "- An extensive number of IROFS are currently in place to prevent chemical spills that could lead to airborne concentrations above ERPG limits, and these same IROFS can be readily utilized to prevent most dermal/ocular exposure accident sequences. "- SNM-1107 License Application, Section 7.0 - Chemical Safety Program, as well as the governing Occupational Health and Safety (OSHA) regulations, already contain requirements for worker protection from these hazards. The Columbia plant recognizes these hazards through its PHA and Job Safety Analysis (JSA) processes and identified the need for controls, where applicable. "- Robust procedures, training and appropriate Personal Protective Equipment (PPE) are in place to ensure worker safety from these types of hazards. "However, failure to specifically identify the dermal/ocular exposure as potentially high or intermediate consequence events in accident sequences in the framework of the ISA process led to these sequences not being included in the ISA Summary, and therefore, IROFS were not designated for these sequences as required by 10 CR 70.61. As noted above, this issue has been entered into CAPs (IR 12-277-C001). Until the PHA and JSA are reviewed for identification of specific IROFS, the applicable elements of our license-required Chemical Safety Program will be treated as IROFS for purposes of compliance with 10CFR70.61 and reporting under 10CFR 70 Appendix A." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-10-04
48374 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-27 | 2012-10-04 15:58 | 2012-10-04 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK OPEN "On September 27, 2012, the Agency was notified by the licensee that the shutter on a Berthold nuclear gauge model number LB300L was found in the stuck open position during a routine inspection. The activity was not provided. The gauge shutter is stuck in the open position, which is the normal operating position. The licensee stated that the gauge does not create an increased exposure risk to any personnel. The manufacturer has been contacted and is scheduled to repair the gauge the first week in October. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-8992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-10-12
48373 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-10-04 08:02 | 2012-10-04 11:34 | 2012-10-04 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM REPAIRS "At approximately 0802 EDT on 10/04/2012, [Air Handler] AH-17, TSC Cooling Fan, was discovered not running. The fan belt for AH-17 TSC was found broken. AH-17 TSC belt has been replaced; it is expected to be placed back in service by 1200 [EDT], 10/04/2012 and after verification of proper operation will be declared operable. This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2. In addition, at approximately 0900 EDT, on October 4, 2012, the Harris Nuclear Plant Technical Support Center (TSC) ventilation system was removed from service to perform planned maintenance on TSC outside air fan OA-2 (belt replacement). The fan was out of service for greater than one hour for this activity then returned to service for an 8 to 24 hour run in period for the new belts. After the run in period, the TSC outside air fan and AH-17 TSC will be taken out of service again for greater than one hour for belt adjustment. Following the belt adjustment, the fans will be returned to service and TSC ventilation will be declared operable. Compensatory actions are in place for periodic monitoring of TSC temperatures and the two other TSC HVAC units which are operating satisfactorily. The assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the TSC ventilation system is non-functional. The on-call Site Emergency Coordinator and Emergency Response Manager have been notified. The alternate TSC is available per plant procedure if required." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-04
48372 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-10-03 16:00 | 2012-10-03 20:22 | 2012-10-03 | FIRE SAFE SHUTDOWN ANALYSIS FAILED TO IDENTIFY UNPROTECTED CABLE "During logic and cable routing reviews for Multiple Spurious Operations (MSO), an existing unprotected cable issue was identified that impacts the D22 emergency Diesel Generator (EDG) output breaker. This unprotected cable could fail due to fire damage in fire area 067W when the associated 4kV safeguard bus is credited for Post-Fire Safe Shutdown. "The single spurious fire induced cable failure identified can cause the D22 EDG output breaker to spuriously close when the 4kV safeguard bus is credited using the offsite power source. The existing fire safe shutdown analysis failed to identify this cable required protection in order to credit the 4kV safeguard bus in area 067W postulated fire." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | UNANALYZED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2012-10-03
48371 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2012-10-03 18:08 | 2012-10-03 19:06 | 2012-10-05 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM BILL LINNELL TO CHARLES TEAL AT 1606 EDT ON 10/05/12 * * * This event has been retracted by the licensee. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified the R1DO (Trapp) and the 73.71 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-10-03
48370 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-05 21:25 | 2012-10-03 12:26 | 2012-10-03 | RPS SUB-COMPONENT FAILURE CAUSED HALF SCRAM WITH GROUP 2 PCIV ACTUATION "On August 5, 2012, at 21:25 EDT, Unit 1 received a Reactor Auto SCRAM System 'A' Trip signal in the main control room. The annunciator was initially reset by operators, but the operating crew noted that some white SCRAM lights and some Group 2 PCIV indication lights were flickering in the control room. This anomaly coupled with the ability to reset the annunciated condition immediately indicated an issue with fluctuating voltage on the power supply for RPS [Reactor Protection System] 'A'. Approximately 30 seconds after the annunciator was reset, the 'A' RPS bus tripped, causing a half SCRAM in conjunction with the automatic actuation of the Standby Gas Treatment system (SGT) and isolation of PCIVs in multiple systems, both of which are normal responses to this loss of the 'A' RPS bus. The crew entered the appropriate abnormal operating procedures and confirmed the actuations automatically occurred as required given the loss of the RPS bus. They investigated the 'A' RPS Motor/Generator (M/G) set, placed the 'A' RPS bus on its alternate supply, reset the SGT and PCIV actuation logic, and returned the PCIVs to their normal position. "Upon investigation, the 'A' RPS M/G set was found running, but the Over Voltage Relay in the power monitoring cabinet was chattering. The field investigation team determined that the RPS trip was caused by the failure of its voltage regulator which was then replaced. The 'A' RPS M/G set was consequently returned to service as the primary RPS power source on August 6, 2012. Maintenance personnel subsequently determined that a voltage regulator subcomponent was defective. Because the malfunctioning subcomponent caused the loss of RPS 'A' as the initiating event rather than a valid SGT or PCIV actuation signal, the resulting actuation of SGT and the isolation of multiple PCIVs are considered invalid actuations. Based on that information, 10CFR50.73(a){2)(iv) allows this event to be reported via a telephone notification within 60 days instead of submitting a written LER." The licensee has notified the NRC Resident Inspector. | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-10-03
48369 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2012-10-03 08:43 | 2012-10-03 12:15 | 2012-10-03 | FAILURE OF STARTUP TRANSFORMER CAUSED UNDERVOLTAGE CONDITION ON ESSENTIAL BUS "On October 3, 2012, with Unit 2 in a defueled condition, a failure occurred on the 2B Startup Transformer, causing an undervoltage condition on an essential bus and resulted in the automatic start and loading of the 2B Emergency Diesel Generator (EDG). Prior to the event, the 2B EDG was available and not required by Technical Specifications; however, the 2B EDG was inoperable. Additionally, the 2A EDG is available. All equipment responded as expected. Currently maintaining the plant in a defueled condition. Decay heat removal is being supplied by the 2A Fuel Pool Cooling train and was never interrupted. There was no impact on the Shutdown Safety Assessment. "This event is reportable pursuant to 10CFR50.72(b)(3)(iv)(A). "Due to common high side feed, the loss of the 2B Startup Transformer resulted in the loss of the 1B Startup Transformer. Prior to the event, the 1A EDG was out of service for maintenance. As a result, Unit 1 entered Technical Specification 3.8.1.1 Action C. due to the loss of one offsite AC circuit and one diesel generator inoperable." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-10-03
48368 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-10-03 08:00 | 2012-10-03 07:25 | 2012-10-26 | TECHNICAL SUPPORT CENTER OUTAGE DUE TO PLANNED MAINTENANCE "This report is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the planned loss of an Emergency Response Facility (ERF). Calvert Cliffs will be implementing a scheduled modification to renovate the site's common Technical Support Center (TSC) which will temporarily remove it from service. The planned maintenance window is expected to be three weeks beginning on 10/3/12 and concluding on 10/26/12. Should an emergency be declared requiring TSC activation during this period, the procedurally identified alternate TSC will be staffed and activated (CCNPP Simulator). All TSC responders and other key ERO personnel have been briefed on this activity and the applicable contingency actions that will be required to be taken in their specific emergency response procedures. This condition has no adverse impact to the health and safety of the public. An update will be provided once the TSC has been restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM TOM JONES TO DONG PARK AT 1302 EDT ON 10/26/12 * * * The TSC has been restored to normal operation. The licensee will notify the NRC Resident Inspector. Notified R1DO (Caruso). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-03
48367 | -1 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2012-10-03 00:10 | 2012-10-03 07:25 | 2012-11-19 | UNANALYZED CONDITION DUE TO HIGH ENERGY LINE BREAK BARRIER BEING PARTIALLY OPEN "At 0010 [EDT] on 10/3/12, it was determined that an unanalyzed condition existed for the switchgear rooms on Unit 1. A degraded condition of a high energy line break (HELB) barrier was created during security surveillance. A HELB barrier door for the 27' elevation switchgear room was partially opened for a 14 minute period and could have allowed steam from a HELB on the 27' elevation of the Turbine Building to potentially impact equipment in both the 27' and 45' elevation switchgear rooms because these rooms are connected by a common ventilation system. The switchgear rooms are not analyzed for a steam environment. The degree of the impact could not be readily determined, but could likely affect the safety related equipment in the switchgear rooms. At 0024 [EDT] on 10/3/12, the HELB barrier door for the 27' elevation switchgear room was closed and the barrier restored which eliminated the potential unanalyzed condition. An 8 hour report to the NRC is required under 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety' since there was not a reasonable expectation that the switchgear room environment could support operation of safety related equipment with the 27' elevation switchgear room door partially open. Further analysis is underway." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM CHARLES MORGAN TO HOWIE CROUCH AT 1241 EST ON 11/19/12 * * * "Subsequent engineering analysis conducted for this condition demonstrated that having the roll-up door stuck open six inches would not, should a HELB occur in the vicinity of the 27' switchgear room roll-up door, result in conditions within both switchgear rooms that would challenge the design limits and which would render the Class 1E electrical busses inoperable. Therefore the unit was not in a degraded or unanalyzed condition. "As a result this condition is not reportable under 50.72(b)(3)(ii)(B). Based on this information, Calvert Cliffs is retracting notification message EN #48367." The licensee has notified the NRC Resident Inspector. Notified R1DO (Dwyer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-10-03
48366 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2012-10-02 07:30 | 2012-10-02 20:56 | 2012-10-02 | UNANALYZED CONDITIONS MAY LEAD TO INTERMEDIATE CONSEQUENCE EVENTS "On Friday 9/28/2012, while completing ISA [Integrated Safety Analysis] meetings on a new process, several accident sequences were identified that had the potential for creating ocular exposures that could lead to intermediate consequences in accordance with 10CFR70. The sequences involved uranyl nitrate (UN) solutions. IROFS [Item Relied On For Safety] were identified for the new process. "As a follow-up to this activity, on 10/02/2012, plant safety personnel reviewed existing ISA accident sequences for other process systems where UN solution is present and at 0730 [PDT], reported to the EHS&L Manager that similar loss of containment accident sequences in other process systems were determined to be 10CFR70 low consequence events within the approved existing ISA. "This report is being made under 10CFR70 Appendix A, criterion (b)(1) which states, 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR70.61.' "10CFR70.61 (4)(e) states in part, '...Each engineered or administrative control or control system necessary to comply with paragraphs (b), (c), or (d) of this section shall be designated as an item relied on for safety.' "While this report is being made based on the treatment of UN sprays to the eye, this scenario can be applied to other hazardous chemicals falling under the scope of the ISA treatment. "Based on information obtained during the ISA activities for this new process, two other types of accident sequences documented in the existing facility ISA as 10CFR70 low consequence events need to be re-evaluated with respect to the 10CFR70 consequences of concern thresholds. These types of accident sequences are dermal contact and inhalation of liquid aerosols. These two types of accident sequences are being re-evaluated throughout the plant. The status of this re-evaluation effort will be reported in a 30-day follow-up report to this initial notification. "The personal protective equipment (PPE) that is used to provide protection to workers during work evolutions and the safety protocols for limiting exposures to UN are not categorized as IROFS for some of the existing processes. The PPE and safety protocols used by AREVA based on 40 years experience for these types of scenarios are considered to be adequate. AREVA's re-evaluation of these scenarios will be utilized to confirm their adequacy, or if applicable, to identify needed enhancements. "This discrepancy has potentially existed since 10/18/2004. This report does not involve potential criticality accident scenarios. "Corrective Actions in Progress: 1) verify that appropriate spray shields/deflectors are in place, 2) verify existing safety protocols that are in place are adequate, and 3) update the safety analysis and implementing documents to declare as IROFS the appropriate PPE and safety protocol." The licensee will be notifying Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-10-02
48365 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-09-05 10:45 | 2012-10-01 16:15 | 2012-10-01 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE UNABLE TO BE RETRACTED The following information was provided from the State of Louisiana via facsimile: "IRISNDT dispatched a radiography crew to Marathon Petroleum on September 5, 2012. The crew set up and began work around 6:30 am. The crew worked with a camera, associated equipment, and a collimator for hours before there was a problem. [At 1045 CDT] the source setup was about 15 feet up above the ground in the pipe rack when the source would not return into the shielded position. After several attempts to retrieve the source, the RSO was notified. The crew was instructed to secure the barricade at the 2 mR distance and maintain observing the area until the RSO could arrive. The RSO arrived and secured the source into the exposure device's shielded position. "The equipment, QSA Global Delta 880, s/n# D6460, the source is s/n# 86363B ...Ir-192, last leak tested on 08/07/2012. The investigation concluded a gear in the crank assembly was damaged and it caused the drive cable to jam. The assembly was red tagged and removed from service. Event exposures were 29 mR [Radiographer Trainer], 6 mR [Radiographer Trainee] and 2.4 mR [RSO]." Louisiana Event Report ID No. LA1200004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-10-09
48364 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-10-01 07:40 | 2012-10-01 12:12 | 2012-10-02 | TECHNICAL SUPPORT CENTER OUT-OF-SERVICE FOR PLANNED MAINTENANCE "On October 1, 2012, at approximately 0740 hours [CDT], the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned TSC ventilation system maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service for approximately 7 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1020 EDT ON 10/02/12 FROM JACK GADZALA TO S. SANDIN * * * "On October 2, 2012, at approximately 0828 hours [CDT], the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service for planned TSC ventilation system maintenance. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization (ERO) team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service for approximately 7 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that results in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-01
48363 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2012-10-01 04:24 | 2012-10-01 12:06 | 2012-10-01 | EMERGENCY RESPONSE DATA SYSTEM IS UNAVAILABLE FOR SERVICE "Seabrook personnel determined that the Emergency Response Data System (ERDS) is unavailable due to a malfunction of its process computer. The condition occurred around 0430 EDT today after a plant electrical bus was de-energized and subsequently reenergized during a maintenance activity. The plant is presently in a refueling outage with the reactor vessel defueled. Following repair of the process computer, Seabrook expects to return ERDS to service later today. "This event is being reported in accordance with 10 CFR50.72(b)(3)(xiii), loss of emergency preparedness capabilities, for loss of the ERDS function. "The NRC Resident Inspector has been notified of this event." * * * UPDATE FROM MIKE TAYLOR TO HOWIE CROUCH AT 1333 EDT ON 10/1/12 * * * The ERDS system has been returned to service. The licensee will be notifying the NRC Resident Inspector. Notified R1DO (Schmidt). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-01
48362 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-10-01 08:45 | 2012-10-01 08:50 | 2012-10-01 | TECHNICAL SUPPORT CENTER (TSC) / EMERGENCY OPERATIONS FACILITY (EOF) OUT-OF-SERVICE FOR PLANNED MAINTENANCE "On October 01, 2012, at approximately 09:00 hours Eastern Daylight Time (EDT), the Brunswick TSC/EOF Emergency Ventilation System is scheduled to be removed from service to perform planned maintenance consisting of emergency filtration unit charcoal testing and replacement. The removal of the ventilation system can potentially affect the TSC and EOF habitability during a declared emergency requiring activation. If an emergency is declared requiring TSC/EOF activation during this period, the facilities will be staffed and activated using existing emergency planning procedures unless uninhabitable due to ambient temperature, radiological, or other conditions. The Emergency Response Organization duty team has been notified of the maintenance and the possible need to activate the TSC and EOF at their alternate locations. This condition has no adverse impact to the health and safety of the public. "The ventilation system is scheduled to be out of service for approximately 2 days." The licensee informed the NRC Resident Inspector. | 96 | 100 | 0 | 96 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-10-01
48361 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-09-30 19:30 | 2012-09-30 23:22 | 2012-09-30 | OFFSITE NOTIFICATION DUE TO FIRE IN THE MAINTENANCE BUILDING "At 1804 hrs. CDT on Sunday, September 30, 2012, security personnel reported a fire in the mechanical maintenance shop. Fire Brigade responded and due to the severity of the fire, Coal City Fire Department was called for assistance. The fire was successfully extinguished at 1834 hrs. There were no personnel injured in the fire. The fire did not affect any structures, systems, or components that are required to provide for nuclear safety. At no time was the health and safety of the public adversely affected by this condition. "The maintenance shop is not attached to safety related structure of the operating units; therefore Dresden Station Unit 2 and Unit 3 were not affected by the fire. "At approximately 1930 hrs., information was released to the media due to fire in the mechanical maintenance shop requiring Coal City Fire Department assistance. This condition is reportable under 10 CFR 50.72(b)(2)(xi) due to a release of information to the media. No official press release was made." The cause of the fire is under investigation. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-30
48360 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-09-29 08:09 | 2012-09-29 14:50 | 2012-09-29 | LOSS OF POWER SUPPLY FOR NUCLEAR EMERGENCY TELECOMMUNICATION SYSTEM "At 0809 [EDT] on 9/29/12 a loss of power to the Nuclear Emergency Telecommunication System (NETS) at the PSEG Nuclear Emergency Operations Facility (EOF) located in Salem, New Jersey resulted in a loss of dial tone to the NETS phones located at the Salem and Hope Creek Generating Stations. This failure had no effect on the safety system or ability to safely control or monitor the Salem and Hope Creek generating stations: back-up emergency telecommunications (Direct-Inward-Dial, and Centrex) remained available. At 1038 [EDT] on 9/29/12, power was restored along with full NETS functionality. No injuries have occurred." The NETS communicates between the site and the County and State. A card in the UPS power supply failed resulting in this loss of power. Power was restored by bypassing the UPS. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-29
48359 | 0 | FAIRBANKS MORSE |  |  |  |  | 2012-09-28 | 2012-09-28 21:03 | 2012-09-28 | PART 21 - FAIRBANKS MORSE OPPOSED PISTON EDG FUEL OIL PUMP LEAK The following information was received via fax and email: "Utilities operating Fairbanks Morse (FM) Opposed Piston (OP) Emergency Diesel Generators (EDG) are as follows: "Constellation Energy - Calvert Cliffs; "Dominion - North Anna, Millstone; "DTE - Fermi II; "Entergy - Vermont Yankee; Arkansas Nuclear One; "Exelon - Limerick, Peach Bottom, Three Mile Island; "Next Era Energy - Duane Arnold; "Progress Energy - H.B. Robinson, Crystal River 3; "Southern Company - Georgia Power (Plant Hatch), Alabama Power (Plant Farley); "Xcel Energy - Prairie Island. "The defect is a significant oil leak from the fuel oil pump shaft. Leakage will occur if the mechanical seal area within the pump is displaced by an impact to the pump shaft during shipment and handling. "Even with a significant leak the pump has sufficient capacity to provide the proper operating pressure and volume of fuel oil to start the engine / EDG within the design specifications and continue operating the EDG at 100% load. However, the significant amount of fuel oil leaking while the system is under pressure, during standby and operating conditions, could potentially result in having an inadequate volume of stored fuel for the EDG to fulfill the seven day operating mission. "FM has instituted the following corrective actions which will be effective on all shipments after September 28, 2012: "1. Hydrostatic testing will be performed at FM during the dedication. "2. Outgoing shipments will be packaged in accordance with a new packaging procedure which requires the pump be secured to a piece of wood or directly to a skid, thus prevents an impact to the shaft during shipment. "Customers should perform a visual inspection after installation to ensure the fuel pump has no leaks. Defective pumps will have an immediate and significant leak. "All installed pumps that are free of leaks are acceptable for continued operation." Fairbanks Morse Report Number 12-01 - Issued Sept 28, 2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-09-28
48358 | 0 | TRISTATE MATERIALS TESTING LAB, LLC |  |  |  |  | 2012-09-27 | 2012-09-28 19:35 | 2012-09-29 | LOST MOISTURE DENSITY GAUGE On 9/27/12, at about 1100 EDT, the Radiation Safety Officer of Tri-State Materials Testing was notified that an employee of Tri-State Materials Testing did not show at a jobsite as expected at 0900 EDT. The employee was carrying a Troxler Model 3411 moisture density gauge, S/N 4783. This gauge typically has a 9 milliCurie Cs-137 source and a 44 milliCurie Am:Be source. The RSO reported that the gauge was in the proper container and properly secured to the employee's vehicle when last seen. The RSO searched for the employee and attempted to contact him numerous times with no result. The gauge is assumed lost and a report has been filed with the Wallingford Police Department. * * * UPDATE AT 0002 ON 09/29/12 FROM HABIB CHAUDHARY TO PETE SNYDER * * * The employee contacted the RSO and confirmed that he was in possession of the gauge and would return it on 09/29/12. The RSO notified the Wallington Police Department that the gauge was still in the possession of the Authorized User and secured. Notified R1DO (Bellamy) and FSME Event Resource via email. * * * UPDATE FROM HABIB CHAUDHARY TO DONALD NORWOOD AT 0143 EDT ON 9/29/2012 * * * As of 0115 EDT, the gauge was in the possession of the RSO. Notified R1DO (Bellamy) and FSME Event Resource via E-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-10-08
48357 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-09-28 14:10 | 2012-09-28 17:49 | 2012-09-28 | PART 21 - DEFECTIVE MASONEILAN TRANSDUCER MODEL 8005N "This message is notification to the NRC, pursuant to 10 CFR 21.21(d)(3)(i) requirements, that the Vice President Operations at Waterford 3 was notified on September 28, 2012 at 14:10 CDT of a condition which will be conservatively reported as a defect under the rule. A written report to the NRC will follow within 30 days. "The basic component that is subject to reporting is the Masoneilan I/P (current to pneumatic) Transducer Model 8005N. These transducers are utilized in safety related applications at Waterford 3. This condition has been corrected in the plant." Waterford has identified that the subject transducer fails to calibrate at the high end of its span. No defective components are currently installed. "Waterford 3 is operating normally at 100% power. This identified condition caused no loss of safety function and had no impact on public health and safety." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2012-09-28
48356 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-09-19 | 2012-09-28 17:19 | 2012-09-28 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The State of Arizona reported the following via email: "The Agency was notified on 9/19/2012 that the licensee had wipe test results which indicated that two of the Americium-241 sealed sources they possessed are leaking or contaminated. Each Am-241 sealed source has 3 solid metal foils of Am-241 with an activity of 2.1 mCi for each foil, for a total activity of 6.3 mCi for each source. Sealed source number 004 was never installed in an instrument and was stored in a canister provided by the manufacturer. The failed leak test, which showed 0.022 microCuries of removable contamination, occurred on April 19, 2012, but was not reported to the Agency until September 19, 2012. The second failed leak test occurred on source number 003 on September 19, 2012. It was previously installed in a positive mode ion mobility spectrometer where an engineer viewed signs of corrosion on the source. A subsequent leak test showed 0.92 microCuries of removable contamination. The Agency laboratory confirmed the results. "The licensee has already sent one source, serial number 004, back to the vendor and is in the process of returning the second source." Arizona First Notice 12-023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | MAT | [5 empty] | 0 | 2012-10-08
48355 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-09-27 | 2012-09-28 14:21 | 2012-09-28 | AGREEMENT STATE REPORT - THERASEED MODEL 200 SEED CARTRIDGES FAILED TO FUNCTION The State of Wisconsin submitted the following information via email: "On September 27, 2012 the Wisconsin Radiation Protection Section received a notification that Pd-103 Theraseed model 200 seed cartridges from Theragenics failed to function as designed while preparing for a prostate seed implant procedure. "The procedure was scheduled and pre-planned as a 'linked' procedure, with 145 Pd-103 seeds ordered from Theragenics. The order was received timely and the seed calibration was verified. Upon arriving in the Operating Room, the pre-implant testing routinely performed on the linker device worked appropriately, the procedure is performed with blank seed and spacer cartridges. The intraoperative pre-plan was performed from the ultrasound images as normal. "While attempting to make the linked seeds + spacers the licensee ran into immediate jams. They initially thought it was the link making device, retrieved a spare and encountered the same issue. Shortly after they discovered the seed cartridges had a flaw, the hole on the entrance side of the cartridge was not completely open, thus the link wire could not enter the cartridge to push a seed through. A second cartridge was found with the same problem. On a third cartridge they were able to make a linked needle but the operation was not smooth. "The Authorized User then decided to change the implant to a MICK applicator technique. All seeds were transferred to sterilized MICK cartridges. The implant proceeded with the MICK applicator. Upon completion of the implant it appears to be a satisfactory implant. "DHS [Wisconsin Department of Health Services] plans to investigate on Wednesday, October 3, 2012 when a Theragenics representative is present." Event Report ID No.: WI20014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-10-08
48354 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-09-28 08:30 | 2012-09-28 09:00 | 2012-09-28 | PLANNED EMERGENCY OFFSITE FACILITY/TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "On September 28, 2012, the EOF/TSC air handler chiller unit was removed from service to perform planned maintenance. This maintenance activity will not affect the air filtration portion of the system and these facilities remain available for use during an emergency. This maintenance activity will be performed in a manner to minimize the time that the air handler chiller is out of service. This maintenance activity impacts the ability to maintain ambient air temperature in the facilities. The [estimated] duration of this activity is planned to be 4 hours. "If an emergency condition occurs that requires activation of the emergency response facilities, the EOF and TSC will be utilized. The Emergency Response Organization team members have the ability to relocate to alternate locations in accordance with emergency implementing procedures based on conditions. Alternate emergency response facilities will remain available in the event that relocation is necessary. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update message will be provided when the emergency response facilities are restored." The licensee notified the NRC Resident Inspector, the State of South Carolina and the local counties of Lee, Chesterfield and Darlington. * * * UPDATE FROM ARNOLD TO KLCO ON 9/28/12 AT 1125 EDT * * * "The EOF/TSC Chiller is back in service as of 1102 [EDT] on 9/28/12. The ability to maintain ambient air temperature in the EOF/TSC facilities has been restored." The licensee notified the NRC Resident Inspector. Notified the R2DO (Nease). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-28
48353 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-09-27 12:12 | 2012-09-27 22:17 | 2012-10-26 | PART-21 REPORT - FAULTY MASTER TRIP UNITS, SLAVE UNITS, AND RESISTANCE TEMPERATURE DETECTORS "On September 27, 2012, the Site Vice President was notified that a 10CFR21 evaluation of thirteen (13) reworked Master Trip Units, Resistance Temperature Detector Units, and Slave Units supplied by Rosemount Nuclear Instruments, Inc. (Rosemount) determined that a non-compliant condition involving a basic component existed. "Rosemount informed James A. FitzPatrick Nuclear Power Plant (JAF) that 13 reworked Master Trip Units, Resistance Temperature Detector (RTD) Units and Slave Units were received at JAF which did not comply with their rebuild repair specification. Specifically, epoxy was not applied under certain resistors as required. In accordance with JA FitzPatrick plant procedures, this condition was determined as a 10CFRPart 21 condition involving a defect in a basic component. "As noted by an engineering review, some of the applications for the trip units require them to energize to perform the associated safety functions. Therefore, a failure occurrence by an installed non-conforming unit could potentially have an adverse affect on the associated systems' safety/accident mitigation functions. "JAF verified that none of the 13 deficient units were installed in any plant systems. Therefore, this condition had no actual safety consequences as the deficiency was identified by Rosemount prior to installation. The 13 units that were received at JAF without the epoxy have been returned to Rosemount for the addition of the epoxy and have subsequently been reworked and returned to JAF. "This notification is made pursuant to 10CFR21.21(d)(3)(i)." * * * RETRACTION ON 10/26/12 AT 1519 EDT FROM MARK HAWES TO DONG PARK * * * "Subsequent to the original notification dated 9/27/2012, a study was performed by Rosemount (DS-RNII-2012-049). The study analyzed the reported condition of the Master Trip Units for a Static Coefficient Load Analysis and a calculation of the rigidity of the 2-Watt wire-wound resistor when installed without being secured by epoxy. The conclusion was that there is sufficient design margin to ensure that the resistor will remain rigid during qualified seismic conditions. "Based on this assessment, there is not a significant safety concern related to the absence of epoxy and the previous 10 CFR 21.21(d)(3)(i) notification may be retracted." The NRC Resident Inspector has been notified. Notified R1DO (Caruso) and Part 21 group. | 100 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2012-09-27
48352 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-27 12:54 | 2012-09-27 14:08 | 2012-10-06 | PARTIAL LOSS OF EMERGENCY ASSESSMENT DURING PLANNED MODIFICATIONS "On September 27, 2012, Comanche Peak Nuclear Power Plant began a cyber security related modification to the Unit 1 and 2 Plant Computer Systems (PCS) and associated network infrastructure. The entire PCS for each unit will be out of service for approximately 6 hours. During that time, the PCS satellite display systems (SDSs) in the TSC and EOF will be inoperable. After approximately 8 hours, the PCS will be restored to service along with the SDSs in the TSC. The SDSs in the EOF will remain out of service until the modification and related site acceptance testing is complete, currently scheduled for October 5, 2012. During this period. the remote display of Radiation Monitoring System (RMS) information in the EOF and OSC will be unavailable. "The loss of EOF SDS terminals will be compensated by use of an alternate plant parameter display system, and loss of EOF/OSC RMS remote display will be compensated by means of the status board recorder telephone loop. Therefore, it is expected that appropriate assessment of plant conditions. notifications, dose projections, and communications could still be made, if required, during the time that the SDSs and RMS remote displays are inoperable. "The extended loss of the EOF SDSs and EOF/OSC remote RMS data is being reported in accordance with 10.CFR.50.72(b)(3)(xiii). which is any event that results in a major loss of emergency assessment capability, offsite response capability, or off site communications capability. The NRC Resident Inspector has been notified. A follow-up ENS communication will be made when the EOF SDSs and EOF/OSC remote RMS remote displays are fully restored to service." * * * UPDATE FROM RAUL MARTINEZ TO JOHN SHOEMAKER AT 0224 EDT ON 10/06/12 * * * Maintenance has been completed on the Unit 1 and Unit 2 Plant Computer System. The system has been tested and returned to service. The licensee will notify the NRC Resident Inspector. Notified R4DO (Powers). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-27
48351 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-27 09:30 | 2012-09-27 13:55 | 2012-09-27 | FITNESS FOR DUTY - CONTRABAND MATERIAL IDENTIFIED IN THE PROTECTED AREA A licensee contractor discovered contraband material concealed above ceiling tiles in a locker room during a renovation of the area. Contact the Headquarters Operations Officer for details. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2012-09-27
48350 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2012-09-27 11:01 | 2012-09-27 11:01 | 2012-09-27 | ERROR IN MAIN STEAM LINE HIGH FLOW CALCULATIONAL METHODOLOGY The following information was received by facsimile: "GEH [General Electric Hitachi] has recently discovered that calculations of choked flow rate in the Main Steam Line (MSL) of GEH BWRs may not be conservative, with the potential impacts to be evaluated for existing MSL high-flow setpoints and Analytical Limits (ALs). "GEH has not completed the evaluation of this condition to determine reportability under 10CFR Part 21 and is therefore issuing this 60-day Interim Notification. GEH will close or issue an update on this matter on or before December 12, 2012. Given the early status of the evaluation, GEH has no recommended actions at this time. This 60-day Interim Notification is issued in accordance with 10CFR Part 21.21(a)(2), and will be sent to all GE BWR/2-6 plants and ABWR plants." Affected plants include the following: Nine Mile 1-2, Fermi 2, Columbia, Grand Gulf, River Bend, FitzPatrick, Pilgrim, Vermont Yankee, Clinton, Dresden 2-3, LaSalle 1-2, Limerick 1-2, Oyster Creek, Peach Bottom 2-3, Quad Cities 1-2, Perry 1, Duane Arnold, Cooper, Susquehanna 1-2, Brunswick 1-2, Hope Creek, Hatch 1-2, Browns Ferry 1-3, and Monticello. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-09-27
48349 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2012-09-20 12:00 | 2012-09-27 07:17 | 2012-09-27 | AGREEMENT STATE REPORT- PATIENT UNDEREXPOSURE USING YTTRIUM-90 THERASPHERES TREATMENT New York City was notified by the licensee Radiation Safety Officer of a patient receiving an underdose of Yttrium-90 TheraSpheres for liver treatment. The prescribed dose was 120 gray, but only 11.4 gray was delivered to the patient. A review of the licensee's patient delivery system indicates that about 90% of the prescribed dosage remained in the catheter. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2012-10-05
48348 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-26 15:15 | 2012-09-26 22:27 | 2012-10-04 | TECHNICAL SPECIFICATION 3.0.3 ENTERED DUE TO SURVEILLANCE TESTING NOT BEING COMPLETED AS REQUIRED "Pressurizer Pressure LO Instrument surveillance testing was discovered to not have been completed as required. Existence of an internal jumper on solid state protection system input to logic cards prevented complete circuit testing. Unit 1 and unit 2 entered Technical Specification [TS] 3.0.3 at 1515 hours." Alternate method of surveillance testing on one of the trains was completed and TS 3.0.3 was exited on Unit 1 at 2203 EDT and Unit 2 at 2132 EDT. The licensee plans to complete surveillance testing on the second train before 1515 hours on 9/27/12. The licensee is currently in TS 3.3.2. The licensee has notified the NRC Resident Inspector. The states of North Carolina and South Carolina will be notified. Local county governments of York, Gaston, and Mecklenberg counties will also be notified. * * * RETRACTION AT 1652 EDT ON 10/04/12 FROM AARON MICHALSKI TO HUFFMAN * * * "Catawba nuclear station is retracting EN #48348 for both units 1 and 2 based on completion of testing and investigation of system operability. The testing determined that both units respective train 'A' and 'B' pressurizer pressure low were operable and would have functioned as needed. This condition is not reportable under 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D). The licensee has notified the NRC Resident Inspector." R2DO (O'Donohue) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-09-26
48347 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2012-09-26 13:36 | 2012-09-26 19:49 | 2012-09-26 | ATTEMPTED ENTRY ONTO THE SITE BY AN ILLEGAL ALIEN WITH FALSE IDENTIFICATION "This event is being reported as a newsworthy concern to the public under 10 CFR 50.72(b)(2)(xi). All times listed are approximate Mountain Standard Time. "On September 26,2012, at 13:36 pm, Arizona Public Service (APS) was notified of the intention of Maricopa County Sheriff's Office (MCSO) to issue a press release regarding an attempted entry to the Palo Verde Nuclear Generating Station's (PVNGS) Security Owner Controlled Area (SOCA) by an individual with suspicious identification earlier this morning. "An individual employed with a construction project sub-contractor arrived at the SOCA checkpoint and presented suspicious identification to PVNGS security officers to gain access to the site. The individual was not admitted through the checkpoint into the SOCA. MCSO was notified and placed the individual into custody. MCSO determined the identification was false and the individual was an undocumented immigrant. "The individual did not enter nor was he previously granted access to the site's Protected Areas surrounding the three units and Independent Spent Fuel Storage Installation. No evidence of malicious intent has been identified. MCSO is investigating the incident. "The station notified NRC Resident Inspectors and Region IV staff of the condition. "APS does not intend at this time to issue a press release, but is responding to media inquiries." | 100 | 90 | 100 | 100 | 90 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-26
48346 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2012-09-24 | 2012-09-26 12:56 | 2012-09-26 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE A Troxler model 3411B moisture density gauge was run over by a front end loader at a construction site in Silver Spring, MD. The area was roped off and the Radiation Safety Officer and the Maryland State Inspector were able to verify that though the control rods were detached, the sources had remained in their shielded positions. The damaged gauge was placed in the transport case and will be taken to a licensed repair facility. This model gauge typically has a 9 mCi Cs-137 and a 44 mCi Am-241:Be source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2012-10-04
48345 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-09-26 08:00 | 2012-09-26 09:47 | 2012-09-26 | TECHNICAL SUPPORT CENTER (TSC) PLANNED MAINTENANCE ACTIVITY "On 9/26/12, the Monticello Nuclear Generating Plant's TSC power supply will be isolated to perform a planned maintenance activity. The maintenance activity requires implementation of compensatory measures to maintain TSC functions during the planned activity. Compensatory measures include having the Emergency Director report to Control Room and relocating the remaining TSC staff at the EOF should an event be declared requiring Emergency Response Organization (ERO) activation. Maintenance activity is scheduled to be complete with the TSC fully functional by end of dayshift on 9/26/12. Site ERO has been notified of maintenance activity and instructed on planned compensatory measures to be implemented during activity if required. This event is considered reportable per 10CFR50.72(b)(3)(xiii). The licensee notified the NRC Resident Inspector." The licensee will notify the Minnesota State Duty Officer, and the Sherriff Departments for both Wright and Sherburne Counties. * * * UPDATE ON 9/26/12 AT 1734 EDT FROM TOM PROELL TO DONG PARK * * * "At approximately 1520 Central time, a disturbance occurred in the 12.5kV system during restoration activities for the TSC power supply. This would have caused a Major Loss of Emergency Assessment Capability and thus is reportable under 10CFR50.72(b)(3)(xiii). The licensee is investigating the disturbance. The EOF and all other emergency assessment capabilities were verified functional. The licensee notified NRC Resident Inspector." The disturbance to the 12.5kV system did not affect plant operations. Notified R3DO (Lipa). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-26
48344 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2012-09-25 17:07 | 2012-09-25 22:50 | 2012-09-25 | OFFSITE NOTIFICATION DUE TO A FREON LEAK FROM BUILDING AIR CONDITIONER "The control room was notified by the Environmental Protection Group that 43 lbs of Freon was released [from an air conditioning unit] at the Administration Warehouse Supply/Shop, not in the Protected Area, and that it was reported to the California Emergency Management Agency at 17:19 PDT and San Diego County at 17:12 PDT, per lAW procedure SO123-XV-17.3, 'Spill Contingency Plan'. "There is no longer a Freon release in progress." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-25
48343 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-09-25 15:00 | 2012-09-25 18:23 | 2012-09-25 | OFFSITE NOTIFICATION DUE TO HYDRAULIC LEAK "On September 25, 2012 at 1055 CDT, a road grader developed a hydraulic leak on a steering hose. This resulted in a light mist of approximately 20 gallons of oil being sprayed for a quarter mile. Three hundred feet of that was on gravel and the rest on blacktop. There is no actual or potential impact to the environment. "There is no impact to plant operation. At 1500 CDT, [the licensee was] notified by Xcel Energy Environmental Services that the State has been notified." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-25
48342 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-09-25 15:30 | 2012-09-25 18:07 | 2012-09-25 | OFFSITE NOTIFICATION DUE TO TRITIUM IN OVERFLOW "At 1215 hours on September 24, 2012, Surry Power Station personnel confirmed the presence of tritium at a level of 1,450 picoCuries/Liter (pCi/L) in a Unit 2 Turbine Building heating steam drain receiver (HSDR) tank. This tank collects condensate from steam which is used to heat buildings. A sample of the condensate was analyzed following failure of the pump (used to control level) which resulted in the tank overflowing to a drain line on September 17 and 23. The sample was taken because the drain line was degraded and the overflow resulted in a release to the environment. "The normal inputs into this drain line had been isolated from use in August when the degraded pipe was discovered. Currently, the tank contents are being diverted to a sump until repairs to the drain line and pump are complete. These are expected to complete in the next couple of weeks. "Both releases were estimated to be greater than 100 gallons. The location of the leak was within the Protected Area of Surry Power Station. There has been no tritium detected in any monitoring wells in the vicinity of the degraded drain line, nor in any monitoring wells outside the Protected Area. Because the leak remained onsite, no offsite impact to ground water is expected. Furthermore, the leak posed no threat to employees or the public. "Because there was a detectable amount of licensed material in the water, Surry implemented communication to offsite agencies as part of [licensee] commitment to the Nuclear Energy Institute (NEI) Ground Water Protection Initiative. "This notification is being transmitted due to Notification of Other Government Agencies under 10CFR50.72(b)(2)(xi). The Virginia Department of Environmental Quality, Virginia Department of Health, Virginia Department of Emergency Management, NRC Senior Resident Inspector and Surry County Administrator were notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-25
48341 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-09-25 10:44 | 2012-09-25 15:11 | 2012-09-25 | AUTOMATIC REACTOR SCRAM DURING MAINTENANCE ON 4160V BUS 12 AMMETER "During maintenance on 4160V Bus 12 ammeter, a Bus 12 lockout occurred. The station power was from 1R Reserve transformer for work on the 2R Auxiliary transformer. Net effect was Bus 12 locked out, removing power from 12 Reactor Feed Pump and 12 Reactor Recirculation pump. Reactor level lowered to +23 inches then began to rise. With both Main Feed Reg Valves in AUTO, the level transient reached +48 inches, the Reactor Water Level Hi Hi setpoint. The Main Turbine and 11 Reactor Feed Pump tripped as designed, and a Reactor SCRAM occurred. Reactor water level began to drop, and C.4.A Abnormal Procedure for SCRAM was used to restart 11 Reactor Feed Pump and recover water level. Minimum water level reached was -26 inches. Reactor Low Level SCRAM signal and Group 2 Primary Containment isolation occurred at +9 inches as designed, No Safety Relief valves lifted during this transient. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) did not receive an initiation signal due to not reaching their setpoints. There were no Emergency Core Cooling Systems initiation setpoints reached. Prior to the event, both divisions of Standby Liquid Control were inoperable as part of planned maintenance." All control rods fully inserted. Decay heat is being removed through the turbine bypass to the main condenser. The plant is in a normal shutdown electrical lineup and stable in Mode 3. The licensee has notified the NRC Resident Inspector and will notify the State and local governments. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-09-25
48340 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2012-09-25 01:00 | 2012-09-25 10:10 | 2012-09-26 | AGREEMENT STATE REPORT - LOST HUMBOLDT DENSITY GAUGE The following report was received from the NJ Department of Environmental Protection Bureau of Environmental Radiation via facsimile: "Licensee: South State Inc. "Event date and time: September 25, 2012 at 01:00 am "Event location: NJ Turnpike Interchanges 1-3 N-S "Event type: Lost density gauge - Humboldt Model 5001EZ Serial No. 2872 (Am-241 44 mCi and Cs-137 11 mCi) "Notifications: NJDEP BER and NJDEP Hotline "Event Description: South State Inc. reported a missing density gauge on September 25, 2012 at 01:29 am. South State was working on the NJ Turnpike. South State reported that the gauge was lost somewhere between exits 1 and 3 on the north or south bound lanes of the turnpike. Additionally, South State is looking along the route that was taken from their office on 202 Reeves St in Bridgeton, NJ and the turnpike. "As of 9:00 am this morning, the gauge has not been recovered and the search continues. "Media attention: None "NJ Event Report ID No: 12-09-25-0129-19" * * * UPDATE ON 9/26/12 AT 1239 EDT FROM PATRICIA GARDNER TO DONG PARK * * * The following report was received from the NJ Department of Environmental Protection Bureau of Environmental Radiation via email: "The Humboldt Model 5001EZ Serial No. 2872 has been recovered. The gauge is back at the licensee's (South State Inc.) facility. There is no observable damage to the transportation case and/or the gauge. The NJ State Police assisted with the recovery. Details of the event are being summarized and the NMED event report will be updated when completed." Notified R1DO (Bellamy), FSME, and ILTAB (Johnson) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-10-03
48339 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-25 05:55 | 2012-09-25 09:46 | 2012-09-27 | TECHNICAL SUPPORT CENTER REMOVED FROM SERVICE FOR MAINTENANCE "On September 25, 2012, power was removed from various Technical Support Center (TSC) systems to perform planned system preventative maintenance (PM) and corrective maintenance (CM) activities. During these maintenance activities, the normal TSC and Operational Support Center (OSC) are unavailable for use during an emergency. The Plant Data Network (PDN) will not be available to the TSC. This will render the Safety Parameter Display System (SPDS), Emergency Response Facility Display System (ERFDS), Emergency Assessment and Response System (EARS) and the Post LOCA Sampling System in the TSC unavailable. System alarms and data displays will still be available to the plant operators in the Control Room. The expected duration of the power outage is approximately 39 hours. "As compensatory measures, the backup emergency response facilities will be manned during an emergency. This compensatory measure has been communicated to the emergency response organization. It is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the normal TSC and OSC are unavailable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update message will be provided when the emergency response facilities are restored." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM GOELZER TO KLCO ON 9/27/12 AT 0025 EDT * * * "This is an update to EN #48339 report on September 25, 2012, where Pacific Gas & Electric company (PG&E) reported that a planned maintenance power outage caused the normal Technical Support Center (TSC) and Operational Support Center (OSC) to be unavailable for use during an emergency. "PG&E has completed all preventative maintenance (PM) and corrective maintenance (CM) activities that required the power outage to the TSC and OSC and has completed the restoration of these emergency response facilities. Plant personnel have been notified that the normal emergency response facilities have been restored. "PG&E personnel have informed the NRC Resident Inspector." Notified the R4DO (Werner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-25
48338 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-09-24 04:07 | 2012-09-24 11:23 | 2012-10-06 | EMERGENCY RESPONSE DATA SYSTEM PROCESS COMPUTER DATA SERVER FAILURE "At 04:07 EDT on September 24, 2012, Fermi 2 experienced a failure of a data server within the Process Computer system. The failure of the data server does affect data input to the server providing information to the Emergency Response Data System (ERDS). ERDS is currently not receiving updated information from Fermi data systems. This loss in capability is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "Indications of related plant variables are available in the Main Control Room. The Visual Annunciator System (VAS) and other portions of the Process Computer system remain functional. Meteorological and process effluent radiological monitor indications are available and dose assessment capability is available. Fermi 2 personnel will use normal phone communications to update NRC Operations Center in the case of an event declaration. Information normally provided by ERDS can be transmitted via the notification system as described in the Radiological Emergency Response Preparedness Plan." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MARK EGHIGIAN TO CHARLES TEAL AT 1435 EDT ON 10/6/12 * * * "On September 24, 2012, Fermi experienced a failure of a data server within the process computer system which feeds data to Emergency Response Data System (ERDS), and report #48338 was made to the NRC. "On October 6, 2012, corrective maintenance is complete, which repaired the data server and ERDS functionality is restored." The licensee has notified the NRC Resident Inspector. Notified R3DO (Valos). | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-24
48337 | 0 | AIR FORCE MASTER MATERIAL LICENSE |  |  |  |  | 2012-08-25 09:00 | 2012-09-24 09:10 | 2012-09-24 | GENERALLY LICENSED NICKEL- 63 SOURCE MISSING The following information was provided by the Air Force Medical Support Agency via email: "Per 10 CFR 20.2201(b)(2)(ii), we are providing a written report for the loss of radioactive material. The loss of material was reported on 24 Sep 2012; 1) telephonically to NRC Operations Center, Event No. 48337 and 2) via E-Mail to NRC, Region IV (Ms. Cook). The following information addresses the reporting requirements: "Description of the licensed material: The subject device contained nickel 63 (Ni-63), one source, at 15 milliCuries. The source is encapsulated in a hollow brass cylinder which in turn is sealed in a ceramic shield as referenced in Sealed Source & Device Registry (SS&DR) NR-0163-D-102-E, dated 19 Oct 2010. This generally licensed device (GLD) was used by USAF Security Forces Personnel (802nd SFS) of Lackland AFB, San Antonio, TX. "Description of circumstances for loss: The missing Ionscan 400B was added to the Installation Radiation Safety Officers inventory of all GLDs on Lackland AFB in May 2010. The serial number of the missing source is 10859. It was surveyed semi-annually until November 2011. At that point, the Lackland AFB installation radiation safety officer was told that particular device had been sent in October 2011 to the manufacturer for maintenance along with four (4) other devices. In November 2011, three (3) of the repaired devices had been returned from maintenance and were checked. The remaining two (2) units were assumed to still be at the manufacturer. During the May 2012 leak test/ inventory of GLDs, the two (2) devices were assumed to still be at the repair facility. The Lackland AFB Radiation Safety Officer (RSO) again raised the question as to the location and was assured the two (2) devices would be returned soon. In August 2012, when the devices had not been returned, the unit initiated a concerted effort to find the devices. The Air Force Radioisotope Committee was contacted to report the missing devices. "Statement of disposition: One (1) device has been located at the manufacturer's repair facility. According to Smith's Detection personnel, the serial number of the other missing device (10859) is not a valid serial number. The device in question with that serial number was inventoried and leak tested in May 2010, November 2010 and May 2011. The USAF believes that this is a valid serial number for the missing Ionscan. "Exposures to individuals: Because the device contains Ni-63, which is sealed and incorporated into the Ion Mobility Spectrometer assembly, the radiation level surrounding the device would be indistinguishable from background and dose to radiation workers or the general public is and will be negligible. "Actions taken: Numerous contact has been made with Smith's Detection to attempt to locate the missing device. Lackland personnel have used their chain of command to determine if the source was transferred to any other Air Force location. The storage area where the devices were stored have been searched. During the next 30 days, all Security Forces equipment will be moved to another location and special attention will be devoted in an attempt to locate the missing Ionscan. To date, the source has not been located. "Procedures/measures to rectify future loss: The installation radiation safety officer will reinforce the policies outlined in Air Force Instruction (AFI) 40-201, Managing Radioactive Materials in the United States Air Force for procurement and shipping and receiving of radioactive material. The shipper will require receipt confirmation from the manufacturer when items are shipped for maintenance or repair." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2012-10-02
48336 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-09-23 22:30 | 2012-09-23 23:16 | 2012-09-23 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for Details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2012-09-23
48335 | 0 | DOW CORNING |  |  |  |  | 2012-09-21 22:30 | 2012-09-21 22:51 | 2012-09-21 | DENSITY GAUGE SHUTTER FAILURE A density gauge with a 4 milliCurie Cs-137 source was identified to have a stuck shutter. The gauge is an Ohmart Vega Model SHF1A-0, S/N 0964CO, and is permanently installed on a process line in an isolated tower area. This event did not result in exposure to any personnel. The licensee barricaded the area, which read less than 1mR/hr. The licensee plans on having the gauge repaired by the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-10-01
48334 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-09-21 16:00 | 2012-09-21 21:29 | 2012-09-21 | ISOLATION VALVES COULD FAIL TO FULLY CLOSE "A review of load sequencing during a design basis loss of coolant accident (LOCA) with offsite power available has identified an issue with 24 motor operated valves (MOVs - 12 per unit). These valves all use limit switch 8 (LS-8) as an isolation permissive and may indicate closed if they are in a dead band zone when stroking closed from a containment isolation signal at the time of the load shed. The valves will then not resume movement to full isolation when power is restored potentially impacting containment leakage. This condition could occur during specific LOCA conditions, dependent on several variables. "The systems affected by this issue are: - RWCU - DWCW - PCIG - CAC - Suppression Pool Cleanup "Actions are in progress to resolve the LS-8 issue with a modification to remove this vulnerability. Appropriate testing will be done to prove that all valves perform their required safety function after the modifications are complete for each valve. "All affected valves are either closed and de-energized, or have been modified at this time." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2012-09-21
48333 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2012-09-21 14:00 | 2012-09-21 20:28 | 2012-09-28 | UNANALYZED CONDITION IDENTIFIED IN APPENDIX R FIRE SCENARIO "On September 21, 2012, a condition was identified where hydrogen may become entrained in the charging pump suction after the credited pump is restarted as part of the alternate shutdown procedure for the Auxiliary Building basement and mezzanine levels. "An air operated valve separates the Volume Control Tank (VCT) from the charging pump suction and this valve fails open on loss of air or power caused by the postulated fire. The alternate flow path from the Refueling Water Storage Tank (RWST) fails closed on a loss of air or power. A manual valve is provided to bypass this closed valve. However, due to hydrogen pressure in the VCT and the potential for significant pressure losses in the piping from the RWST to the charging pump suction, insufficient elevation head exists in the RWST to ensure that hydrogen will not become entrained. If this condition is left unmitigated, the credited charging pump is assumed to fail. "Due to the location of the postulated fire and its impact on equipment and cables, no other inventory makeup sources are credited. "Compensatory Measures have been implemented as follows: 1. All fire detection and suppression systems in the Appendix R fire zones have been verified functional. 2. All Hot Work in the area has been suspended. 3. Continuous Fire Watch has been posted in the Appendix R fire zone. 4. Combustion engine powered vehicles are restricted from entering the Auxiliary Building. 5. Within 24 hours remove all non-attended transient combustible materials from Appendix R fire zones. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM REISNER TO SNYDER ON 9/28/12 AT 1415 EDT * * * "This is a retraction of ENS report 48333 that was submitted at 2028 EDT on Friday, September 21 , 2012. "A 10 CFR 50.72(b)(3)(ii)(B) ENS notification was made due to a condition that was identified where hydrogen may become entrained in the charging pump suction after the credited pump is restarted as part of the alternate shutdown procedure in the event of a fire in the Auxiliary Building basement and mezzanine levels. "A subsequent engineering evaluation calculated the amount of gas that will be entrained into the charging pump suction flow and the duration of the entrainment. This evaluation demonstrates that for the most limiting Appendix R scenario that the charging pump will entrain a minimal amount of gas for a short duration, and is unaffected by this condition. Inventory control for the reactor coolant system is maintained throughout the scenario. "Based on the above information the 'Unanalyzed Condition' ENS notification made on September 21, 2012 is being retracted." The licensee notified the NRC Resident Inspector. Notified R1DO (Bellamy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-09-21
48332 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2012-09-21 14:49 | 2012-09-21 18:48 | 2012-09-21 | DRYWELL RADIATION MONITOR INOPERABLE "At 1449 CDT on September 21, 2012, the 2B Drywell Radiation Monitor was found downscale during control room panel monitoring. This monitor provides the input into one division of the primary containment isolation logic for a Group II isolation. As a result, the channel was placed in a tripped condition at 1515 hours in accordance with Technical Specification 3.3.6.1, Condition B. "Initial troubleshooting indicates that one of the two divisions of the isolation logic was inoperable. Given both divisions are required to complete the Group II isolation logic, this condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The station is currently taking action to restore the 2B Drywell Radiation Monitor to an operable condition. "The NRC Senior Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-09-21
48331 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-09-20 | 2012-09-21 16:37 | 2012-10-08 | CREMATORY CONTAMINATED DUE TO MEDICAL IMPLANT The following information was provided via facsimile transmission: "The Wisconsin Department of Health Services (DHS) received a phone call from the Radiation Safety Officer (RSO) at the University of Wisconsin-Madison informing them that the university had received a phone call from a funeral home that had just cremated remains of a person who had received an I-125 lung mesh implant. The implant was put in the patient on September 13, 2012 at the University of Wisconsin-Madison hospital. The patient was implanted with a lung mesh with 40 seeds totaling 23 mCi. The funeral home received a phone call during the cremation, from a family member notifying them that the person had received a radiation treatment a few weeks prior to the cremation. The cremation took place on September 20, 2012. After the cremation was completed, the crematory remained closed until DHS inspectors arrived. DHS conducted an investigation on September 21, 2012. Radiation readings inside the crematorium were 0.75 mR/hr with a Victoreen, Model 451 (#199588, calibrated on 1/20/2012). The cremains read 3.8 mR/hr on contact with a plastic bag. They have placed the cremains in a concrete container and radiation levels were at background on the outside of the container. No other areas of the facility were contaminated. The facility has agreed to suspend the operations until clean-up." * * * UPDATE FROM KUHLMAN TO KLCO ON 10/8/2012 AT 1012 EDT* * * The following corrected information was received by email: The State of Wisconsin made the clarification that the funeral home received notification from an authorized medical physicist from the University of Wisconsin-Madison. Notified the R3DO(Valos) and FSME via email. Wisconsin Event Report ID No.: WI120013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-10-01
48330 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-19 | 2012-09-21 16:46 | 2013-05-06 | AGREEMENT STATE REPORT - STUCK SHUTTER ON DENSITY GAUGE The following information was provided by the State of Arkansas via email: "During an on-site inspection on September 19, 2012, the licensee stated that a Berthold Model 7440, density gauge was in storage and that the shutter was not operating (stuck open). The gauge is serial number 2718 and contains 50 millicuries of Cesium-137. "On or about March 30, 2009 the licensee was preparing to replace this gauge. While preparing to remove the gauge from service, it was determined that the shutter would not close. The gauge was removed from service, under the direction of the Radiation Safety Officer (RSO), and placed in a secure storage location by the RSO. The gauge is contained in a metal storage locker, facing down toward a concrete slab. "In accordance with RH-1502.f.2 (10 CFR 30.50(b)(2) the stuck shutter should have been reported to the State of Arkansas within 24 hours. "With the manufacturer no longer being in business, the RSO contacted another gauge service company for assistance. The service company indicated they could supply a shielded container to ship the gauge to their facility. At this time, the gauge is still in storage at the licensee's facility. "The State of Arkansas is awaiting a written report from the licensee and final disposition information for the gauge. The State's event number is AR-2012-010. " * * * UPDATE FROM STEVE MACK TO DONALD NORWOOD AT 1216 EDT ON 5/6/13 VIA EMAIL *** "The following updates and closes Event 48330. "The licensee provided a letter dated May 6, 2013 stating that the cause of the shutter malfunction was determined to be the harsh environmental conditions the gauge had been subjected to. This letter also documented the receipt/disposal of the gauge [by Thermo MeasureTech]. The Department [Arkansas Department of Health] considers this event to be closed." Notified R4DO (Vasquez) and FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-10-01
48329 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-20 18:00 | 2012-09-21 16:09 | 2012-11-09 | AGREEMENT STATE REPORT - MISSING OHMART BETA GAUGE The following information was provided by the State of Arkansas via email: "While conducting an investigation of a citizen's allegation on September 20, 2012, the Department [Arkansas Department of Health] recovered a generally licensed device in a scrap yard in Dermott, Arkansas. The device is: "Ohmart Beta Gauge: Model BAL Gauge Serial Number: 3780BC Isotope: SR-90 Activity: 25 millicuries "This device was retrieved and transported to the Department's [Arkansas Department of Health] storage location in Little Rock at approximately 1800 CDT on September 20, 2012. "Ohmart provided information concerning the shipment date (12/1994) and the location. The device was shipped to Burlington House Mill in Monticello, Arkansas. Ohmart also informed the Department [Arkansas Department of Health] that a second device had also been shipped with this source. The source holder serial number for this device is 3779BC. "Health Physicists visited the old Burlington site after finding the device in the scrap yard in Dermott, Arkansas. "Health Physicists returned on September 21, 2012 to the Monticello and Dermott areas to search in locations where the second device may have been disposed. At the time of this notification, the Department [Arkansas Department of Health] considers the second device to be missing. "The Department [Arkansas Department of Health] has notified the Mississippi Department of Health. "The Department [Arkansas Department of Health] is still investigating and searching for the missing device. An investigation is on-going to identify the possible owner of the devices. "The Department [Arkansas Department of Health] considers this event open at this time pending the completion of the investigation." Arkansas Incident Number AR-2012-009. * * * UPDATE AT 1014 EDT ON 10/02/12 FROM ROBERT PEMBERTON TO S. SANDIN * * * The following update was received from the State of Arkansas via email: "On October 1, 2012, while conducting a follow-up investigation of allegation ARK-2012-009, the Department recovered the second generally licensed device originally shipped to the Burlington House Mill in Monticello, Arkansas. The device is described as follows: Manufacturer: Ohmart S.O. : AR940603068A Source Holder: BAL Source Serial Number: 3779BC Isotope: Sr-90 Activity: 25 mCi Date 12/94 "The device was retrieved from property on East Calhoun Street, Monticello, Arkansas and transported to the Department's storage vault in Little Rock. "The device housing was not damaged and preliminary wipes of the device showed no removable contamination. "An investigation is on-going to identify the possible owner of the devices. "The Department considers this event open at this time pending the completion of the investigation." Notified R4DO (Powers), FSME RESOURCE and ILTAB via email. * * * UPDATE FROM THE ARKANSAS DEPT. OF HEALTH VIA FAX ON 11/9/12 AT 1530 EST * * * "On November 9, 2012, both recovered sources were picked up for disposal from the Department's storage vault in Little Rock Arkansas. Neither source has been found to be leaking. "The Department has completed its investigation and considers this event closed." Notified R4DO (Farnholtz) and FSME Resources email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-10-01
48328 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-20 20:35 | 2012-09-21 01:20 | 2012-09-21 | TECHNICAL SUPPORT CENTER VENTILATION INOPERABLE "At 2035 CDT on 9/20/2012 power was removed from the Technical Support Center ventilation for planned maintenance on the supply breaker and the supply breaker cubicle. At 2109 CDTduring restoration, it was discovered that the breaker for the Technical Support Center ventilation could not be closed. "The cause for not being able to close the supply breaker is unknown. Troubleshooting is currently in progress and the Technical Support Center ventilation is expected to be returned to service on 09/21/2012. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev.2 since this work activity affects an emergency response facility." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-21
48327 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-09-20 12:40 | 2012-09-20 20:47 | 2012-09-20 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO INOPERABLE SEISMIC MONITORING INSTRUMENTATION "At 1240 CDT on 9/20/2012, Operations personnel determined that Browns Ferry Nuclear Plant had experienced a loss of assessment capability. The loss of assessment capability identified was due to not having functional seismic monitoring instrumentation during performance of a modification. The loss of seismic monitoring capability was determined to have existed from 8/17/2012 until 9/15/2012. "The ability to declare an Unusual Event per Emergency Action Level 7.1-U or an Alert per Emergency Action Level 7.1-A could potentially be hampered by the unavailability of the seismic monitoring instrumentation, because the declarations would be based on personnel feeling an earthquake. In addition, the unavailability of the seismic monitoring instrumentation could potentially hamper the operators in determining the magnitude of an earthquake in order to determine if it reached Operating Basis Earthquake levels or Safe Shutdown Earthquake levels. Therefore, this event is being considered reportable as it results in a loss of emergency assessment capability. Compensatory measures were established on 9/15/2012 which restored assessment capability. "This condition is reportable per 10CFR50.72(b)(3)(xiii). The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-20
48326 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-09-11 | 2012-09-20 16:38 | 2012-09-20 | AGREEMENT STATE REPORT - PATIENT RECEIVED UNDERDOSE OF Y-90 MICROSPHERES The following information was provided by the State of Tennessee via facsimile: "On September 11, 2012, the Division of Radiological Health received a report from the University of Tennessee Medical Center regarding a misadministration that occurred September 11, 2012. A patient was prescribed a dose of 20.0 mCi of Y-90 SirSphere microspheres, and only 15.32 mCi was administered. The administered dosage was 23% less than prescribed and will result in an absorbed dose of 40.1 Gy less than the calculated 171.3 Gy. The reason why this event occurred is not known. "The residual activity was detectable in the SirSpheres waste container which contained the V-vial; tubing, catheters, and protective radioactive waste cloths. The administered dosage is still considered to be within therapeutic range, but less than that prescribed by the physician. The patient and the referring physician were both notified on September 11, 2012. Inspectors from the Knoxville Field Office will follow-up on this incident." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-09-28
48325 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-09-20 14:16 | 2012-09-20 16:15 | 2012-09-20 | AUTOMATIC REACTOR TRIP DUE TO REACTOR PROTECTION SYSTEM ACTUATION "On September 20th at 1416 EDT, Three Mile Island automatically tripped due to a flux to flow imbalance as a result of a trip of the 'C' reactor coolant pump. The cause of the trip of the 'C' reactor coolant pump is still under investigation. "The electrical grid is stable and unit 1 is being supplied by offsite power. All control rods have fully inserted. Decay heat is being removed by main feedwater flow to both steam generators that are exhausting via the normal main condenser cooling loop under manual control. Preliminary evaluation indicates that all plant systems functioned normally following the reactor trip, except for automatic operation of turbine bypass valve control due to failure of the automatic control function to control precisely at setpoint. Three Mile Island remains stable in hot shutdown mode while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, and under 10 CFR 50.72 (b)(2)(xi) due to an information release to local officials. Both are four hour reports. "The licensee notified the NRC Resident Inspector." The licensee has notified the state and local governments, and will be making a media release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  |  | 0 | 2012-09-20
48324 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-09-18 | 2012-09-20 13:21 | 2012-09-20 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following information was provided by the State of Pennsylvania via facsimile: "On September 19, 2012, the licensee sent notification via email to the Department's Central Office regarding an event that took place on September 18, 2012. The event is reportable within 24 hours per 10CFR 30.50(b)(2). "The licensee discovered during a routine maintenance inspection that the pin which allows the shutter handle to move was stuck in the closed position, rendering the shutter inoperable. No radiation exposure to personnel is believed to have occurred. The cause of the event was normal wear of gauge. The handle is in the closed position and the gauge has been taken out of service. A reactive inspection is planned by the Department's Western Regional Office. "The device is identified as: Manufacturer: Berthold Technologies USA, LLC Model: LB8010 Serial #: 10055 Isotope: Cs-137 Activity: 20 mCi Source Serial Number: 0800/08" Event Report ID No: PA120031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-09-28
48323 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-09-20 09:23 | 2012-09-20 11:55 | 2012-09-20 | AUTOMATIC SCRAM AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION "On September 20, 2012 at 0923 EDT, Nine Mile Point Unit 1 experienced an automatic reactor scram due to a turbine trip at power. The cause of the turbine trip is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0924 EDT, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. One 115kv off site power source (Line 4) is unavailable for planned maintenance at the James A Fitzpatrick Nuclear Power Plant. Both Reserve Station Transformers are in service and being supplied by the other 115kv offsite power source (Line 1). Both Emergency Diesel Generators are operable and in standby. The unit is currently implementing post scram recovery procedures." The licensee has notified the NRC Resident Inspector. Licensee has notified the state. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-09-20
48322 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2012-09-18 14:00 | 2012-09-19 17:34 | 2012-09-19 | AGREEMENT STATE REPORT - SURFACE CONTAMINATION IDENTIFIED ON A SHIPMENT The following information was received from the State of Utah via email: "During the normal receipt process of a shipment #0870-09-0101 of LLRW [low level radioactive waste] on September 18, 2012, Energy Solutions personnel found one barrel in a shipment of five barrels that had removable beta contamination (tritium) which exceeded U.S. DOT limits. There was no visible damage to the barrel and no indication that the barrel had leaked during transport. Licensee personnel surveyed the other barrels in the shipment and the vehicle. No removable beta contamination was found and the vehicle was released on September 18, 2012. "[Utah Division of Radiation Control] staff are investigating this incident." Utah Incident No.: UT120002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2012-09-27
48321 | 0 | THE SHAW GROUP INC. |  |  |  |  | 2012-09-19 | 2012-09-19 15:15 | 2012-09-19 | INTERIM 10 CFR PART 21 REPORT REGARDING EMBEDMENTS FOR AP1000 PROJECT VOGTLE UNITS 3 AND 4 "[This notification] provides an interim report in accordance with 10 CFR 21.21 pertaining to the identification of noncompliances and deviations associated with embedments being supplied as basic components for the Vogtle Units 3 and 4, nuclear project. "The evaluation of reportability in accordance with 10 CFR Part 21 could not be completed within the 60 day evaluation period due to the number of components found with noncompliances and deviations. It is currently expected that the evaluation of these conditions will be completed by November 6, 2012. "If you have any questions, please contact Mr. Geoffrey Grant, Vice President of Licensing, Regulatory Affairs and Compliance." "Component Supplier: Cives Steel Company of 102 Airport Road; Thomasville, GA 31757 "During receipt inspection, QC inspectors found that some of the embedments received from Cives Steel Company had noncompliances and deviations, some of which warranted evaluation under 10 CFR Part 21. Examples of the types of deviations identified include unacceptable welds and weld repairs, missing Nelson studs, damaged Nelson studs, improper painting, incorrect dimensions, and illegible markings for identification. Approximately 211 embedments have been identified as having a noncompliance or deviation. "It is currently expected that the reportability evaluation for 10 CFR Part 21 will be completed by November 6, 2012, due to the quantity of embedments identified and the time required to evaluate the effects from these noncompliances and deviations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-09-19
48320 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-19 | 2012-09-19 14:47 | 2012-09-19 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTERS STUCK OPEN State of Texas provided the following information via email: "On September 19, 2012, the licensee notified the Agency [Texas Department of Health] that during a routine inspection it had discovered that the shutters on two Berthold LB-300L gauges were stuck in the open position. Both gauges contained cobalt-60 sources: one source was 1.9 milliCuries and the other was 1.68 milliCuries. Since these gauges normally operate in the open position, there was no increased risk of exposure to any individual. The licensee is making arrangements for a licensed vendor representative to make repairs as soon as possible. Information will be provided in accordance with SA-300 as it is obtained. "Source holder/source information: 1.9 mCi cobalt-60 source holder/source SN: 1412/1-7-98; 1.68 mCi cobalt-60 source holder/source SN: 1771/2-11-00." Texas Incident #: I-8990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-09-27
48319 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-07-23 20:57 | 2012-09-18 12:58 | 2012-09-18 | INVALID SYSTEM ACTUATIONS "On July 23, 2012, at 2057 hours, the Perry Nuclear Power Plant experienced a loss of the normal power supply to the Reactor Protection System (RPS) A electrical bus. The loss of RPS bus A caused an actuation of several Division 1 containment outboard isolation valves. The actuation signal caused full closure of one or more valves in each of the following Division 1 subsystems: Main Steam line drains, Containment Radiation Monitor, Drywell Radiation Monitor, Reactor Water Cleanup, Fuel Pool Cooling and Cleanup, Liquid Radwaste Sumps, Containment Vessel Chilled Water, Containment Vacuum Relief, Condensate Transfer and Storage, Mixed Bed Demineralizer and Distribution, Containment Personnel Airlocks, Service Air, and Instrument Air. Division 2 components and valves were not affected. "This event is considered an invalid system actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. Therefore, this notification is provided via a 60 day optional phone call in accordance with 10 CFR 50.73(a)(1) instead of submitting a written Licensee Event Report. "The event meets reporting criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation valve signal affecting containment isolation valves in more than one system. All affected systems functioned as expected in response to an outboard isolation signal. The valves were reopened in accordance with plant procedures. The failure mechanism that caused the loss of RPS bus A was a degraded voltage regulator. The voltage regulator was replaced and retested with satisfactory results. "The NRC Resident Inspector has been notified." | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-09-18
48318 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-18 10:55 | 2012-09-18 11:58 | 2012-09-20 | OUTAGE OF PLANT RADIATION MONITORING SYSTEM REMOTE READOUT DUE TO PLANNED MODIFICATION "On September 18, 2012, power was removed from SCADA A of the Radiation Monitoring System (RMS) to perform a planned system modification. During this period, data for most Unit 1 radiation monitors will not be electronically available in the emergency response facilities and will not be supplied to the Emergency Response Data System (ERDS), if activated. System alarms and data displays will still be available to the plant operators in the Control Room. The expected duration of RMS remote data partial inoperability is approximately 72 hours. The loss of Unit 1 remote readout capability requires compensatory measures to be used for the acquisition of radiological data in the emergency response facilities. These compensatory measures have been communicated to the emergency response organization, Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the portions of the RMS are inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update message will be provided when the RMS is restored." The NRC Resident has been notified. * * * UPDATE FROM TONY SIROIS TO JOHN KNOKE AT 1749 EDT ON 09/20/12 * * * "The Radiation Monitoring System alarms and data displays have been restored to the Comanche Peak Emergency Response Facilities (ERFs) following completion of planned system modifications. The emergency assessment capability of the Comanche Peak ERF have been re-established. The licensee has notified the NRC Resident Inspector. Notified the R4DO (Geoffrey Miller) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-18
48317 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2012-09-18 01:15 | 2012-09-18 05:59 | 2012-09-18 | MALFUNCTION OF THE SECONDARY CONTAINMENT DOOR INTERLOCK "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), Event or Condition that could have prevented fulfillment of a Safety Function needed to Control the Release of Radioactive Material. An employee entered a secondary containment interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately 10 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, has remained less than -0.25" H20 at all times. Initial investigation determined that a mechanical interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the mechanical interlock." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-09-18
48316 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-09-17 14:25 | 2012-09-17 18:03 | 2012-09-17 | PRESS RELEASE REGARDING LABOR NEGOTIATIONS "Entergy became aware of incorrect information that had been given to the media regarding employees being locked out of the Grand Gulf Nuclear Station. Entergy will be making the following statement: "Grand Gulf Nuclear Station Negotiations Update "Entergy will continue to negotiate with UGSOA [United Government Security Officers of America] Local 36, representing Grand Gulf security officers, in good faith to bring contract negotiations to a successful closure, and those security officers remain on the job today. The current contract expires at midnight September 30. "In keeping with the best interest of safety and maintaining formal organizational controls at the plant site, the company will pursue contingency plans for alternate staffing, consistent with Nuclear Regulatory Commission regulations, as the contract expiration date nears." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-17
48315 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-17 14:20 | 2012-09-17 17:19 | 2012-09-18 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MISSING IN TRANSIT This report submitted by email from the Agreement State of Arkansas: "On September 17, 2012 at 1420, the Radiation Safety Officer for Applied Inspection Systems, Inc. (ARK-576-03310) in Benton, Arkansas notified the Department that a radiography camera shipped via [a transportation company] had not been delivered to their location. The camera was shipped from a jobsite in Montoursville, Pennsylvania on September 11, 2012. The camera was scheduled for delivery on September 14, 2012 at the licensee's facility in Benton, Arkansas. "The licensee has begun investigating the location of the camera through use of the tracking number and in conversation with customer service. The licensee has verified that the camera is not at the Pennsylvania location as of September 17, 2012. "Camera Information: SPEC Model 150; Serial Number: 1301; Source: Iridium-192; Source Serial Number: TF0807 "The camera was shipped in an overpack cardboard container supplied by SPEC. "The licensee and [the Arkansas Department of Health] are continuing to monitor and search for the camera. Investigation remains on-going." Arkansas Incident Number: AR-2012-007 Additionally notified: DHS SWO, FEMA, DHS NICC, EPA, DOE, HHS, and USDA. * * * UPDATE ON 9/18/12 AT 1240 EDT FROM JARED THOMPSON TO PETE SNYDER VIA EMAIL * * * "The radiography camera and source have been located and has arrived at the licensee's facility on September 18, 2012 at 1040 [CDT]. The package was found in the [transportation] facility in Newark, New Jersey in the afternoon of September 17, 2012. It appears that the shipping documentation had been changed and the package was misplaced. "The camera was surveyed and there appears to be no damage to the source or camera. "The licensee will be preparing a report for the [Arkansas Department of Health]. "The [Arkansas Department of Health] considers this event closed." Notified R4DO (Miller), R1DO (Cahill), FSME-Day EO (McIntosh), ILTAB (Wray), DHS SWO, FEMA, USDA, HHS, DOE, DHS, and EPA. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-09-25
48314 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-09-17 09:30 | 2012-09-17 16:29 | 2012-09-17 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED EMPLOYEE "An employee reported to the dispensary this morning with a thermal burn from a steam line to the neck area [at approximately] 0930 CDT. The plant nurse administered preliminary treatment and decided to transport the employee to a local medical facility. A whole body survey of the employee in his plant clothing was performed; the maximum amount of contamination was present on his left boot, 36,866 dpm/100cm2. Prior to leaving the Restricted Area, the employee removed all plant clothing, changed into his personal clothing, and was re-surveyed. The employee was free of contamination upon release." The contamination was from uranium ore concentrates. The licensee informed R2 (Richard Gibson) via voicemail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-09-17
48313 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-09-17 08:58 | 2012-09-17 15:23 | 2012-09-17 | LOSS OF EMERGENCY SIRENS "At 0858 hrs. [CDT], Corporate Communications notified the control room that there was a communication issue with the emergency siren router. Based on the report, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) were declared nonfunctional and notifications were completed. Local law enforcement has been notified in the required surrounding counties and compensatory measures are in place to ensure notification of the public in case of an actual emergency. "Troubleshooting of the siren's communication system revealed that a peripheral router power supply had failed. The power supply was replaced at 0935 and router restarted. At 0955 sirens were restored to the counties of Harrison and Pottawattamie in Iowa. Communications were restored to all but one siren, in Washington County Nebraska by 1031, with that one siren (Siren 35) restored at 1103. All repairs completed and retested satisfactorily with proper communications confirmed with each siren. The power supply failure resulted in 2.1 hours with the sirens being unavailable. Notifications have been completed with compensatory actions by local law enforcement secured. "This is being reported per 10CFR50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability.'" The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-17
48312 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-09-16 10:55 | 2012-09-16 12:57 | 2012-09-16 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 1055 EDT on September 16, 2012 with the James A. FitzPatrick Nuclear Power Plant (JAF) at 0% power while performing a planned reactor shutdown for a refueling outage, multiple control rods were conservatively declared inoperable due to the potential for control rod channel interference in the event of a seismic event. In response to [the] GE Hitachi Nuclear Energy (GEH) recommendations regarding the 10CFR Part 21 issue for control rod blade interference, JAF has implemented compensatory measures that require control rods with a Cell Friction Metric (CFM) greater than or equal to 100 be declared inoperable upon RPV pressure decreasing below 800 psig if a full stroke insertion test has not performed within the past 14 Effective Full Power Days (EFPD). During a planned shutdown, reactor pressure decreased below 800 psig before all control rods could be fully inserted using normal control rod insertion methods. With nine or more control rods inoperable in Mode 1 or 2, JAF Technical Specifications (LCO 3.1.3 Condition E) require the unit be placed in Mode 3 within 12 hours. This condition was entered at 1055 EDT and the unit was placed in Mode 3 at 1226 EDT. This event is reportable under 10CFR50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-09-16
48311 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-09-14 19:00 | 2012-09-15 03:10 | 2012-09-15 | DEGRADED CONDITION DUE TO INDICATIONS ON REACTOR VESSEL HEAD DURING DYE PENETRANT TEST "On September 14, 2012, during the Byron Station Unit 1 refueling outage, it was determined that the results of planned Liquid Penetrant (PT) examinations performed on two previous overlay repairs of the reactor vessel head do not meet applicable acceptance criteria. Both penetrations require repairs prior to returning the vessel head to service. These indications are not in the reactor coolant pressure boundary; however they are very near the previously repaired J-groove weld. The examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to ensure the structural integrity of the reactor vessel head pressure boundary. No ultrasonic indications have been identified at this time. Repairs are currently being planned, which will include buff of the rejectable area and retest, and will be completed prior to returning the vessel head to service. If retest of the rejectable areas is unacceptable, then additional repairs will be required prior to returning the vessel head to service. "This condition is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as found indications did not meet applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. Any further examination failures and repairs will be updated under this ENS Notification. "The NRC Resident Inspector has been notified." The original indications that led to the two overlay repairs were discovered during ultrasonic testing and were reported to the NRC and assigned EN #46686. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-09-15
48310 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2012-09-14 20:25 | 2012-09-14 22:05 | 2012-09-14 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "[At] 2025 [EDT] reactor tripped on 'C' Steam Generator Low Low Level due to feed water regulating valve failing closed due to a 7300 process cabinet card failure. Control Room entered E-0, Reactor Trip or Safety Injection, then transitioned to ES-0.1, Reactor Trip Response. "Emergency Feedwater actuated due to the Low Low Steam Generator Level. All other plant equipment functioned as expected. Plant is being stabilized in mode 3. "Emergency News Manager will update the states and local media. "NRC Resident Inspector was notified at 2045 [EDT]." The trip was uncomplicated and all rods fully inserted. Decay heat is being removed to the condenser via the turbine bypass valves. Electrical buses are powered by offsite power. | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-09-14
48309 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-09-14 16:03 | 2012-09-14 19:27 | 2012-09-14 | AUTOMATIC REACTOR SCRAM DUE TO THE LOSS OF THE 120 KV SWITCHYARD "At 1603 EDT, Fermi 2 automatically scrammed due to onsite loss of 120 kV switchyard. All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 98 inches. Division I diesels, EDG-11 and EDG-12, automatically started and loaded. HPCI and RCIC automatically started and restored RWL. RWL is currently being maintained in the normal level band with Condensate/Feed and Control Rod Drive (CRD) systems. No Safety Relief Valves (SRV) actuated. All isolations and actuations for RWL 3 and 2 occurred as expected. Investigation into loss of 120 kV switchyard continues. "At the time of the scram, all Emergency Core Cooling (ECCS) and Emergency Diesel Generators (EDG) were operable with the exception of EDG-11 which was available vice operable due to ventilation work, and no other safety related equipment was out of service. This report is being made in accordance with 10CFR50.72(b)(2)(iv)(A), any event that results in ECCS discharge into the reactor coolant system as a result of a valid signal and 10CFR50.72(b)(2)(iv)(B), any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." EDG-11 and EDG-12 are performing all of their functions and providing power to the Division I AC buses. Temperatures are being monitored in the room containing EDG-11 and the room is not approaching any temperature limits. The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2012-09-14
48308 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-09-10 | 2012-09-14 16:57 | 2012-09-28 | AGREEMENT STATE REPORT - A PATIENT RECEIVING AN INCORRECT DOSAGE OF I-131 The following report was received from the State of Mississippi via email: "On 9-10-2012, the licensee administered 163 mCi of I-131 from an admission order dated 9-6-2012, instead of the prescribed 100 mCi of I-131 from the written directive dated 9-5-2012. The licensee's investigation revealed a misinterpretation of an admission order as a written directive by the nuclear medicine technologist due to inclusion of the authorized user's name and 150 mCi of a radionuclide activity on the admission order. The written directive was never received by the Nuclear Medicine Department. The licensee determined the root cause of the error stemmed from a new communication process by which written directives are conveyed from the authorized user to Central Scheduling and then to the Nuclear Medicine Department. "The administered dose is described as not out of line with doses typically prescribed for patients with similar disease and the authorized user indicates an expectation of no adverse effect for the patient. The referring physician and patient were both notified on 9-10-2012 by the authorized user. "The licensee is correcting its procedure for written directives and how they are communicated to the Hospital's Nuclear Medicine Department and will submit them for review to DRH." Mississippi Event Report No.: MS-267-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM MOAK TO SNYDER ON 9/28/12 AT 1656 EDT * * * "[The] licensee's inspection revealed the medical event was an isolated incident. The new procedures for communicating written directives were only in place for two (2) months with one (1) I-131 administration during this time. The licensee has since changed back to their old procedures where written directives are communicated directly from the authorized user to the nuclear medicine department." Notified R4DO (O'Keefe) and FSME Event Resource (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-09-24
48307 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-09-13 09:00 | 2012-09-14 13:22 | 2013-02-01 | AGREEMENT STATE REPORT - STOLEN HUMBOLDT NUCLEAR GAUGE The following report was received from the State of Arizona via email: "At approximately 9:00 AM September 13, 2012, the [Arizona Radiation Regulatory] Agency was informed that the Licensee had a Humboldt Model 5001, SN 3920, portable gauge stolen from the back of a truck. The theft occurred between 9:00 PM September 12, 2012, and 6:00 AM September 13, 2012. The gauge was locked in a 16 gauge steel box bolted to the bed of the truck which was parked unattended at an employee's resident. The gauge contains 370 MBq (10 mCi) of Cesium-137 and 1.62 GBq (44 mCi) of Am:Be-241. "El Mirage PD is investigating and has issued report number 12-09000902. "The Agency continues to investigate this event. "The Governor's Office, the States of CA, NV, CO, UT and NM and Mexico, US NRC, and FBI are being notified of this event." Arizona Event Number: 12-020 * * * UPDATE FROM AUBREY GODWIN TO JOHN SHOEMAKER AT 1652 EST ON 1/31/13 * * * NOTE: The following information was originally provided as a new report by the Arizona Radiation Regulatory Agency. After additional information was obtained on 2/1/13 all information was combined into the original report concerning this event. The following information was received from the Arizona Radiation Regulatory Agency via email: "The Agency [Arizona Radiation Regulatory Agency], in checking a scrap metal shipment being returned to Glendale, Arizona from California, found a source rod from a moisture density gauge. No other parts of a moisture density gauge were identifiable in the shipment. Based upon experience, it is estimated that the source contained approximately 8 millicuries of Cesium-137. It was confirmed in the field that Cesium-137 was the only isotope present. The Agency was unable to locate any identifying markings with which to trace the source. The Agency has taken possession of the source and has stored the device in a secure location. "The Agency continues to investigate this event. "This notice is being provided to the State of California, US NRC, and FBI." Arizona Event Report: First Notice 13-005. Notified R4DO (Walker). Notified FSME Events Resource via E-mail. * * * UPDATE FROM AUBREY GODWIN TO DONALD NORWOOD AT 1341 EST ON 2/1/2013 * * * The following was received from the Arizona Radiation Regulatory Agency via email: "The Agency, in checking a scrap metal shipment being returned to Glendale, AZ from Taiwan through California, found a source rod from a moisture density gauge. No other parts of a moisture density gauge were identifiable in the shipment. The manufacturer, Humboldt, estimated the source as approximately 10 millicuries of Cesium-137. We did confirm in the field that Cesium-137 was the only isotope present. Based on the identifying numbers found on the source rod this is part of Humboldt Model 5001, SN3920, reported stolen September 13, 2012. See First Notice 12-020 sent out September 14, 2012. The Americium-241 source has not been located. "The Agency has taken possession of the Cesium-137 source and will store it in a secure location. Arrangements for proper disposal are being made. "The Agency continues to investigate this event. "This notice is being provided to the State of California, US NRC, and FBI." Arizona Event Report: Supplemental Notice 13-005. Notified R4DO (Walker) and ILTAB (Johnson). Notified FSME Events Resource and Mexico via E-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2012-09-24
48306 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2012-09-14 | 2012-09-14 11:20 | 2012-09-14 | FITNESS FOR DUTY - CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-09-14
48305 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-09-13 14:28 | 2012-09-13 19:36 | 2012-09-14 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO TSC VENTILATION EQUIPMENT ISSUE "The Technical Support Center (TSC) at the Point Beach Nuclear Plant (PBNP) is non-functional as a result of conservatively securing an exhaust fan that exhibited an abnormal noise in the TSC Ventilation system. The fan is currently in service and being monitored as part of the troubleshooting, with maintenance repair plans being conducted in parallel. "Functional alternate locations described in the emergency plan procedures for events resulting in radiological conditions affecting habitability will be used and are currently available. The Control Room or EOF will be selected as the alternate facility. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using the procedure and functional facilities selected. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MARY SIPIORSKI TO CHARLES TEAL ON 9/14/12 AT 1942 EDT * * * "At 1737 on 9/14/12, maintenance activities are complete on the TSC ventilation system. The TSC ventilation has been restored to normal operation and the TSC [has been] returned to fully functional." The licensee has notified the NRC Resident Inspector. Notified R3DO (Kunowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-13
48304 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-13 07:40 | 2012-09-13 13:08 | 2012-09-13 | TECHNICAL SUPPORT CENTER (TSC) UNAVAILABLE DUE TO VENTILATION SYSTEM FAILURE "On 09/13/12 at 0740 [EDT] the TSC ventilation was determined to be non-functional. Investigation is underway to determine the cause of the ventilation failure and make the necessary repairs. While the TSC is unavailable, the Catawba Emergency Plan has provisions to relocate TSC personnel if required to the alternate TSC location." The licensee has notified the NRC Resident Inspector. The licensee will inform State and local agencies as a courtesy. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-13
48303 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-09-11 | 2012-09-13 12:05 | 2012-09-13 | AGREEMENT STATE REPORT - PATIENT UNDEREXPOSURE USING YTTRIUM-90 SIR-SPHERES TREATMENT The following event was received from the Commonwealth of Pennsylvania via facsimile: "Event type: A medical event (ME) involving the administration of yttrium-90 SIR-Spheres which is reportable under 10 CFR 35.3045(a)(1)(i). "Notifications: On September 12, 2012, an inspector was performing a reactive inspection for a recent event (PA120026) that occurred on August 23, 2012. During the inspection the licensee reported another similar Sir-Sphere event. "Event Description: A patient was being treated for disease of the liver with 33.04 millicuries (mCi) of Y-90 and received 25.6 mCi resulting in 77.5% of the intended dose. The treating physician, who also is the referring physician, notified the patient. "Cause of the Event: Currently under investigation and unknown at this time. "Actions: No harm to the patient is expected. The Department's reactive inspection occurring on September 11, 2012 incorporated this new event and therefore no new inspection is planned." PA Report Number: 120030 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-09-21
48302 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-09-11 | 2012-09-12 16:26 | 2012-09-12 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE FOUND WITH STUCK SHUTTER The following information was received from the State of Illinois via email: "On Tuesday afternoon, the Agency [Illinois Emergency Management Agency] received a call from the RSO for Flint Hills Resources Chemical Intermediates, LLC (IL-01337-01). He called to report a shutter failure of a fixed gauge which he cannot close. The device manufacturer, Ronan Engineering, has been contacted and arrangements are pending for repair of the device. The RSO has isolated the area, posted warning signs and instituted a lock out/tag out procedure for the manway entrance to the vessel in order to prevent exposures which might occur from someone attempting to perform work within the tank that the gauge is located. Area surveys performed show no variations above normal (i.e., less than 1 milliR/h at 1 foot) for when the shutter is open and the unit is in operation. The shutter had last been tested in March with no abnormalities noted. The gauge has not been subjected to any corrosives or solvents or other conditions which exceed the gauge's prototype test conditions. "The RSO was reminded of the requirement to provide a written report within 30 days of the event and to contact the Agency when the manufacturer was able to perform the site visit to evaluate/repair the device. The Agency considers this matter open pending those additional actions." The Ronan gauge is model X90-SA1, S/N M7389, contains 24.5 mCi Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-09-20
48301 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-09-12 08:06 | 2012-09-12 09:33 | 2012-09-13 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance activity at Cooper Nuclear Station will remove the TSC [Technical Support Center] ventilation system from service. The TSC ventilation system will be rendered non-functional during this maintenance period. The repair to the TSC ventilation is expected to last less than 2 days. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless uninhabitable due to ambient temperature, radiological, or other conditions. CNS Station procedures provide appropriate monitoring and compensatory measures to ensure habitability of the TSC and, if necessary, instructions for relocation of TSC personnel should the need arise. In the event of TSC activation, maintenance will be expedited to restore ventilation to service. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM CURTIS MARTIN TO PETE SNYDER AT 1026 EDT ON 9/13/12 * * * At 0910 CDT on 9/13/12 the TSC ventilation system has been returned to service. The licensee notified the NRC Resident Inspector. Notified R4DO (Lantz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-12
48300 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-11 21:00 | 2012-09-12 08:37 | 2012-10-05 | AGREEMENT STATE REPORT - LOST AM-241/BE WELL LOGGING SOURCE The following information was obtained from the Texas Department of State Health Services Radiation Branch via e-mail: "On September 11, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee that an Americium-241/ Beryllium [well logging] source could not be located. The source had been used earlier that day at a well site near Pecos, Texas. The well logging crew left the Pecos site and went about 130 miles to a well site south of Odessa, Texas. When the crew went to remove the Am-241 source they discovered the source transport container lock and plug were not in place and that the source was missing. The crew returned to the well site near Pecos and searched for the source, but did not find it. The Radiation Safety Officer (RSO) stated that the lock was found in the storage compartment in the back of the truck. The transport container plug was not in the container. The RSO stated they were putting together a group to look for the source along the roadway between the two locations. "The RSO stated that the crew stated that they did not stop anywhere along the route between the two locations. The RSO stated they were verifying that using the vehicles black box. The RSO agreed to contact the appropriate local law enforcement. The RSO stated he would send a copy of the latest dose rate readings for the source to the Agency. "The Agency has notified their local inspectors of the event. Additional information will be provided as it is received in accordance with SA-300 [Reporting Material Events]." The source was described as approximately 7 inches long by 1 inch in diameter stainless steel cylinder. The State has not requested any assistance in locating the source at this time. Texas Report I-8988 * * * UPDATE AT 1744 EDT ON 09/12/12 FROM ART TUCKER TO S. SANDIN * * * The following update was received from the State of Texas via fax: "[At] 1430 hours [CDT] the Agency [Texas Department of State Health Services] was contacted by the licensee and provided the following information. "The licensee has completed a press release which provides a description of the source, actions to take if found, and stated that they would offer a reward. The press release will be issued by their Public Information Group. The licensee has completed logging of the well near Pecos and the source was not located. "The licensee stated that the well site had been searched and surveyed twice. The licensee stated that the road between Pecos and Odessa had been surveyed using well logging tools extended from pickup trucks and driven between 5 and 10 miles per hour and the source was not found. The licensee stated they have had people on the ground searching, but did not know how much area away from the well site in Pecos had been searched. "The licensee has sent a Radiation Safety Officer and a second supervisor to the Pecos well site. The RSO is bringing scintillation survey instruments to the well site for additional surveys. An Agency inspector will meet the RSO at the well site. "The licensee has reviewed the well logging data and confirmed that the source was installed on the tool during logging operations. The licensee has performed preliminary interviews with the operator involved. The licensee indicated that additional interviews are required. They have not been able to determine how the source could have been lost during transport. The licensee stated that they completed a review of the truck's black box and confirmed that the truck did not stop while traveling between the two well sites. "The license stated that the local sheriff has responded to the Pecos location and was interviewing the tool operators. The licensee stated they believe that the group supervisor involved had been evaluated under the IC's [Increased Controls] as trust worthy and reliable. "The licensee stated that other entities at the well site as well as the lease holder have been notified of the event. The licensee stated that they will continue to search for the source until it can be located. The Agency has offered their assistance to the licensee. Additional information will be provided as it is received in accordance with SA - 300 [Reporting Material Events]." Notified R4DO (Lantz) and FSME (McDermott), IRD (Marshall), ILTAB (Whitney) and Mexico via email/fax. * * * UPDATE ON 9/13/12 AT 1015 EDT FROM ART TUCKER TO HUFFMAN * * * The following update was received from the State of Texas via e-mail: "A third search of the well site was completed on September 12, 2012 at 2030 hours. The source was not found. The licensee will resume the search early today. The licensee stated that surveys will be conducted on the road between Odessa and Pecos today. The licensee stated that a mud pit at the Pecos site will be logged today. The logging truck is at their shop in Odessa now and they are literally stripping it down, removing every piece of equipment looking for the source. The licensee stated that the three individuals who were conducting the well logging operations when the source was lost were interviewed by individuals from the Federal Bureau of Investigation working with the Department of Transportation. The licensee stated that the FBI would only say that they believed there was no criminal activity involved with the missing source. Additional information will be provided as it is received in accordance with SA - 300." Notified R4DO (Lantz) and FSME (McDermott), IRD (Marshall), ILTAB (Whitney) and Mexico via email. * * * UPDATE ON 10/05/12 AT 0915 EDT FROM ART TUCKER TO DONG PARK * * * The following update was received from the State of Texas via e-mail: "On October 5, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee that the missing Americium - 241/Beryllium source had been recovered. No additional information was available at the time of the report. Additional information will be provided as it is received in accordance with SA-300. Notified R4DO (Powers). ILTAB (Hahn), FSME Events Resource and Mexico informed via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-09-12
48299 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-09-11 12:05 | 2012-09-11 14:28 | 2012-09-11 | AGREEMENT STATE REPORT - LEAK TEST RESULTS FOR NI-63 SOURCE > .005 MICROCURIES The following information was received from the Commonwealth of Massachusetts via fax: "[The licensee] called the Agency [Massachusetts Radiation Control] to report that [the licensee] received leak test results that were above 0.005 microCurie for their 'Shimadzu' [Manufacturer] Ni-63 gas chromatograph instruments, each containing approximately 10 milliCurie foil sources. [The licensee] reported that the leak test results were 0.0053 and 0.0069 microCurie. [The licensee] stated that wipe surveys for Ni-63 were taken of the lab areas where these instruments were used. [The licensee] did not yet have the LSC [liquid scintillation counter] results of the wipe surveys. [The licensee] also disassembled the electron capture detectors (ECD) from the GC [Gas Chromatograph] instruments and placed them inside a scaled poly bag to store the ECD's until [the licensee] can return the ECD's to 'Shimadzu'." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-09-19
48298 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2012-08-28 | 2012-09-11 13:07 | 2014-05-30 | AGREEMENT STATE REPORT - PATIENT RECEIVED TWO UNDERDOSES OF Y-90 TO DIFFERENT TREATMENT SITES The following information was received from the State of Rhode Island via fax: "Event Type: Medical event involving the administration of Yttrium-90 microspheres. "Notification(s): On August 30, 2012, the RI Department of Health Office of Facilities Regulation, Radiation Control Program received a phone call from the facility's Radiation Safety Officer, with a follow-up e-mail the same day. "Event Description: On 08/28/2012, two incorrect doses were prepared for a Y-90 microsphere treatment. Both doses were for the same patient (i.e., two different treatment sites). One dose was drawn at 28.7% less than prescribed and the other dose was drawn at 22.9% less than prescribed. The final administered doses were less than 40.3% and 27.2% prescribed, respectively. "Cause of the event: Under investigation and unknown at this time. "Actions: Adverse effects to the patient are not expected; a follow-up reactive inspection is planned. "[Rhode Island] Event Report ID: 2012-001" * * * UPDATE FROM CHARMA WARING TO PETE SNYDER AT 1503 EDT ON 10/24/12 * * * The State of Rhode Island provided the following information via fax: "Cause of the event: For both doses, after withdrawing the microspheres from the shipping container, the licensee nuclear medicine technologist added sterile water to the syringe prior to transferring them into the v-vial. The policy is that the Y-90 is transferred into the v-vial prior to adding sterile water. The technologist then added additional sterile water to the v-vials in accordance with procedure. "For both doses, after placing the v-vial into the dose calibrator, the technologist noticed that the dose was less than the 10% prescribed by the physician. The technologist was confused about the correction factor of 0.82 required for the v-vial when placed into the dose calibrator. The technologist did not understand why the original dose drawn from the shipping vial was within +/- 10%, but the v-vial dose was not. The technologist ultimately concluded that the shipping v-vial should have also been corrected by 0.82 and sent the dose to Interventional Radiology (IR) where it was administered. "Although the dose withdrawn from the shipping container was originally within +/- 10%, some of the microspheres were most likely lost during transfer to the v-vial. The most likely cause was due to adding sterile water, prior to transfer. The doses drawn by the Nuclear Medicine Technologist were 9.84 mCi for the right lobe (Vial 1) and 10.41 mCi for segment VII, neither of which are within the +/- 10% established by policy. "After administration of both doses, the v-vials were sent back to Nuclear Medicine per procedure and assayed in the dose calibrator for residual activity. The dose to the right lobe (Vial 1) and the dose to segment VII (Vial 2) had 1.6 mCi and 0.57 mCi remaining, respectively. Therefore, not all of the microspheres were administered. As a result, the final administered dose to the right lobe was 8.24 mCi and the dose to Segment VII was 9.84 mCi. This resulted in an under administered dose of 40.3% to the right lobe and an under administered dose of 27.2% to segment VII. "Licensee Actions: As a result of this event, the RSO performed an in-service training [that] was held on 9/21/12. The licensee also does an additional 'timeout' when the dose is brought to the IR suite to verify prescribed versus drawn dose. The Nuclear Medicine staff alternate drawing the Y-90 doses to maintain familiarity with the procedure. "RI RCP [Rhode Island Radiation Control Program] Actions: The corrective actions outlined by the licensee have been complete therefore, no further action is required at this time." Notified R1DO (Caruso) and FSME Events Resource (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1144 EDT ON 5/30/14 FROM CHARMA WARING TO MARK ABRAMOVITZ * * * The following information was received via fax: "Per the physician, this misadministration, which was lower than the planned dose based on body surface area, will not result in any harm to the patient. Repeat administration was already anticipated, if there was evidence for a response. The Bremsstrahlung scan shows increased activity in the tumor bed as well, consistent with an adequate delivery to the target. As a result of this event, the RSO will perform an in-service training on the Y-90 SirSphere Worksheet which will include practice runs so staff are comfortable with the math involved (specifically the correction factor of 0.82). The RSO has requested and the Director of Diagnostic Imaging has agreed that the Nuclear Medicine technologists shall rotate frequently on performing Y-90 microsphere dose preparations. Additionally, once the dose is brought to IR there will be an additional timeout to verify that the prepared dose by Nuclear Medicine matches that of the WD [written directive]. "[The physician] notified that patient via telephone on August 30, 2012." Notified the R1DO (Rogge) and FSME Event Resources (via e-mail).. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2012-09-19
48297 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2012-09-11 07:33 | 2012-09-11 11:11 | 2012-09-11 | VOLUNTARY OFFSITE NOTIFICATION WITH POTENTIAL MEDIA INTEREST "This ENS [report] is being voluntarily issued to notify the NRC that voluntary communications were made to offsite agencies this morning between 0700 and 0830 [EDT] due to an event of potential public interest. "At approximately 1 a.m. on September 11, 2012, Peach Bottom outage workers on the Unit 2 refuel floor were disassembling the reactor head vent when steam discharged from the flange, causing a small but detectable amount of airborne contamination that was contained in the building. All workers were wearing the proper protective equipment and no significant personal [personnel] exposure has been reported. As a precaution, employees were asked to temporarily leave the area for onsite evaluation while radiation protection technicians investigated. Approximately 50 workers were impacted by the radiological airborne event at Peach Bottom and had to stay over shift for radiological monitoring. In accordance with station Radiological procedures, affected personnel are being monitored and as required bioassay is being conducted. Radiation monitors in the reactor building initially detected the airborne contamination, but all have returned to normal levels. This event resulted in no significant impact to the health and safety of our workers or the public. The station made voluntary notifications to the NRC Senior Resident, the State Bureau of Radiation Protection and state and local stakeholders. "This issue has been entered into the site Corrective Action Program for evaluation and implementation of further corrective actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-11
48296 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-09-11 03:08 | 2012-09-11 04:08 | 2012-09-12 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO PLANNED MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will remove the TSC [Technical Support Center] ventilation system from service. The TSC would be rendered non-functional with the loss of ventilation. The repair to the TSC ventilation is expected to last 3 days. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be expedited to restore ventilation to the TSC. "This notification is being made in accordance with 10CR50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation." The licensee notified the NRC Resident Inspector * * * UPDATE FROM MIKE STROPE TO CHARLES TEAL ON 9/12/12 AT 1157 EDT * * * The TSC maintenance has been completed. The TSC has been restored to service. The NRC Resident Inspector has been informed. Notified R3DO (Kunowski). | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-11
48295 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-09-10 14:43 | 2012-09-10 22:07 | 2012-09-10 | LOSS OF SECONDARY CONTAINMENT "At 1443 CDT, indication was received in the Control Room that both the inner and outer personnel access doors to the Reactor Building were open simultaneously. This caused entry into Technical Specification 3.6.4.1 for Secondary Containment inoperable and is a loss of safety function per station procedure 2.0.11.1. An event or condition that could have prevented fulfillment of a safety function requires an 8 hour report per 10CFR50.72.b.3.v.D for Accident Mitigation. The doors were open for several minutes until station personnel could reset the interlock to allow for door closure. The doors were reclosed and Secondary Containment was restored to operable at 1451 CDT. "The NRC Resident Inspector has been informed of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-09-10
48294 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-10 21:00 | 2012-09-10 21:30 | 2012-09-10 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PLANNED MAINTENANCE "On 9-11-12 the Technical Support System (TSC) ventilation will be removed from service for a planned maintenance activity. The ventilation system will be out of service for approximately 9 hours. During this time the TSC will be unavailable should an event involving a radiological release occur. The Catawba Emergency Plan has provisions to relocate TSC personnel if required to the alternate TSC location." The licensee will inform State and local agencies as a courtesy and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-10
48293 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-09-10 10:25 | 2012-09-10 17:15 | 2012-10-08 | BOTH UNITS ENTERED TECHNICAL SPECIFICATION 3.0.3 DUE TO INOPERABLE CONTROL STRUCTURE CHILLERS "Unit 1 and Unit 2 entered LCO 3.0.3 due to both Control Structure (CS) chillers 'A & B' concurrently inoperable. "At 1025 [EDT], the control room was notified that the 'B' CS Chiller was not running. There were no control room alarms due to this condition. Review of indications on control room panel 0C681 noted that the loop circ pump and all three CS fans remained in service. Indication of CS loop flow and loop temperature remained normal, approximately 600 gpm and 44 degrees. "The 'B' CS Chiller restarted at 1027 [EDT] and normal system parameters were observed. "Work on the 'A' CS Chiller was released at 0928 [EDT] on 9/10/2012 for scheduled maintenance, LCO's 3.7.3 and 3.7.4 were entered, however no work had actually commenced or was performed. The 'A' CS Chiller remained available and in standby during the entire evolution. "Since the cause of the 'B' CS Chiller to shutdown has not been determined, the 'B' CS Chiller was declared inoperable. Inoperability of both CS chillers 'A & B' required immediate entry into LCO 3.0.3 per TS 3.7.4 Condition D. Both chillers were inoperable from 1025 [EDT] until 1042 [EDT] (17 minutes), when the 'A' CS Chiller was restored to operable status. "This condition is being reported as an event or condition that could have prevented fulfillment of a safety function per 10CFR 50.72(b)(3)(v)(D)." The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM LICHTNER TO CROUCH AT 2008 EDT ON 10/08/12 * * * "This event was reported as a condition that could have prevented fulfillment of a safety function per 10 CFR 50.72(b)(3)(v)(D) because the 'A' Control Structure (CS) chiller was released for scheduled maintenance (LCO's 3.7.3 and 3.7.4 were entered), although no physical work had begun on the 'A' CS chiller. Concurrent with the 'A' chiller being in the aforementioned status, the 'B' CS chiller shutdown for approximately 2.5 minutes before automatically restarting. "Following the ENS report, Susquehanna determined that although it had shutdown, the 'B' CS chiller remained operable and capable of fulfilling all its design functions. The chiller shutdown was not due to operation of a safety trip. Under safety trip conditions, automatic restart of the chiller would have been prevented and alarms would have been received in the control room. Rather, the event was due to chiller load recycle operation during which the chiller is designed to shutdown at approximately 5 degrees F below the normal operating chilled water temperature and automatically restart. Troubleshooting did not detect any faulty components and the chiller has remained in operation for greater than 48 hours since the shutdown, without a repeat event. "Additionally, although the 'A' CS chiller was declared inoperable due to entry into LCO's 3.7.3 and 3.7.4 to perform routine maintenance, no physical action had been taken to disable the 'A' chiller. Therefore, the 'A' CS chiller was capable of auto-starting and performing its safety function for all design conditions while in the LCO's. "Based on the above information, Susquehanna has determined that since both the 'A' and the 'B' CS chillers were available and capable of performing their design safety functions, there was no loss of safety function therefore this ENS report is retracted." The licensee has notified the NRC Resident Inspector. Notified R1DO (Trapp). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-09-10
48292 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-07-15 16:00 | 2012-09-10 15:47 | 2012-09-10 | AGREEMENT STATE REPORT - LOST TRITIUM SIGN The following information was received on 9/7/2012 via email: "The Corporate RSO for Bed, Bath and Beyond (B3) called to advise that an exit sign containing H-3 appears to be missing from their Illinois store. The sign had been taken down by an electrician in July in anticipation of recovery and disposal by Shaw Environmental. A representative from Shaw had arrived this past week to collect and package the sign only to find that the sign was missing from the storage location where it had been placed at the time of removal. The electrical company hired by the licensee to perform the un-installation had noted that there were no signs of damage or loss of contents at the time of removal on July 13, 2012. The manager of the licensee's store can only definitely recall having seen the sign on July 14 or 15th in secure storage. Subsequent visual surveys of the store were conducted in an attempt to locate the sign with no success. "The sign involved is made by Safety Light Corporation (m/n SLX-60). It was purchased in November of 2004. Based on the serial number involved (289354) it was determined that the sign was sold with a nominal H-3 content of 11.5 Ci. As of this date, that activity is approximately 7.4 Ci. Currently, it is believed that the device has been inadvertently disposed with the facilities normal trash stream." Illinois Number: IL-12014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-09-18
48291 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-09-07 11:00 | 2012-09-10 14:15 | 2012-09-10 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED NUCLEAR GAUGE The following information was received from the Commonwealth of Kentucky via fax: "KY RHB [Kentucky Radiological Health Branch] was notified on Monday, 9/10/12 by a representative from Domtar Paper Company, a routine shutter check was performed 9/7/12 on a fixed nuclear gauge and the shutter did not function as designed. Operation of the shutter required use of a tool. The gauge involved is Ohmart model SR-A, S/N 9296GG, containing 10 mCi Cs-137. It appears corrosive atmosphere caused damage to the source holder. The licensee requested proposal from Vega Americas, Inc. to repair or replace the source holder." KY Event Report ID No.: 48291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-09-18
48290 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-09-10 09:00 | 2012-09-10 11:34 | 2012-10-03 | PLANT PROCESS COMPUTER REMOVED FROM SERVICE FOR MAINTENANCE "At 0900 CDT on September 10, 2012, the Unit 1 Plant Process Computer (PPC) was removed from service for a planned replacement in the current Unit 1 Refueling Outage. The Unit 1 PPC feeds the Safety Parameter Display System (SPDS) used in the Main Control Room (MCR) and the Technical Support Center (TSC). The Unit 1 PPC also feeds the Emergency Response Data System (ERDS). "The Unit 1 and Unit 2 PPCs also feed the Plant Parameters Display System (PPDS) used in the MCR, TSC and Emergency Operations Facility (EOF). Meteorological data will remain available. The dose assessment program will remain functional as the Unit 2 PPC will be capable of providing the necessary data through PPDS to run the program. The dose assessment program is not affected by the Unit 1 PPC being out of service. As compensatory measures, a proceduralized backup method to fax or communicate via a phone circuit applicable data to the NRC, TSC, and EOF exists. There is no impact on the Emergency Notification System (ENS) or Health Physics Network (HPN) communication systems. "The new Unit 1 PPC is scheduled to be functional on September 17, 2012. However, based on the Mode Unit 1 will be in, this will limit the number of points that would provide usable data. The Unit 1 PPC will be tested as Mode changes occur. The Unit 1 PPC is planned to be declared functional by Mode 2. A follow-up ENS call will be made once the Unit 1 PPC is declared functional. "The loss of SPDS and ERDS is a 'major loss of assessment capability' and is reportable under 10CFR50.72(b)(3) (xiii). "The NRC Senior Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS call." * * * UPDATE FROM BRYAN GAPINSKI TO JOHN KNOKE AT 1510 EDT ON 10/03/12 * * * As of 1245 CDT on October 3,2012, the Unit 1 PPC is considered operational with respect to the Safety Parameter Display System (SPDS), Plant Parameter Display System (PPDS), and Emergency Response Data System (ERDS). Therefore, a major loss of assessment capability no longer exists on Unit 1. The Byron EP manager contacted the NRC ERDS Center on 10/02/2012 to conduct an ERDS test for Unit 1 to ensure the data was being satisfactorily sent to the NRC. Unit 1 and Unit 2 ERDS data to NRC was tested satisfactory lAW EP-AA-124-FÀ01. "The NRC Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS update. Notified the R3DO (Dave Passehl) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-10
48289 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-09-08 12:30 | 2012-09-08 13:12 | 2012-09-08 | HISTORICAL TECHNICAL SUPPORT CENTER VENTILATION EVALUATION DEFICIENCY "FPL (Florida Power & Light) previously reported (EN 47819) that a portion of the Turkey Point Technical Support Center (TSC) Heating Ventilation and Air Conditioning System (HVAC) was deenergized for maintenance during two extended periods. FPL concluded that due to the condition, the TSC may not have been fully functional under every postulated design basis accident scenario. As a result of further investigation, FPL has been unable to validate the historical TSC design basis assumptions for habitability for an indeterminate period in the past. Among the issues identified include (a) seized HVAC isolation damper, (b) unsecured HVAC balancing damper, and (c) voids in the concrete shield wall. Additionally, while the original design basis did not provide for any unfiltered air inleakage, the HVAC system was constructed and maintained to ensure only that a positive pressure could be achieved. "FPL has addressed the TSC issues. A new dose analysis and recent tracer gas test have established TSC compliance with the current licensing basis. Therefore, the TSC is fully functional at this time. "This report is made for historical conditions in accordance with 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 12 | 100 | 0 | 12 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-08
48288 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-09-08 08:00 | 2012-09-08 08:16 | 2012-09-08 | EMERGENCY OFFSITE FACILITY/TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed today to the Emergency Offsite Facility (EOF)/Technical Support Center (TSC) HVAC. The work entails replacement of a pressure switch. The filtration portion of the system will not be affected by this work. This work activity is planned to be performed and completed expeditiously within about 3.5 hours including establishing and removing the clearances and performing post maintenance testing; however, restoration time required during the maintenance could exceed the time required to activate the TSC. "If an emergency condition occurs that requires activation of the EOF and TSC, plans are to utilize the EOF and TSC during the time this work activity is being performed as long as habitability conditions allow. The Emergency Response Organization team members will be relocated to alternate locations if required by habitability conditions in accordance with emergency implementing procedures. Alternate emergency response facilities will remain available in the event that relocation is necessary." The licensee has notified the NRC Resident Inspector. Licensee has also notified state and local agencies. * * * UPDATE FROM GEORGE CURTIS TO DONALD NORWOOD AT 1025 EDT ON 9/8/2012 * * * The maintenance work was completed. The TSC and EOF were declared operable as of 1025 EDT. The licensee will notify the NRC Resident Inspector. Notified R2DO (Lesser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-08
48287 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2012-09-07 15:53 | 2012-09-07 19:18 | 2012-09-07 | FIRE IN PLASMA CUTTER RECIRCULATING VENTILATION SYSTEM "At 1553 PDT Areva Richland declared an Alert due to a fire [greater than 15 minutes] in the waste handling / packaging area within the UO2 Building. The fire was associated with a plasma cutter HEPA filter in the recirculation system. The plasma arc filter is a stand alone filter that recirculates the air into the room. The room ventilation system has two HEPA filters in series before it exhausts out of the stack. "Personnel in the building evacuated when a smoke alarm activated. All personnel from the evacuated building were accounted for. The fire was confined to the plasma cutter filters and is now believed to be extinguished." Notified DHS, DOE, DHS NICC, HHS, EPA, USDA and Canada. * * * UPDATE FROM CALVIN MANNING TO JOHN KNOKE AT 0036 EDT ON 09/08/12 * * * At 1609 PDT the fire was extinguished and a re-flash watch set. The ventilation system in the UO2 Building was restored. The area of the fire is quarantined off, pending further investigation. No injuries were reported and there were no offsite radiological releases. At 2135 PDT, Areva Richland exited the Alert. Notified R2DO (Lessor), IRD (Marshall), NMSS (Bjorkman), DHS, DOE, DHS NICC, HHS, EPA, USDA and Canada. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | WA | FUE |  | 70.32(i) |  |  |  | 0 | 2012-09-07
48286 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-09-06 | 2012-09-07 14:29 | 2012-09-07 | AGREEMENT STATE REPORT - YTTRIUM-90 MICROSPHERES ADMINISTERED TO THE WRONG TREATMENT SITE "On September 6, 2012, the [Pennsylvania Department of Environmental Protection, Bureau of Radiation Protection (PADEPBRP)] Central Office received notification via a phone call about this medical event. "The patient received an administration of approximately 1.4 millicuries (mCi) of Y-90 microspheres to the wrong treatment site. The intended treatment was to administer approximately 24 mCi to the left lobe of the liver through three different arteries. During the administration of one of the split doses, the Interventional Radiologist (IR) incorrectly positioned the catheter in the right hepatic artery. A portion of the one split dose was administered to the right lobe of the liver before the IR realized that the catheter was not in the correct artery. "Cause of the event: Human Error. "Actions: Both the referring physician and the patient have been notified of the medical event. The [PADEPBRP] plans to do a reactive inspection." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-09-17
48285 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2012-03-14 | 2012-09-07 12:45 | 2012-09-07 | PART 21 - IMPROPER SELECTION OF INVERTER CAPACITORS "PRODUCT: 10 KVA inverter Model 86VC0100-15, 3 phase 480 VAC output. Limited to systems supplied to Exelon Byron and Braidwood units. Capacitors C10 through C15 part number 03-040060-00. "COMPONENT DESCRIPTION: Suppression capacitors, Ametek part number 03-040060-00, used in positions C10 through C15 on Model 86-VC0100-15 only. "PROBLEM YOU COULD SEE: Capacitor could arc internally and open internally and externally. "CAUSE: the manufacturer's investigation revealed that due to improper selection of capacitor used may fail due to a corona effect internally. "EFFECT ON SYSTEM PERFORMANCE: The capacitor may short internally and open circuit by forcing lead separation from the device. "ACTION REQUIRED: Replace the capacitor(s) with Ametek part 03-040041-20. The replacement is rated at 370 VAC and used in a 277 VAC circuit. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: The defect is limited to the units supplied to Exelon Byron and Braidwood plants under Ametek joc C103552." Both the Byron and Braidwood plants are already informed of this condition. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-09-07
48284 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-09-05 20:06 | 2012-09-06 23:28 | 2012-09-06 | INOPERABLE ACCIDENT RADIATION MONITORS "This is a non-emergency report. No actual event has occurred. "At 2006 EDT, on 9/5/2012, Oconee Nuclear Station Operations declared the radiation monitors out of service for Low Gas Unit Vent monitoring (3RIA-45) and High Gas Unit monitoring (3RIA-46) when the Unit 3 Vent Skid lost its internal memory during a monthly PM to replace the filter cartridge. These monitors are used for determination of Emergency Action Levels (EALs) in ALL modes. "Oconee Nuclear Station did not initially recognize that criteria for reporting in accordance with 10 CFR 50.72 (b)(3)(xiii) (Major Loss of Emergency Preparedness Capabilities) was met and acknowledge this notification is outside of the eight (8) hour notification window. "There is no adverse impact on nuclear safety. Redundant methods for sampling and determination of activity levels were implemented per SLC 16.11.3. "This report is submitted based upon a loss of emergency assessment capability in accordance with 50.72(b)(3)(xiii). "Redundant methodology was employed [when the inoperable status was recognized]. "Repair and restoration of the effected radiation monitors was completed at 2145 on 9/6/2012. "The NRC Resident Inspector has been informed." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-06
48283 | -1 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-09-06 14:16 | 2012-09-06 19:20 | 2012-10-01 | BOTH OFFSITE POWER SOURCES INOPERABLE "At 1416 EDT, after consultation with the Unit 1 control room, the #1 138 KV bus in the Beaver Valley switchyard was deenergized by the grid system operator in response to a degraded switchyard breaker. The bus loss caused the Unit 1 A train offsite power supply to be inoperable. The Unit 1 B train offsite power supply was previously inoperable due to planned maintenance on its transformer cooling fan control circuit. The Unit 1 B train offsite power supply remained energized and available during this event. Both Emergency Diesel Generators remained operable and both emergency buses remained energized from the onsite source and operable during this event. "At 1425 EDT the #1 138 KV bus was re-energized. The planned maintenance was completed on the B train offsite power supply transformer. Following testing, at 1452 EDT both offsite power supplies were declared operable. "This notification is provided in accordance with 10CFR50.72(b)(3)(v)(D) since both offsite power supplies were inoperable from 1416 EDT to 1452 EDT on 9/6/12." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DAN SCHWER TO JOHN KNOKE AT 1242 EDT ON 10/01/12 * * * "Beaver Valley Unit 1 is retracting EN # 48283 based on completion of an engineering evaluation. The evaluation determined that the Unit 1 'B' train offsite power supply was operable and capable of performing its safety function with its transformer cooling fan control circuit out of service for planned maintenance. Since one train of offsite power was determined to be operable, this condition is not reportable under 10CFR50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." Notified R1DO (Wayne Schmidt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-09-06
48282 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2012-09-06 13:14 | 2012-09-06 18:39 | 2012-09-06 | LOSS OF SECONDARY CONTAINMENT VENTILATION FOR EIGHT SECONDS "On September 6, 2012, at 1314 hours, the reactor building ventilation system was being restored to service following planned maintenance and surveillance activities. During the reactor building pressure transition when restoring reactor building ventilation (from the Standby Gas Treatment System), an employee entered a secondary containment interlock and identified a door leading to the environment had opened. The employee immediately secured the door and notified Operations personnel. A review of the door alarm history determined the door was open for approximately eight seconds. "Given the temporary breech in secondary containment, this event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-09-06
48281 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2012-09-06 06:02 | 2012-09-06 16:25 | 2012-09-06 | AGREEMENT STATE REPORT - SOURCE RACK STUCK IN UNSHIELDED POSITION The State of South Carolina submitted the following information via email: "The SC Department of Health and Environmental Control [SCDHEC] was notified on Thursday, September 6, 2012, at 1500 EDT, that rack #2 failed to return to a shielded position at 0605 EDT due to a cleaning rag that was inadvertently wrapped around the source rack hoist cable. The RSO/Maintenance Manager for the facility stated that authorized personnel were able to clear the obstruction and return the rack to a shielded position at 0700 EDT. There were no personnel exposures and no equipment damage. "This event is open and pending the licensee's investigation and report to the SCDHEC. Updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2012-09-14
48280 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-05-24 | 2012-09-06 11:17 | 2012-09-06 | AGREEMENT STATE REPORT - RECOVERED PACEMAKER "A patient with a Pu-238 pacemaker died on 5/16/12 and was scheduled to be buried on 5/26/2012. Berkshire Medical Center (BMC) observed the obituary in the newspaper on 5/24/2012 and contacted funeral home to retrieve the pacemaker. The funeral home still possessed the pacemaker as it was extracted before the patient was cremated. On 5/24/2012, the BMC Radiation Safety Officer retrieved the pacemaker. Radiation measurements of the pacemaker were less than 1 mR/hr near the surface and not detectable above background at 1 meter. Leak tests were also not detectable above background. "BMC registered the source with the DOE Off-Site Recovery Project (OSRP) to have it disposed." Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-09-14
48279 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2012-09-05 13:25 | 2012-09-05 17:10 | 2012-09-05 | OFFSITE NOTIFICATION OF SMALL OIL SPILL A small amount of oil spilled from a forklift hydraulic oil connection. The amount was estimated at about 1 quart. The release has been terminated. However, the oil was washed into the navigable waterway at the site by heavy rains and as indicated by an oil sheen that was observed. Oil booms have been distributed around the sheen to contain the oil and prevent its spread to the environment. The licensee reported this spill to the Connecticut Department of Environmental Protection and the Waterford Dispatch. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-05
48278 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-05 12:25 | 2012-09-05 16:32 | 2012-09-05 | OFFSITE NOTIFICATION OF SODIUM HYPOCHLORITE SPILL "At 1225 on 9/5/12, the Main Control Room received a report of a Sodium Hypochlorite spill estimated at 100 gallons at the Byron Circulating Water Pump House. The spill was caused by a leak from the hose of the Chemical Delivery truck. "A spill of greater than 80 gallons of Sodium Hypochlorite is considered a reportable quantity. "The spill was reported to the Illinois Emergency Management Agency (IEMA) in accordance with 29 IAC 430.30 and 35 IAC 750.304, and the National Response Center in accordance with 40 CFR 302.6. "Notification to IEMA was performed at 1235 on 9/5/12, and notification to the National Response Center was performed at 1245 on 9/5/12. "The notifications to other government agencies is reportable to the NRC in accordance with 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 91 | 95 | 0 | 91 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-05
48277 | -1 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-22 12:36 | 2012-09-05 16:35 | 2012-09-20 | MISSING FLOOD SEAL "During flooding walkdowns being performed on August 22, 2012, with the unit at 100 percent power, South Texas Project Unit 2 discovered the potential for water intrusion into the 10' Elevation Electrical Auxiliary Building (EAB) via a 2-inch underground conduit that was found to be missing its flood seal. It has been determined that the missing flood seal compromised the external flood design controls for the EAB. If flooding of the 10 [foot] EAB were to occur as a result of the missing flood seal, the operability of the Train A Engineered Safety Features (ESF) switchgear and the ESF Sequencers for all three Standby Diesel Generators could have been affected. Additionally, the Qualified Display Parameter System process cabinets (which control Auxiliary Feedwater flow and Steam Generator PORVs) and the Auxiliary Shutdown Panel are also located on the 10' Elevation. "Repairs have been made and the 2-inch conduit is sealed. "The event is being reported under 10 CFR 50.72(b)(3)(ii)(B) for Unit 2 being in an unanalyzed condition that significantly degraded plant safety, and under 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM JAMES MORRIS TO JOHN KNOKE AT 1658 EDT ON 09/20/12 * * * "The purpose of this call is to retract the notification made on 09/05/2012, Event Number 48277. Further analysis indicates that water intrusion resulting from the missing 2-inch conduit seal would not have been sufficient to affect the operability of the equipment located on the 10-foot elevation of the Unit 2 Electrical Auxiliary Building. It has been determined that the maximum water depth would not have exceeded 2 inches in depth and all safety related equipment on the 10-foot elevation is greater than 2 inches above the floor, therefore there would be no impact to any safety-related equipment. Accordingly, this event notification is being retracted." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Geoffrey Miller). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2012-09-05
48276 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-05 10:40 | 2012-09-05 10:54 | 2012-09-05 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PREVENTATIVE MAINTENANCE ON HVAC SYSTEM "This [report] is being issued in advance of a planned activity. Today, 9/5/2012, the (TSC) Technical Support Center Emergency Ventilation System will be removed from service to support preventative maintenance activities. The Emergency Ventilation System will not be available and cannot be restored within the time period (75 minutes) required to staff and activate the Emergency Response Organization (ERO). This work is scheduled to complete today. "If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperature, radiological conditions, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-05
48275 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-09-01 | 2012-09-04 17:55 | 2012-09-04 | AGREEMENT STATE REPORT - DAMAGED PROCESS GAUGE SHUTTER The Texas Department of State Health Services Radiation Branch provided the following report via e-mail: "On September 4, 2012, the Agency [Texas Department of Health] was notified by the licensee that the shutter on an Ohmart / Vega nuclear gauge model SHLD-1 containing a 20 millicurie cesium - 137 source had been damaged and no longer functioned as designed. The licensee stated that the gauge is mounted on the side of a truck trailer. The licensee stated that the gauge operator had tried to close the gauge shutter and could not get the shutter to move. The operator obtained a hammer and struck the shutter mechanism. The four bolts holding the shutter mechanism in place snapped and the shutter fell off the gauge. The operator placed the shutter back on the gauge to provide shielding, but the shutter is not attached to the gauge housing. The gauge is at the licensee's facility isolated inside of a locked fence. A barrier has been placed around the gauge to prevent inadvertent entry to the area around the gauge. The licensee has contacted the manufacturer to repair the gauge. The licensee stated that the gauge does not present an exposure hazard to any individual. Additional information will be provided as it is received in accordance with SA 300: 'Reporting Material Events'." Texas Incident # I-8984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-09-12
48274 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-09-04 | 2012-09-04 17:10 | 2012-09-04 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 1320 EDT, on September 4, 2012, the High Pressure Coolant Injection (HPCI) system was declared inoperable during performance of HC.OP-IS.BJ-0001, HPCI Main and Booster Pump Set - 0P204 and 0P217 - In Service Test (IST). The HPCI system was being started for the quarterly IST when 1-FD-HV-F001, HPCI Turbine Steam Supply Valve, failed to open per step 5.21.7 of the test. The control room operators returned the system to a standby line up. The Outage Control Center was staffed to investigate the cause of the valve misoperation. "Loss of the HPCI system is reportable under 10 CFR 50.72(b)(3)(v) as loss of a single train safety system required to mitigate the consequences of an accident. The 'A' Residual Heat Removal System was aligned for Suppression Pool Cooling to support the HPCI IST surveillance and was inoperable for Low Pressure Coolant Injection function until realigned to a standby lineup at 1340 EDT. No additional Emergency Core Cooling Systems or safety-related equipment was inoperable during this time period." The NRC Resident Inspector has been notified. Lower Alloways Creek Township will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-09-04
48273 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-07-24 | 2012-09-04 15:01 | 2012-09-04 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was provided by the Ohio Bureau of Radiation Protection via e-mail: "Licensee experienced a source disconnect with an industrial radiography camera. The radiographers were working at a temporary job site and attempted to retrieve source after completing the first exposure of the workday. Source would not retrieve and a source disconnect was suspected, with the source remaining at the exposure end of the guide tube. The source position was verified by on-site radiation surveys. The guide tube (containing the source at the far end) was disconnected from the camera and moved to an isolated location at the client site. The radiographers established appropriate barriers and entry controls for the temporary area and maintained constant surveillance until licensee's source retrieval personnel arrived. Retrieval personnel were able to reconnect the source using a special tool and the source was able to be retracted back into the camera. The camera and all associated equipment were sent to the manufacturer for evaluation. Cause of the problem was determined to be a worn connecting collar around the plug assembly and failure to follow a source connect procedure recommended by the manufacturer. Ohio Bureau of Radiation Protection will visit site and conduct an investigation. "The licensee's report was received at Ohio Bureau of Radiation Protection today, 9/4/12, at approximately 1240 EDT. "Based on manufacturer's evaluation of the equipment used, Ohio Bureau of Radiation Protection will conduct an investigation of licensee's maintenance program and to determine reasons for failure by licensee to make initial notification and follow-up written report in a timely manner." No significant personnel exposure was received during retrieval procedures. Ohio Report OH 120003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-09-12
48272 | 0 | PPG INDUSTRIES INC. |  |  |  |  | 2012-09-01 18:45 | 2012-09-04 14:10 | 2012-09-05 | TWO TRITIUM EXIT SIGNS DESTROYED IN WAREHOUSE FIRE "At approximately 6:45 pm on 9-1-12, there was a fire in two warehouses at the PPG Industries, Inc. Natrium Plant located in New Martinsville, WV. The warehouses are storage areas for product, where personnel are usually not stationed. The facility does have a specific license from the NRC. However, the mentioned signs are not covered under the license. They are generally licensed. "Two tritium exit signs, one in each warehouse, were destroyed in the fire. The signs were: - manufactured by Self-Powered Lighting, LTD. - Model No. CPI-700 - Activity on the manufacture date of 2-1983 was 12.5 Curies - Decay corrected activity on 9-1-2012 was calculated to be 2.4 Curies The area around the former location of the signs is barricaded off. This afternoon an outside contractor performed testing to determine if there is tritium contamination. The area will remain barricaded off until results are received. "A follow-up report will be submitted within 30 days." * * * UPDATE AT 1210 EDT ON 9/5/12 FROM BALDAUFF TO HUFFMAN * * * Sampling has been completed and analyzed to determine if any contamination was present from the destroyed tritium exit signs. The results verify that there is no contamination present. R1DO (Conte) notified. FSME Events Resource e-mailed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2012-09-12
48271 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-09-01 | 2012-09-04 09:49 | 2012-09-04 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Florida via email: The State of Florida was notified by the licensee that one of their Troxler moisture density gauges has been stolen. The theft is believed to have occurred on the night of September 1st, 2012. The gauge was properly stored in a secure storage shed when the theft occurred. The licensee has notified the manufacturer and local law enforcement and will be offering a reward for its recovery. The State of Florida will investigate. Gauge Information: Troxler Model 3440, Serial # 14471 Sources: Americium-241/Beryllium, 40 millicuries Cesium-137, 8 millicuries Florida Incident #: FL12-065 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-09-12
48270 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-09-03 02:25 | 2012-09-03 07:40 | 2012-09-04 | HPCI INOPERABLE DUE TO ERRONEOUS INDICATION ON FLOW INDICATING CONTROLLER "At 0225 EDT on September 3, 2012, with the James A. Fitzpatrick Nuclear Power Plant (JAF) operating at 93% reactor power, High Pressure Coolant Injection (HPCI) was declared inoperable due to abnormal indication on the HPCI Flow Indicating Controller (FIC). The FIC was found to be indicating a HPCI System flow rate of 700 gpm while the system was in the standby lineup. Under these conditions, the capability of the system to achieve the required flow rate cannot be assured. "This failure meets NRC 8 hour reporting criterion 10CFR50.72(b)(3)(v)(D). Reactor Core Isolation Cooling (RCIC) and other Emergency Core Cooling Systems (ECCS) remain operable. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1418 EDT ON 9/4/12 FROM DeFILLIPPO TO HUFFMAN * * * "The improper HPCI flow indication was determined to be due to minor air intrusion following restoration of the system after maintenance. The flow transmitter for the HPCI system was repeatedly vented with no air observed. The HPCI system has been restored to a normal standby line-up and is OPERABLE as of 9/4/2012 at 1415 EDT." The NRC Resident Inspector has been notified. R1DO (Conte) notified. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-09-03
48269 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2012-09-02 22:04 | 2012-09-03 05:17 | 2012-10-26 | TRANSFER OF EMERGENCY RESERVE AUXILIARY TRANSFORMER ISOLATING FUEL POOL COOLING AND CLEANUP SYSTEM, AND FUEL BUILDING VENTILATION SYSTEM "At 22:04 CDT on 9/02/2012, the Emergency Reserve Auxiliary Transformer (ERAT) transferred unexpectedly to the Reserve Auxiliary Transformer (RAT). During this transfer, the Fuel Pool Cooling and Cleanup (FC) system pump 'A' tripped and the Fuel Building Ventilation (VF) system isolated. Upper containment pool level dropped below the minimum required level per Technical Specifications (TS) 3.6.2.4 and Secondary Containment differential pressure increased above 0.25 inches vacuum per TS 3.6.4.1. Upper Containment Pool level was restored above the minimum level at 01:27 CDT on 9/3/2012 within the 4 hour completion time. The Upper Containment Pool is a part of the suppression pool makeup system used to ensure the Primary Containment function. Secondary Containment differential pressure was restored at 22:19 on 9/2/2012 when the Standby Gas Treatment System was started. Maintaining secondary containment differential pressure helps to control the release of radioactive material. "This event is being reported as a condition that could have prevented the fulfillment of a safety function per 10 CFR 50.72(b)(3)(v)(B) and 10 CFR 50.72(b)(3)(v)(C). The station is currently in a 72-hour action to restore the ERAT to an operable status per TS LCO 3.8.1 Required Action A.2. Plant conditions are stable and actions are underway to repair the ERAT. "The NRC Resident [Inspector] has been notified." * * * RETRACTION ON 10/26/12 AT 1322 EDT FROM KEN LEFFEL TO DONG PARK * * * "Upper Containment Pool level dropped below the normal pool level of 827 feet-3 inches when the Fuel Pool Cooling and Cleanup system pump 'A' tripped, and was initially reported as dropping below the minimum level (825 feet-6 inches) required by Technical Specification (TS) 3.6.2.4. However, subsequent reports from the field confirmed that the lowest level reached was 827 feet 0 inches, which is greater than the minimum required TS level. Therefore, no loss of safety function occurred for the Upper Containment Pool level as a result of this event, and the event is not reportable under 50.72 (b)(3)(v)(B). "The NRC Resident [Inspector] has been notified." Notified R3DO (Pelke). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) |  |  | 0 | 2012-09-03
48268 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-09-02 10:31 | 2012-09-02 14:45 | 2012-09-02 | OFFSITE NOTIFICATION DUE TO NON-RADIOLOGICAL LEAKAGE FROM THE NEUTRALIZATION TANK "In response to identification of a non-radiological leak from the Neutralization Tank at Callaway Plant today (9/2/2012), notification was made to the EPA National Spill Response Center at 1031 CDT and to the Missouri Department of Natural Resources at 1043 CDT. The leak was initially identified at 0926 CDT. From testing of a sample taken from the tank, the pH of the tank fluid was reported to be 1.9. Initially, the leak was to the ground and into a ditch that is part of a flow path that ultimately leads off site via a storm sewer. However, there is no indication of any of the leakage flowing beyond the site boundary via that pathway since action was promptly taken to divert the leakage to the sump area of the equalization tank (on site). The leakage will thus be collected there until it terminates. At 0926 CDT, the leakage rate was estimated to be approximately 20 gpm; at 1025 CDT the leakage was estimated to be approximately 50 gpm. The leak is at the bottom of the Neutralization Tank, and thus will terminate when the tank is emptied. At 1218 CDT, the fluid level in the Neutralization Tank was at 17%. The initial quantity of fluid in the tank (at the onset of the leak) was approximately 110000 gallons. "This spill was reported to offsite organizations, as noted. This event is reportable to the NRC pursuant to 10CFR50.72(b)(2)(xi). "The NRC Senior Resident Inspector has been notified of the event and this ENS notification." 17% tank fluid level corresponds to approximately 25000 gallons. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-09-02
48267 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-02 12:00 | 2012-09-02 09:21 | 2012-09-02 | PLANNED OUTAGE OF EMERGENCY OPERATIONS FACILITY "As part of preparation for the upcoming Democratic National Convention (DNC), contingencies are in place associated with the common Emergency Operations Facility (EOF) for Catawba, McGuire, and Oconee Nuclear Stations. The common EOF is located in Charlotte, NC. Because of the potential for event security to delay staffing of the facility within the prescribed time frame, Duke Energy is implementing its business continuity plan for the EOF during the period from 12:00 PM (noon) on September 2nd until 24:00 (midnight) on September 6th. "If a declared emergency were to occur at Catawba Nuclear Station, the EOF would be set up in the McGuire Alternate Technical Support Center (TSC) location. This facility is used as a backup location for the McGuire TSC as specified in station procedures. "This report is being made in accordance with 10CFR50.72, criterion (b)(3)(xiii), and in accordance with NUREG-1022, Revision 2, as a condition that may impair the functionality of an Emergency Response Facility." The licensee will notify the State of North Carolina, State of South Carolina, York County, Gaston County, and Mecklenburg County. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-02
48266 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-09-02 12:00 | 2012-09-02 08:52 | 2012-09-02 | PLANNED OUTAGE OF EMERGENCY OPERATIONS FACILITY "As part of preparation for the upcoming Democratic National Convention (DNC), contingencies are in place associated with the common Emergency Operations Facility (EOF) for Catawba, McGuire, and Oconee Nuclear Stations. The common EOF is located in Charlotte, NC. Because of the potential for event security to delay staffing of the facility within the prescribed time frame, Duke Energy is implementing its business continuity plan for the EOF during the period from 12:00 PM (noon) on September 2nd until 24:00 (midnight) on September 6th. "If a declared emergency were to occur at McGuire Nuclear Station, the EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location. This facility is used as a backup location for the Catawba TSC as specified in station procedures. "This report is being made in accordance with 10CFR50.72, criterion (b)(3)(xiii), and in accordance with NUREG-1022, Revision 2, as a condition that may impair the functionality of an Emergency Response Facility." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-02
48265 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-09-02 12:00 | 2012-09-02 08:35 | 2012-09-02 | PLANNED OUTAGE OF EMERGENCY OPERATIONS FACILITY "As part of preparation for the upcoming Democratic National Convention (DNC), contingencies are in place associated with the common Emergency Operations Facility (EOF) for Catawba, McGuire, and Oconee Nuclear Stations. The common EOF is located in Charlotte, NC. Because of the potential for event security to delay staffing of the facility within the prescribed time frame, Duke Energy is implementing its business continuity plan for the EOF during the period from 12:00 PM (noon) on September 2nd until 24:00 (midnight) on September 6th. "If a declared emergency were to occur at Oconee Nuclear Station, the EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location. This facility is used as a backup location for the Catawba TSC as specified in station procedures. "This report is being made in accordance with 10CFR50.72, criterion (b)(3)(xiii), and in accordance with NUREG-1022, Revision 2, as a condition that may impair the functionality of an Emergency Response Facility." The licensee notified the South Carolina Department of Health and Environmental Control, Pickens County, and Oconee County. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-02
48264 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-09-01 22:30 | 2012-09-02 06:22 | 2012-09-02 | RADIATION MONITOR DECLARED INOPERABLE "This is a non-emergency report. No actual event has occurred. "At 2230 hours EDT, on September 01, 2012, Oconee Nuclear Station Operations determined that the radiation monitor for Low Gas Unit Vent monitoring failed its check source and was declared inoperable. This monitor is used for determination of Emergency Action Levels (EALs) in ALL Modes. Specifically, the criterion states that an Unusual Event should be declared if this radiation monitoring reading reaches 9.35E5 for greater than 60 minutes. This condition was discovered during weekly radiation monitor setpoint determinations. "There is no adverse impact on nuclear safety. A redundant method for sampling and determination of activity levels has been implemented per SLC 16.11.3. The same EAL criterion has a redundant determination of Unusual Event classification based on these activity levels. "This report is submitted based upon a loss of emergency assessment capability in accordance with 50.72(b)(3)(xiii). "The NRC Resident Inspector has been informed." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-09-02
48263 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2012-08-31 09:40 | 2012-08-31 17:50 | 2012-08-31 | HIGH PRESSURE CORE SPRAY DIESEL GENERATOR DECLARED INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During the conduct of the Unit 2 Division 3 High Pressure Core Spray (HPCS) Diesel Generator (DG) air start system receiver blowdown, a low air pressure system alarm was received. Starting air pressure in one of 2 redundant air receiver banks lowered to the point requiring the DG to be declared inoperable per Technical Specifications. This event appears to have been caused by a degraded receiver drain valve. The air system degraded equipment condition has cleared and the DG has been restored to operable status following 42 minutes of inoperability. Although a redundant air bank was fully available and charged, during this time of inoperability the DG was at reduced margin to successfully start if required. Due to this loss of margin and inoperable condition, it has been determined that this failure could potentially affect the safety function of this system, and is being reported as an 8 hour ENS notification." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-08-31
48262 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-08-31 15:27 | 2012-08-31 17:32 | 2012-08-31 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for illegal drugs during a follow-up fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2012-08-31
48261 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-10-01 | 2012-08-31 15:48 | 2013-04-24 | AGREEMENT STATE REPORT - STUDENT RECEIVED POTENTIAL INHALATION OVEREXPOSURE The following information was received from the State of Nevada via email: "A graduate student inhaled a mixture of U-233 and U-238 while working in the lab grinding a compound of Uranium Octoxide. [The graduate student] used a glove box instead of the hood with the HEPA filter, contrary to UNLV [University of Nevada Las Vegas] approved procedure. "This happened twice and could have been between October 1, 2011 and April 1, 2012. "The first bioassay, based on an inhalation date of October 1, 2011, showed 17.72 rem total. When the inhalation date was assumed to be April 1, 2012, the result was 5.52 rem. "[U-233]*1.6 = [U-238] contribution. "The student will be getting a third bioassay on September 5, 2012 at the Lawrence Livermore National Lab (LLNL). This will involve a low-energy chest count to detect Th-234 and an organ count, looking at the kidneys for Uranium. "The student has been restricted from all lab work since April. "The bioassay was done at Test America." * * * UPDATE AT 1553 EDT ON 10/24/12 FROM SNEHA RAVIKUMAR TO S. SANDIN * * * The following update was received from the State of Nevada via email: "NMED Item No.: NV120022 "Preliminary results: "1. September 5, 2012: Low-energy lung count, kidney count and hand count were performed at LLNL. The lung count was less than MDA for U-233, Th-234, U-234 & U-2235. The detect/non-detect kidney & hand counts were both non-detect. "2. September 12, 2012: Third Bioassay results received. U-238 - 0.66 dpm/sample U-235 - less than CRDL U-233/234 - 1.25 dpm/sample" Notified R4DO (Hagar) and FSME Events Resource via email. * * * UPDATE AT 1540 EDT ON 11/15/12 FROM RAVIKUMAR TO HUFFMAN * * * The following update was received from the State of Nevada via email: "All personnel having access to the UNLV lab where the original uptake occurred had bioassay samples taken. UNLV determined that 46 persons should be in this group, including the RSO and ARSO. From the data submitted thus far, an additional graduate student appears to have received an uptake. This student has been restricted from further RAM work and a dose assessment undertaken. The actual dose will be dependent on the time and source of the uptake. If the timeframe and source are the same as that of the original graduate student, the magnitude will be the same. Thirteen remaining bioassays remain to be analyzed. Three of the thirteen are yet to be collected. The RSO attributed his elevated uptake to previous DOD work. The latest ten bioassays were collected within the last three weeks and with expedited processing results, should be available by mid-December." Notified the R4DO (Drake) and FSME Events Resource via e-mail. * * * UPDATE AT 1411 EST ON 02/12/13 FROM RAVIKUMAR TO SNYDER * * * The following update was received from the State of Nevada via email: "Dependent on the particle size of the uptake the grad student's exposure could be either 6760 mrem for size M (medium) particles versus 154 mrem for size S (small) particles. UNLV has indicated a delay till March, 2013, for this analysis. It appears only the one Grad Student had an uptake. "What corrective action(s) were taken to prevent a recurrence? "Existing procedures were reviewed & rewritten, and additional new monitoring, controls, training and procedures are now in place to prevent a recurrence." Notified the R4DO (Hagar) and FSME Events Resource via e-mail. * * * UPDATE AT 1152 EDT ON 04/24/13 FROM SNEHA RAVIKUMAR TO CHARLES TEAL * * * The following is excerpted from an email received from the State of Nevada: "All of the activity ratios (especially the one from the ICP-MS [Inductively Coupled Plasma Mass Spectrometry], which has the lowest uncertainty) are consistent with that of natural uranium. This supports the conclusion that the student's observed bioassay results are the result of an intake of natural uranium form non-occupational sources and not a result of material she was handling at UNLV." Notified R4DO (Whitten) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2012-09-10
48260 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-08-31 | 2012-08-31 15:19 | 2012-08-31 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN THE PRESCRIBED FRACTIONAL DOSE The following information was received from the Commonwealth of Virginia via email: "On August 31, 2012, the licensee reported that a wire drift error occurred during a high dose rate afterloader procedure on August 31. The patient undergoing a tandem and ovoid treatment was scheduled to receive a fraction dose of 6 Gray. Because of the wire drift error the fraction was terminated prior to completion and the patient received only 0.73 Gray. The licensee has informed the patient and the referring physician. The cause of the error and the patient's revised treatment plan are being reviewed by the licensee. The Virginia Radioactive Material Program will review the circumstances of the event." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-09-10
48259 | 0 | ACUREN INSPECTION |  |  |  |  | 2012-04-28 09:45 | 2012-08-31 09:54 | 2012-08-31 | IR-192 SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA At 0945 hours on 4-28-2012, the radiographer at the jobsite in Willeysville, WV reported to his Division Manager that the source in a Sentinel 880 Delta camera, S/N D4132, was disconnected and could not be retracted into the shielded position following the first exposure. The Division Manager contacted the Acuren Cincinnati RSO for assistance. Arrangements were made for both the Division Manager and Cincinnati RSO who had extensive experience in source retrieval to respond to the jobsite. The source was successfully retrieved by 1805 hours the same day. The camera, crank, guide tube, and quick connect were transported to the Ona lab to be shipped to QSA for investigation on Monday morning, 4-30-2012. There were no personnel overexposures associated with this incident. Corrective actions included: All radiographic personnel were immediately notified of the source disconnect incident to raise awareness of equipment checks and no-go-gage test. Acuren Division Manager and RSO conducted the misconnect test [Acuren terminology] on all radiographic equipment cranks and cameras as of 5-4-12. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-09-10
48258 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-08-30 12:15 | 2012-08-30 17:48 | 2012-08-30 | HPCI INOPERABLE DUE TO FAILED PRESSURE CONTROL VALVE "At 1215 EDT on August 30, 2012, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 95% reactor power, High Pressure Coolant Injection (HPCI) was declared inoperable due to the failure of a pressure control valve on the HPCI oil cooling system. The failure of this pressure control valve results in a safety-valve lifting and releasing approximately 75 gallons per minute to the reactor building equipment drain tank. There was no release to the environment. "This failure meets NRC 8 hour reporting criterion 10CFR50.72(b)(3)(v)(D). Reactor Core Isolation Cooling (RCIC) and other Emergency Core Cooling System (ECCS) systems remain operable. "The NRC Resident Inspector has been notified." | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-08-30
48257 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-08-30 15:45 | 2012-08-30 17:45 | 2012-08-30 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED EMPLOYEE "An employee was transported to the dispensary with a laceration to his left hand approximately at 1540 CDT. The plant nurse evaluated the employee and decided to transport the employee to a regional hospital. Contamination was detected on the employee's plant clothing. The maximum contamination was present on the employee's left boot, 12,682 dpm/100cm2. The employee's plant clothing was removed, and the employee was re-surveyed. No contamination was detected on the employee prior to loading the ambulance. Additionally, the gurney and ambulance personnel shoes were surveyed upon loading the ambulance; no contamination was detected." The contamination was from Uranium ore concentrates. The licensee informed RII (Richard Gibson) via voicemail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-08-30
48256 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-30 | 2012-08-30 14:53 | 2012-08-30 | AGREEMENT STATE REPORT - IMPROPER SALE AND TRANSFER OF RADIOACTIVE SOURCE The following information was received from the State of Texas via email: "On August 30, 2012, a company contracted by a licensee to conduct a closeout of an imaging facility notified the Agency [Texas Department of State Health Services] that the licensee had sold an ADAC Gamma/PET Camera early in 2012 without proper shipping and transfer paperwork and with a 20 millicurie Cesium-137 seal source located inside the PET scanner. The PET scanner with internal source was brokered and sold to a company overseas. Details of the date of sale, broker company, and who purchased the device are unknown. An investigation into this event is ongoing and information will be updated as it is received per SA 300 [Reporting Material Events]. "The State of Texas event number for this event is I - 8982. "Equipment: ADAC Gamma/PET Camera "Source: Cesium-137 -- 20 millicuries -- CZ882" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-09-07
48255 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-08-30 06:20 | 2012-08-30 14:13 | 2012-08-30 | EMERGENCY OPERATIONS FACILITY AND EMERGENCY NOTIFICATION SYSTEM PHONE OUT OF SERVICE "This is a non-emergency notification being made under 10CFR50.72(b)(3)(xiii) due to the potential loss of emergency preparedness capabilities due to the effects of hurricane Isaac. "At approximately 0735, the Emergency Operations Facility (EOF) diesel generator was discovered to be tripped and not available, leaving the primary EOF without AC electrical power and, therefore, unavailable since normal AC power was also lost due to weather conditions. Efforts to repair the EOF diesel generator have been initiated and personnel have verified the Alternate EOF is functional. State, local and federal agencies have been informed of the plan to use the alternate EOF in case of an emergency preparedness activation. "With essential personnel being sequestered at the Waterford 3 power block, the critical EOF functions can be performed from the on-site Technical Support Center (TSC), which is housed within the Control Room ventilated envelope. "At approximately 0620 CDT, Entergy Operations, Inc. Emergency Preparedness staff discovered that the NRC Emergency Notification Systems (ENS) was not working. NRC Headquarters was notified at approximately 0715 CDT and was given an alternate phone number to contact Waterford 3. The ENS phone had previously been verified functional at approximately 0330 CDT. The NRC Health Physics Network (HPN) telephone line was verified to be functional at 0922 CDT." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-30
48254 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-30 09:45 | 2012-08-30 13:25 | 2012-08-30 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of Texas via email: "On August 30, 2012, the licensee notified the Agency [Texas Department of State Health Services] that at approximately 0945 hrs CDT a Troxler model 3430 moisture/density gauge, containing a 40 millicurie Americium-241/Beryllium source and an 8 millicurie Cesium-137 source, had been stolen out of the back of one of its pickup trucks [a white Chevrolet C-1500] outside a hotel in Lubbock, Texas. The licensee's employee had gone inside to check out of the hotel and when he came back outside he found both chains securing the gauge had been cut and the gauge was gone. The local police department was notified by the employee. The licensee will notify the manufacturer and other gauge service companies. The Agency will notify the Texas Association of Pawn Brokers. An investigation into this event is ongoing and information will be updated as it is received per SA-300 [Reporting Material Events]. "Gauge Information: Troxler Model 3430, Serial # 25088 "Sources: Americium-241/Beryllium -- 40 millicuries -- Serial #75-7262, Cesium-137 -- 8 millicuries -- 47-21295" Texas Incident #: I-8981 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-09-07
48253 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-29 21:34 | 2012-08-30 02:34 | 2012-08-30 | LOCAL CONTROL CAPABILITY OF EMERGENCY DIESEL GENERATOR #2 NOT AVAILABLE UNDER CERTAIN CONDITIONS "On August 28, 2012, during planned maintenance on Emergency Diesel Generator No.2, a post-maintenance continuity testing associated with the Alternate Safety Shutdown (ASSD) switch on Emergency Diesel Generator No.2 (EDG 2) revealed unexpected results when the switch was taken to the LOCAL position. Troubleshooting activities determined the switch to be operating properly, meaning the contacts are actually open. However, a current path preventing isolation of the control room circuit remained. It was determined that a wire, not identified in EDG wiring diagrams, created a short between two ASSD switch contacts. "At 2134 hours Eastern Daylight Time (EDT) on August 29, 2012, it was concluded that the condition may impact the ability of EDG 2 to perform its intended ASSD function. In the event of a fire, an induced fault could potentially affect the ability to locally control EDG 2. Local control of EDG 2 is credited in the safe shutdown analysis. Therefore, this condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. "This condition did not result in any adverse impact to the health and safety of the public. This condition has no affect on the Technical Specification operability of EDG 2 and it was fully capable of performing its intended design basis accident response functions given the as-found condition of the circuitry. "The initial safety significance of this condition is minimal. This condition has no affect on the Technical Specification operability of EDG 2 and it was fully capable of performing its intended design basis accident response functions given the as-found condition of the circuitry. "Repairs to the ASSD switch wiring have been completed. Post maintenance testing is occurring at this time. Planning is in progress to inspect the remaining Emergency Diesel Generators for similar conditions." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-08-30
48252 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2012-08-29 19:30 | 2012-08-30 00:31 | 2012-08-30 | PRIMARY PLANT COMPUTER OUT OF SERVICE "Calvert Cliffs Unit 2 Primary Plant Computer (PPC) is out of service. The PPC provides monitoring capability for the Emergency Response Data System and Safety Parameter Display System. The loss of the PPC requires alternate monitoring methods, as described in plant procedures, to be used. Therefore, appropriate assessment of plant conditions, notifications and communications can still be made, if required, during the time that the PPC is unavailable. "This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii) which is any event that results in major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications and accomplish required communications, as necessary." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-30
48251 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-08-29 15:30 | 2012-08-29 23:15 | 2012-08-29 | EVACUATION ROUTE UNAVAILABLE DUE TO FLOODING FROM HURRICANE ISAAC "This is a non-emergency notification being made under 10CFR50.72(b)(3)(xiii) due to the potential loss of emergency preparedness capabilities. At approximately 1530 CDT, Entergy Operations, Inc. was informed of a road closure which could impact the ability to perform a potential evacuation required by the Waterford 3 Emergency Plan. "Louisiana Governor's Office of Homeland Security and Emergency Preparedness (GOHSEP) reported that US Highway 51 to Interstate 10 was closed due to flooding from elevated water levels in Lake Pontchartrain resulting from Hurricane Isaac. "Alternate evacuation routes remain available." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-29
48250 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-08-29 08:27 | 2012-08-29 15:35 | 2012-08-29 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO LIMITED RANGE ON INDICATOR "This is a non-emergency report regarding a condition that does not apply in our current operating mode. No actual event has occurred. "At 0827 hours EDT, on August 29, 2012, Harris Operations discovered that the instrumentation used for determination of Emergency Action Levels (EALs) during Modes 5 and 6 for loss of Reactor Coolant System (RCS) inventory would not provide the required information. Specifically, the criterion states that an Alert should be declared if standpipe level is less than -96.5 inches (72% on the Reactor Vessel Level Indication System [RVLIS]). During a loss of inventory from the reactor vessel below the RCS loop nozzles, the standpipe indication would not reflect a level below -95.5 inches. This condition was discovered during an assessment of EAL implementing procedures in response to industry operating experience. "There is no adverse impact on nuclear safety. All Site Emergency Coordinators and Emergency Response Managers will be directed to use the alternate RVLIS indication to ensure emergency classifications continue to be accurately assessed, which will also be communicated in a shift order. The EAL guidance will be revised to fully resolve the issue in an expeditious manner. "This report is submitted based upon a loss of emergency assessment capability in accordance with º50.72(b)(3)(xiii). "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-29
48249 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-08-29 10:30 | 2012-08-29 14:30 | 2012-08-29 | AGREEMENT STATE REPORT - LOST THEN RECOVERED TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the Commonwealth of Virginia via facsimile: "On August 29, 2012 at 10:30 a.m., the licensee reported that a Troxler Model 3440 portable density gauge was missing. The gauge, in its transport case, apparently fell from the licensee's truck during transport. The licensee notified the local law enforcement and initiated a search for the gauge. At 11:45 a.m., the licensee reported that the gauge had been found by a local resident who called the licensee. The RSO verified that neither the gauge nor the transport case was damaged. The Virginia Radioactive Material Program is investigating the cause of the incident." Virginia Event Number: VA-12-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-09-06
48248 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-08-29 | 2012-08-29 13:04 | 2012-08-29 | ARIZONA AGREEMENT STATE REPORT - ARIZONA WORKER CONTAMINATED WHILE WORKING AT LOS ALAMOS IN NEW MEXICO The following information was obtained from the state of Arizona via email: "On Saturday, August 25, 2012, the Arizona Radiation Regulatory Agency was informed by Tempe Fire Department that they responded to a 911 call for assistance from a private citizen who indicated that he may have received a possible radiation exposure/contamination while working at the Los Alamos National Laboratory in New Mexico. The Tempe Fire Department conducted a radiation survey and found that the shoes were the source of the radioactive contamination. "At 2315 hours MDT, on August 25, 2012, DOE Region 4 sent a radiological response team to Tempe, AZ to investigate and perform a radiological survey of the item/s reported with the radiation contamination. A radiation survey, using a Ludlum survey meter with a beta detector, provided a positive result for contamination on a few articles, bottom of both shoes (350 cpm above background) and a pair of underwear (measured 850 cpm above background). "On Tuesday August 28, 2012, the following occurred: -The source of the contamination as reported by DOE RAP Teams Region 4 is Technetium-99. (Half-Life is 211,000 years and is a Beta emitter) -It is reported that 13 to 16 individuals may be contaminated with the Tc99. -It is reported that several automobiles and other personal articles have been located in New Mexico and were moved to an isolated area. -ARRA laboratory is now in possession/control of the clothing and will conduct a laboratory analysis to determine and confirm the source of the radioactive material. -ARRA reported levels of Beta Radiation several times above background on both the shoes and underwear. -DOE Los Alamos National Laboratory Waste Management team has recovered the contaminated items from ARRA with a chain of custody for the record. "The Los Alamos National Laboratory has released the following information regarding this event: " 'Los Alamos National Laboratory is investigating the inadvertent spread of some Technetium-99 by employees and contractors at the Lujan Neutron Scattering Center at LANSCE [Los Alamos Neutron Science Center]. It's been determined that about a dozen people were exposed, and some tracked small amounts of Technetium 99 off-site. The contamination poses no danger to the public. " 'The Laboratory and Department of Energy RAP teams (Radiological Assistance Program) have been working to survey, assess, and where needed, decontaminate all affected people and property. The teams will continue to address all possible escape paths to be certain that all off-site contamination has been appropriately characterized and remediated. So far, based on multiple direct measurements, no exposures to Lab workers or the public pose a health risk.'" "The Agency [ Arizona Radiation Regulatory Agency] continues to investigate. "The Governor's Office, state of New Mexico and the U.S. NRC are being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2012-09-06
48247 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-29 08:57 | 2012-08-29 10:00 | 2012-08-31 | PARTIAL LOSS OF PLANT RADIATION MONITORING SYSTEM REMOTE READOUT "On August 29, 2012, power was removed from SCADA B of the Radiation Monitoring System (RMS) to perform a planned system modification. During this period, data for most Unit 2 radiation monitors will not be electronically available in the emergency response facilities and will not be supplied to the Emergency Response Data System (ERDS), if activated. System alarms and data displays will still be available to the plant operators in the Control Room. The expected duration of RMS remote data partial inoperability is approximately 72 hours. The loss of Unit 2 remote readout capability requires compensatory measures to be used for the acquisition of radiological data in the emergency response facilities. These compensatory measures have been communicated to the emergency response organization. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the portions of the RMS are inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An update message will be provided when the RMS is restored. "The NRC Resident and Region IV EP Inspectors have been notified." * * * UPDATE FROM ALAN MARZLOFF TO DONALD NORWOOD AT 1921 EDT ON 8/31/2012 * * * "This is a follow-up to ENS report number 48247. The Radiation Monitoring System (RMS) alarms and data displays have been restored to the Comanche Peak emergency response facilities (ERFs) following completion of planned system modifications. The emergency assessment capability of the Comanche Peak emergency response facilities have been re-established [as of 1821 CDT]. The NRC Resident has been notified." Notified R4DO (Azua). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-29
48246 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-28 17:00 | 2012-08-29 00:16 | 2012-09-08 | MITIGATING ACTIONS IMPLEMENTED FOR INOPERABLE CONTROL ROOM ENVELOPE "On August 28, 2012, 17:00 PDT, Pacific Gas and Electric Company (PG&E) identified additional release pathways that could affect the control room (CR) operator dose following a Large-Break Loss-of-Coolant Accident (LBLOCA). Consequently, PG&E declared the control room envelope (CRE) inoperable and is establishing mitigative actions in accordance with TS 3.7.10, Action B.1, 'Initiate action to implement mitigating actions' immediately, and Action B.2, 'Verify mitigating actions ensure CRE occupant exposures to radiological hazards will not exceed limits, and CRE occupants are protected from smoke and chemical hazards' within 24 hours. "PG&E is establishing mitigative actions in accordance with TS 3.7.10 and RG 1.196. These mitigative actions are for operations control room personnel to administer potassium iodide and don self-contained breathing apparatus equipment in a timely fashion should a LBLOCA occur. They will be communicated and controlled by a standing order to the control room staff. "PG&E previously established controls on other release pathways that offset the potential increases to the maximum predicted offsite dose due to the new release pathways. No increase in maximum predicted offsite dose is expected from the new release pathways. "Diablo Canyon (DCPP) is making this 8-hour, non-emergency notification under 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D). "Plant personnel notified the NRC Resident Inspector." * * * UPDATE AT 1600 EDT ON 9/8/12 FROM GLEN GOELZER TO PETE SNYDER * * * "PG&E is retracting EN 48246, based on the results from a new dose analysis coupled with compensatory measures implemented to ensure that the analysis input parameters and assumption will not be inadvertently exceeded. The analysis concluded that the CRE was operable and that CR doses remained below regulatory limits. "Plant personnel notified the NRC resident inspector." Notified R4DO (Gaddy). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-08-29
48245 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-08-28 15:00 | 2012-08-28 18:51 | 2012-08-28 | TECHNICAL SUPPORT CENTER DETERMINED TO BE NON-FUNCTIONAL DUE TO LOW RECIRC FLOW "At 1500 CDT on Tuesday, August 28, the Callaway Plant Technical Support Center (TSC) was declared non-functional due to ventilation recirculation flow rate outside of normal limits. "Efforts are underway to restore TSC ventilation recirculation flow rate to normal. "If TSC activation is necessary during the period of TSC non-functionality, the Emergency Coordinator will evaluate the suitability of the facility for the specific conditions of the event. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the unavailability of an emergency response facility. "The NRC Resident Inspector has been notified" * * * UPDATE FROM MATT SELLERS TO DONALD NORWOOD AT 1517 EDT ON 12/29/2012 * * * "The TSC was restored to functional status at 1228 (CDT) on August 29, 2012." The licensee notified the NRC Resident Inspector. Notified R4DO (Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-28
48244 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-08-26 | 2012-08-28 18:11 | 2012-10-01 | MISSISSIPPI AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK INVOLVED IN AN ACCIDENT The following information was obtained from the state of Mississippi via email: "DRH [Mississippi Division of Radiation Health] was notified 8/26/2012 by MEMA, Mississippi Emergency Management Agency, regarding an overturned radiography truck that occurred on Hwy 45 south of Macon, Mississippi. Two Licensee personnel were involved in the wreck with minimal injuries. The camera remained secured in the overpack but separated from the destroyed dark room. Surveys were performed of the overpack and camera by the driver after the wreck. The driver and MS Highway State Patrol Officer waited with the overpack and camera until DRH and the Licensee's ARSO arrived on site to take possession of the camera." MS Report Number: MS 120004 * * * UPDATE FROM JAYSON MOAK TO HOWIE CROUCH VIA EMAIL ON 10/01/12 AT 1547 EDT * * * "Licensee's leak test reported to DRH was less than 0.005 microCuries." Notified R4DO (Powers) and FSME Events Resources via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-09-05
48243 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-08-24 | 2012-08-28 17:37 | 2012-09-10 | MISSISSIPPI AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK SOURCE The following information was obtained from the state of Mississippi via email: "DRH [Mississippi Department of Radiation Health] was notified on 8/27/2012 by Licensee's RSO regarding a stuck source incident that occurred on 8/24/2012 while performing industrial radiography at a temporary job site in Mississippi. "The RSO claims the camera (880D) fell onto the guide tube during one of the shots and crimped the guide tube preventing the source from retracting back into the camera. The RSO suspects the technician may have pulled on the cranks while trying to crank back in the source after the shot. This could have then caused the camera to fall onto the guide tube and crimp it. "The restricted area boundary was readjusted to one (1) mR/hr, maintained, and the RSO was called by the radiographers at the job site. An ARSO and technician from the company who are trained in source retrieval arrived at the job site and retrieved the source. The camera was wiped and leak tests were submitted for analysis. "The Licensee's ARSO received 82 mR and the technician received 8 mR/hr from actions taken during the source retrieval." MS Report Number: MS 120003 * * * UPDATE AT 1558 EDT ON 09/10/12 FROM JAYSON MOAK TO S. SANDIN * * * The following update was received from the State of Mississippi via email: "Test for leakage and/or contamination received from the Licensee was less than .005 microCuries." Notified R4DO (Lantz) and FSME via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-09-05
48242 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-28 | 2012-08-28 17:27 | 2013-05-03 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following report was obtained from the Arkansas Radioactive Materials Program via e-mail: "On August 27, 2012, the Radiation Control Program of Arkansas received notification from the Arkansas Department of Emergency Management that a tractor trailer had run over a nuclear gauge at the 192 mile marker on Interstate 40 near Hazen, Arkansas. "The driver of a Motorists Assist Truck familiar with moisture density gauges identified the gauge parts on the side of the highway. The gauge had been struck by a vehicle and broken up. The driver reported the presence of the gauge parts to his construction company Project Manager who in turn notified Highway Police. At 1914 the west bound lane of Interstate 40 was closed and remained closed until 2155. The Highway Police asked for assistance from the Radiation Safety Officer of the Arkansas Highway and Transportation Department (AHTD) who drove to the scene. "The 44 millicurie, Americium-241:Beryllium source was still contained within the original threaded cavity with the Caution-Radioactive Material label covering it. The base of the gauge was broken to the point that only the threaded cavity and surrounding lead remained. "The 9 millicurie, Cesium-137 source remained attached to the source rod and inside the original shielding. The shielding was sheared off just above the tungsten sliding block (shutter). "The AHTD Radiation Safety Officer, upon arrival, secured the Americium-241:Beryllium source in a polyethylene box brought to the scene. The Cesium-137 source was removed from the gauge shielding by the AHTD RSO and this source was placed in a lead shield brought to the scene. "Two Health Physicists from the Arkansas Radiation Control Program were also dispatched and upon arrival took wipes of both sources. These smears were field counted utilizing a Ludlum-2241 and Ludlum 44-9 pancake probe. No loose contamination was found. "All potential serial numbers were recorded and the sources were transferred to the Radiation Control Program by the AHTD RSO. The Health Physicists transported the sources to a secure storage area at the State Health Department. "On Tuesday morning, Troxler identified the owner of the gauge by the serial number. The gauge is a Model 3430, Serial Number 21024. The gauge is owned by Anderson Engineering of Little Rock, Arkansas. Arkansas Radioactive Material License Number ARK-0519-03121. "It appears that an Anderson Engineering technician had been working at a construction job site in De Valls Bluff, Arkansas. On Monday evening, he left this job site and returned to the Anderson Engineering Little Rock Office. The gauge was left unsecured in the back of the pickup. On Interstate 40 West at mile marker 192, the gauge fell out of the pickup bed, where it was struck by at least one vehicle. Upon arrival at the Anderson Engineering offices, the technician removed the Troxler Gauge Storage Box from the pickup bed and noted that it was empty. The technician believed that he had left the gauge at the job site. On the morning of August 28, 2012, he returned to the jobsite to search for the gauge. "On Tuesday, August 28, 2012, the Radiation Safety Officer was contacted and retrieved the two sources from the Arkansas Department of Health and secured these in the Anderson Engineering permanent storage area. "The Arkansas Radiation Control Program has assigned Incident Number AR-2012-006 and is continuing to investigate." * * * UPDATE FROM STEVE MACK TO CHARLES TEAL ON 5/3/13 AT 1012 EDT * * * The following was received from the State of Arkansas via email: "The sources were disposed of through the manufacturer on 2/22/2013. The Department [Arkansas Department of Health] considers this event to be closed." Notified R4DO (Haire) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-09-05
48241 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-08-28 | 2012-08-28 15:54 | 2012-08-30 | SAFEGUARDS REPORT CONCERNING PROTECTIVE ACTIONS IN ADVANCE OF HURRICANE ISAAC Defensive protective actions were taken in accordance with site security plans in anticipation of high onsite winds from Hurricane Isaac. Contact the Headquarters Operations Officer to additional details. The NRC Resident Inspector has been notified. * * * UPDATE ON 8/30/12 AT 1106 EDT FROM JESSE BOHNENKAMP TO DONG PARK * * * The licensee has returned to their normal security posture. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R4IRC, R4DO (Proulx) and 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-08-28
48240 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-08-28 11:25 | 2012-08-28 13:23 | 2012-10-03 | DISCOVERY OF POSSIBLE UNCONTROLLED SAFEGUARDS INFORMATION Discovery of possible uncontrolled safeguards information. Compensatory actions taken. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION AT 1735 EDT ON 10/03/12 FROM KLINT KUDLACEK TO HUFFMAN * * * Subsequent review by the licensee determined that there was not uncontrolled safeguards information. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. R4DO (Powers) notified. 73.71 Group informed via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-08-28
48239 | -1 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP |  | 2012-08-28 10:11 | 2013-07-15 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - ALERT - HIGH CO2 CONCENTRATION IN A SAFE SHUTDOWN AREA "At 0927 EDT on 08/28/2012, it was identified that access to a table H-1 Safe Shutdown Area had been prohibited and that an ALERT had not been declared as required by Surry EPIP-1.01, EAL HA 3.1. At 0900 EDT on 08/27/2012, Electrical Maintenance was performing a surveillance on the Unit 2 Cable Vault and Cable Tunnel Low Pressure CO2 System. A high CO2 level was observed using portable gas detection equipment and access to the space was prohibited for a period of approximately 20 minutes. This report is being made in compliance of VPAP-2802, section 6.3.3(h), which states that a one hour report is required if an Emergency Action Level (EAL) is exceeded, the basis for the emergency class no longer exists at the time of discovery, and no other reasons exist for an emergency declaration." The licensee will notify the NRC Resident Inspector and Virginia Emergency Management Agency. * * * RETRACTION ON 7/15/13 AT 1342 EDT FROM BARRY GERBER TO DONG PARK * * * "Based upon initial air monitor readings, EN #48239 reported that an oxygen deficient condition existed in a Table H-1 area for approximately 20 minutes. When the initial information was presented to the Shift Manager on 08/28/2012, it was determined that a one-hour report should have been declared in accordance with EPIP-1.01, Emergency Action Level HA 3.1, which states that an ALERT condition exists if 'access to a Table H-1 area is prohibited due to toxic, corrosive, asphyxiant or flammable gases which jeopardize operation of systems required to maintain safe operations or safely shutdown the reactor.' Since the ALERT condition was not recognized on 08/27/2012, a one-hour report was deemed necessary. "A root cause evaluation reviewed the oxygen monitor data and determined that the maximum time of oxygen deficiency was approximately 8 minutes. Operator Time Critical Actions were reviewed to determine whether prohibition of access to the Cable Vault and Cable Tunnel for approximately 8 minutes would jeopardize operation of systems required to maintain safe operations or safely shutdown the reactor. No specific references to activities within this area were identified. Therefore, this event was determined not to be an Alert. "The root cause evaluation also noted that Operations was notified of the test, administrative control was established for the CO2 Tank shutoff valve, an Electrician was posted in the control room to notify Operations of alarms associated with the test, a fire watch posted, and the test areas were posted and evacuated. The brief period of time the condition existed did not result in a threat to safe plant operation or the health of plant personnel. Therefore, this event was determined not to be an Unusual Event in accordance with EPIP-1.01, Emergency Action Level HU 3.1, which states, 'report or detection of toxic, corrosive, asphyxiant or flammable gases that have or could enter the Owner Controlled Area in amounts that can affect normal plant operations.' "This notification is being made to retract the report made on 08/28/12 based on the above discussion. The NRC Resident [Inspector] has been notified." Notified R2DO (Nease). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2012-08-28
48238 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-08-28 03:32 | 2012-08-28 06:13 | 2012-08-28 | AUTOMATIC REACTOR TRIP FOLLOWING FAILURE OF A FEEDWATER REGULATING VALVE "On August 28, 2012, Watts Bar Nuclear Plant Unit 1 reactor automatically tripped due to low level in steam generator (SG) #2. The low level resulted when the Main Feedwater Control Valve for SG#2 (1-FCV-3-48) failed closed. This is being reported under 10CFR 50.72 (b)(2) (iv) (B). "Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. This is being reported under 10CFR 50.72(b)(3) (iv)(A). "All Control and Shutdown rods fully inserted. "All safety systems responded as designed. The unit is currently stable in Mode 3. "The NRC Senior Resident has been notified." Decay heat is being removed to the main condenser via condenser steam dumps. The plant is in its normal shutdown electrical lineup. No steam safety or relief valves lifted during the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-08-28
48237 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2012-08-27 12:00 | 2012-08-27 20:48 | 2012-08-31 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "At 12:00 CDT maintenance personnel identified a pinhole leak from the Division 1 Service Water System piping in the Service Water Pump Room. Division 1 Service Water [SW] was declared inoperable and LCO 3.7.2 Condition A was entered due to a potential loss of structural integrity. This directs entry into LCO 3.8.1 for Diesel Generator #1 made inoperable by SW. DG 2 was previously made inoperable at 05:39 CDT on 8/25/2012 due to an unrelated issue regarding rain water inleakage into the DG 2 Room. Control Room Emergency Filtration system [CREFs] is aligned to Div 1 power. LCO 3.7.4 Condition A is applicable, requiring restoration of CREFs to operable status within 7 days. TRM LCO 3.6.1 condition A and B also apply, requiring (A) Restoration of containment spray subsystem A to OPERABLE status within 7 days and (B) Restore one RHR containment spray subsystem to operable status within 8 hours. "DG 1 and DG 2 comprise the onsite emergency power systems. Both DGs inoperable is reportable per 10CFR50.72(b)(3)(v)(D) as a condition that could prevent fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. "Actions were taken to expedite repairs of the DG 2 roof leak and to further characterize the Division 1 SW piping leak. LCO 3.8.1 Condition E allows 2 hours to restore one DG to operable status or enter Condition F, to be in Mode 3 in 12 hours, which was entered at 14:00. Repairs to the roof leak on the DG 2 room were completed, after which DG 2 was declared Operable at 18:30. LCO 3.8.1 Conditions E and F required shutdown were exited at this time. LCO 3.8.1 Condition B for DG 1, and 3.7.2 for SW Loop A, continue to be active. Planning to repair the SW piping pinhole leak is continuing. There were no adverse grid conditions during the period both DGs were inoperable. "The NRC Resident has been informed of the condition. No media or press release is planned at this time." * * * RETRACTION FROM FRED SCHIZAS TO DONALD NORWOOD AT 1802 EDT ON 8/31/12 * * * "This notification is being made to retract Event Notification EN #48237 which reported a loss of safety function due to both onsite Emergency Diesel Generators (DGs) being simultaneously INOPERABLE. On 8/25/12 at 0539 CDT, DG#2 was declared INOPERABLE due to rain water in-leakage into the DG#2 room. Condition B of LCO 3.8.1 was entered. and Required Actions were being taken to restore the INOPERABLE DG within 7 days. Subsequently, on 8/27/12 at 1200 CDT Maintenance personnel identified a pinhole leak from the Division I Service Water System piping in the Service Water Pump Room. Division I Service Water was declared INOPERABLE and LCO 3.7.2 Condition A was entered due to a potential loss of structural integrity. This prompted entry into LCO 3.8.1 Conditions E and F which require shutdown, because DG#1 was made INOPERABLE by SW. Both DG's INOPERABLE is reportable per 10CFR50.72.b.3.v.D as a condition that could prevent fulfillment of a safety function of structures or systems needed to mitigate the consequences of an accident. Repairs to the roof leak on the DG#2 room were completed, after which DG#2 was declared Operable at 1830 CDT on 8/27/2012. LCO 3.8.1 Conditions E and F were exited at the time. LCO 3.8.1 Condition B for DG#1, and 3.7.2 for SW Loop A, continued to be active, and planning to repair the pin-hole leak continued. "Subsequent investigation and UT examinations provided data which enabled SW Division 1 and DG#1 to be declared OPERABLE on 8/30/2012 at 0528 CDT. An evaluation of this condition concluded that further characterization of the SW Piping Pin-Hole leak enabled ASME Code Case N-513-3 to be applied to determine piping structural integrity was maintained. SW ability to supply required flows to its loads is not adversely diminished, because the flaw is small. Water leaking from the flaw will not adversely affect any other equipment important to safety by spray or flooding. The piping is compliant with ASME code. Based on this evaluation, the Division 1 SW system can perform its safety function and is OPERABLE. "With Division 1 SW subsystem capable of fulfilling its safety function, DG#1 was therefore also capable of fulfilling its safety function during the period of SW subsystem INOPERABILITY. Consequently, during the period of DG#2 INOPERABILITY, DG#1 was capable of fulfilling the safety function of the onsite emergency power system. NPPD therefore retracts Event Notification EN 48237. "The NRC Resident has been informed of this retraction." Notified R4DO (Azua). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-08-27
48236 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-08-27 15:26 | 2012-08-27 18:36 | 2012-08-27 | OFFSITE NOTIFICATION DUE TO HAZARDOUS MATERIAL SPILL "Notification was made to Missouri Department of Natural Resources and the EPA National Spill Response Center of a Neutralization Tank discharge piping leak on 8/27/12 at 1526 hrs. (CDT). Subsequent testing of the leaking fluid at 1430 hrs. revealed the pH of the leaking fluid was 13, which is a characteristic hazard waste. Reportable quantity is 100 lbs. The estimated total volume released was less than 100 gallons, but greater than 100 lbs. This spill was reported to offsite organizations. Therefore, this event is reportable to the NRC per 10CFR50.72(b)(2)(xi). Mitigating strategy is to neutralize the contents of the tank, and the leaking fluid is being absorbed by absorbent materials." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-27
48235 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-08-24 16:50 | 2012-08-27 14:04 | 2012-08-27 | AGREEMENT STATE REPORT - IODINE-125 SEALED SOURCE SEED FAILURE The following information was supplied by the State of Ohio Department of Health via e-mail: "RE: Leaking I-125 prostate sealed source "Date: August 24, 2012 "Source Type: I-125 Prostate Seed, Model STM1251, distributed by Bard "Activity: 0.334 mCi/seed on 8/24/12 "During a prostate seed implant a seed became jammed in the Mick gun. The gun was placed on sterilization table and examined. It was found that the seed was lodged in the Mick cartridge. The cartridge that held the seed was removed from the gun over a basin full of water and the end result was the seed broke into two pieces. One piece was recovered in the water and the second was still lodged in the end of the Mick cartridge. The area was surveyed for any additional contamination and none was found. All personnel involved in the case were surveyed and no additional contamination was found. "The broken I-125 seed was wiped and analyzed with the equipment below: "Well Chamber- Captus 3000 s/n CNV-376 (located in Nuclear Medicine) "Background- 339 cpm "Wipe- 17.63 Mcpm = 21.24 Mdpm = 9.6 ÁCi "The wipe test revealed that the removable contamination exceeds the 0.005 ÁCi. "Bard, the company that supplied the seeds was contacted. The leaking I-125 seed and contaminated water was sealed and placed in the radiation waste storage area." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-09-04
48234 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-08-27 | 2012-08-27 11:10 | 2012-08-27 | TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "Planned maintenance activities are being performed today (August 27, 2012) to the Technical Support Center (TSC) HVAC. The work entails removing power to system dampers rendering the TSC non-functional during the performance of this work activity. This work activity is planned to be performed and completed expeditiously within about 24 hours including establishing and removing the clearances and performing post maintenance testing. "If an emergency condition occurs that requires activation of the TSC, plans are to utilize the TSC during the time this work activity is being performed as long as habitability conditions allow. The Emergency Response Organization duty team members will be relocated to alternate locations if required by habitability conditions in accordance with emergency implementing procedures." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2014 EDT ON 8/27/12 FROM STRUSINSKI TO HUFFMAN * * * The TSC ventilation maintenance has been completed and the TSC was returned to service at 2005 EDT on 8/27/12. R2DO (Haag) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-27
48233 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-08-26 15:30 | 2012-08-26 17:05 | 2012-08-26 | INADVERTENT EMERGENCY SIREN ACTUATION The Calvert Cliffs control room was notified at 1530 EDT on 8/26/2012 by a site employee that Siren C15 was intermittently alarming. This is a repeat of a similar actuation that had been reported in EN #48231. The licensee has notified the Calvert County Control Center that the siren had actuated. The licensee has deactivated the siren until further investigation and repairs can be accomplished. As was noted in the original event, adverse inclement weather conditions existed at the time the siren was alarming. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-26
48232 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2012-08-26 12:39 | 2012-08-26 16:00 | 2012-08-26 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE FELT ONSITE A Notice of Unusual Event (NOUE) was declared at San Onofre due to an earthquake felt on site (EAL HU1.1). The US Geological Survey indicates that there was a 5.3 magnitude earthquake near Brawley California, about 125 miles southeast of the plant. There were no indication of any impact to site operations other than being felt by personnel. Equipment inspections and walkdowns are in progress. The licensee has notified state and local authorities. The NRC Resident Inspector will be notified. Notified other FEDS (FEMA, DHS, DHS NICC and Nuclear SSA via email). * * * UPDATE FROM BAYER TO HUFFMAN AT 1713 EDT ON 8/26/12 * * * On August 26, 2012 at 1346 PDT, San Onofre exited the Unusual Event based on an earthquake felt on site. Shortly after exiting the UE, the licensee felt more shaking in the control room. The licensee confirmed with the US Geological Survey that there has been an aftershock. The aftershock was approximately the same magnitude (5.4) and location as the original earthquake (about 125 southeast of the site). The licensee declared another unusual event at 1403 PDT. The licensee will re-perform all equipment walkdowns and inspections. The NRC Resident Inspector has been notified and is reporting to the site. R4DO (Hay), NRR EO (Lubinski), and IRD (Gott) notified. * * * UPDATE AT 2352 EDT ON 8/26/2012 FROM ADAM BOW TO MARK ABRAMOVITZ * * * "Exited the NOUE HU1.1 - Earthquake at 2017 PDT on 8/26/12." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Hay), NRR (Lubinski), IRD (Gott), DHS, FEMA, and DHS NICC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-08-26
48231 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-08-26 01:10 | 2012-08-26 02:41 | 2012-08-26 | INADVERTENT EMERGENCY SIREN ACTIVATION "Calvert Cliffs control room was notified at 0110 EDT on 8/26/2012 by the Calvert Control Center (911) that sirens in the Calvert County area were activated. Reports were narrowed down to Lloyd Bowen Rd, Siren C15. At this time the siren is believed to be getting water in the controls due to inclement weather in the area. Maintenance Support is on their way to locally confirm and isolate the suspect siren. "This event is reportable as a 4-hour Non-Emergency Notification 10CFR50.72(b)(2)(xi) as 'Any event resulting in notification to other government agencies that has been or will be made.'" The licensee notified the NRC Resident Inspector. See related EN #48233. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-26
48230 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-08-24 13:32 | 2012-08-24 17:33 | 2012-08-24 | PARTIAL LOSS OF REACTOR BUILDING EMERGENCY ASSESSMENT CAPABILITY "At 1332 CDT on 8/24/12 a failure of power supply RMA-ES-53A was indicated in the Control Room. The power supply was declared Non-Functional. This failure results in the loss of ability to remotely measure and quantify radiological conditions (radiation levels) for multiple areas in the Reactor Building. The power supply provides power to RMA-RA-1 through RMA-RA-10. RMA-RA-11 through RMA-RA-30 remain fully functional and indicating normally. "The loss of ability to monitor and quantify radiological conditions in multiple areas of the Reactor Building represents a major loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii). As specified by station procedures, compensatory measures have been implemented to survey affected areas by installation of portable monitoring devices and trending radiological conditions. RMA-RA-1 through RMA-RA-10 are used for EAL determinations. "The Work Week Director has been notified to initiate repairs." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-24
48229 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-08-23 | 2012-08-24 15:25 | 2012-08-24 | AGREEMENT STATE REPORT - PATIENT UNDEREXPOSURE USING YTTRIUM-90 SIR-SPHERES TREATMENT The following event was received from the Pennsylvania Bureau of Radiation Protection via facsimile: "Event type: A medical event (ME) involving the administration of yttrium-90 SIR-Spheres which is reportable under 10 CFR 35.3045(a)(1)(i). "Notifications: On August 24,2012, the Department's Southeast Regional Office received notification via a phone call and follow-up electronic correspondence about this ME. "Event Description: The patient was being treated for disease of the liver and received 71% of the intended dose as identified by post treatment measurements. The treating physician, who also is the referring physician, notified the patient. "Cause of the Event: Currently under investigation and unknown at this time. "Actions: No harm to the patient is expected. The Department plans to do a reactive inspection" PA Report Number: 120026 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-09-03
48228 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-08-23 19:45 | 2012-08-24 14:20 | 2012-08-24 | MATERIAL CONTROL AND ACCOUNTABILITY ALARM RESOLUTION "10 CFR 74.57 (f)(2) requires notification within 24 hours that a Material Control & Accountability (MC&A) alarm resolution procedure has been initiated. In the Solvent Extraction Area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure has been initiated, this notification is being made. There was no material loss and the issue was resolved on 8/24/2012. "MC&A process monitoring tests for material balance were run as specified by applicable procedures and requirements. Based on the test results for Building 333 solvent extraction area, the test limit was exceeded. The investigation was completed and the alarm was resolved on 8/24/2012. "There was no actual or potential safety consequences to workers, the public, or the environment." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2012-08-28
48227 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-08-23 08:00 | 2012-08-24 13:17 | 2012-08-24 | AGREEMENT STATE REPORT - DAMAGED AND UNACCOUNTED FOR TRITIUM LIGHT SOURCES The following information was received from the Arizona Radiation Regulatory Agency via e-mail: "At approximately 8:00 AM on August 23, 2012, the Agency was informed that the Licensee had one damaged light source, two light sources unaccounted for, and identification of an intake of radioactive material by two TLS Systems employees. "The Licensee was taking back 148 drogue light assemblies for disposal/recycling. After receiving the sources, the Licensee noticed minute fragments of a light source on a stainless steel bench top on which the sources were being examined. The fragments were placed in empty liquid scintillation vials and an initial decontamination of the workbench was performed. In addition, an inventory of the sources was performed and 297 intact sources were counted. A total of 298 sources implied 149 drogue light assemblies, not 148 as indicated by the company who returned the sources. Also, 150 radiation labels, stainless steel housings, and Lucite inserts were counted, which would indicate 300 light sources. "Each drogue light assembly contained two mb-Microtec Model T-4376-1 tritium light sources. The sources had an initial activity of 450 millicuries each. The drogue lights are approximately 4 years old. "Bioassays were given to individuals present in the lab and are currently awaiting results. "The investigation into this event is ongoing. The U.S. NRC and AZ governor's office have been notified." AZ Report Number: 12-013 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2012-09-03
48226 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-08-23 09:00 | 2012-08-24 13:15 | 2012-08-24 | AGREEMENT STATE REPORT - MISSING AMERICIUM-241 AND RADIUM-226 SOURCES The following information was received from the Arizona Radiation Regulatory Agency via e-mail: "At approximately 9:00 AM August 23, 2012, the Agency was informed that the licensee lost a 3 millicurie Americium-241 source and a 0.9 microcurie Radium-226 source. "The licensee was performing a clean-up at their facility between the dates of February 15, 2012 and June 11, 2012. The licensee assumes during those dates is when the sources went missing. However, the radiation safety officer for the license left on October 21, 2011 and the licensee cannot verify the location of the sources after that date. "The licensee is currently interviewing employees involved in the cleanup to attempt to determine the location of the missing sources. "The Arizona Regulatory Agency continues to investigate the event. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." AZ Report Number 12-014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2012-09-03
48225 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-08-06 | 2012-08-23 16:50 | 2012-08-23 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT RELATED TO USE OF I-125 SEED MESH IMPLANT The following report was received from the North Carolina Radiation Protection Section via e-mail: "On August 6, 2012 [the North Carolina Radiation Protection Section, NC-DHHS, RPS] received notice of a possible device failure. [Follow-up by NC-DHHS, RPS was conducted on August 8, 2012, by contacting the Authorized Medical Physicist (AMP)]. "A patient was given an invasive procedure (to right lung) using a mesh that contained permanent I-125 seeds attached as an implant. The implant contained 50 seeds with 5 strands of 10 seeds per strand. The total activity was 16.4 mCi on May 31, 2012. "The patient was discharged from hospital on June 9, 2012. "[The] patient was readmitted to the hospital on July 4, 2012. On July 7, 2012, x-rays revealed an abscess in the right lung with approximately 38 notable seeds in place. On July 9, 2012, the radiation oncologist requested chest and abdomen films. At that time, 35 seeds were noted in the right lung with 3 located in the abdomen. Per the patient; he was coughing up phlegm and subsequently swallowing it. The patient was made aware of seed mobility. "On July 18, 2012 (decayed to 0.187 mCi/seed), there were 13 seeds confirmed in the lung and 17 seeds in the abdomen (total 5.62 mCi). "Upon out-patient visit on July 4, 2012, there were 6 seeds remaining in the chest and 8 in the abdomen; there were no appreciable side effects noted per the radiation oncologist. "Nine seeds were recovered during the patient's hospitalization and placed in the Nuclear Medicine Hot Lab. "The device manufacturer was notified by immediate supervisor. "The above information was received August 6, 2012 via electronic mail and August 10, 2012 via letter. "The below information was received August 20, 2012 via electronic mail. 'This is the follow-up letter as requested in our conversation on Aug 08, 2012. To review, on May 31, 2012, fifty Iodine-125 seeds were implanted in a patient as a permanent implant in the right lung. The activity was 16.4 mCi on that date. Upon re-admission into the hospital, a chest x-ray was done on July 07. Approximately 38 of the 50 original seeds were visible on that date. If one merely accounts for the change in seed count (38/50), the area of the right lung implant received 76% of its intended dose. Therefore, the total dose delivered differs from the prescribed dose by 20% or more. 'This describes a Medical Event, as defined by section 15A NCAC 11.0364 (1) (A). 'On August 08, the patient came to the Radiation Oncology department. Final x-rays revealed no seeds within the lungs or abdomen. 'As an additional note, the failure of the device has been reported to the FDA by our hospital administration and the company that manufactures the device.' "(Intended dose appears to be 25 Sv/hr at .1 cm (contact) on June 9 50 seeds = 16.4 mCi = 25 Sv/hr@ .1 cm (contact) .328 mCi/seed initial activity "On day number 25 (July 4) 38 seeds remain in lung (.328 mCi/seed with 1/2 life factor = .245 mCi/seed) 38*.245 mCi= 9.31 mCi = 14.67 Sv/hr@ .1 cm (contact) "If all seeds were intact the result would be 12.25 mCi -> resulting in a 9.31 mCi/12.25 mCi = 76% "A device NMED notification maybe required and have requested such from the AMP. More to follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-08-31
48224 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-08-20 13:30 | 2012-08-23 13:00 | 2012-08-23 | AGREEMENT STATE REPORT - TEN TRITIUM EXIT SIGNS DAMAGED The following report was received from the Wisconsin Radiation Protection Section via e-mail: "On August 20, 2012, at 1:30 pm the Wisconsin Radiation Protection Section, received a telephone notification from NRC Region III personnel that 10 tritium exit signs, that originally contained 7.5 Ci at the time of purchase 7-10 years ago, were placed in a compactor and damaged at a PSC Environmental Services, LLC facility in Detroit, Michigan (refer to NRC event notification #48205). "The ten exit signs came from a Bed Bath & Beyond store in Wausau, WI. On August 20, 2012 at 2:00 pm, the Vice President of Loss Prevention and Safety was contacted and he informed the state that 14 tritium exit signs were being replaced with LED signs (this is being done nation-wide at all Bed Bath & Beyond stores) at the Wausau location and were intended to be returned to the manufacturer for disposal. The 4 remaining signs are in a secure location within the store. "The Wisconsin Radiation Protection Section will be performing a site visit in Wausau to verify the four remaining signs are intact and will be performing an investigation into the root cause of this incident." Wisconsin Report: WI120011 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-08-31
48223 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2012-08-22 | 2012-08-23 09:21 | 2013-04-08 | PART 21 - DEFECT DUE TO CHANGE IN MANUFACTURING PROCESS CAUSING RELAY FAILURE IN SAFETY RELATED SYSTEMS The following is summary of the information received from the licensee: "The basic component is an Eaton-Cutler Hammer Type ARD660UR DC relay that is commercially dedicated by Westinghouse for use in safety related systems at Palo Verde Units 1, 2 and 3. Except for the Palo Verde plants, Westinghouse is not aware of any other plant that uses this relay as a safety-related component in normally energized applications. "The relay contacts failed to change state when required to do so during postulated events and/or surveillance testing. Westinghouse has identified the kick-out spring as a possible contributing factor for the relay failure due to stress corrosion cracking. Other anomalies such as relay core barrel tolerance and potential material deficiencies are currently under review. Based upon testing at APS, the relay failure rate is low and non-reproducible. This indicates that a combination of factors could be resulting in the failures with different causes for each failure. Results of testing do not identify a common cause for the failures. For ARD660UR relays used in normally de-energized applications, the kick-out spring will be compressed for only a short period of time and exposure to additional heat generated by intermittent coil energization will be minimal. For relays in normally de-energized applications, it is not expected that the force provided by the kick-out spring will decrease significantly over time and the contacts will change position when the relay coil is de-energized. Westinghouse has not received any reports to date of relay contacts failing to properly change position when the relay goes from a de-energized to an energized state. Because of the kick-out spring's limited exposure to compression and heat generated by the relay coil, it is expected that the springs will perform as intended in normally de-energized applications for the qualified life of the relay. "Identification of the firm constructing the facility or supplying the basic component which fails to comply or contain a defect. "Westinghouse Electric Company "1000 Westinghouse Drive "Cranberry Township, Pennsylvania 16066" * * * UPDATE AT 1445 EDT ON 04/08/13 FROM JAMES A. GRESHAM TO S. SANDIN * * * The following update was received via fax and is summarized below: "During the investigation into the cause of the ARD660UR relay sticking, many physical and performance aspects and components of the relay were analyzed, as well as the entire manufacturing process. This investigation uncovered several issues that contributed, or could contribute, to the failure of the relay to release when de-energized. "Based on analysis by Westinghouse, with support from Eaton Corporation, it was determined that the primary cause of the relay failure was a change in the manufacturing process in the plastics molding operation of this relay. This manufacturing change caused the moving cores to adhere to the inner diameter of the relay coil spool when a relay was continuously energized during testing by Westinghouse for longer than 21 days. This change in the manufacturing process began in May 2008 and continued until it was terminated in December 2012. Relay coils manufactured during this time may develop an adhesive like residue in the relay coil spools when energized for an extended period of time. This residue was found on the moving cores of relays which stuck during testing at a Westinghouse facility and relays returned from the customer. This residue was determined to be the primary cause of the relay issue. "Westinghouse shipped Palo Verde a total of 374 potentially affected Eaton-Cutler Hammer Type ARD660UR DC relays. "As a result of the investigation, Westinghouse recommended several manufacturing process improvements that are designed to prevent the reoccurrence of the issue. Eaton has agreed to implement these improvements prior to restarting the manufacture of these relays. Westinghouse is revising its commercial grade dedication process for these relays. This action ensures that the commercial grade dedication criteria include replacing the relay kick-out spring in each relay and verifies other relay enhancements have been implemented before future relays are shipped to the customer as safety related components. "Westinghouse recommends that each plant review the application requirements of each affected relay. If an ARD660UR relay is used in a normally energized application or is required to change state after being energized for at least 21 consecutive days and was manufactured between May 1, 2008 and December 31, 2012, Westinghouse recommends replacing the relay at the next convenient opportunity. "If an ARD relay manufactured during the May 1, 2008 and December 31, 2012 time frame is successfully, periodically cycle tested, this relay may be less susceptible to sticking." Notified R4DO (Deese) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-08-23
48222 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2012-07-20 | 2012-08-22 16:35 | 2012-08-22 | AGREEMENT STATE REPORT- 12 MISSING TRITIUM EXIT SIGNS The Iowa Department of Public Health provided a preliminary notification that 11 or 12 tritium exit signs are missing from a Bed Bath and Beyond store in Council Bluffs Iowa. The store has replaced all its tritium exit signs with LED exit signs. The tritium exit signs were removed by an electrical subcontractor specifically instructed to keep the removed signs segregated for special disposal by Shaw Industries. The removed tritium exit signs could not be located when Shaw arrived at the store to package and ship the signs. A representative for the store believes that either the signs were mixed with fluorescent lights that were being sent to a separate recycling facility or that the subcontractor may have inadvertently disposed of the tritium signs at an unknown location. The fluorescent light recycling facility has been contacted but was unable to find any evidence that the signs were sent to their location. The tritium exit signs were generally licensed with a nominal activity of 11.5 curies each. The sign manufacturer was Shield Source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-08-30
48221 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-08-22 08:01 | 2012-08-22 11:32 | 2012-08-22 | AUTOMATIC REACTOR TRIP DUE TO HIGH REACTOR COOLANT SYSTEM PRESSURE "On August 22, 2012, during a planned load reduction, Three Mile Island Unit 1 Reactor automatically tripped at 0801 EDT due to high reactor coolant system pressure as a result of a main feedwater transient. The cause of the main feedwater transient is still under investigation. The Emergency Feedwater System (EFW) actuated at 0801 EDT. "The electrical grid is stable and Unit 1 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via the Emergency Feedwater System (EFW) flow to both Steam Generators that are exhausting via the normal main condenser cooling loop under manual control. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip and EFW actuation except for manual operation of Turbine Bypass Valve control due to failure of the automatic control function. Three Mile Island Unit 1 remains stable in Hot Shutdown mode while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, and under 10 CFR 50.72(b)(2)(xi), due to an information release to local officials, both are four (4) hour reports. This event is also reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B), due to a valid actuation of the Emergency Feedwater System. "The licensee notified the NRC Resident Inspector." Licensee notified the State, local and other Government agencies. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2012-08-22
48220 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-08-22 02:28 | 2012-08-22 03:53 | 2012-08-22 | TECH SPEC REQUIRED SHUTDOWN DUE TO REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAK "On August 22, 2012, it was determined, based on a remote video camera inspection inside the secondary shield wall, that a primary system leak at a Pressurizer Heater bundle exists and is not isolable. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.6.4 does not allow any leakage through a nonisolable RCS strength boundary. The discovery of leakage from the Pressurizer Heater bundle is considered a degradation of a principal safety barrier. This condition does not represent a reduction in the public health and safety. "This is reportable as a 4-hour ENS notification under 10CFR50.72(b)(2)(i) due to the initiation of a nuclear plant shutdown required by the plant's Technical Specifications. "The licensee notified the NRC Resident Inspector." The licensee expects to also notify state and local government agencies of the shutdown. The current leak rate, as calculated by the plant process computer, is approximately .2 gallons per minute. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-08-22
48219 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-21 19:30 | 2012-08-21 20:13 | 2012-08-21 | DAMAGED PACKAGING CONTAINING RADIOACTIVE MATERIAL "In accordance with 49 CFR 171.15, Duke Energy contacted the Department of Transportation National Response Center at 1930 [EDT] on August 21, 2012, Report Number 1021811, to inform them of a breach of a package containing a limited quantity of radioactive material. This breach was considered 'breakage' in accordance with Title 49 of the Code of Federal Regulations, Transportation. Although the packaging of the radioactive material was damaged during transportation, the radioactive material itself was not released, and the damage did not result in any external radioactive contamination or any radiation exposure. This event did not result in any adverse impact to the health and safety of the public. The State of North Carolina (NC) has also been notified of this event. Mecklenburg County, NC will be notified of this event. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as a result of the notification to another government agency. "The safety significance of the breached package is minimal. "The condition will be entered into the Corrective Action Program for evaluation. Corrective actions will be determined based on the results of this evaluation." The container held a torque wrench calibration test tool and cable. The tools had penetrated the container, but no other damage to the tools was noted. The tools will be normally processed for use at the station. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-21
48218 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-08-21 | 2012-08-21 16:27 | 2012-08-21 | AGREEMENT STATE - RADIATION TREATMENT OVERDOSE RESULTING FROM A POTENTIAL GENERIC ISSUE The following information was provided by the State of Pennsylvania via facsimile: "On Monday, August 20, 2012, the licensee informed the Pennsylvania Department of Environmental Protection's Southcentral Regional Office of a medical event which occurred the same day. It is reportable within 24-hours under 10 CFR 35.3045(a)(1)(iii). "During the first fraction of radiation therapy treatment, using a Nucletron Corporation microSelectron HDR (High Dose Rate) Model 106.990 remote afterloader, the unit's treatment planning software malfunctioned, resulting in an overdose to the patient of approximately 76.5%. Facility staff also failed to complete a required worksheet which may have alerted the Authorized User to the dosage difference prior to treatment. A total dose of 600 cGy (rad) was delivered instead of the prescribed 340 cGy (rad). The patient was notified on the same day, while the referring physician was notified the following day. The treating physician anticipates no effect to the patient, however, dose reconstruction is currently in progress. We believe this incident also qualifies the event as an Abnormal Occurrence. "Cause of the event is equipment malfunction and human error. "Licensee is contacting a service provider for the HDR unit to investigate the incident, and if needed, repair the equipment. The Pennsylvania Department of Environmental Protection will be evaluating possible generic implications and plans to do a reactive inspection as soon as possible." PA Event Report No: PA120025 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-08-29
48217 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2012-08-20 15:30 | 2012-08-21 10:45 | 2012-08-21 | FITNESS FOR DUTY POLICY VIOLATION A non-licensed contract employee supervisor and a non-licensed contract employee committed a Fitness-For-Duty policy violation. Construction area access for both contract employees have been suspended, and the licensee has initiated an investigation. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2012-08-21
48216 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2012-08-08 | 2012-08-21 09:23 | 2012-08-21 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF TRITIUM EXIT SIGNS The following information was received from the State of New Hampshire: "On August 8, 2012, a [Bed Bath and Beyond Vice President] called to report the loss of seventeen tritium exit signs. After taking the signs down, they were stored for Shaw Environmental to package and ship them for disposal. While being stored, they were mistakenly taken by another contractor as part of the waste from light bulb removal. This removal was viewed on videotape after Shaw Environmental reported that the box of signs was missing from the storage area. "[The Bed Bath and Beyond VP] contacted RL Carriers (the removal contractor) to find out where they send the waste for disposal. The location was Waste Management in South Carolina. [The Bed Bath and Beyond VP] contacted Waste Management and was told that they had not received any exit signs but if they had, they would have sent them to Synergy Recycling in North Carolina. When contacted, Synergy Recycling stated that they had not received any exit signs. "The serial numbers for the 17 Tritium Exit Signs that cannot be located are listed below. The Manufacturer is Safety Light, model SLK-60. 301364 - 301367 301370 - 301376 301381 303792 303794 - 303797" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2012-08-29
48215 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2012-08-21 00:38 | 2012-08-21 07:50 | 2012-09-04 | BOTH EMERGENCY DIESEL GENERATORS INOPERABLE At 0038 EDT on 08/21/12, EDG "A" was declared inoperable after the Engineered Safeguards Actuation System (ESFAS) fuse failed . EDG "B" had been inoperable for planned maintenance since 2223 EDT on 08/15/12. With both EDGs inoperable, Unit 2 entered Tech Spec LCO 3.8.1.2 which requires suspension of all operations involving core alteration and positive reactivity additions. At 0713 EDT on 08/21/12, the licensee declared EDG "B" Operable exiting the Tech Spec LCO. The cause of the ESFAS fuse failure on EDG "A" is under investigation. The licensee will notify state and local agencies and has informed the NRC Resident Inspector. * * * RETRACTION FROM WAYNE WOOLERY TO DONG PARK AT 1027 EDT ON 9/4/12 * * * "The purpose of this call is to retract the report made on 8/21/2012, Event Number 48215. Upon further review, the fuse failure did not render the 'A' Emergency Diesel Generator (EDG) inoperable in MODE 5. If called upon, the safety functions would have been met. The Engineered Safeguards Actuation System (ESFAS) was repaired prior to restart of the unit. Notified R1DO (Conte). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-08-21
48214 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-08-21 04:07 | 2012-08-21 06:14 | 2012-08-23 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will remove the emergency power supply to the TSC from service. The TSC would be rendered non-functional with the loss of emergency power. The repair to the power supply is expected to last three days. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be expedited to restore the emergency power supply to service. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an Emergency Response Facility (ERF). An update will be provided once the TSC emergency power supply has been restored to normal operation. "NRC Resident has been notified." * * * UPDATE FROM STEVE BREWER TO CHARLES TEAL ON 08/23/12 AT 1346 EDT * * * Maintenance has been completed on the TSC. The TSC has been returned to service. Notified R3DO (Duncan). | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-21
48213 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-20 16:45 | 2012-08-20 19:54 | 2012-08-20 | OSHA NOTIFIED CONCERNING AN ONSITE NON-WORK RELATED FATALITY "The control room received a 4911 notification [emergency on-site 911 call] regarding an employee illness where the employee was unresponsive. Site Medical Emergency Response Team responded, and requested offsite assistance via ambulance. The employee was transported to Piedmont Medical Center via ambulance where he was pronounced deceased. A notification to OSHA [Occupational Safety and Health Administration] was made at 1645 EDT on 8/20/12 due to the on-site fatality." The employee had gone to a meeting and feeling ill went to the break room on-site. When the on-site medical team arrived at the break room they were unsuccessful in resuscitating the employee. The licensee will be notifying the state and local agencies. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-20
48212 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-08-20 15:20 | 2012-08-20 19:11 | 2012-09-27 | RWCU SYSTEM ISOLATION DIFFERENTIAL FLOW - HIGH FUNCTION INOPERABLE "On 8-20-2012 during scheduled surveillance testing, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow - High function was discovered to be inoperable at 1520 CDT. The high differential flow signal is provided to detect a break in the RWCU system when area or differential temperature would not provide detection (i.e. cold leg break). This instrumentation provides isolation signals to both inboard and outboard isolation valves and its loss is being reported pursuant to 10CFR50.72(b)(3)(v)(C). "The NRC Resident Inspector was notified." * * * RETRACTION AT 1513 EDT ON 9/27/2012 FROM BOB MURRELL TO MARK ABRAMOVITZ * * * "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the RWCU Differential Flow High instrument loop was, at all times, capable of performing its TS function. Specifically an engineering analysis of the impact of the instrument as-found and as-left values on the overall instrument loop setting was performed. The analysis determined that the instrument in question was set at a value which would have isolated the RWCU Primary Containment Isolation Valves prior to reaching the Technical Specification (TS) allowable value and therefore the instrument loop remained capable at all times of performing its TS function. "This event is not considered a Safety System Functional Failure or a Condition Prohibited by TS and is not reportable to the NRC as a Licensee Event Report (LER) per 10CFR50.73. "The NRC Senior Resident Inspector has been notified." Notified the R3DO (Lipa). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-08-20
48211 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-20 11:06 | 2012-08-20 18:21 | 2012-08-20 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM "At 1106 EDT, on August 20, 2012 Computer Engineering personnel discovered a computer component failure which would have prevented the transmission of Emergency Response Data (ERDS) to the NRC if the system were to be activated. The actual component failure was determined to have occurred at approximately 2000 EDT on 8/19/12. This resulted in an out of service duration of greater than 8 hours, which was not discovered until after the fact. The system was repaired and returned to service at 1720 EDT on 8/20/12. "Since Unit 1 and Unit 2 ERDS was unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-20
48210 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-08-20 14:17 | 2012-08-20 17:30 | 2012-08-20 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTIVATION "At 1432 EDT on 08-20-2012, the Beaver Valley Unit 2 Shift Manager was notified by the Beaver County 911 call center that some sirens in the Beaver County area were activated at 1417 EDT. Investigation revealed that approximately 94 of the 120 sirens in the Beaver County area had been inadvertently activated for approximately 20 seconds in a Fire Alert mode during siren maintenance activities. All States and Counties within the Beaver Valley Emergency Planning Zone have been notified. "This event is reportable as a 4-hour Non-Emergency Notification 10CFR50.72(b)(2)(xi) as 'Any event resulting in notification to other government agencies that has been or will be made.' "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-20
48209 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-08-20 11:00 | 2012-08-20 16:26 | 2012-08-20 | MINOR THRU-WALL LEAK AT WELD IN SAFETY INJECTION SUCTION PIPING "While working In the vicinity of valve SI-3, the isolation valve between the Boric Acid Storage Tanks and the common Safety Injection (SI) pump suction piping header, plant staff discovered a thru-wall leak at the weld between the SI-3 valve body and the piping upstream of SI-3. Minor leakage (less than 1 drop per minute) was observed at the flaw location. Upon being informed of this condition, plant operators closed SI-3 at 1109 [CDT] to isolate the affected portion of the piping from the SI suction piping. The time period from when the leak was discovered until it was isolated from the SI piping was less than 10 minutes. "As part of the immediate operability determination, plant staff attempted to characterize the flaw to determine the degradation mechanism. Because the flaw could not be readily characterized, the common SI suction piping exposed to the leakage was considered to have been inoperable from the time of discovery until valve SI-3 was closed. "This condition resulted in both Safety Injection Train A and Safety Injection Train B being inoperable per LCO 3.5.2, ECCS - Operating, Condition A, due to an inoperable common suction line. Since the flaw could not be readily characterized, required ECCS flow was conservatively deemed to not be available and LCO 3.0.3 was conservatively entered per Condition C of LCO 3.5.2 during this brief period (less than 10 minutes) until valve SI-3 was closed. This event is reportable under 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "Closing SI-3 restored both Safety Injection Train A and Safety Injection Train B to Operable status and LCO 3.0.3 was exited at 1109 CDT on 8/20/2012. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-08-20
48208 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-05-12 | 2012-08-20 14:52 | 2012-08-20 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RADIOGRAPHER The following information was provided by the State of Louisiana via facsimile: "On approximately May 14, 2012, a radiographer was performing industrial radiography. He dropped his badge approximately 7 feet from the industrial radiography camera for one to two welds. On approximately May 12, 2012 he was performing Mag inspections and had left his dosimetry in his parked car. He noticed some industrial radiography crews performing work near his vehicle. His badge read 7028 DDE [Deep Dose Equivalent] and 6972 SDE [Shallow Dose Equivalent]. "He stated that his pocket ion chamber never went off scale. None of his crew members badges and pocket ion chambers showed any exposure during the time they worked together. Louisiana Department of Environmental Quality is sending an inspector to investigate the dosimetry over exposure." LA Event Report ID No.: LA120003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-08-28
48207 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2012-08-13 | 2012-08-20 13:26 | 2012-08-20 | AGREEMENT STATE - MEDICAL EVENT INVOLVING DELIVERY OF UNDERDOSAGE The following information was received from the State of Oregon via email: "[The licensee reported] a misadministration on Monday, August 13, 2012, during a treatment with [Y-90] TheraSpheres. The misadministration was due to a malfunction of the syringe plunger of the delivery device, and is the first time that this problem has occurred at Oregon Health & Science University. "This was a two-vial treatment, and the malfunction occurred with the first delivery set. (The activity from the second vial, and with a new delivery set, was administered with no difficulty. Delivery sets are single-use.). The nurse who was setting up the system, and who routinely sets up the systems, noticed a stiffness when she was snapping the plunger into position through the vial septum. She was not able to retract the needles (the plunger is designed not to be removable), and it appeared to be placed properly. "The physician was informed of the 'stickiness'. The patient's catheter was correctly hooked up to the delivery device, and the catheter in the patient was in the desired position. As soon as the administration was started, blood backed up into the catheter, which was unusual. Normal attempts to administer the activity by pushing saline into the vial resulted in fluid running into the over-pressure vial. The treating physician ended the attempt to deliver the activity, and the system was removed in the normal way by placing the used items in the waste container. "The second delivery set and the second dose vial were placed in position, the patient catheter hooked up, and the delivery of the activity went smoothly. "The patient was notified of the problem and of the possibility of a retreat. The Oregon Department of Health Radiation Protection are waiting for the Nordion technical adviser to call mid-day today. "The Y-90 TheraSphere treatment consisted of: Vial 1 - Script 66 Gray, Administered 12 Gray, 81.8 % Error of 54 Gray Vial 2 - Script 55 Gray, Administered 50.2 Gray, 8.7 % Error of 4.8 Gray Treatment Total - Script 121 Gray, Administered 62.2 Gray, 48.5 % Error of 58.8 Gray" Oregon Incident # - 12-0031 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2012-08-28
48206 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2012-08-20 05:05 | 2012-08-20 05:55 | 2012-08-20 | INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-08-20
48205 | 0 | PSC ENVIRONMENTAL SERVICES LLC |  |  |  |  | 2012-08-17 | 2012-08-17 16:50 | 2012-08-17 | TEN TRITIUM EXIT SIGNS DAMAGED Ten tritium exit signs belonging to Bed Bath and Beyond were inadvertently placed into a compactor and damaged. The signs originally contained 7.5 Ci of tritium when they were purchased 7-10 years ago. Shaw Environmental will take smears of the site next week to determine if there is residual contamination or cleanup required. The signs have been placed in drums and the area quarantined. See report of this same event from the State of Wisconsin EN #48224 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-08-27
48204 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-06-18 23:49 | 2012-08-17 14:11 | 2012-08-17 | INVALID ACTUATION OF CONTAINMENT VENTILATION ISOLATION "Watts Bar Nuclear Plant's (WBN's) containment ventilation isolation systems provide the means of isolating ventilation systems that pass through containment penetrations to confine to the containment any radioactivity that may be released following a design basis event. The containment ventilation system isolates following a manual or automatic safety injection signal, high containment purge exhaust radiation levels, or manual actuation. "On 6/18/12 at 2349 EDT, a B train containment ventilation isolation signal was received in the Main Control Room due to an invalid high radiation signal from a containment purge exhaust radiation monitor (1-RM-131). Corrective action replaced the 1-RM-131 ratemeter following the 6/18/12 B train containment ventilation isolation. However, on 7/2/12 at 1252 EDT, a second B train containment ventilation isolation signal was received in the Main Control Room due to another invalid high radiation signal from 1-RM-131. An investigation found that 1-RM-131 was spiking repeatedly due to a defective Power On indicating light socket which affected the 120 VAC power circuit that is common with the 24 volt power supply. 120 VAC signal fluctuations could affect the 24 volt power supply signal to the rate meter causing output spikes. Corrective action replaced the defective Power On indicating light socket on 7/3/12. "This event notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a 60 day telephone notification of the invalid initiation of a containment isolation signal. The specific system and train that was actuated was B train containment ventilation isolation. The system functioned as designed and the complete train operated. "WBN's NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-08-17
48203 | 0 | NEBRASKA DEPARTMENT OF HEALTH |  |  |  |  | 2012-06-11 | 2012-08-17 13:57 | 2012-08-17 | AGREEMENT STATE REPORT INVOLVING 28 MISSING TRITIUM EXIT SIGNS The following report was received from the State of Nebraska via email: "This is a preliminary report. We [Nebraska Department of Health and Human Services] will amend when we receive more information. "On June 9, 2012, about 28 tritium exit signs (SLX 60 model, 11.5 Ci in 2005) were removed and new electrical exit signs were installed in the store by electricians. New lighting fixtures were also installed. The old fluorescent lighting was packaged to be picked up by a recycling facility. On June 11, 2012, the fluorescent lights were picked up. On August 12, 2012, Shaw Industries came to package the tritium exit signs and put labels on them. UPS would then pick them up to ship them to a facility licensed to receive the tritium signs. Shaw Industries could not find the exit signs on August 12, 2012. The store thinks that the tritium exit signs were picked up by the fluorescent lighting recycling company on June 11, 2012. The store is trying to find where the fluorescent lights were taken. "[The State] has called all Bed and Bath stores that have had signs removed to make sure that only Shaw Industries can pick up the signs. Attempting to determine where the exit signs were taken and retrieve them for proper disposal." Cause of this event is inattention to detail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2012-08-27
48202 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-08-17 12:39 | 2012-08-17 13:36 | 2012-08-17 | ONLY ONE IROFS AVAILABLE FOR A SPILL IN THE CERAMICS AREA "At 12:39 PM (EDT) it was discovered that only one Items Relied On For Safety (IROFS) remained in place to prevent a Criticality Event in the ceramics area of the Fuel Manufacturing Operations facility. The failed IROFS was Fuel Business System (FBS) Control of Mass of Uranium Transportable Container (IROFS 900-01), due to an overweight pellet boat. The IROFS that remained in place at all times was Spill Identification and Cleanup (IROFS 900-11). The initiating event for the accident sequences (spill of a pellet boat) did not occur." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1456 EDT ON 8/17/2012 FROM SCOTT MURRAY TO MARK ABRAMOVITZ * * * "The pellets have been removed from the overweight boat and placed into an approved container; the IROFS for these accident sequences have been restored. The extent of condition is being evaluated and at this time no other overweight boats have been identified. "Region II and NMSS HQ and other notifications have been completed." Notified the R2DO (Guthrie) and NMSS (Waters). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2012-08-17
48201 | 0 | WEST VIRGINIA UNIVERSITY HOSPITAL |  |  |  |  | 2005-10-08 | 2012-08-17 11:38 | 2012-08-17 | MISSING SEALED AMERICIUM-241 SOURCE "Subject: Official Notification "This is to inform the NRC Operations Center that West Virginia University [WVU] Hospitals License # 47-23066-02 is not in possession of Item 6.I. Am-241 sealed sources (Amersham Model Dwg. ARC 10048B and 10040B) with an activity of 9.825 millicuries. "NRC Region 1 is aware of this situation and has been working with us to resolve it. In August of 2005, a request was made to remove the item from our license. At that time NRC Region 1, via an October 8, 2005 email control # 137502, requested documentation of the shipment/disposal of the source. Based on NRC Region1 recommendations, on November 1, 2005 West Virginia University Hospitals withdrew the request to remove the item from the license. Control # 137502. "In a search of the WVU Radiation Safety Department and Vendor records, no evidence of a shipment of the source was found. It was last listed on our physical inventory on May 7, 1991. The former RSO informed us via phone conversation that he believed it was shipped in the early 1990's. "All of the search results were documented in writing to NRC Region 1 on May 23, 2012 during our license renewal process. Control # 576453. "There is a current license amendment request to remove the source from our license. Control # 577671. "West Virginia University Hospitals is officially notifying the NRC Operations Center at this time to document the situation in an effort to bring the situation to a close, and ultimately remove the source from our license." The licensee has been working with Janice Nguyen in Region 1 to resolve this issue. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-08-27
48200 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-08-17 04:50 | 2012-08-17 12:20 | 2012-08-17 | INADVERTENT ACTUATION OF PRIMARY CONTAINMENT ISOLATION SYSTEM "On 08/17/2012, while performing 2-SR-3.3.6.1(3DFT) - HPCI [High Pressure Coolant Injection] Steam Line Space Temperature Functional Test, an inadvertent PCIS [Primary Containment Isolation Signal] Group 4 (HPCI) isolation signal occurred. All automatic actions occurred as designed. Cause of the isolation is unknown with investigation in progress. "This incident is reportable as an 8-hour ENS notification under 10 CFR 50.72 (b)(3)(v)(D). "The incident also requires a 60 day written report. "The NRC [Resident] Inspector has been notified." The steam supply valves to HPCI remain closed during trouble shooting and repair, however, HPCI remains available for use if needed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-08-17
48199 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-08-17 05:52 | 2012-08-17 06:32 | 2012-08-17 | UNUSUAL EVENT DECLARED DUE TO THE UNPLANNED LOSS OF ANNUNCIATORS > 15 MINUTES At 0552 EDT Control Room Operators experienced a Loss of Annunciators. At 0607 EDT, the licensee declared an Unusual Event per EAL SU4.1, " Unplanned loss of most or all Annunciators or Indicators associated with Safety Systems on the RTGB [Remote Turbine Gage Board] Sections A and B, Primary System Annunciators and Indicators > 15 minutes." During an alarm test, the annunciators lit up as expected but did not clear at the completion of the test. Exit criteria for the Unusual Event will be restoration of the annunciator functions. The licensee has compensatory measures in effect. ERFIS [Emergency Response Facility Information System] and the normal RTGB instruments are available. The licensee notified the state and informed the NRC Resident Inspector. Notified Other FEDS (FEMA, DHS and NNSA via email). * * * UPDATE FROM HILL TO KLCO ON 8/17/2012 AT 0954 EDT * * * On August 17, 2012 at 0940 EDT, the licensee terminated the Unusual Event based on restoring annunciator capability. The licensee notified the NRC Resident Inspector and has terminated ERDS transmission. Notified NRR-EO(Thomas), R2DO(Guthrie), IRD(Gott) and other FEDS (FEMA, DHS and NNSA via email) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-08-17
48198 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-16 19:26 | 2012-08-16 22:09 | 2012-08-16 | REACTOR TRIP FROM A REACTOR COOLANT PUMP TRIP "At 1926 EDT on 8/16/2012, Unit 2 reactor automatically tripped on single loop loss of flow, following #4 RCP trip. Cause of RCP trip is under investigation. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater actuated as expected on loss of the operating main feedwater pumps. "Unit 2 is currently being maintained in Mode 3 at NOP/NOT [normal operating pressure/normal operating temperature], with auxiliary feedwater supplying the steam generator. "Method of decay heat removal is via steam dumps to condenser. Current RCS conditions: Temp = 547 degrees F and stable, Pressure = 2235 psig and stable. No indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from offsite power. No impact to Unit 1: Unit 1 is operating at 100% power / Mode 1." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-08-16
48197 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-08-16 14:58 | 2012-08-16 21:02 | 2012-08-17 | INTEGRATED PLANT COMPUTER FAILURE "At approximately 1458 EDT on 8/16/12, a portion of the Fermi 2 Integrated Plant Computer System (IPCS) failed. This resulted in a loss of approximately 60 percent of data on the Safety Parameters Display System (SPDS). "While IPCS and SPDS are not fully functional, the Emergency Plan can still be implemented if a plant emergency does occur, as assessment capabilities are available under alternate means. "Repairs are in progress. A follow up message will be made when IPCS and SPDS are restored to fully functional status. "This notification is being made pursuant to the requirements 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM GROFF TO KLCO ON 8/17/12 AT 0429 EDT* * * "At approximately 1458 EDT on 8/16/12, a portion of the Fermi 2 Integrated Plant Computer System (IPCS) failed. This resulted in a loss of approximately 60 percent of data on the Safety Parameters Display System (SPDS). "At 2340 [EDT], plant personnel were able to restore full functionality of IPCS and SPDS, restoring full Emergency assessment capabilities to all onsite emergency response facilities." The licensee notified the NRC Resident Inspector. Notified the R3DO (Giessner). | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-16
48196 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-08-02 | 2012-08-16 15:02 | 2012-08-16 | PATIENT RECEIVES UNDER DOSE The following report was received via fax. "Received report from the RSO on 2 Aug 2012 at approximately 1430 [EDT] hrs of a medical event that occurred on 1 Aug 2012. Two patients with similar procedures (mammosite) were being treated with an HDR [High Dose Rate]. First patient correctly treated, second patient treated with the same plan as the first. Second patient only under dosed by 0.5%. Their treatment plans were allegedly the same. "Orlando office investigated licensee and found violation to be caused by operator error. Corrective action consists of a 'Time Out' to verify patient's name, plan, and treatment settings. Further action referred to the Office of Licensing and Materials, this office will take no further action on this incident." The device is a Nucletron Microselection HDR; S/N 31591. Florida Incident: FL12-061. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-08-24
48195 | 0 | DEACONESS HOSPITAL |  |  |  |  | 2012-08-15 10:00 | 2012-08-16 10:58 | 2012-08-16 | MEDICAL EVENT DUE TO OFFSET OF THE INTENDED DELIVERY A HDR (High Dose Rate) treatment was planned for a patient's mammary area, but the delivery of the source position was offset from the intended delivery. The patient and referring physician were informed of the difference between the planned and the delivered dosage. The patient will receive follow-up to discuss potential options. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2012-08-24
48194 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-08-15 15:30 | 2012-08-15 16:21 | 2012-08-15 | OFFSITE NOTIFICATION DUE TO TRITIUM IN DEGRADED DRAIN LINE "At 1000 hours [EDT] on 8/14/12, Surry Power Station personnel confirmed the presence of tritium at a level of 1,250 picoCuries/liter (pCi/l) in the #3 Turbine Building sump. The sump water had been tested upon discovery of a degraded drain line on the sump discharge that resulted in a leak to the environment. The exact volume could not be determined, but it is estimated to be greater than the 100 gallon reporting criteria. The location of the leak is within the Protected Area of Surry Power Station. To prevent additional releases, water from the #3 Turbine Building sump has been redirected to another turbine building sump. There is no Indication that this water has migrated offsite. Because there was a detectable amount of licensed material in the water, Surry has implemented our voluntary communication protocols to the state and Surry County as per our commitment to the Nuclear Energy Institute (NEI) Ground Water Protection Initiative. "An adjacent ground water monitoring well was sampled, and no tritium activity was detected in the well water. There has been no tritium detected in any monitoring wells in the vicinity of the drain line, nor in any monitoring wells outside the Protected Area. "The activity of the leak was approximately 6% of the criteria for reporting actual ground water activity (20,000 pCi/l). Because the leak remained on site, no offsite impact to ground water is expected. Furthermore, the leak posed no threat to employees or the public. "The degraded drain pipe is currently being repaired. "This notification Is being transmitted due to Notification of Other Government Agencies under 10CFR50.72(b)(2)(xi). The Virginia Department of Environmental Quality, Virginia Department of Health, and Virginia Department of Emergency Management were notified. The NRC Senior Resident [Inspector] and Surry County Administrator will be notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-15
48193 | 0 | UNITED STATES AIR FORCE |  |  |  |  | 2012-08-15 | 2012-08-15 14:31 | 2012-08-16 | POTENTIALLY LOST AMERICIUM-241 SOURCE "The potentially lost source is a M43A1 Chemical Agent Detector Cell (Americium-241, 0.25 mCi). The source exceeds 1000 times the quantity listed in Appendix C to Part 20. "The source was made ready for shipment to our recycling and disposal office and given to the local traffic management office. Currently, we have no record of the shipment and cannot locate the shipping package. A comprehensive physical and document search is under way. "Device Serial # Z03-C-30470 "Source Serial # Z03-C-31725" The licensee notified R4 (Cook). * * * UPDATE FROM DANLEY TO KLCO ON 8/16/2012 AT 0956 EDT * * * The following information was received by email from the licensee: The licensee received a call from the permit RSO [Radiation Safety Officer] that the Am-241 source has been recovered. It was located in the traffic management office. Notified the R1DO(Powell), R4DO(Hagar) and FSME via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-08-23
48192 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-08-14 11:26 | 2012-08-15 10:51 | 2012-08-15 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A licensed employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's unescorted access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2012-08-15
48191 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-15 | 2012-08-15 10:37 | 2012-08-15 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY CAMERA The following information was received by email: "On August 15, 2012, the licensee notified the Agency [Texas Department of State Health Services] that sometime during the evening, a QSA Global 880D radiography camera was stolen out of the dark room of one of their trucks. The camera contained Iridium-192. The truck was parked at the licensee's office, however the Radiographer left the camera in the truck instead of transferring the camera to the vault. The thieves broke into five radiography trucks taking various items including generators and the one camera. A police report was filed with the Chamber County Sheriff's Department. The thieves did not take the crank outs or source tube." "The State of Texas event number for this event is I- 8979. Additional information will be provided in accordance with SA 300." Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC and EPA EOC. * * * UPDATE ON 8/15/12 AT 1330 EDT FROM CHRIS MOORE TO DONG PARK * * * "On August 15, 2012, around 1130 [CDT], the licensee and Local Law Enforcement recovered the stolen QSA Global 880D Radiography Camera. The camera is stored in the vault at the licensee facility and is in normal working condition. [A person of interest has been identified]. The truck used by the thief was identified on video surveillance tape. The camera was in the back of truck at the residence of the thief. Investigation will continue for the company and radiographers [concerning] Increased Controls (IC) security violations." Notified R4DO (Hagar), FSME (McIntosh), ILTAB (Whitney), IRD (Gott), Mexico via fax, DHS, FEMA, USDA, HHS, DOE, DHS NICC and EPA EOC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-08-23
48190 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-08-14 20:45 | 2012-08-15 04:37 | 2012-08-23 | SAFETY SYSTEM OVERPRESSURE PROTECTION FAILURE DUE TO CLOSED VALVES "At 2045 [CDT] on 8/14/12, MNGP [Monticello Nuclear Generating Plant] Operations determined that valves RHR-82 and RHR-84 had been inappropriately closed as part of an isolation clearance order for work on shutdown cooling suction piping. These valves are required to be open to provide overpressure protection for RHR piping passing through primary containment penetration X-12. Upon discovery of the condition, Primary Containment was declared Inoperable and the Required Actions of Tech Spec 3.6.1.1 were entered. Following discovery, the isolation was restored and the valves opened. At 0001 [CDT] on 8/15/12, Primary Containment was declared Operable. "This issue is being reported in accordance with 10CFR50.72(b)(3)(v)(C) and 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety functions of a system needed to control the release of radioactive material or to mitigate the consequences of an accident. "The MNGP Senior NRC Resident Inspector has been notified of this issue." The licensee will contact the Minnesota State Duty Officer. * * * RETRACTION FROM RANDY SAND TO CHARLES TEAL ON 08/23/12 AT 1545 EDT * * * "This notification is a retraction of ENS 48190 based on further engineering evaluation. Monticello had previously evaluated penetration X-12 for thermally induced over pressurization. The evaluation qualified the piping components in the penetration for a maximum pressure of 3,306 psig using ASME Section III Appendix F operability criteria. The peak pressure calculated for the penetration was 2,743 psig based on Reactor pressure of 1000 psig with Reactor in Mode 1, and at worse case LOCA conditions for the Drywell. These assumptions and parameters envelop those that were present when valves RHR-82 and RHR-84 were closed on August 14, 2012. Therefore, this event would not have prevented the fulfillment of the safety function reported. "The NRC Resident Inspector has been notified." Notified R3DO (Duncan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-08-15
48189 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2012-08-14 20:31 | 2012-08-15 00:02 | 2012-08-15 | UNIT 1 MANUALLY TRIPPED IN ANTICIPATION OF AN AUTOMATIC TURBINE TRIP "Unit 1 Manual Reactor Trip was initiated in anticipation of an auto turbine trip due to operators noticing the turbine governor valves closing in response to an Electro-Hydraulic Control System signal. All Control Rods are fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feedwater system. The auxiliary feedwater system actuated based on low steam generator level, but has since been secured. There were no unexpected (inconsistent with nature of trip) pressure or level transients. Offsite power remains available. No release occurred nor is ongoing. Emergency Core Cooling did not actuate. No unexpected isolations occurred. Emergency Plan entry was not required." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-08-15
48188 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-08-14 07:45 | 2012-08-14 13:03 | 2012-08-14 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee was complaining of chest and jaw pain this morning at approximately 0745 CDT. The employee was admitted to the plant dispensary in his plant clothing. The employee's plant boots were contaminated, with a maximum activity of 17,552 dpm/100cm2. The plant nurse evaluated the employee and decided to transport the employee to a regional hospital. Before going into the ambulance the employee removed his plant clothing. A whole body survey was performed of the employee; no contamination was detected. Additionally, the gurney and ambulance personnel shoes were surveyed upon loading the ambulance; no contamination was detected. The ambulance tires were also surveyed prior to release from the Restricted Area; no contamination was detected." R2(Gibson) was also notified by licensee. Contamination was from Uranium Ore Concentrates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-08-14
48187 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-08-14 10:06 | 2012-08-14 10:40 | 2012-08-14 | OFFSITE NOTIFICATION TO STATE AND LOCAL AGENCIES CONCERNING TRITIUM FOUND IN GROUNDWATER INLEAKAGE "On Monday, August 13, 2012, analyses of samples taken from groundwater inleakage to the Nine Mile Point Unit 1 (NMP1) Screenhouse building confirmed the presence of tritium at concentrations of approximately 32,000 to 44,000 picocuries per liter (pCi/l). This discovery was made during the conduct of the site's ongoing groundwater monitoring program. These concentrations are above the 30,000 pCi/l threshold for voluntary reporting for a non-drinking water pathway, as indicated in Nuclear Energy Institute (NEI) 07-07, Industry Ground Water Initiative - Final Guidance Document. "These test results do not indicate any threat to public health or safety, since the building inleakage is not a drinking water source, and there is no indication that tritium has migrated off the Nine Mile Point site in the groundwater. Nine Mile Point Nuclear Station, LLC, is continuing an investigation to identify the source of tritium and implement a corrective action plan. "Voluntary notification of this discovery has been made to the New York State Department of Environmental Conservation and the New York State Department of Health." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-14
48186 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2012-08-14 03:12 | 2012-08-14 08:52 | 2012-08-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN BASED ON BOTH EMERGENCY DIESELS BEING DECLARED INOPERABLE "Prairie Island Unit 1 is currently being shutdown per Tech Spec 3.8.1.F due to both Diesel Generators inoperable for Unit 1. "On August 13th at 0939 CDT, a planned entry to Tech Spec 3.8.1.B was performed for one Diesel Generator inoperable, due to the scheduled monthly surveillance run of D1 Emergency Diesel Generator. At 1048 CDT, a small candle sized flame was identified at the exhaust manifold and D1 was subsequently shutdown. Subsequent investigation by maintenance determined that there appeared to be a gasket leak on the turbocharger. D1 was tagged out of service and repairs are currently in progress. "Tech Spec 3.8.1 required action B.3.1 requires a determination be made to verify the operable Diesel Generator is not inoperable due to a common cause failure. On August 14th at 0230 CDT, Unit 1 entered the Limiting Condition for Operation to perform the monthly surveillance run to verify no common cause failure existed. At 0312 CDT, the Shift Manager reported a small candle sized fire on the exhaust manifold for D2. Unit 1 entered an event or condition that could have prevented fulfillment of a safety function, a 10 CFR 50.72 (b)(3)(v)(D) report is required due to a loss of both D1 and D2. D2 was subsequently shutdown and declared inoperable. "A Technical Specification shutdown was also required and a Unit 1 Shutdown was commenced at 0425 CDT and a 4 hour non-emergency notification is required per 10 CFR 50.72(b)(2)(i). "With both Diesels inoperable at 0230 CDT, Tech Spec 3 8.1.E requires one diesel to be returned to operable status within 2 hours. However, as neither diesel generator could be returned to service in this time period, Tech Spec 3.8.1.E requires the plant to be in Mode 3 within 6 hours and Mode 5 within 36 hours." The NRC Resident Inspector has been notified. * * * UPDATE ON 8/14/12 AT 1452 EDT FROM TERRY BACON TO DONG PARK * * * "A Technical Specification shutdown has been completed at 1025 CDT as planned for Unit 1. It was a normal manual reactor trip with no unexpected equipment issues. As expected due to plant electrical conditions, the Auxiliary Feedwater System auto started. This is reportable per 10 CFR 50.72(b)(3)(iv)(A) as a valid System Actuation, The Auxiliary Feedwater System operated as expected. Unit 1 is currently in Mode 3." The NRC Resident Inspector has been notified. Notified R3DO (Giessner). | 52 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) | 50.72(b)(3)(iv)(A) |  | 0 | 2012-08-14
48185 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-13 16:30 | 2012-08-13 19:10 | 2012-08-13 | OFFSITE NOTIFICATION TO THE NORTH CAROLINA WILDLIFE RESOURCES COMMISSION "Duke Energy notified the NC Wildlife Resource Commission of dead catfish in the vicinity of the McGuire low level intake. Notification was made on 8/13/12 at 1630 EDT. In addition, the NC Dept. of Environment and Natural Resources will be notified. "The dead fish are suspected to have been caused by increasing lake temperature and decreased oxygen levels, which is common during the late summer." The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-13
48184 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-08-11 | 2012-08-13 12:29 | 2012-08-14 | AGREEMENT STATE REPORT - INDIUM-111 VIAL DAMAGED IN SHIPMENT The following information was provided by the State of Tennessee via facsimile: "On August 11, 2012, the shipper contacted the Division of Radiological Health to report that a package containing 31.7 mCi of Indium-111 was run over in the 'courtyard' area. Caps were off all six internal shielding pigs. Vials in four pigs were intact. The fifth vial was found and returned to the pig. The sixth vial was crushed and the contents (5.3 mCi) released. The shipper's fire personnel responded and washed the area (20 to 30 feet in diameter) and released the water to the storm water runoff drain. One area about 4 inches by 4 inches could not be decontaminated. A steel plate was bolted onto the asphalt in that area and dose rates of 0.5 mR/hr at a meter was observed. This area is not an occupied area. The half-life for Indium-111 is 2.8 days. The plate will be removed in 30 days and the area will be reassessed. No injuries, [and] no personnel contamination." Event Report ID No.: TN-12-207 * * * UPDATE ON 8/14/12 AT 1456 EDT FROM BETH SHELTON TO DONG PARK * * * The following update was provided by the State of Tennessee via email: "The sixth vial was crushed and the contents (4.4 mCi) released. One area about 4 cm in diameter could not be decontaminated. A steel plate was bolted onto the asphalt in that area and dose rates of 0.05 mR/hr at a meter were observed." Notified R1DO (Powell) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-08-21
48183 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2012-08-12 12:34 | 2012-08-12 14:37 | 2012-08-12 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO FULLY INSERTED CONTROL ROD WHILE OPERATING "Calvert Cliff Nuclear Power Plant, Unit 1 Control Element Assembly (CEA) #9 fully inserted (CEA dropped) into the core. Technical Specification 3.1.5, Action B was entered and requires the CEA to be realigned within 2 hours. With this action not met Technical Specification 3.1.5, Action C requires the Unit be placed in Mode 3 within 6 hours. A plant shutdown has been initiated in accordance with this Technical Specification. Therefore, this is reportable under 10 CFR 50.72. (b) (2) (i) Plant Shutdown Required by Technical Specifications." The licensee has notified the NRC Resident Inspector. The licensee will also notify local government agencies. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-08-12
48182 | 0 | PALISADES | 1 |  |  | [1] CE | 2012-08-12 04:18 | 2012-08-12 11:05 | 2012-08-12 | DEGRADED CONDITION REPORTED BASED ON THE DISCOVERY OF PRESSURE BOUNDARY LEAKAGE "Following a planned shutdown to investigate the source of elevated Primary Coolant System (PCS) Unidentified Leakage, the Mode 3 PCS walk-down identified a steam leak on CRD-24, Control Rod Drive Mechanism (CRD), pressure housing. The leak is ~ 1 foot above the CRD to Reactor Head flange. The leak was observed from the Refueling floor deck and appears to be coming from an area of the CRD with no bolted connections. Leakage from this area is unexpected and the mechanism of failure is not understood at this time. Closer examination of the leak is expected to occur in parallel with plant cool-down. "The plant entered T.S. 3.4.14 (PCS Operational Leakage) Condition B. at 0418 EDT hours this morning and this requires the plant to be placed in Mode 5 within 36 hours. The leakage is considered Pressure Boundary Leakage. Operations is in progress of performing the plant cool-down from Mode 3 to Mode 5." The licensee discovered this condition following a shutdown the morning of 8/12/12 to investigate unidentified primary coolant leakage of about 0.3 gpm that had been recently trending upwards. Plant conditions are currently 400 degrees F with primary system pressure at about 1000 psi. The licensee has notified the NRC Resident Inspect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-08-12
48181 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2012-08-12 00:44 | 2012-08-12 01:48 | 2012-08-12 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO ULTIMATE HEAT SINK EXCEEDING TEMPERATURE LIMIT Millstone Unit 2 reported that it is in a technical specification shutdown condition based on the ultimate heat sink average water temperature exceeding a temperature limit of 75 degrees Fahrenheit. The ultimate heat sink is supplied by water from Niantic Bay. At the time of this report, the bay water temperature is slightly below the 75 degree temperature limit but the time average calculation for the ultimate heat sink temperature limit still exceeds 75 degrees. The Ultimate Heat Sink Technical Specification, TS 3.7.11.a, requires the unit to be in hot shutdown within 6 hours when the average temperature limit is exceeded. The licensee is in a slow power ramp-down while monitoring the ultimate heat sink average temperature for water temperature conditions to drop below the limit. The high heat sink temperatures are based on natural environmental conditions and not from plant operation. Millstone Unit 3 is not impacted at this time. The licensee has notified State and local authorities and will notify the NRC Resident Inspector. * * * UPDATE AT 0518 EDT ON 8/12/12 FROM WOLLERY TO HUFFMAN * * * The licensee reported that it had exited the Technical Specification LCO based on a current average heat sink temperature below 75 F. However, the licensee will hold power at 65% to ensure the temperature is stable and will remain below the limit during the day shift. The licensee has notified the NRC Resident Inspector. R1DO (Burritt) notified. * * * UPDATE AT 1001 EDT ON 8/12/12 FROM NICHOLS TO HUFFMAN * * * At 0943 EDT on 8/12/12, the average ultimate heat sink temperature on Unit 2 exceeded the 75 degree limit again. The licensee re-entered TS LCO 3.7.11.a and commenced to shutdown the unit from a starting power level of 65%. The licensee plans to proceed to Hot Standby in compliance with the TS action statement even if the heat sink temperature drops back below the TS limit. The licensee has notified State and local authorities and the NRC Resident Inspector. R1DO (Burritt) notified. * * * UPDATE AT 1650 EDT ON 8/12/12 FROM PATRICK SIKORSKI TO JOHN KNOKE * * * At 1645 EDT on 8/12/12, Unit 2 is in Hot Standby and the heat sink temperature is below the 75 degree limit. The licensee has notified State and local authorities and the NRC Resident Inspector. R1DO (Burritt) notified. | 0 | 66 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-08-12
48180 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-08-11 07:30 | 2012-08-11 07:58 | 2012-08-11 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR SCHEDULED MAINTENANCE "At 0730 hours EDT on Saturday, August 11, 2012, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, Technical Support Center (TSC)/Emergency Response Facility (EOF) air conditioning system will be removed from service to facilitate the replacement of the HVAC chiller system. Unavailability of the primary chiller system will last greater than 8 hours. The duration of work is expected to be approximately 31 hours. The filtration portion of the system will not be affected by this work. "In order to ensure habitable conditions in the TSC/EOF, as a compensatory measure, a temporary chiller system will be onsite to maintain habitability in the event of emergency facility activation and will remain onsite until such time that the TSC/EOF ventilation system has been returned to service. "Emergency Responders assigned to these facilities and all offsite agencies have been informed of this scheduled maintenance and will be informed of any updates. "Alternate emergency response facilities will remain available in the event that relocation is necessary. "TSC/EOF ventilation system maintenance and post maintenance testing is scheduled to be completed by 1400 hours EDT on Sunday August 12, 2012. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-11
48179 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-08-10 12:30 | 2012-08-10 19:44 | 2012-08-10 | FLOOD BARRIER SEALS COULD NOT BE VERIFIED INSTALLED "On August 10, 2012 during an inspection in the Air Intake Tunnel, six 4-inch conduits that carry cabling from yard vaults through the Air Intake Tunnel (AIT) to the Auxiliary Building (AB) were inspected for flood seals. This was done by opening the conduit seals bottom drain openings to inspect the condition by boroscope. These seal components are just inside the AIT from the electrical vaults. During the inspections no sealant could be readily identified. Each conduit from the yard vaults that is not sealed could potentially provide a leak path during flood conditions from the yard vaults to the Auxiliary Building via the electrical conduit. Flood water entering the Auxiliary Building could impact the decay heat removal function. "This is reportable as an 8 hour ENS notification under 10CFR50.72(b)(3)(v)(B) and 10CFR50.72(a)(1)(ii) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-08-10
48178 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-07 17:34 | 2012-08-10 17:13 | 2012-08-10 | DRY FUEL STORAGE TRANSFER TRAILER DETECTED WITH REMOVABLE CONTAMINATION "On Aug 7, 2012 at 1734 EDT, PPL Susquehanna personnel were in the process of releasing the Dry Fuel Storage Transfer Trailer from the Unit 1 Reactor Building 101 rail bay and detected removable contamination on the trailer. "PPL Susquehanna Health Physics personnel identified removable surface contamination up to 30,000 dpm/100 sq cm on the transfer trailer. Gamma spectroscopy performed on smears identified the presence of Cs-137. No other radionuclides were identified on any of the analyzed smears. Cs-137, by itself, is not a nuclide characteristic to Susquehanna due to Susquehanna's high fuel integrity performance. In addition, no loose surface alpha contamination was identified. "The area around the trailer, located in the 101 bay, has been posted and controlled as a contaminated area. Decontamination of the transfer trailer is in progress. Onsite surveys of areas that were occupied by the transfer trailer, indicate no removable surface contamination. In addition, no Susquehanna personnel contamination events have been attributed to the contamination found on the transfer trailer. "Although the receipt of this transfer trailer was not identified as an incoming radioactive shipment to Susquehanna from its' supplier, this event is immediately reportable to the NRC Operations Center in accordance with 10 CFR 20.1906(d), since the Department of Transportation acceptance limits identified in 49 CFR 173.433 for this type of container are 22,000 DPM/100 sq. cm and PPL Health Physics personnel identified removable radioactive surface contamination in excess of the limits of 10 CFR 71.87(i) which refer to the DOT limits of 49 CFR 173.433. "The final delivery carrier and NRC Senior Resident Inspector have been notified." The licensee will be notifying the Commonwealth of Pennsylvania. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SURFACE CONTAM LEVELS > LIMITS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 20.1906(d)(1) |  |  |  | 0 | 2012-08-10
48177 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-08-09 | 2012-08-10 13:41 | 2012-08-10 | AGREEMENT STATE REPORT - STUCK SHUTTER ON GAUGE The following information was provided by the Commonwealth of Pennsylvania via facsimile: "On Thursday, August 9, 2012, the licensee informed the Department's [Department of Environmental Protection (DEP)] Southwest Regional Office about the discovery of a shutter failure. It is reportable within 24- hours under 10CFR 30.50(b)(2). "During a semi-annual leak test being performed by a consultant, the shutter was found inoperable and stuck in the open position. No dose is believed to have been received by any personnel. "The device is identified as: Manufacturer: LFE, Model #: SS-3A, Device Serial #: 300-483L, Sealed Source Model #: SS-3A, Sealed Source SN: 02311, Isotope: Am-241, Activity: (1 Ci). "The cause of the event was equipment malfunction. Licensee continued running the mill with permission granted by DEP until the consultant arrived later that same day. Repairs were made to the shutter mechanism, followed by a radiation survey, wipe test, and function check of the gauge. The gauge is now operating properly. DEP scheduled a reactive inspection for August 10, 2012." PA Event Report No. PA120024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-08-20
48176 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-07-23 | 2012-08-10 11:07 | 2012-08-11 | AGREEMENT STATE REPORT - SOURCE UNACCOUNTED FOR IN SHIPMENT The following information was received from the State of Massachusetts Radiation Control Program via e-mail: "Containers from REVISS Services, Inc were used to ship return Co-60 sources from Steris Isomedix Services, Northborough, MA to REVISS's UK facility. When the container arrived on 8/7/12 and was opened by the REVISS (UK) staff, they identified that the basket contained only 52 sources rather than the 53 that were expected. When the container arrived the tamper proof seals that were installed by engineers at the plant were intact. A review of the documentation for the operations at the plant indicate that only 52 sources were loaded into the basket. A positive check of the serial numbers confirmed that the one source that was unaccounted for was a Nordion model C-188, Co-60 source, serial number 41313. "Steris Isomedix Services was contacted and at their earliest chance will inspect the pool to ensure that the source was not dropped onto the floor of the pool. There were no abnormal radiation readings that would indicate that the source was removed from the pool during operations. Because the documentation does not indicate that the source was ever removed from the source module, Steris Isomedix Services has a high level of confidence that the source is still in the irradiator pool. "Steris Isomedix Services, Northborough, MA and REVISS will continue updating as information is acquired.." * * * UPDATE AT 1047 EDT ON 8/11/12 FROM JOSH DAEHLER TO HUFFMAN * * * The subject missing Co-60 source, serial # 41313, was discovered this morning (8/11/12) to be located in module 10, position 23, in the Steris (Northborough) pool irradiator. The serial number of the source was visually confirmed by Steris, REVISS, and a State of Massachusetts Inspector. The source is no longer missing. The State is continuing its investigation into the circumstances of this event. Notified R1DO (Burritt), R3DO (Lipa), FSME (Henderson), and IRD MOC (Marshall). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-08-20
48175 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-08-10 08:48 | 2012-08-10 08:57 | 2012-08-10 | UNUSUAL EVENT DECLARED DUE TO TOXIC GAS RELEASE At 0848 EDT, on 8/10/12, Watts Bar declared an Notification of Unusual Event (NOUE), EAL Tab 4.4, based on access restrictions to the turbine building due to a toxic gas release (Ammonia). The leak has been secured. Operators are currently in protective gear in the turbine building in an effort to ventilate the residual gas from all affected areas and re-establish normal access. The gas release has caused no personnel injuries or equipment damage. The licensee continues to operation at 100% power. Watts Bar will remain in an NOUE until the area can be ventilated and normal access is reestablished. The NRC Resident Inspector will be notified. The licensee has notified state and local government. Notified DHS SWO, FEMA OPS, DHS NICC, and NUCLEARSSA via email. * * * UPDATE FROM NEWTON LACY TO JOHN KNOKE AT 1331 EDT ON 08/10/12 * * * At 1325 EDT Watts Bar terminated the Notification of Unusual Event (NOUE). The Ammonia leak was due to a valve in the fill line to the Ammonia Mixing Tank not being fully closed, thereby causing the tank to overflow. The NRC Resident Inspector has been notified. Notified R2DO (Rich), NRREO (Evans), IRD MOC (Marshall). Notified DHS SWO, FEMA OPS, DHS NICC, and NUCLEARSSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-08-10
48174 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2012-08-09 18:45 | 2012-08-10 02:27 | 2012-09-19 | CONTROL BUILDING A/C UNIT MAY NOT PERFORM DESIGN FUNCTION ON LOSS OF REDUNDANT A/C UNIT "Affected equipment includes two 4160 volt safety buses, four 480 volt safety buses, four 120 volt AC safety trains, and four 125 volt DC safety trains. "Following an accident Class 1E AC Unit SGK05B may not be able to perform is design safety function if a single failure causes a loss of redundant Class 1E AC unit SGK05A. This is due to continued latent heat input from A train Control Room Pressurization Fan which continues to operate. SGK05A and B provide room cooling for all safety related electrical busses. "Action Taken: Established the following compensatory measure - During accident conditions with both trains of CRVIS [Control Room Ventilation Isolation System] actuated if at any time SGKO5A trips then following completion of immediate actions Control Room pressurization fan CGK04A will be secured to reduce latent heat removal requirements for SGK05B." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MOORE TO KLCO ON 8/11/2012 AT 1058 EDT * * * "[On August 11, 2012 at 1845 CDT, the licensee identified] this condition applies to SGK05A. Action taken: Established compensatory measures that during an accident condition with both trains of CRVIS actuated, if at any time SGK05A or SGK05B trips for any reason then, following completion of immediate actions, Control Room pressurization fan on the same train with the tripped A/C unit will be secured if the other pressurization fan is running." The licensee notified the NRC Resident Inspector. Notified the R4DO (Drake). * * * RETRACTION FROM MARCY BLOW TO DONG PARK ON 09/19/12 AT 1520 EDT * * * "Further engineering evaluation determined that the Class 1E AC unit SGK05A and SGK05B have the ability to remove the heat addition of the Control Room Pressurization Fans. As a result, the condition has been determined to not be reportable per 10 CFR 50.72(b)(3)(v)." The NRC Resident Inspector has been notified. Notified R4DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2012-08-10
48173 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2012-08-09 18:00 | 2012-08-09 19:46 | 2012-08-09 | OFFSITE NOTIFICATION - NON WORK RELATED ON-SITE FATALITY "This is a non-emergency 4 hour informational notification to the NRC in accordance with the reporting requirements of 10 CFR 50.72(b)(2)(xi). "On August 9, 2012 at approximately 1510 hours [EDT], a contract employee suffered a non-work related personal medical event while in an office environment that was located outside of the protected area. The individual was transported offsite and was pronounced deceased at a local hospital. "OSHA is being notified pursuant to the requirements of 29 CFR 1904.39. There was no radioactive contamination involved in this event. Duke Energy has not observed any heightened media interest as a result of the fatality. No other notifications to government agencies are expected and no press releases are intended to be made at this time. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-09
48172 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2012-08-09 08:55 | 2012-08-09 13:34 | 2012-08-09 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a follow-up fitness for duty test. The employee's unescorted access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2012-08-09
48171 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-08-09 10:00 | 2012-08-09 11:47 | 2012-08-09 | EMERGENCY OPERATIONS FACILITY DATA NETWORK MAINTENANCE "At about 1000 PDT on August 9, 2012, Pacific Gas and Electric Company (PG&E) will disconnect the Diablo Canyon Power Plant (DCPP) Plant Data Network to the Emergency Operations Facility (EOF) and redirect the data via the Utility Data Network for hosting the emergency facility data systems. These systems include the Safety Parameter Display System, Plant Process Computer, Emergency Response Facility Display System, and Emergency Assessment and Response System in the EOF. "PG&E expects to have the Emergency Response Data System and the EOF data network unavailable for about 8 hours. During this time, if needed, the TSC will have command and control once staffed, and will have classification, notification and dose assessment responsibility until the display systems are restored to the EOF. Also, if required, a dedicated licensed operator will be available in the control room to provide plant data to the NRC's Emergency Operations Center. "DCPP is making this 8-hour, non-emergency notification under 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-09
48170 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-08-08 13:50 | 2012-08-08 23:32 | 2012-08-09 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 1350 PDT on 08-08-2012, during the performance of an annual surveillance, power supply ARM-E/S-603A was discovered to have out of tolerance voltage readings. ARM-E/S-603A was declared non-functional. This resulted in a loss of the ability to monitor and quantify radiological conditions in multiple areas of the reactor building, due to the loss of ARM-RIS-1 through 10 (Area Radiation Monitor Radiation Indicating Switches 1 through 10). "The loss of ability to monitor and quantify radiological conditions in multiple areas of the reactor building represents a major loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii). As directed by station procedures, compensatory measures have been enacted to have Health Physics personnel tour the affected areas once per shift to document and trend the radiological conditions. ARM-RIS-1 and 4 thru 10 are used for EAL determinations. "ARM-E/S-603A was returned to service at 1524 PDT on 08/08/2012." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-09
48169 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2012-08-08 08:23 | 2012-08-08 13:15 | 2012-08-08 | AUTOMATIC REACTOR TRIP DUE TO HIGH REACTOR COOLANT SYSTEM PRESSURIZER PRESSURE "At 0823 hours on August 8, 2012, Arkansas Nuclear One, Unit 2 (ANO-2) experienced an automatic reactor trip. The reactor automatically tripped due to High Reactor Coolant System Pressurizer Pressure that was caused by a Main Turbine trip due to high condenser back pressure from a degraded vacuum condition. The Reactor Protection System (RPS) performed as designed in response to the High Reactor Coolant System Pressurizer Pressure condition resulting in automatic shutdown of the reactor from approximately 100 percent power. All Control Element Assemblies (CEAs) fully inserted on the trip. The Emergency Feedwater Actuation System (EFAS) actuated for the 'A' Steam Generator only due to level trending slightly below the setpoint. The plant has transitioned to supplying the steam generators using the Auxiliary Feedwater (AFW) system. "The unit is currently in Mode 3 and implementing the transient response process. The investigation into the cause of the trip is ongoing and the local NRC Resident Inspectors have been notified." The unit is in a normal electrical lineup, and the decay heat is being removed by the main condenser via the turbine bypass valves. The State Department of Health was notified and ANO-2 will be issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-08-08
48168 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-07-25 | 2012-08-07 13:34 | 2012-08-07 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED PROCESS GAUGE Louisiana provided the following information via fax: "Georgia-Pacific (GP), AI#2617, had a shutter that failed open on a Ronan Engineering, Model SA-1-F37, Cs-137 2 Ci. The fixed gauge was located at the GP Consumer Operations LLC's GP Port Hudson facility and reported as not functioning properly. The device is used in production to measure chip level within the Esco Digester. This production unit was currently down for annual maintenance. The handle turned but subsequent surveys could not verify that the shutter was completely closed. As a precaution, GP did not allow any personnel to work in the affected area. [A person] with BP Sales evaluated the device and cycled the shutter to an open position so that the receiver got a positive reading. Therefore, the gauge appears to be functioning properly so that the Esco Digester can restart. The fixed gauge passed previous shutter tests on October 2011 and April 2012. GP plans to replace the gauge within the next 90 days. The gauge is 500 feet above ground and no employees work daily around the gauge." NMED Item Number: LA120002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-08-15
48167 | 0 | TEAM INDUSTRIAL SERVICES, INC. |  |  |  |  | 2012-08-06 15:00 | 2012-08-07 14:24 | 2012-08-07 | RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT DUE TO DAMAGED GUIDE TUBE A radiography crew working at the Marathon Refinery in Detroit, MI experienced a failure of the source to retract on their QSA-880-D radiography camera due to the source binding in the guide tube. While the source was out, the radiography camera fell approximately 18 inches from the scaffolding and landed on the guide tube end. The personnel cordoned off the area and called for assistance. The site supervisor was able to fully retract the source into the shielded position. The radiography camera was removed from service and is being sent to the manufacturer for evaluation. Based on dosimetry readings, exposure levels were not above normal readings. The highest badge reading resulted in 54 mrem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-08-15
48166 | -1 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-08-07 | 2012-08-07 13:31 | 2012-08-08 | AGREEMENT STATE REPORT - MISSING SOURCE "The licensee's RSO at the University of Chicago called to advise that while performing a routine inventory of sealed sources, one radioactive source was determined to be missing . A radioactive strontium source which was believed to have been constructed at the University in 1972 was examined more closely than in the past and no radiation readings were detected from it. The source had been made at the University in 1974 to contain 0.828 milliCi of Sr-90. The source was not officially added to the sealed source inventory and leak test records until the mid '90s. For the past 12 years (and perhaps longer) the source had been in storage and unused while use of a similar commercially constructed source was favored. On this occasion the source was removed from the locked storage safe and from the presence of the other stored sources and direct readings from the 3 inch bolt showed no elevated radiation levels. "No ready explanation as to why the radioactivity which had been embedded into the bored centerline of the bolt was not present was available. The item had been transferred to a new researcher in 2000 when the original researcher had retired and had not been used since. A comprehensive review of records suggests that a similar source and quantity was disposed in the 80's however direct correspondence to provide strong assurance that the disposed material and the missing quantity were a match was not possible. Interviews were conducted with the current responsible investigator, past students and colleagues of the original user. Those interviews were inconclusive on the fate of the radioactive material. No other items or sealed sources have been identified as missing from the secure storage location or the researcher's inventory. "Without additional information to verify the source's whereabouts, the licensee has declared the source as missing with little chance of recovery. The licensee advised that a written report will be filed in advance of the 30 day deadline. The current activity of Sr-90 involved would be 317 microCi." Illinois Item Number: IL12013 * * * RETRACTION ON 8/8/12 AT 1518 EDT FROM DAREN PERRERO TO DONG PARK * * * "The licensee's Radiation Safety Officer called the Agency [State of Illinois] on the morning of August 8, 2012 with additional information concerning the August 7, 2012, reported missing Sr-90 source. Based on continued reviews of purchase records, inventories and direct radiation measurements from sources present at the laboratory location, the missing source of Sr-90 has been identified as being in their possession but as a different and mislabeled source. Discrepancies noted between purchase records, inventory records and leak test records caused radiation safety staff to look closer at the existing results of the physical inventories they had performed in an attempt to locate the missing source. After conducting reference radiation measurements from a known quantity source of Sr-90 and then taking measurements from the remaining Sr-90 sources on the inventory, a source holder incorrectly identified as containing a larger activity Sr-90 source was confirmed as being the missing source. The licensee's 30 day report will detail the cause of the event, corrective action taken as well as actions taken to prevent future occurrences." Notified R3DO (Lipa) and FSME Events Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-08-15
48165 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-07 | 2012-08-07 11:30 | 2012-08-07 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK OPEN Texas provided the following information via email: "On August 7, 2012, the licensee notified the Agency that on August 6, 2012, the shutter on a Ronan Model SA-1 fixed nuclear gauge, containing 100 millicuries of cesium-137, at its facility in Longview, Texas, was found to be stuck in the open position. During routine inspection and operation checks in March 2012, the licensee observed that the shutter was difficult to operate. The licensee's maintenance staff had made several unsuccessful attempts to fix the problem. On August 6th, the maintenance staff was going to make another attempt but the shutter was completed stuck and could not be freed. The shutter on this gauge is in the open position during normal operation so there was no increased risk to any individual and there have been no exposures. The licensee has contacted the manufacturer to schedule repairs, has notified employees of the gauge's status, and has implemented administrative controls to restrict access until repairs are completed. More information will be provided as it is obtained, per SA-300. "Source/Source Holder information: "Model: Ronan SA-1 "Cesium-137 -- 100 millicuries "Serial #: JJ590" Texas Incident #: I-8973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-08-15
48164 | 0 | ITT ENIDINE |  |  |  |  | 2012-06-22 | 2012-08-07 09:09 | 2012-08-07 | PNEUMATIC FILTER REGULATOR FAILURE TO COMPLY WITH SPECIFICATIONS The following was received via fax: "The ITT Conoflow model GFH25 pneumatic filter regulator sales literature specifies the effect of supply pressure change as 0.12 psi of output pressure decrease per 25 psi increase in supply pressure. On June 22,2012, this specification was evaluated and a discrepancy between the published supply pressure effect and the actual supply pressure effect was discovered. The effect of changing supply pressure may be as great as 3.7 psi decrease, per 25 psi increase in supply pressure. "This supply pressure effect specification applies to all past, current, and future production of this product line. This product was previously denoted as the GFH20 series filter regulator. "Sales literature and instruction manuals will be revised to remove the erroneous specification. "Facilities which use this product should evaluate this increase in supply pressure effect against their compressed air systems pressure fluctuation, to determine if the associated change in regulated output pressure could pose a safety risk. "The attached table [below] is a list of customers, and the specific part numbers procured from ITT since 2002. These customers will be notified of this change in specification by August 17, 2012." Contact ITT ENIDINE - JEFFREY GOTTHELF Ph. 864-647-9521 Ext. 318 for details. GFH20 / GFH25 filter regulator customer list (2002 to present): CUSTOMER NAME PRODUCT ACSYR SL GFH20XT1767F and GFH20XT1767G ALABAMA POWER COMPANY GFH25XT1767F APTRADE INC GFH20XT1767G ARGO TURBOSERVE CORP (ATC) GFH20XT1767F and GFH25XT1767G CAMERON LTD GFH20XT1767G CONTROL COMPONENTS INC GFH20XT1767G and GFH20XT1767C and GFH20XT1761F DOMINION ENERGY KEWAUNEE GFH20XT1767C DUKE POWER COMPANY GFH20XT1767F EFH CORPORATE SERVICES GFH20XT1767G and GFH25XT1767G ENTERGY NUCLEAR OPERATION GFH20XT1767G and GFH20XT1767F ERGYTECHINC GFH20XT1767F EXCELON BUSINESS SERVICES GFH20XT1767G and GFH20XT1767F and GtFH25XT1767G FIRST ENERGY CORPORATION GFH25XT1767F and GFH25XT1767G FLOWSERVE US INC GFH25XT1767G GEFRAN BENELUX NV GFH20XT1767F INDIANA MICHIGAN POWER CO GFH20XT1767C KOREA HYDRO & NUCLEAR PWR GFH20XT1767C and GFH20XT1767G and GFH20XT1767F and GFH25XT1767G OMAHA PUBLIC POWER DIST GFHZOXT1767F ONTARIO POWER GENERATION GFH20XT1767G and GFH25XT1767G and GFH25XT1767F PACIFIC GAS & ELECTRIC CO GFH20XT1767C PREMATCENICA S A GFH20XT1767G SANGJIE COMMERCIAL CO LTD GFH20XT1767G SPX VALVES & CONTROLS GFH20XT1767G STP NUCLEAR OPERATING CO GFH25XT1767C SYG, SA GFH20XT1767G and GFH20XT1767F and GFH25XT1767G TENNESSEE VALLEY AUTH GFH20XT1767G and GFH25XT1767F TXU TEXAS GENERATION COMPANY GFH20XT1767G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-08-07
48163 | 0 | ITT ENIDINE |  |  |  |  | 2012-06-20 | 2012-08-07 09:09 | 2012-08-07 | PRESSURE TRANSDUCERS FAILURE TO COMPLY WITH SPECIFICATIONS The following was received via fax. "The ITT Conoflow model GT25 series current to pressure transducer specifies air consumption of 0.2 scfm. On June 20, 2012, a discrepancy between the published air consumption specification and the acceptance procedure for production verification was discovered. Units manufactured prior to June 20, 2012 may have air consumption as high as 0.299 scfm. "Corrective and preventive actions have been implemented to bring the product into specification, and insure compliance to specification prior to shipment. "Nuclear facilities which use this product should evaluate this potential increase in instrument air consumption against their systems air capacity, to determine if this condition could pose a safety risk. "ITT Enidine will evaluate and correct any affected product. The attached table [below] is a list of customers, and the specific part numbers procured from ITT since 2002. These customers will be notified of this potential product defect by August 17, 2012." Contact ITT ENIDINE - JEFFREY GOTTHELF Ph. 864-647-9521 Ext. 318 for details. The following is an ITT GT25 Series customer list (2002 to present): CUSTOMER NAME PRODUCT ACSYR SL GT25CA1826 ALABAMA POWER COMPANY GT25CA1826 ASIAM INT'L (TAIWAN) INC. GT25CA1826 ONTARIO POWER GENERATION GT25CD1826 CONTROL COMPONENTS INC GT25CD1826 DETROIT EDISON GT25CD1826 DTE ENERGY GT25CD1826 ENERGY NORTHWEST GT25CA1826 ERGYTECH INC GT25CD1826 ENRICO FERMI POWER PLANT 2 GT25CD1826 EXELON BUSINESS SERVICES GT25CA1826 FLOWSERVE GT25CA1826 GEFRAN BENELUX NV GT25CA1826 KOREA HYDRO & NUCLEAR PWR GT25CA1826 NEBRASKA PUBLIC POWER GT25CA1826 NUCLEAR POWER PLANT KRSKO GT25CA1826 OMAHA PUBLIC POWER DIST GT25FA1826 TVA NUCLEAR ASSURANCE AND LICENSING GT25CD1826 and GT65CD1826 CENTRAL NUCLEAR DE ALMARAZ GT25CD1826 AMERGEN ENERGY, LLC GT25CA1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-08-07
48162 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-06-30 | 2012-08-06 16:29 | 2012-08-06 | AGREEMENT STATE REPORT - RADIOACTIVE IODINE SEED DETECTED IN REFUSE The Commonwealth of Virginia submitted the following information via facsimile: "On Monday July 30th, the VRPM [Virginia Radioactive Materials Program] was notified by the Maryland Radiation Program that SteriCycle's monitor detected radiation from a Bio box picked up at INOVA Fairfax Hospital. RSO, Inc. of Maryland performed a radiation survey with the highest reading of 0.7 mrem/hr on contact. They also performed radioisotope identification with a Bicron Fieldspec which indicated I-125. The Bio box was returned to INOVA Fairfax Hospital on August 1st where it was examined by Radiation Safety staff. A red bag of infectious waste containing one I-125 seed was discovered. The seed was assayed using a well-counter which indicated it to be 0.22 mCi. INOVA Fairfax decay corrected this activity to the normal seed activity of 0.28 mCi, which indicated it was implanted on July 10th. A review of patient implants for July 10th is being performed and staff involved are being interviewed. "Media attention: none." VA Event Report ID No.: VA-12-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-08-14
48161 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-12-15 | 2012-08-06 16:29 | 2012-08-06 | AGREEMENT STATE REPORT - MISSING ELECTRON CAPTURE DETECTOR The Commonwealth of Virginia submitted the following information via facsimile: "Virginia Tech reported a missing radioactive source to VRMP [Virginia Radioactive Materials Program] by telephone. The lost material is an electron capture detector (ECD) containing a foil source of 15 mCi of Ni-63 (serial number F2162), dated 4/1/91, installed in a Hewlett Packard model 5890 Gas Chromatograph (GC). The source was missed during the December 2011 leak testing period but actually had not been seen since its December 2010 leak test. For the June 2011 leak test some GCs with ECDs were packed up in preparation for a move to a different facility and it was assumed that all four ECD containing GCs were crated but only three were apparently included. All Chemistry laboratories at Virginia Tech have been checked, but it has not been found. It appears that a contractor may have removed the source containing equipment along with other materials as scrap during the demolition of Davidson Hall where the source had last been seen. Attempts are being made to determine where the 'scrap' material has been taken and efforts will continue to investigate further. "Media attention: none." VA Event Report ID No.: VA-12-03 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-08-14
48160 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-05-18 | 2012-08-06 12:59 | 2012-08-14 | AGREEMENT STATE REPORT - UNACCOUNTED FOR BARIUM-133 SOURCES The following information was received from the Mississippi Department of Radiation Health via e-mail: "Two (2) Ba-133 [3.86 mCi each] attenuation sources were discovered missing from a quarterly health physics audit at Grenada Lake Medical Center by their consultant. It was discovered by the health physics consultant in early July that documentation regarding the receipt of the sources was not available. "On 5-18-2012, Bayshore Medical, a third party company was contracted by Philips Healthcare to disassemble and remove a Marconi Axis gamma camera from Grenada Lake Medical Center. The sources were encased inside tungsten holders that were installed inside beacon devices attached to each head of the camera. The nuclear medicine technologist at Grenada Lake Medical Center showed the service engineer for de-installation of the camera the location of the camera and explained to him that Grenada Lake Medical Center would need a receipt record for the two (2) sources removed. The technologist left work for a week during the time the gamma camera was being disassembled and removed from the facility. Upon returning back to the facility the technologist forgot to verify receipt of the sources from the service company. "Bayshore Medical claimed there was no radioactive sources installed on the Marconi camera removed from Grenada Lake Medical Center. Neither Bayshore Medical or the company that de-installed / bought the camera has a radioactive materials license. Grenada Lake Medical Center has been in contact with Bayshore Medical to track the location of the beacon devices and return them to their facility. The licensee has contacted Philips Healthcare for copies of service records to show the sources were previously installed in the camera. DRH [Mississippi Department of Radiation Health] was contacted by Grenada Lake Medical Center's health physics consultant on 8-3-2012 with a scheduled return date of 8-6-2012, for the beacon devices and sources in question. "DRH [Mississippi Department of Radiation Health] received a written report of the incident on 8-3-2012. Grenada Lake Medical Center's Radiation Safety Committee has discussed the issue and has developed a policy for future source transfers to prevent a reoccurrence of this incident. Grenada Lake Medical Center will have a person physically verify the removal of any radioactive source along with completing a transfer record prior to any source transfer. Also, Grenada Lake Medical Center will verify that a service company has a radioactive material license to possess and transfer radioactive material." MS Event: 120002 * * * UPDATE ON 8/14/12 AT 1237 EDT FROM JAYSON MOAK TO DONG PARK * * * The following information was received from the Mississippi Department of Radiation Health via e-mail: "Between 5-18-2012 and 5-28-2012, a service engineer from IRS disassembled and removed a Marconi Axis gamma camera from Grenada Lake Medical Center. The camera was previously sold to Philips Healthcare by the licensee. Philips Healthcare then sold the camera to Bayshore Medical who then sold the camera to IRS. The camera remained at the licensee's location throughout the multiple transactions. "On 8-10-2012, IRS, the company who bought the camera from Bayshore Medical and de-installed the camera from the licensee's location on 5-18-2012, was contacted by DRH [Mississippi Department of Radiation Health]. IRS claimed there were no sources present prior to de-installation of the camera from the licensee's facility." Notified R4DO (Hagar) and FSME Resources Events via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-08-20
48159 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-04 10:35 | 2012-08-04 12:53 | 2012-08-04 | OFFSITE NOTIFICATION DUE TO LOSS OF TONE ALERT RADIO "On Saturday August 4, 2012, at 1035 EDT the National Weather Service (NWS) Jacksonville Florida Office notified Plant Hatch Nuclear Plant [HNP] of a loss of the NWS Tone Alert Weather Radio System. Site emergency procedures define a loss of Tone Alert Radio for greater than 15 minutes as a significant loss of Emergency Communications. "The NWS Tone Alert Weather Radio is utilized as the Prompt Notification System (PNS) for HNP. The loss impacts the ability to notify the Emergency Planning Zone (EPZ) Population for the HNP. This failure meets NRC 8-hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "The State of Georgia Department of Homeland Security/Georgia Emergency Management Agency (GEMA) 24-hour warning point and the '911' dispatch centers of Appling, Jeff Davis, Tattnall and Toombs counties were notified so compensatory measures would be available should the PNS be needed. This consists of utilizing route alerting and the 'Code Red' system, which is a reverse 911 feature available from the county 911 center. This notification meets the 4-hour notification reporting criteria 50.72(b)(2)(xi)." The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 8/4/12 AT 2212 EST FROM FRANK GORLEY TO DONG PARK * * * The NWS Tone Alert Weather Radio System has been restored to service as of 2130 EDT. The licensee will notify the NRC Resident Inspector. Notified R2DO (Ernstes). | 100 | 63 | 0 | 100 | 63 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-08-04
48158 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-08-03 14:00 | 2012-08-03 15:27 | 2012-08-03 | CONFIRMED POSITIVE ON A FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's unescorted access has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2012-08-03
48157 | 0 | FLOWSERVE |  |  |  |  | 2012-08-03 | 2012-08-03 14:34 | 2012-08-03 | PART 21 - DEFECTIVE VALVE SEAL CAP The following was provided via fax: "Background: "On July 17, 2012, Duke Power - McGuire NPP notified Flowserve Corporation that they had attempted to install a Seal Cap supplied by Flowserve on a Kerotest 1-1500 Y-Type Globe Valve. They found that the Seal Cap could not be installed on the valve due to interference with the Valve Stem. "Discussion: "The Seal Cap is used to contain leakage past the Valve Diaphragm. The Seal Cap fits over the Valve Stem after Handle removal and is screwed onto the Yoke until it contacts the top of the Body. It is then seal welded to the Body to create a leak tight cap. At this point the Seal Cap is considered pressure retaining. "Inspection of the Seal Cap revealed an inside flat bottom in lieu of the conical bottom shown on the drawing. The conical drill point allows clearance for the valve stem when the Seal Cap is installed on the valve. Review of a layout shows the Seal Cap with a Flat bottom cannot be completely installed whether the valve is open or closed. "Conclusion: "The Seal Cap with a flat bottom cannot be properly installed on the Kerotest Series R9900 size 1/2 to 2 Valves for which it was designed. The Valve Stem will prevent complete installation and the ability to seal weld the Seal Cap to the Body. The Seal Caps supplied would not be available at the Nuclear Power Plant site for an urgent repair if required. The following Nuclear Power Plant Utilities were provide these Seal Caps without the conical shaped area. TVA - Purchase Order# 00020077-00050 and 00020077-00018 First Energy - Purchase Order# 45108999, and 45254808 Alabama Power - Purchase Order# QP040387, QP040872 and QP060575 Duke Power - Purchase Order # NM18494 001, NM25245, 00108212 and 00124677. "Based on the above, the Nuclear Utilities need to be notified concerning this deviation so that an evaluation may be performed to determine if this constitutes a defect that could create a substantial safety hazard." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-08-03
48156 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-08-03 12:05 | 2012-08-03 14:03 | 2012-08-03 | LOSS OF COMMUNICATIONS CAPABILITY "At 1205 EDT on August 3, 2012, the primary telephone service provider for the James A. FitzPatrick Nuclear Power Plant (JAF) experienced a failure of their communications circuit. This failure has resulted in a major loss of communications equipment at the JAF site. The JAF dedicated Emergency Notification System (ENS), Health Physics Network (HPN), and Radiological Emergency Communications System (RECS) phone and all other plant phones served by this provider are not functioning as a result of this failure. Alternate dedicated cellular, satellite, and land-based phone lines serviced by other providers remain available to perform communications with off-site facilities. "This communication failure impacts the ability to readily receive and transmit information between the NRC and JAF. The loss of both the ENS and the HPN constitutes a major loss of communications capability and meets NRC 8 hour reporting criterion 10CFR50.72(b)(3)(xiii). "The communications provider has been contacted to enact repairs to the affected communications circuit. There is currently no estimated time of restoration." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 8/3/12 AT 1601 EDT FROM STEVE DEFILLIPPO TO DONG PARK * * * "The communication lines reported as lost in the original notification have been restored to service and are functional. The NRC Resident Inspector had been notified." Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-03
48155 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-08-03 | 2012-08-03 12:03 | 2012-08-31 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following was received from the State of Arkansas via email: "On August 3, 2012, a licensee notified the Department (Arkansas Department of Health, Radioactive Materials) that the shutter mechanism on a RONAN Model# SA1-F37 gauge (SN# 6481GQ), mounted at the apex of a mixing bin, was stuck in the open position. This was discovered during routine maintenance. Since the shutter is in the open position and does not pose an immediate safety risk, the plant continues to operate. The Department was told that even though the gauge is only accessible via man-lift, the gauge has been tagged with a caution sign. The facility has sent email notifications to all personnel as well as posting notices in the plant. The gauge contains 100 mCi of Cs-137. The facility has contacted the manufacturer and the Department will make an onsite visit to coincide with the repair. Further information will be provided as it is obtained. "Arkansas Incident # AR-2012-005" * * * UPDATE VIA E-MAIL FROM ROBERT PEMBERTON TO DONALD NORWOOD ON 8/31/2012 AT 1139 EDT * * * "On 8/9/12, a RONAN technician performed repairs on a RONAN Model SA1-F37, SN# 6481GQ fixed gauge at the Del-Tin facility in El Dorado, Arkansas to correct a stuck shutter. The device was removed from its mounting, disassembled, cleaned, reassembled and remounted. The shutter is now functional. A wipe test showed no leakage. "The root cause was found to be a dry rotted seal that allowed moisture and debris into the mechanism. "The Department considers this event closed." Notified R4DO (Proulx) and E-mail to FSME Event Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-08-13
48154 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-08-02 09:00 | 2012-08-02 16:16 | 2012-08-02 | NON-WORK RELATED ONSITE FATALITY "This is a non-emergency 4 hour informational notification to the NRC in accordance with the reporting requirements of 10CFR50.72(b)(2)(xi). "At approximately 0900 on 8/02/12, a contract employee suffered a non-work related personal medical event and was transported offsite. The contract employee was pronounced deceased at a local hospital. A courtesy notification was made to OSHA at 1304." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-08-02
48153 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-08-02 10:51 | 2012-08-02 15:51 | 2012-08-02 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE "A plant worker was overcome with heat and became unconscious while working in a non-contaminated area inside the Radiological Control Area. Onsite medical personnel determined the individual should be transported to an offsite medical facility for treatment. Radiation protection personnel were unable to fully verify the individual was not contaminated prior to transport to the offsite medical facility. Radiation protection personnel accompanied the individual to the medical facility, and while en route, completed the required surveys. No contamination was found. "This report is being made in accordance with 10CFR50.72 (b)(3)(xii) for an event requiring the transport of a potentially radioactively contaminated individual to an off-site medical facility for treatment." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-08-02
48152 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-08-02 08:40 | 2012-08-02 11:53 | 2012-08-02 | AGREEMENT STATE REPORT - POTENTIALLY STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of Colorado via email: "On Thursday August 2, at approximately 0840 MDT (Mountain Daylight Time) a portable gauge licensee (AG Wassenaar, Inc. License 212-01 Amendment 21) based in Denver, Colorado notified the Colorado Department of Public Health and Environment (CDPHE) Radioactive Materials Unit on-call duty officer that a gauge was missing and possibly stolen. The gauge had last been seen on Monday July 30 at 4:00 pm at the temporary work site. Upon returning to the office, the gauge user unlocked the box but became distracted and did not check-in the gauge. The gauge user then returned to his residence and parked his truck. The employee did not return to work until the morning of Thursday August 2nd, when he realized that the gauge was not in its case in the truck. The employee believes it may have been stolen from his residence on Tuesday night, however the licensee's employees are currently searching the residence, surrounding neighborhood, and last job site. "The gauge involved was a Troxler model 3430 (gauge serial number 26071), containing 8 mCi of Cs-137 (serial #75-9099) and 40 mCi of Am-241:Be (serial #47-22450). "The licensee was instructed to conduct a thorough search for the gauge in all known locations where it could be, and to also notify the local police should it not be found within the hour. "Additional information and an incident report from the licensee is pending." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-08-10
48151 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-08-02 11:09 | 2012-08-02 12:08 | 2012-08-02 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "This is a one-hour report for the discovery of a condition which met the Emergency Plan criteria for an emergency action level (EAL) declaration of an Unusual Event (UE). At 0320 hours on August 2, 2012, a flame was observed coming from a hydrogen vent pipe on the Turbine Building roof. At 0519 hours the hydrogen supply from the hydrogen storage facility was secured and the flame was extinguished. At 1109 hours, a detailed review of the event determined that the emergency plan criteria for declaration of an Unusual Event existed due to a flame greater than 15 minutes in the Protected Area. This report is being provided within one hour of the discovery of the undeclared event. As discussed in NUREG 1022, Revision 2, an actual declaration of an Unusual Event is not necessary. The basis for the emergency classification no longer existed at the time of discovery. "The safety significance of this event is minimal. There was no known damage to plant equipment and no adverse effect to any plant safety systems. This event had no impact on the health and safety of the public." The NRC Senior Resident Inspector has been notified, as well as the State and local governments. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW | [5 empty] | 0 | 2012-08-02
48150 | 0 | BETTER ROADS ASPHALT CORP |  |  |  |  | 2012-08-01 11:45 | 2012-08-01 17:14 | 2012-08-02 | DAMAGED CPN MOISTURE DENSITY GAUGE A construction roller damaged the outer housing of a CPN moisture density gauge while it was sitting on the asphalt. The sources were fully contained. A portable radiac verified no abnormal radiation and swipe tests were performed to verify the sources were not leaking. Gauge Model: MC-1 DRP CPN Sources: Cs-137 10 milliCuries Am-241 50 milliCuries * * * UPDATE ON 8/2/12 AT 1415 EDT FROM MARIA CORDERO TO DONG PARK * * * At 1145 EDT on 8/1//12, a construction roller damaged the upper housing of the nuclear gauge. The RSO was notified at 1150 EDT. A Radiation Physicist Consultant from the Department of Health conducted a visual inspection and radiation surveys to verify shielding integrity. The leak tests of the two sources were negative. The authorized user placed the gauge in a shipping case for storage in the company area. The gauge will be returned to the manufacture for repairs. Notified R1DO (Krohn) and FSME Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PR | OTH | GEN |  |  |  |  | 0 | 2012-08-01
48149 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-08-01 12:12 | 2012-08-01 16:08 | 2012-08-01 | TSC INOPERABLE DUE TO NON-FUNCTIONAL VENTILATION SUPPORT SYSTEM "At 1212 EDT on August 1, 2012, Harris Operations discovered that cooling function was degraded on Technical Support Center (TSC) air handler 17. The TSC has three air handlers that provide the ventilation function, and the other two are operating with no known problems. Air Handler 17 has been removed from service and troubleshooting is in progress. This event is reportable per 10CFR50.72(b)(3)(xiii) due to the Technical Support Center ventilation support system being potentially non-functional. The on-call Site Emergency Coordinator and Emergency Response Manager have been notified. The Alternate TSC is available per plant procedure if required. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-01
48148 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-08-01 10:10 | 2012-08-01 13:24 | 2012-08-01 | LOSS OF ENS, HPN, PMC, AND RSC PHONE LINES "At 0327 CDT, a call was received from the NRC Operations Center for Emergency Notification System (ENS) phone status check on the commercial phone line. The ENS phone system had no incoming rings, nor a dial-tone. The NRC Headquarters Operations Officer (HOO) was to submit a trouble ticket. "At 0949 CDT, Emergency Planning personnel were working with Verizon Communications to determine the cause of the loss of the ENS phone. Verizon had isolated the problem to the American Broadband network and was working to resolve the problem. "At 1010 CDT, Emergency Planning personnel identified that the Health Physics Network (HPN) line, the Protective Measures Counterpart [PMC] and Reactor Safety Counterpart [RSC] lines with the NRC had also been lost. The Conference Operations Network (COP) and all other commercial phone lines were functional and remained available. All areas were reachable by commercial phone lines. "At 1022 CDT, the FCS Control Room was informed by Emergency Planning personnel of the communication means that were lost. The Emergency Plan per EPIP-OSC-1 was reviewed and verified no initiating conditions applied. "At 1034 CDT, Emergency Planning personnel verified the communications problem with ENS, HPN, the Protective Measures Counterpart and Reactor Safety Counterpart lines was limited to the Fort Calhoun site. The Emergency Operations Facility (EOF) was not affected. "At 1054 CDT, the ENS phone was restored to the FCS Control Room. This was verified by FCS placing a call to the NRC Operations Center. The NRC Operations Center then returned the call. All communications were satisfactorily restored. "At 1132 CDT, the Protective Measures Counterpart line was restored. "At 1142 CDT, the HPN and Reactor Safety Counterpart lines were restored. "This is being reported per 10CFR50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability.'" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-08-01
48147 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-07-31 | 2012-08-01 13:34 | 2012-08-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following was received from the State of North Carolina via email: "On July 31, 2012 a portable nuclear gauge owned by ECS of Raleigh (License Number 092-0253-1) was run over and crushed by a tracked dozer. The incident occurred off Caveness Farm Road in Wake Forest, NC. "The gauge user stated that he had finished performing density testing for the day and was proceeding to leave the job-site. After exiting the job site and traveling the length of Caveness Farms Road to US Highway 1, he noted that his tailgate was down on his pick-up truck. He exited the truck to close the tailgate and noticed that the gauge was missing. He then traveled back to the job site and retraced his path to his testing location. He then observed the gauge approximately 100 feet from where he had been testing. Upon approaching the gauge he noted that it had been crushed by the dozer. The rod on the gauge was in the safe position with the source being shielded. A trigger lock was not present on the gauge at this time. "The ECS RSO was notified and the user instructed the other workers in the area to remain at least 50 feet from the damaged gauge. They did. "The ECS RSO arrived on the job site at approximately 3:00 pm. Upon arrival, he surveyed the damaged gauge with survey meter. A reading of 0.4 mrem/hr was noted at approximately 1 meter and a reading of 1 mrem/hr was noted on contact with the source. The RSO interviewed the dozer operator, who said that he did not see the density gauge in his path of travel but felt the gauge under the dozer as he traveled over it. He proceeded to a safe distance and notified his supervisor. He stated that moments later the ECS technician returned to the area of the damaged gauge. "The RSO contacted the NC Radiation Protection Section and notified them of the incident. A NC RPS inspector was dispatched to the scene. Troxler Laboratories (gauge Mfg) was also contacted about the incident. "When the NC RPS inspector arrived on the job site, he and the ECS RSO surveyed the damaged gauge. Once it was determined the gauge was safe to move, the gauge source rod and shield assembly was placed into the transport case. The rest of the gauge was collected and contained. After the pieces of the gauge were removed from the area where it was damaged, the area was surveyed and no reading over 0.03 mrem/hr were noted. The Inspector indicated that the sources had been recovered and the area was safe to resume work. "Survey readings were taken of the transport case after the sources had been placed in the case. The highest reading was 70 mR/hr contact on the outside of the transport case at the end where the damaged source shield was located. The tungsten sliding block was damaged and was loose. Dose rates on the rest of the transport box were in the 0.1 range, with higher doses on the end. Dose at 1 meter (app) from the transport box end where the source was 0.2 mR/hr. "At 6:00 pm the gauge was transported back to the ECS office. It arrived at the ECS office at approximately 6:45 pm and was stored in the appointed nuclear gauge storage location. The gauge was marked 'Do Not Use' and ECS technicians were instructed not to move the damaged gauge. "ECS will take leak tests on August 1, 2012 and upon being notified of the results of the leak test, Troxler Labs will be notified of our intent to transport the gauge to their RTP location." North Carolina Incident NC 12-43. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-08-09
48146 | 0 | QUALTECH NP CURTISS WRIGHT |  |  |  |  | 2012-08-01 | 2012-08-01 10:56 | 2012-09-10 | POTENTIAL PART 21 ISSUE RELATED TO TYCO TIMING RELAY The following information was provided via facsimile: "QualTech NP is providing this notification as a potential 10 CFR Part 21 issue. We have discovered a manufacturing defect in a timing relay which prevents the relay from operating at a specific setting. This relay was purchased as a commercial grade item and dedicated through our dedication process for safety related applications at our Cincinnati facility. "The subject equipment is TYCO Model CNT-35-96, a timing relay with adjustable trip ranges from seconds up to 9,990 hours. QualTech NP has recently identified a failure mode for this relay in that the device will not trip in the 10H setting. In communications with the manufacturer, they have confirmed that there is a flaw in the design that prevents this specific setting from tripping. "QualTech NP has only sold this unit to two plants, both Exelon. We recognize, however that other utilities could have these installed. Based on the information in hand we are evaluating the need for a 10 CFR Part 21 notification. Since the item was qualified under the EPRI SQURTS [Seismic Qualification Reporting and Testing Standardization] Program, the recommended corrective action is to notify EPRI of the condition in order for SQURTS members to perform an impact evaluation. "Additional details will be provided in the formal written report. Please contact Tim Franchuk at 513-528-7900, ext. 176 (office), [redacted] or via email tfranchuk@curtisswright.com for any additional information." * * * UPDATE ON 8/2/12 AT 1659 EDT FROM MARGIE BREWER TO DONG PARK * * * The licensee has revised the third paragraph to read as follows: "QualTech NP has only sold this unit to two plants, Exelon LaSalle and Quad Cities. We recognize, however that other utilities could have these installed. Based on the information in hand we are evaluating the need for a 10 CFR Part 21 notification. Since the item was qualified under the EPRI SQURTS [Seismic Qualification Reporting and Testing Standardization] Program, QualTech NP recognizes that other SQURTS members may have used the qualification basis as part of licensee dedication activities, and therefore, will notify EPRI of the condition." Notified R3DO (Kunowski) and Part 21 group via email. * * * UPDATE AT 1803 EDT ON 09/10/12 FROM TIM FRANCHUK TO S. SANDIN * * * The following update was received via fax: "QualTech NP is issuing this letter to provide additional details from our initial notification dated July 31, 2012 with regard to a potential defect in a timing relay (Log No. 2012-31-00 and 2012-031-01). The affected equipment is TYCO Model CNT 35-96 and the defect is the failure of the component to trip in the 10H setting. The following actions have been taken since the time of the initial notification. "QuaITech NP has notified EPRI, who in turn has notified SQURTS members of the defect in the 10H setting. In addition, supplemental testing has been performed to provide reasonable assurance that the defect is limited to the 10H setting. "Please contact Tim Franchuk at 513-528-7900 ext. 176 (office) or via email tfranchuk@curtisswright.com for any additional information." Notified R3DO Giessner) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-08-01
48145 | -1 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2012-07-31 14:06 | 2012-07-31 16:00 | 2012-08-03 | DISCOVERED VULNERABILITY IN A SAFEGUARDS SYSTEM There was a discovered vulnerability in a safeguards system that could have allowed access to a controlled area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 8/3/12 AT 1437 EDT FROM WAYNE CLAYTON TO DONG PARK * * * This event notification is being retracted based on review of guidance criteria. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R3DO (Kunowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-07-31
48144 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-30 13:50 | 2012-07-30 14:29 | 2012-07-31 | NOTIFICATION OF NORTH CAROLINA WILDLIFE RESOURCES DUE TO STRIP BASS MORTALITY "Duke Energy notified the NC Wildlife Resource Commission of dead striped bass in the vicinity of the McGuire low level intake. Notification was made 7/30/12 at 1350 EDT. In addition, the NC Dept. of Environment and Natural Resources will be notified. "Dead fish are suspected to have been caused by increasing lake temperature and decreased oxygen levels, which is common during the late summer." The NRC Resident Inspector will be notified. Notified both R2DO (Franke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-31
48143 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2012-07-30 12:43 | 2012-07-30 19:39 | 2012-07-30 | ONSITE FATALITY "A fatality occurred at the facility due to cardiac arrest. The individual was a maintenance supervisor, not actively engaged in work. He was en-route to an on site meeting. Specific details if requested by regional office will be included in a 30 day follow-up report. "In accordance with 10 CFR 70 Appendix A(c) this event is being reported concurrently with a report to the New Mexico Occupational Health and Safety Bureau. The report is required within 8 hours of a fatality at the facility. "The event did not impact plant safety or systems, structures or components nor did it involve the release of any material. "Facility medical personnel provided first aid until Eunice Fire and Rescue transported the individual to the Lea County Regional Medical Facility." No press release is planned. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2012-07-30
48142 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-07-30 06:43 | 2012-07-30 13:16 | 2012-07-30 | FAILED PRE-ACCESS FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a pre-access fitness-for-duty test. The employee was not granted access to the site. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2012-07-30
48141 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2012-07-26 21:20 | 2012-07-27 00:29 | 2012-07-27 | LOSS OF AC POWER TO THE EMERGENCY OPERATIONS FACILITY "At 2120 [CDT] [on 07/26/12], a loss of AC power to the Emergency Operations Facility (EOF) occurred effecting emergency response capability. The Technical Support Center (TSC) remained available. In the event of on emergency declaration requiring an EOF, the emergency Response Organization (ERO) would have been directed to report to the Backup EOF. "Assessment capability via SPDS was not lost during this time period and communications equipment also remained available. "Coincident with no local offsite power being available, the backup diesel generator was unable to supply AC power to the facility due to an overvoltage condition present on the transfer switch. No power was available from the time period of 2120 [CDT] to 2133 [CDT] when local offsite power was restored to the building. "This notification is being made in accordance with 10 CFR 50.12(b)(3)(xiii) due to the unavailability of an emergency response facility." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-27
48140 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-07-26 21:51 | 2012-07-26 23:24 | 2012-07-26 | TECH SPEC REQUIRED SHUTDOWN FOR DIESEL MAINTENANCE EXCEEDING ALLOWED OUTAGE TIME "At 21:51 [CDT] [on 7/26/12], Farley has commenced shutdown of Unit 1 in accordance with T.S. 3.8.1, AC Sources - Operating. 1B Diesel Generator was removed from service on 7/16 at 21:52 [CDT] for a planned 24 month outage. Due to emergent equipment issues with the diesel, the RAS (Required Action Statement) time of 10 days to return the diesel generator to service has not been met. Unit 1 shutdown to Mode 3 has commenced. The unit must be in Mode 3 by 03:52 [CDT] on 7/27/12, and Mode 5 by 09:52 [CDT] on 7/28/12." The licensee has informed the NRC Resident Inspector. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-07-26
48139 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-05-31 05:35 | 2012-07-26 17:52 | 2012-07-26 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID PRIMARY CONTAINMENT ISOLATION VALVE ACTUATION "At 0535 [PDT] on 5/31/12 during power ascension following a maintenance outage, a loss of power to the Reactor Protection System (RPS) 'B' occurred due to the unexpected opening of the circuit breaker (RPS-CB-MG2) for the RPS 'B' motor generator. The loss of RPS 'B' resulted in a half scram signal, closure of Primary Containment Isolation Valves (PCIVs) from multiple systems and loss of power to main steam line radiation monitors (MS-RIS-610B & MS-RIS-610D). No plant parameters or maintenance activities existed which would cause the opening of RPS-CB-MG2; therefore, this is considered to be an invalid actuation of a system listed in 10CFR50.73(a)(2)(iv). "The half scram signal, closure of Primary Containment Isolation Valves (PCIVs) from multiple systems, and loss of power to MS-RIS-B & D were an expected response to the loss of RPS 'B'. "Power ascension was temporarily halted. RPS 'B' was repowered from an alternate power supply. The half scram signal was reset, the containment isolation valves were opened and the affected systems were returned to normal operation. Power ascension was resumed. The circuit breaker (RPS-CB-MG2) was replaced and RPS 'B' was returned to its normal power supply. "Initial investigation efforts have not determined a cause for RPS-CB-MG2 opening. Investigations into the cause of RPS-CB-MG2 opening are continuing. "As indicated in 10CFR50.73(a)(1), in the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv)(A), the licensee may, at its option, provide a telephonic notification to the NRC Operations Center within 60 days of discovery of the event instead of submitting a written LER. This 60-day telephone notification is being made to meet the reporting requirements instead of submitting an LER since the actuation was invalid. "The following additional information is provided as specified in NUREG-1022: "The specific train(s) and system(s) that were actuated: PCIVs in multiple systems EDR-V-19 Drywell Equipment Drain Inboard Isolation Valve EDR-V-20 Drywell Equipment Drain Outboard Isolation Valve FDR-V-3 Drywell Floor Drain Inboard Isolation Valve FDR-V-4 Drywell Floor Drain Outboard Isolation Valve RWCU-V-1 Reactor Water Cleanup Suction Inboard Isolation Valve RWCU-V-4 Reactor Water Cleanup Suction Outboard Isolation Valve RRC-V-19 Reactor Water Sample Inboard Isolation Valve RRC-V-20 Reactor Water Sample Outboard Isolation Valve TIP-V-15 Traversing In-Core Probe Purge Isolation Valve CRD-V-11 Control Rod Drive Scram Discharge Volume Drain Valve "Whether each train actuation was complete or partial: All PCIVs actuations for a loss of RPS 'B' were complete The reactor half scram for a loss of RPS 'B' was a partial activation "Whether or not the system started and functioned successfully: All PCIVs functioned successfully" The licensee notified the NRC Resident Inspector. | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-07-26
48138 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-07-26 14:00 | 2012-07-26 15:43 | 2012-07-27 | AGREEMENT STATE REPORT - MISSING MOISTURE DENSITY GAUGE "At 1400 on July 26, 2012, the Agency [Texas Department of Health] was notified by the licensee that a Humboldt Scientific Inc. (HSI) Model 5001 moisture density gauge was missing and suspected as stolen by a company employee. The employee, a company truck, 2012 white Toyota Tacoma, and the moisture density gauge have been missing all day. The worker failed to report to a job site this morning and his wife reported that she had no contact with him yesterday. Local law enforcement was notified. The gauge contained 10 millicuries of cesium-137 and 40 millicuries of americium-241. "The State of Texas event number for this event is I-8972." * * * UPDATE AT 1241 EDT ON 7/27/12 FROM CHRIS MOORE TO PETE SNYDER * * * "At 0830 on July 27, 2012, the Agency [Texas Department of Health] was notified by the licensee that the Humboldt Scientific Model 5001 Moisture Density gauge reported stolen on July 26, 2012, had been recovered. The licensee stated that the missing worker called the company and reported that the truck with gauge was parked at his residence. The licensee recovered the gauge. The licensee stated that the gauge was still locked and stowed properly in the truck. The licensee stated that an inspection and radiation survey of the moisture density gauge was found to be normal. The employee was fired." Notified the R4DO(Drake), ILTAB(Johnson), FSME Events Resource(Email), and Mexico. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-08-03
48137 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-07-26 | 2012-07-26 15:24 | 2012-07-26 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN UNDERDOSE WITH YTTRIUM-90 SPHERES "Event Type: A medical event (ME) involving the administration of yttrium-90 SIR-Spheres which is reportable under 10 CFR 35.3045(a)(1)(i). "Notifications: On July 25, 2012, the Department's Southeast Regional Office received notification via telephone about this event. "Event Description: The patient received 77% of the intended dose. "Cause of the Event: Currently under investigation and unknown at this time. "Actions: No harm to the patient is expected. The Department [PA Bureau of Radiation Protection] plans to do a reactive inspection. Updates will be provided upon receipt of information." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-08-03
48136 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2012-07-26 09:25 | 2012-07-26 14:27 | 2012-07-26 | CONFIRMED POSITIVE ON A FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a follow-up fitness for duty test. The employee's unescorted access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2012-07-26
48135 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-07-24 | 2012-07-26 13:20 | 2012-07-26 | AGREEMENT STATE REPORT - MISSING OR ABANDONED AND FOUND RADIOACTIVE MATERIALS "During conversion of the former Waltham Watch Co. property to offices and apartments the property owner discovered sub-floor areas to be contaminated with radium-226 and americium-241. "The consultant submitted that the property had functioned as a watch factory; that during World War II the site was used to support the war effort; and that radium was used in self-luminous paints for watches, nuclear panels, aircraft switches, clocks, and instrument dials starting in the early 1900s and was still used as late as the 1960s. The americium was likely not part of the dial painting process and may have been associated with a former tenant. "The consultant reported on radioactive waste manifest dated July 24, 2012 that a total of 890 microCuries (approximately 727 microCuries of americium-241 and approximately 163 microCuries of radium-226) was removed from the property. These materials are in addition to 10 microCuries of radium-226 that was removed from the property on May 23, 2012. In aggregate, the activities of materials meet the reporting requirements of 105 CMR 120.281(A)(1). Radioactive materials discovered and removed were mostly found under layers of flooring in areas of original wood subflooring materials in apartments not yet inhabited. The americium-241 was confined to two areas whereas the radium-226 was discovered in many areas. Final status surveys performed by the consultant indicate that no radioactivity is present above natural background levels in post-remediation areas. "The Agency [Massachusetts Radiation Control Program] continues to investigate this incident and has performed on-site inspection of the specifically licensed person providing decontamination and decommissioning services to the property owner of the site." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-08-03
48134 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2012-07-25 16:02 | 2012-07-25 22:14 | 2012-09-19 | IDENTIFICATION OF A DEGRADED OR UNANALYZED CONDITION "At 1602 [CDT], Engineering personnel notified the control room that during review of a pipe stress calculation it was identified that non-conservative or incorrect methodologies were used in the calculation. This calculation was for a modification to install four; 3 [inch] drain lines between the Essential Service Water (ESW) (safety) and the Service Water (SW) (non-safety) in 1991. A preliminary ME101 stress analysis performed, which corrects the above-identified discrepancies, indicates that the pipe stresses at the drain line weldolet connection exceed the ASME code of record allowable stresses by approximately 50%, when the revised Stress Intensification Factor (SIF) is applied. This modification affected both trains (A & B) ESW trains. "The normal system alignment uses the SW water to supply the ESW, then during accident conditions the SW and ESW systems isolate from each other so that two redundant separate train isolation valves isolate the ESW system. These 3 [inch] drain lines are located in the section of piping that is isolated from the ESW and SW systems. "At the time of notification 'A' ESW was isolated from SW and 'B' ESW was in normal system alignment. 'B' ESW was declared inoperable and action was taken to separate the SW and ESW and isolate the 3 [inch] drain valves. With this action complete the non-conforming components have been removed from service and OPERABILITY of the ESW has been restored. "This condition is been reported per 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." * * * RETRACTION FROM MARCY BLOW TO DONG PARK ON 09/19/12 AT 1520 EDT * * * "Further engineering evaluation determined that the four drain lines [3-inch] between the Essential Service Water (ESW) (safety) and the Service Water (SW) (non-safety) were found to be within the allowable limits for operability and are acceptable. As a result, the condition has been determined to not be reportable per 10 CFR 50.72(b)(3)(ii)(B)." The NRC Resident Inspector has been notified. Notified R4DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-07-25
48133 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-07-25 15:34 | 2012-07-25 17:32 | 2012-07-25 | UNACCOUNTED FOR SOURCE RANGE MONITOR DETECTOR "During annual physical inventory of Special Nuclear Material (SNM) conducted at Grand Gulf Nuclear Station (GGNS), a replacement Source Range Monitor (SRM) detector could not be accounted for. The SRM detector was being stored in the refuel floor storage locker after maintenance activities during RF18. This detector did not function and was removed prior to the start-up therefore, the SRM detector was not subjected to a critical reactor. Actions continue to locate the missing SRM detector. There is no evidence of sabotage or tampering associated with this activity." The licensee notified the NRC Resident Inspector. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | CRIT LOSS/THEFT OF SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 72.74 |  |  |  | 0 | 2012-07-25
48132 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2012-07-25 14:30 | 2012-07-25 14:45 | 2012-07-25 | PRESS RELEASE DUE TO AN ELEVATED LEVEL OF TRITIUM DETECTED ON SITE "TMI is issuing a press release and performing courtesy stakeholder communications as a result of an elevated level of tritium detected in one of 55 on-site ground water monitoring wells near the plant structure. The tritium concentration in the well is contained to the site and well [within] EPA drinking water standards. TMI is performing voluntary communications in accordance with NEI 07-07 Industry Ground Water Protection Initiative and contacting local and state stakeholders as a courtesy. As a result of the press release, a four-hour notification is being made per 10 CFR 50.72 (b)(2)(xi)." The licensee notified the NRC Resident Inspector, the Commonwealth of Pennsylvania and local counties (Dauphin and York). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-25
48131 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-07-24 11:22 | 2012-07-24 19:29 | 2012-07-24 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE DUE TO THE TRIP OF SECONDARY CONTAINMENT SUPPLY AND EXHAUST FANS "Reactor Building (Secondary Containment) Supply Fan 1B (ROA-FN-1B) and Reactor Building Exhaust Fan 1B (REA-FN-1B) inadvertently tripped. Secondary containment pressure exceeded atmospheric pressure which does not meet the surveillance requirement to have secondary containment vacuum greater than or equal to 0.25 inches of water vacuum. This event is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. Alternate supply and exhaust fans were manually started within 4 minutes and Secondary Containment pressure was restored to normal (greater than 0.25 inches water vacuum) within 5 minutes, returning Secondary Containment to operable status. "Event investigation is on-going to determine exact cause of the fans tripping; however, electrical maintenance activities were in progress at the time. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-07-24
48130 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-07-18 | 2012-07-24 15:50 | 2012-07-24 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The following information was received by email: "On the evening of July 18, 2012 the licensee's radiation safety officer contacted the [Illinois Emergency Management] Agency's Radiation Duty Officer to advise that a fixed gauge had failed to perform as expected when an attempt was made to close the shutter in advance of work scheduled to be performed on the vessel it was mounted on. The RSO reports that although the spindle of the handle rotated, the shutter did not close. The shutter remained stuck in the 'open' position and would not close. As a result, the planned work was deferred and access to the confined space has been prohibited. The gauge is mounted such that there are no adjacent work stations and unrestricted access is not possible. Radiation monitoring performed by the radiation safety officer showed no abnormal readings. "The gauge shutter had been successfully tested in March with no abnormalities at that time. The gauge is mounted in such a way that although it is exposed to ambient temperatures, it is not directly exposed to the elements by virtue of an overhead cover. The gauge has not been subjected to any corrosives or solvents or other conditions which exceed the gauge prototype's test conditions. Arrangements have been made to have the manufacturer's representative on-site to conduct an evaluation and effect repairs as necessary at the end of the week." The fixed gauge is a model SA-1 manufactured by Ronan Engineering (serial number 69094). The gauge contains a Cs-137 sealed source (.082 Ci). Illinois Incident: IL 12011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-08-01
48129 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-07-23 | 2012-07-24 14:24 | 2012-07-24 | AGREEMENT STATE REPORT - BROKEN PROCESS GAUGE SHUTTER MECHANISM The following information was received via E-mail: "On July 24, 2012, the licensee notified the Agency [Texas Department of State Health Services] that on July 23, 2012, it discovered a shutter mechanism on an Ohmart SH-F2-45 gauge mounted on the side of a tank at the licensee's facility was broken and the shutter could not be closed. The gauge contained 200 millicuries of cesium-137. The 3/8 inch cast iron shutter rod broke approximately 1/4 inch below the top surface of the gauge. The licensee has submitted the appropriate request to the Agency for the gauge to remain in operation until repairs can be made. The licensee contacted the manufacturer and scheduled the repair. Further information will be provided as it is obtained. "Gauge information: Ohmart SH-F2-45 Serial number: 5334GK "Source information: cesium-137 200 millicuries Serial number: 9-1999" Texas Incident #: I - 8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-08-01
48128 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-07-24 | 2012-07-24 14:23 | 2012-07-24 | AGREEMENT STATE REPORT- UNDERDOSE DURING A BRACHYTHERAPY TREATMENT The following information was received by email: "Wisconsin Department of Health Services (DHS) received notification via voicemail from the licensee on July 23, 2012 regarding the discovery of a brachytherapy medical event that occurred on July 17, 2007. The medical event involved a procedure during which the administered dose differed from the prescribed dose by more than 20% (underdose) for permanent prostate implants using Cs-131 seeds. The prescribed dose was 115 Gy. The delivered dose was 60 Gy. The medical event was identified by DHS inspectors during a recent routine inspection, at which time the inspectors also determined that the licensee had not conducted adequate review of their prostate brachytherapy cases against their medical event criteria. "Per the licensee's procedures, a post-implant CT is performed the same day as the procedure and analyzed within two working days after. If the post-implant analysis reveals an underdose, which occurred in this situation, additional seeds are implanted and another post-implant CT/analysis process follows. The licensee is currently reviewing additional cases dating back to 2003 for medical events against the revised medical event criteria submitted to DHS on June 22, 2012. DHS is investigating the event and is currently in the process of communicating with the licensee regarding decisions on patient notifications. A special inspection team will be sent following the licensee's review." Wisconsin Event: WI 120009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-08-01
48127 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-07-24 05:55 | 2012-07-24 13:43 | 2012-07-25 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "At approximately 0555 [EDT] on 07/24/2012, the AH-17 TSC Cooling Fan was found with the cooling system not fully working. The fan is running, but the condensing compressor is not. Repairs are being planned and will be worked immediately. This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Revision 2. The on call Site Emergency Coordinator and Emergency Response Manager have been notified. The Alternate TSC is available per plant procedure, if required." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM CASPER JERNIGAN TO JOHN SHOEMAKER AT 0929 EDT, ON 07/25/12 * * * TSC cooling system repairs have been completed and the system has been returned to normal. The licensee notified the NRC Resident Inspector. Notified the R2DO (Franke). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-24
48126 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-23 05:08 | 2012-07-24 11:04 | 2012-07-24 | TSC VENTILATION SYSTEM OUT OF SERVICE "On July 23, 2012, at 0508 EDT, the Technical Support Center (TSC) ventilation was tagged out for routine maintenance. It was believed that only the cooling function was affected and that the TSC ventilation system was still capable of performing its intended function of pressurization and filtration. A review by operations today determined that the TSC filtration and pressurization portion was also affected. Under certain accident conditions, the TSC may become unavailable due to the inability of the filtration system to maintain a habitable atmosphere. Compensatory measures exists to relocate the TSC to an alternate location. Currently it is expected that the TSC ventilation system maintenance will be completed by the end of the day shift today and turned over to operations. Operations should start up the system early during night shift (7/24). "This is reportable to the NRC per 10 CFR 50.72 (b)(3)(xiii) as an eight hour non-emergency notification. The event had no effect on plant operations and no impact on public health and safety has been identified. The licensee will notify the NRC Resident Inspector, States and Counties." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-24
48125 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-07-23 03:29 | 2012-07-23 04:24 | 2012-09-12 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0329 EDT, Oyster Creek experienced a loss of offsite power. As a result of the loss of offsite power, the unit automatically scrammed from 100% with all control rods fully inserting and all safety systems functioning as required. Both Emergency Diesel Generators automatically started and are carrying loads on the safety buses. At 0341 EDT, Oyster Creek declared an Unusual Event based on a loss of offsite power for greater than 15 minutes. The unit is stable in Hot Shutdown with decay heat removal via the Isolation Condenser. The cause of the loss of offsite power is currently under investigation by JCP&L. The licensee notified the State and local agencies, as well as the NRC Resident Inspector. The licensee will be making a press release. * * * UPDATE ON 7/23/12 AT 0625 EDT FROM ROBERT SALES TO DONG PARK * * * "Oyster Creek has terminated from the loss of offsite power Unusual Event [at 0538 EDT]. All safety systems functioned as expected for this event." The licensee has notified the NRC Resident Inspector. Notified R1DO (Dimitriadis), NRR EO (Nieh), IRD (Gott), DHS SWO, FEMA, and DHS NICC. * * * UPDATE ON 7/23/12 AT 1205 EDT FROM ANDREW ZUCHOWSKI TO VINCE KLCO * * * "As a result of the loss of offsite power, both Emergency Diesel Generators automatically started and carried loads on the safety buses, as required. Offsite power was returned to service at 0457 EDT and both Emergency Diesel Generators were secured at 0520 EDT. "Per 50.72(b)(3)(iv)(A), Oyster Creek is reporting any event or condition that results in valid actuation of an Emergency AC electrical power system. "Additionally, the Reactor Building (Secondary Containment) differential pressure indicated positive 0.25 inches W.G. at approximately 0357 EDT. Reactor Building differential pressure indication returned to normal at 0434 EDT. Oyster Creek is currently investigating the cause of the positive Reactor Building pressure indication. "Per 50.72(b)(3)(v)(C), Oyster Creek is reporting an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material." The licensee notified the NRC Resident Inspector. Notified R1DO (Gray). * * * UPDATE AT 0914 EDT ON 9/12/12 FROM ERIC SWAIN TO HUFFMAN * * * As a result of further investigation it was found that the Reactor Building Differential Pressure issue was an indication issue only and not indicative of a loss of the secondary containment barrier. The positive indication was caused by a degradation of instrument air pressure to the instrument used to generate the differential pressure indication. The degradation of instrument air pressure was an expected condition caused by the loss of offsite power. Alternate indication, not affected by instrument air pressure, was available throughout the event. The alternate indication read negative 0.4 Inches water gauge throughout the event. Based on this information Oyster Creek is retracting the portion of this report that was reported per 50.72(b)(3)(v)(C), an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material. The licensee has notified the NRC Resident Inspector. R1DO (Newport) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2012-07-23
48124 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2012-07-21 12:10 | 2012-07-21 13:10 | 2012-07-21 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO RCS PRESSURE BOUNDARY INSTRUMENT LINE LEAKAGE "[Calvert Cliffs Nuclear Power Plant] CCNPP U1 identified RCS Pressure Boundary Leakage from the instrument line to 1-PDT-123A, 11A reactor coolant pump differential pressure transmitter. Technical Specification 3.4.13, Action B was entered and requires that the Unit be placed in Mode 3 within 6 hours and Mode 5 within 36 hours. [The licensee has] initiated plant shutdown in accordance with this Technical Specification. Therefore, this is reportable under 10CFR50.72(b)(2)(i) Plant Shutdown Required by Technical Specifications. This is also reportable under 50.72(B)(3)(ii)(A) as a material defect in the primary coolant system that cannot be found acceptable under ASME Section XI, IWB-3600 or ASME Section XI, Table IWB-3410-1." The leak is from an instrument line which monitors reactor coolant pump differential pressure. It is for monitoring purposes only. The leak rate is currently about .08 gpm. The licensee has begun power reduction of the unit and is currently at approximately 73% rated thermal power. The recovery plan is to complete the unit shutdown and then enter containment and repair the leak. The leak is believed to be coming from the same instrument line that was reported to be leaking on July 17, 2012 (see EN #48116). At that time, power was reduced to approximately 10% and a containment entry was made. At that time it was believed that the leak had been isolated and full power operations were resumed. Based on containment sump pump run times and another containment entry, it was determined that the leak apparently had not been isolated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2012-07-21
48123 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2012-07-20 22:30 | 2012-07-20 22:27 | 2012-07-24 | ANTICIPATORY LOSS OF SPDS AND ERDS DUE TO POSSIBLE LOSS OF INTEGRATED PLANT COMPUTER SYSTEM DURING TROUBLESHOOTING "Beginning July 20, 2012, at approximately 2230, troubleshooting of MUX A components and fiber optic cables on the Fermi 2 Integrated Plant Computer System (IPCS) will be performed. A loss of IPCS during the troubleshooting is possible. "The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform and will be out of service if IPCS is lost. These systems would be unavailable to the Control Room and all other Emergency Response Facilities (ERFs). During this time dose assessment capability would only be available in the manual data input mode. The majority of the Control Room indications will remain available to the plant staff, and would be used for emergency response, if needed. Information would be communicated to the NRC using other available communication systems as needed. A follow-up notification will be submitted when the IPCS troubleshooting is complete. "This notification is being made per the requirements of 8 Hour Non-Emergency Notification 10CFR50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BRETT JEBBIA TO VINCE KLCO ON 7/24/2012 AT 2243 EDT * * * "Troubleshooting and repairs have been completed to the Fermi 2 Integrated Plant Computer System (IPCS) as of July 24, 2012 at 1855 [EDT]. No loss of communication ability occurred from initial notification while repairs and restoration were in progress. Event 48123 is retracted. "[The initial anticipatory] notification was made per 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee notified the NRC Resident Inspector. Notified the R3DO (Bloomer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-20
48122 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-07-20 14:00 | 2012-07-20 16:55 | 2012-07-20 | UNIT 2 EMERGENCY DIESEL GENERATORS INOPERABLE DUE TO MISSING FLOOD CONTROL BARRIER SEAL "D5 and D6 Diesel Generators (DG) were declared inoperable at 1400 CDT due to a missing internal flood control barrier seal. The missing flood control barrier seal is required to be installed with Unit 2 in Modes 1, 2, 3, and 4 when the MSIV's are open. "LCO 3.8.1 Condition B was entered for both DGs and LCO 3.8.1 Condition E was entered for two DGs inoperable on the same unit. The DGs could start and run if required at the time of entry. "This condition is reportable per 10CFR50.72(b)(3)(v) as an event or condition that could have prevented the fulfillment of a safety function. "At 1505 CDT the missing internal flood barrier seal was verified in place restoring the safety function. LCO 3.8.1 Condition B and E were exited. "The NRC Resident Inspector has been informed." At this time, it is not known how long the seals had been missing. An investigation is on-going. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2012-07-20
48121 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-07-19 15:37 | 2012-07-19 21:56 | 2012-07-19 | REACTOR PROTECTION SIGNAL ACTUATION DUE TO CHANGING MODE SWITCH POSITION DURING SURVEILLANCE TESTING "During surveillance testing, the reactor mode switch was moved from the locked shutdown position and placed in the refuel position without the minimum required operable source range monitors per Limerick Generating Station Technical Specifications. "Upon discovery of the issue, the reactor mode switch was returned to the locked shutdown position causing an expected but valid RPS actuation. "No control rod motion occurred because all control rods were already inserted at the time of the event." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-07-19
48120 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-07-19 15:30 | 2012-07-19 18:28 | 2012-07-19 | TECH SPEC REQUIRED SHUTDOWN DUE TO INABILITY TO RESTORE MAIN STEAM ISOLATION AUTOMATIC ACTUATION LOGIC AND ACTUATION RELAYS WITHIN THE REQUIRED TIME "At 1530 on July 19, 2012, operators commenced shutdown of DC Cook Unit 1 to comply with LCO 3.3.2, Condition I when the 6 hour time limit to complete Condition C Required Action could not be completed. "At 0734 on July 19, 2012, operators identified that power had been lost to two of four Steam Generator Stop Valve Dump Valves (Dump Valves) on one of the two trains. DC Cook entered LCO 3.3.2 Condition B for Function 4a, manual initiation: 'restore required channel or train to operable within 48 hours.' DC Cook also entered LCO 3.3.2 Condition C for Function 4b, automatic actuation logic and actuation relays: 'restore required channel or train to operable within 6 hours.' Power was restored to one Dump Valve which was then declared operable at 1030. Efforts continue to restore power to the remaining Dump Valve. "Enforcement Discretion was verbally granted by the Nuclear Regulatory Commission at 1736 on July 19, 2012 to begin at 1934 and end at 1934 on July 20, 2012. Upon receiving the Enforcement Discretion, the power reduction was stopped at 1738 at 50% power. "This event is reportable under 10CFR50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications,' as a four (4) hour report. The DC Cook Sr. Resident NRC Inspector has been notified." | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-07-19
48119 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2012-07-01 23:45 | 2012-07-19 17:18 | 2012-07-19 | UNABLE TO RETRACT SOURCE INTO RADIOGRAPHY CAMERA "On July 1, 2012 at 11:45 pm, a radiography crew using remote access technology at the Kuparuk Oil Field on the North Slope of Alaska had the jig, collimator and guide tube dislodge and fall while cranking out the source. With the added weight of the connected jig and collimator, the guide tube ended up hanging straight down 30 feet above a platform floor, creating a sharp bend where the guide tube connects to the camera. The crew was not able to retract the source immediately after the accident. Kakivik's onsite Radiation Safety Supervisor and the RSO were immediately notified. The 2 mr/hr boundary was re-surveyed and adjusted. Constant surveillance and control of the boundary was maintained. Per guidance from the Kakivik's emergency procedures and RSO, the exposure device was to be lowered by ropes onto a suitable working surface. During the camera decent, the guide tube came in contact with piping and was straightened sufficiently to allow the source to be safely cranked into the fully shielded and secured position while still suspended from the ropes. The source was fully shielded within the exposure device by 2:13 am July 2nd. The operation to lower the camera to straighten the guide tube and crank in the source to the fully shielded position took approximately one minute. No exposure to the public or overexposure to Kakivik employees or unauthorized entry into the restricted area was made. All the radiographic equipment was inspected after the accident. The ball connector at the end of the crank drive cable was bent and was replaced. The outside of the guide tube was damaged and taken out of service. The camera including the source pigtail connector was not damaged and was returned to service. "After investigation, the cause of the incident was determined to be the improper use of a magnetic jig that was attached to a surface that did not have sufficient force to hold the combined weight of jig, collimator, guide tube and source. "The corrective actions taken to prevent recurrence included writing a company policy that clearly states that a radiographer may not use magnetic jigs to support the guide tube and collimator unless it is also supported with ratchet straps or a chain wrench or unless the magnetic jig is being used on a flat steel floor surface. This policy will be required to be read and adhered to by all current and new radiographers. This incident will be reviewed with all the Kakivik radiographers and assistants by the RSO or RSS." There were no injuries as a result of this event and there were no overexposures to members of the public or employees. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-07-26
48118 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-07-19 | 2012-07-19 17:06 | 2012-07-19 | AGREEMENT STATE REPORT - 15 PROSTATE BRACHYTHERAPY MEDICAL EVENTS The following information was received via facsimile: "On July 19, 2012, the licensee reported the identification of 15 medical events that were discovered on July 18, 2012, involving permanent implants of iodine-125 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. During a recent inspection, DHS [Department of Health Services] inspectors determined that the licensee was not reviewing prostate brachytherapy cases against the medical event criteria. The licensee established dose based criteria used by post-operation CT, prostate D90 values <80% or >130% for classifying medical events. The licensee has evaluated all prostate implants performed since 2001. "--Overdose to the prostate (medical event criteria used -D90>130%): 08/20/2009: 137.3% "--Underdose to the prostate (medical event criteria used -D90<80%): 07/15/2005: 79.27% 03/13/2006: 79.17% 03/15/2006: 67.10% 07/26/2006: 72.35% 07/26/2006: 57.06% 02/13/2006: 78.37% 05/14/2009: 78.67% "--Overdose to the rectum (medical event criteria used -V100>2cc): 12/13/2006: 2.42cc 12/19/2007: 2.23cc 03/03/2009: 2.54cc 07/08/2009: 3.32cc 11/19/2009: 2.89cc 05/05/2010: 2.41cc 05/20/2010: 3.92cc "DHS inspectors conducted an investigation of these medical events and are awaiting completion of the licensee's review." Wisconsin Event Report ID No.: WI120008 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-07-27
48117 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-07-18 08:15 | 2012-07-18 09:33 | 2012-07-18 | UNUSUAL EVENT DECLARED DUE TO FLASHOVER IN THE LOAD CENTER TRANSFORMER CABINET "An electrical transformer fault occurred resulting in a loss of both Recirc Pumps. The reactor was manually scrammed from 100% power as required by Plant Procedure OT-112. "The electrical transformer was walked down by Operations supervisor. Licensee's assessment was that a flashover occurred, and was confined to the load center transformer cabinet. Based on observed damage, EAL declaration of HU3 was made." HU3 is identified as an explosion within the Protected Area. The licensee has notified the NRC Resident Inspector. Licensee also notified state, local and other government agencies. Notified other agencies (DHS SWO, FEMA, DHS NICC) * * * UPDATE FROM BRIAN DEVINE TO JOHN KNOKE AT 1022 EDT ON 07/18/12 * * * "Limerick, Unit 1 is terminating from their Unusual Event (HU3) due to the initiating event and conditions no longer being present. The 124A Fault was isolated by the trip of the designed protection features (feeder breaker trip). A walkdown of the area/equipment was completed with no adverse conditions noted. Normal plant shutdown activities are in progress. The area/equipment is quarantined for investigation." The licensee will be issuing a press release. Notified other agencies (DHS SWO, FEMA, DHS NICC) The licensee has notified the NRC Resident Inspector. Notified R1DO (Dimitriadis) and NRR EO (Davis) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2012-07-18
48116 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2012-07-17 | 2012-07-17 19:32 | 2012-07-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO SMALL RCS PRESSURE BOUNDARY INSTRUMENT LINE LEAK "At 1715 EDT on July 17th, 2012, Calvert Cliffs Nuclear Power Plant Unit 1 identified RCS Pressure Boundary Leakage from the instrument line to 1-PDT-123A, 11A reactor coolant pump differential pressure transmitter. Technical Specification 3.4.13, Action B was entered and requires that the Unit be placed in Mode 3 within 6 hours and Mode 5 within 36 hours. The licensee has initiated plant shutdown in accordance with this Technical Specification. Therefore, this is reportable under 10 CFR 50.72(b)(2)(i) Plant Shutdown Required by Technical Specifications. This is also reportable under 50.72(B)(3)(ii)(A) as a material defect in the primary coolant system that cannot be found acceptable under ASME Section XI, IWB-3600 or ASME Section XI, Table IWB-3410-1." The licensee initially discovered the leak during an RCS leak rate surveillance that indicated RCS leakage on the order of 0.08 gpm. A video camera was used to look for the leak and was found to be on the identified instrument line. The licensee has initiated a power reduction and is currently at approximately 50%. The recovery plan at this time is to reduce power to about 10% which will reduce radiation levels in the area of the leak and isolate the instrument line and isolate the leakage. The instrument line is for a reactor coolant pump differential pressure transmitter which is for monitoring purposes only and does not provide any safety related functions. If the leak can be secured, the licensee intends to return to power. If the leak cannot be secured, the plant will shutdown in compliance with the technical specification action statement. The licensee has notified the NRC Resident Inspector. | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2012-07-17
48115 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2012-05-17 | 2012-07-17 16:11 | 2012-07-17 | STUCK OPEN SHUTTER ON SEALED SOURCE GAUGE The following report was received via email. "During an unannounced health, safety, and security inspection conducted on July 12, 2012 at SSAB Iowa, Inc. the Agency [Iowa Department of Public Health] discovered that the licensee had a shutter fail open on an EG & G Berthold, model LB 300 MLT, serial number 1739-10-05 containing approximately 50 millicuries of Cobalt-60. This failure occurred on May 17, 2012 while the device was measuring the level of molten metal in a caster. On May 22, 2012 a contractor arrived on site and repaired the shutter. Cause of failure appears to have been binding due to the extreme heat conditions of the castor. Precautions were taken to ensure that no individual received a radiation dose and normal operations continued until the shutter was repaired." Iowa Event Report # IA 120003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-07-25
48114 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2012-07-17 11:20 | 2012-07-17 17:36 | 2012-09-10 | CONTROL ROOM EMERGENCY VENTILATION AC SYSTEM INOPERABLE "On July 17, 2012, at 1120 hours the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable due to a cooling water leak from the condenser on the Refrigeration Compressor Unit (RCU). The leakage originates from an apparent gasket leak at a bolted connection on the condenser. As a result, Technical Specification 3.7.5, Condition A, was entered. A repair plan and schedule is being developed. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1317 EDT ON 09/10/12 FROM DEREK DROCKELMAN TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract the ENS Report made on July 17, 2012, at 1120 hours (ENS Report # 48114). "Further evaluation performed by Quad Cities Station confirms the CREV AC system would have performed its safety function. "Based on this subsequent evaluation, ENS Report # 48114 is being retracted. "Note: On July 18, 2012, the CREV AC system was successfully repaired and CREV AC system was returned to Operable status." The licensee informed the NRC Resident Inspector. Notified R3DO (Giessner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-07-17
48113 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-05-24 10:20 | 2012-07-17 16:07 | 2012-07-17 | 60 - DAY OPTIONAL TELEPHONE NOTIFICATION OF AN INVALID DIVISION 2 CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(3)(1) to describe an invalid actuation signal affecting containment isolation valves in more than one system. "On May 24, 2012, Nine Mile Point Unit 2 (NMP2) received a Division 2 primary containment isolation signal which resulted in closure of Group 3, 8, and 9 primary containment isolation valves (PCIVs) in the following systems: "Group 3 PCIVs: Traversing Incore Probe (TIP) ball valves (the TIPS were already withdrawn and the ball valves were already closed); nitrogen purge to TIP indexing mechanism. "Group 8 PCIVs: Reactor building closed loop cooling system; drywell equipment drain system; drywell floor drain system; instrument air system; hydrogen recombiner system; containment monitoring system; reactor recirculation system flow control valve hydraulic system; containment leakage monitoring system. "Group 9 PCIVs: Containment purge system (the containment purge valves were already closed). "All affected PCIVs responded as designed. In addition, the Division 2 containment isolation signal resulted in isolation of the Reactor Building normal ventilation system, starting of the Division 1 and Division 2 standby gas treatment subsystems, starting of the Division 1 and Division 2 Reactor Building safety-related unit coolers, and starting of the Division 2 Control Room envelope filtration subsystem. "The Division 2 isolation signal was generated during a maintenance activity involving the replacement of a relay in a main control room panel. During the activity, an installed jumper became dislodged from its point of origin, leading to a blown control power fuse and generation of the Division 2 isolation signal. Since the isolation signal was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation, the isolation signal was determined to be invalid. "This event was entered into the corrective action program as Condition Report (CR) 2012-005128. There were no safety consequences or impact on the health and safety of the public as a result of this event." The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-07-17
48112 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-07-17 11:40 | 2012-07-17 15:18 | 2012-07-18 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO DEGRADED CHARCOAL ADSORBER "At 1140 [EDT] on Tuesday, July 17, the Callaway Plant Technical Support Center (TSC) was declared non-functional due to a degraded charcoal filter in the building's filter absorber unit. At 1140 [EDT] on July 17, 2012, Callaway was notified of the test results for a charcoal test sample that was taken on July 5, 2012. The results did not meet surveillance procedure acceptance criteria. "Efforts are underway to replace the charcoal in the unit. "If an emergency were to be declared requiring activation of the TSC while it is non-functional, TSC emergency response personnel would report to their backup locations in accordance with Callaway Plant emergency planning procedures. "This notification is being made in accordance with 10 CPR 50.72(b)(3)(xiii) due to the unavailability of an emergency response facility. "The NRC Resident Inspector has been notified." The licensee indicated the TSC will be functional within 24 hours. * * * UPDATE AT 1012 EDT ON 07/18/12 FROM TIM HOLLAND TO JOHN KNOKE * * * "The TSC was restored to functional status at 2200 [CDT] on July 17, 2012." The licensee informed the NRC Resident Inspector. Notified R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-17
48111 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-07-17 10:00 | 2012-07-17 15:04 | 2012-07-17 | DEGRADED CHARGING LINE SOCKET WELDS BASED ON THERMAL FATIGUE ANALYSIS "Results of a thermal fatigue analysis on the Chemical and Volume Control System (CVCS) charging line concluded that the socket weld fittings above the RCS piping cannot be qualified. "As an interim action, shut down cooling purification has been secured and charging has been isolated to the RCS. "The plant is shutdown and in Mode 5 with the reactor vessel head removed, so RCS is not intact and not required to be for current plant conditions. This report is being made in accordance with 10CFR50.72(b)(3)(ii)(A) for a degraded condition." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-07-17
48110 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2012-07-17 11:18 | 2012-07-17 13:23 | 2012-07-17 | AUTOMATIC REACTOR SCRAM DUE TO HIGH NEUTRON FLUX "On July 17 2012, at 1118 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram due to high neutron flux as measured by the Average Power Range Monitoring system. The cause is currently under investigation. All control rods fully inserted and all plant systems responded per design following the scram. The High Pressure Coolant Injection [HPCI] system, which is an operating mode of the feedwater system, initiated as expected. There were no planned activities in progress at the time which could have contributed to the event. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. All emergency power sources are available in standby. "The unit is currently implementing post scram recovery procedures." This was an uncomplicated Reactor Scram and the plant is stable with normal levels, temperature, and pressure. Offsite power is in a normal alignment. HPCI has been secured and returned to normal alignment. The cause to the high neutron flux is still under investigation. This event had no impact on Unit 2. The licensee has informed the NRC Resident Inspector and State Authorities. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-07-17
48109 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-07-16 14:03 | 2012-07-16 18:47 | 2012-07-16 | LOSS OF AC POWER TO EMERGENCY OPERATIONS FACILITY "At approximately 1403 [CDT] on 7/16/12, a loss of AC power (Linn Street substation) occurred affecting emergency response capability of the primary Emergency Operations Facility (EOF). The Technical Support Center (TSC) remained functional throughout the event. The Backup EOF located in Minneapolis, MN was inspected and verified to be functional. In the event of an emergency declaration requiring an EOF, the Emergency Response Organization (ERO) would have been directed to report to the Backup EOF. "At approximately 1540 [CDT], the Linn Street substation power was restored. "The primary EOF was inspected and declared functional at 1725 [CDT]. "The NRC Resident Inspectors were notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-16
48108 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2012-07-15 10:30 | 2012-07-15 16:05 | 2012-08-17 | UNIT 1 HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE DUE TO VALVE LEAK "On July 15, 2012, at 1030 hours, a defect (pinhole through-wall leak) was identified on the 1-2301-29 valve (HPCI Steam Line to Main Condenser Isolation Valve). The defect was identified during a routine system walkdown. The 1-2301-29 valve (1" valve downstream of the HPCI drain pot) is normally open during HPCI standby operation and closes upon system initiation. Due to the location of the defect, the 1-2301-29 valve would not have completely isolated the steam line as designed. As a result, HPCI was declared inoperable. Given that HPCI is a single train system, this notification is being made in accordance with 10CFR50.72(b)(3)(v)(D). HPCI will remain inoperable until system repairs are complete." The NRC Resident Inspector has been informed. * * * RETRACTION AT 1216 EDT ON 8/17/2012 FROM DALE STEEL TO MARK ABRAMOVITZ * * * "The purpose of this notification is to retract the ENS Report made on July 15, 2012, at 1030 hours (ENS Report # 48108). "Further evaluation performed by Quad Cities Station confirms the Unit 1 HPCI system would have performed its safety function. Based on this subsequent evaluation, ENS Report # 48108 is being retracted. "Note: On July 21, the 1-2301-29 valve (HPCI Steam Line to Main Condenser Isolation Valve) was successfully repaired and HPCI was returned to Operable status." The licensee notified the NRC Resident Inspector. Notified the R3DO (Giessner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-07-15
48107 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-07-14 10:06 | 2012-07-14 16:52 | 2012-07-14 | FITNESS FOR DUTY A licensed operator employee had a confirmed positive during a random fitness-for-duty test. The employee's unescorted access has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 60 | 100 | 0 | 60 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2012-07-14
48106 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-07-14 02:06 | 2012-07-14 08:59 | 2012-07-14 | UNEXPECTED INTEGRATED PLANT COMPUTER SYSTEM FAILURE "At approximately 0206 EDT on July 14, 2012, the Femi 2 Integrated Plant Computer System (IPCS) failed. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform. "At 0525 EDT, plant personnel were able to reboot IPCS and restore the system to normal with prime and backup CPUs. Emergency assessment capabilities have been restored to all onsite emergency response facilitates. "This notification is being made per the requirements of 8 hour non-emergency notification 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-14
48105 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-07-13 17:40 | 2012-07-13 21:05 | 2012-07-16 | OFFSITE NOTIFICATION OF EMERGENCY SIREN ACTIVATION "On Friday, July 13, 2012 at approximately 17:40 EDT, Oswego County Emergency Management Office notified Nine Mile Point via the Radiological Emergency Communications System (RECS) line of a false activation of Siren 34. The Oswego County Emergency Management Office has issued a press release. "Currently, the siren has been silenced and is inoperable. Technicians are dispatched and investigating. Backup measures are in place to notify residents if an actual emergency were to occur while the siren is out of service." The licensee has notified the NRC Resident Inspector and the State. See related event notification from FitzPatrick - EN #48104 * * * UPDATE ON 7/16/12 AT 1613 EDT FROM JONES TO HUFFMAN * * * As of 1349 EDT on 7/16/12, the siren vendor had completed repairs and retuned siren number 34 back to service. The licensee will notify the NRC Resident Inspector. R1DO (Dimitriadis) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-13
48104 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-07-13 17:40 | 2012-07-13 20:39 | 2012-07-16 | OFFSITE NOTIFICATION OF EMERGENCY SIREN ACTIVATION "The purpose of this report is to provide a telephone notification under 10CFR50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of Oswego County emergency notification siren number 34 at approximately 17:40 EDT on 7/13/12. Personnel have been dispatched to the siren location and it has been deactivated pending further investigation. Backup measures are in place to notify residents if an actual emergency were to occur while the siren is out of service. "The NRC Senior Resident Inspector has been notified. "Oswego County Emergency Management Office has issued a press release as follows: "EMERGENCY SIREN SOUNDS INADVERTENTLY "Fulton - One of the emergency notification sirens surrounding the nuclear power plants in Scriba inadvertently sounded at about 5:40 p.m. today, July 13, due to a malfunction. There is NO emergency at the three nuclear power plants in Oswego County. "[The] Director of the Oswego County Emergency Management Office, said siren repair personnel from Constellation Energy and Entergy responded to the site near the intersection of Middle Road and Route 104 in Scriba as soon as they were notified the siren was sounding. The cause for the sounding is under investigation. The other sirens in the system are functioning properly. "While the siren system is being repaired, backup measures are in place to notify residents if an actual emergency occurs at one of the plants. "The siren is one of 37 located within a 10-mile radius of the nuclear power plants in Scriba. A system of sirens and tone-alert weather radios is in place to alert residents in the event of an emergency. "In the event of an emergency at one of the plants that would require protective actions for the public, the sirens would be sounded for three minutes to alert residents of the area to turn their AM/FM radios or televisions to local Emergency Alert System (EAS) stations for further information and instructions. EAS stations are listed in the Emergency Public Information Calendar mailed to residents of the Emergency Planning Zone surrounding the plants and in local telephone books. The calendar can be viewed online at www.oswegocounty.com/emo." See related event notification from Nine Mile Point - EN #48105 * * * UPDATE ON 7/16/12 AT 1613 EDT FROM SMOLINSKI TO HUFFMAN * * * As of 1349 EDT on 7/16/12, the siren vendor had completed repairs and retuned siren number 34 back to service. The licensee will notify the NRC Resident Inspector. R1DO (Dimitriadis) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-13
48103 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2012-07-13 10:50 | 2012-07-13 15:37 | 2012-07-13 | TSC OUT OF SERVICE DUE TO FAILED FAN BELT "This telephone notification is provided in accordance with Exelon reportability manual SAF 1.10, 'Major Loss of Emergency Preparedness Capabilities', and 10CFR50.72(b)(3)(xiii). "On July 13, 2012 at 1050 CDT, it was determined that the onsite Technical Support Center (TSC) ventilation system supply fan belts had failed, resulting in loss of ventilation for the facility. Repairs have been completed, and the TSC ventilation system was returned to service July 13, 2012 at 1225 CDT; however repairs were not completed within the time required had the TSC needed to be staffed. During this time, there was no emergency event in progress requiring TSC staffing. The Main Control Room remained fully available as a backup facility, should an event have occurred requiring emergency facilities to be staffed. "The licensee has notified the NRC Senior Resident Inspector of the issue." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-13
48102 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-07-13 12:00 | 2012-07-13 14:20 | 2012-07-14 | INTERMITTENT SIGNAL INTERFERENCE WITH EMERGENCY SIRENS " At 12:00 on July 13, 2012 it was determined, during a conference call with the Exelon siren vendor, that Oyster Creek emergency planning zone (EPZ) sirens may be unreliable. The unreliability is being caused by an intermittent signal on the frequency used to activate the sirens. Therefore, an 8-hour report is required under 10 CFR 50.72(b)(3)(xiii) due to a potential 'Loss of Emergency Preparedness Capabilities.' "Additionally, Exelon is contacting the Federal Communications Commission (FCC) for troubleshooting and reporting purposes, as well as, the New Jersey Office of Emergency Management (NJ OEM) and the Ocean County Office of Emergency Management to institute compensatory actions. Due to contacting other government agencies a 4-hour report is required per 10 CFR 50.72(b)(2)(xi). "Exelon will notify the NRC Operations Center upon full-restoration of the Oyster Creek EPZ siren system." The NRC Resident Inspector has been informed. * * * UPDATE AT 2110 EDT ON 7/14/12 FROM CLARK TO HUFFMAN * * * As of 2058 EDT on July 14, the licensee has declared that all 42 sirens have been restored to a reliable status. The siren vendor has shifted the activation frequency to avoid the interference. The vendor is still working with the FCC to determine the cause of the interference signal at the original frequency. The licensee has notified the NRC Resident Inspector. R1DO (Doerflein) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-07-13
48101 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-07-12 13:15 | 2012-07-12 23:29 | 2012-07-12 | POWER SUPPLY PROBLEMS TO VARIOUS AREA RAD MONITORS "At 13:15 PDT on 7-12-2012, during the performance of an annual surveillance, power supply ARM-E/S-603A was discovered to have out of tolerance voltage readings. ARM-E/S-603A was declared non-functional. This resulted in a loss of the ability to monitor and quantify radiological conditions in multiple areas of the reactor building, due to the loss of ARM-RIS-1 thru 10 (area radiation monitor radiation indicating switches 1 thru 10). "The loss of ability to monitor and quantify radiological conditions in multiple areas of the reactor building represents a major loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii). As directed by station procedures, compensatory measures have been enacted to have Health Physics personnel tour the affected areas once per shift to document and trend the radiological conditions. ARM-RIS-1 and 4 thru 10 are used for EAL determinations. "Work to return the ARM-E/S-603A to service is underway and is a high priority." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-12
48100 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-07-11 17:40 | 2012-07-12 16:29 | 2012-07-12 | CRITICALITY HORNS RENDERED INOPERABLE DUE TO LIGHTNING STRIKE "At approximately 1740 EDT on 7/11/12, lightning strikes near the Wilmington Field Service Center (WFSC) rendered several alarm annunciators (horns) of the Criticality Accident Alarm System (CAAS) inoperable. There are no active fissile material operations in WFSC, thus no unsafe condition existed. "Until the system is repaired, personnel have either been removed from the affected area or other compensatory measures have been established. Longer term preventative actions are being evaluated. "This event is being reported pursuant to the requirements of 10CFR70.50(b)(2)." The licensee will notify NRC R2 (Thomas), and the State and Hanover County Emergency Management Agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2012-07-12
48099 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2012-07-12 12:00 | 2012-07-12 15:07 | 2012-07-16 | 24 HOUR REPORT RELATED TO CRITICALITY CONTROL BULLETIN 91-01 "Around noon on July 12, 2012, workers noticed that a Nuclear Criticality Safety (NCS)-controlled 5-gallon container, formally identified as a 'Field Container' being used as part of burial pit remediation at the Westinghouse Hematite Decommissioning Project, looked unusual. Field Containers are white standard-size 5-gallon buckets with a locking lid and are supposed to be unique to other containers being used at the facility. Upon investigation, it was determined that the container was actually a 6-1/2-gallon container - white with a locking lid, almost identical to a Field Container except for height. The container was in the midst of being used to consolidate exhumed radiologically elevated soil, formally identified as a Hot Spot. One shovel's worth of dirt had been transferred into the 6-1/2-gallon container when the condition was noticed. The workers called their supervisor upon discovery. The supervisor issued a verbal stop work order, and went to investigate the condition in the field. The use of a 6-1/2-gallon container is a violation of an NCS Control (specifically, Safety Feature 01 of NSA-TR-09-15, Rev. 3). "NCS was called to assess the condition and direction was given to transfer the shovel's worth of soil from the 6-1/2-gallon container into an empty 5-gallon Field Container. The 6-1/2-gallon container, now empty, was destroyed. Other 6-1/2-gallon containers (the remaining 18 out of 20 containers that were identified as being purchased for different purposes) were removed and are under control pending their destruction. (It was confirmed that the one missing container of the purchase lot had been used for other non-NCS purposes.) "The work crew on the other end of the burial pit remediation area was informed of the problem and cautioned to confirm the labeled volume capacity on the bottom of Field Containers to be used. The other areas where Field Containers are staged in the field and at the work site were inspected to confirm that no other 6-1/2-gallon containers were present. The consolidation points where these containers are staged when filled were also inspected to confirm that no 6-1/2-gallon containers were present. "An investigation is under way to determine: 1) how the 6-1/2-gallon containers were inadvertently brought out to the burial pit, 2) how and why 6-1/2-gallon containers looking very similar to 5-gallon Field Containers were purchased and became available for misidentification as Field Containers, and 3) what actions need to be put in place to assure that future purchases of containers that may be mistaken for Field Containers do not occur." Westinghouse Hematite is undergoing decommissioning. The location of this event was at the burial pit remediation area. The licensee plans to also notify NRC Region 3 (Lafranzo) and NRC HQ (Hayes). * * * UPDATE FROM DENNIS RICHARDSON TO JOHN SHOEMAKER AT 1707 EDT ON 07/16/2012 * * * "In the original report, Hematite stated that "the remaining 18 out of 20 (6-1/2-gallon) containers that were identified as being purchased...were removed and are under control..." (Parenthetical statement added for clarity.) During the destruction of the 6-1/2-gallon containers, it was noticed that 6 of the 18 quarantined containers were actually 5-gallon containers. A second search of all inventoried, staged, and used/in-process containers was conducted to find the missing six 6-1/2-gallon containers. None of the missing six 6-1/2-gallon containers were found. The complete facility was then searched in an effort to find the 6 missing 6-1/2-gallon containers; but, none were found. The identified 5-gallon containers, which were in the middle of a stack of 6-1/2-gallon containers, were taken directly from the original shipping pallet; and, as the 6 missing 6-1/2-gallon containers cannot be found, were, mostly likely, mistakenly shipped by the supplier as 6-1/2-gallon containers. At this point, all identified 6-1/2-gallon containers on site have been destroyed." The licensee will notify the NRC Inspector. Notified R3DO (Kozak) and NMSS (Silva). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0 | 2012-07-16
48098 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-07-10 17:00 | 2012-07-12 13:10 | 2012-07-12 | AGREEMENT STATE REPORT - UNDERDOSE DURING A YTTRIUM-90 THERASPHERE TREATMENT The following information was provided by the Ohio Bureau of Radiation Protection via e-mail: "A written directive was given for a patient to receive 115 mCi of Y-90 TheraSpheres microspheres. "During the delivery of the microspheres, stasis occurred before the full quantity of the written directive delivered. The licensee did not expect to reach stasis, and will be sending the delivery system to the manufacturer after the remaining Y-90 decays to verify that there was not an equipment malfunction. The licensee calculates that the patient received 68.6 mCi, which is only 60% of the written directive (a 40% underdose). The written directive did not indicate include the phrase 'or until stasis'. "The licensee has notified the attending physician. The licensee will be contacting the patient's physician prior to contacting the patient. "The licensee states that there are no adverse effects to the patient. No corrective action is planned at this time. "Event Discovered: July 11, 2012 at 11:00 am Event Date: July 10, 2012 at 5:00 pm "Reporting criteria - medical event OAC 3701:1-58-101(a)(1)(a) 10 CFR 35.3045(a)(1)(i) " Ohio Event Report #2012-017 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-07-20
48097 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-07-12 02:20 | 2012-07-12 04:49 | 2012-07-12 | MANUAL REACTOR SCRAM DUE TO LOWERING CONDENSER VACUUM "On July 12, 2012, at 0200 EDT, clean steam reboiler 'B' failed, causing a loss of sealing steam. This resulted in degrading condenser vacuum and rising off gas system pressure. The main steam backup supply for sealing steam also failed, and condenser vacuum and off gas system pressure continued to degrade. "In response to rising off gas system pressure and lowering condenser vacuum, reactor power was lowered to 85% in accordance with Special Operating Procedures. With off gas system pressure approaching the procedural limit and condenser vacuum degrading rapidly, a manual reactor scram was inserted at 0220 EDT. "All control rods fully inserted and all systems functioned as expected on the scram. "Plant is currently shutdown and parameters are stable. "The unit is currently implementing post scram recovery procedures and plant cooldown is in progress. "The cause of the loss of both the primary and backup sources of sealing steam is under investigation." The shutdown electrical lineup is normal and decay heat is being removed via steam bypass valves to the main condenser. The licensee has notified the NRC Resident Inspector and the Public Service Commission. | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-07-12
48096 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-07-12 05:00 | 2012-07-12 02:30 | 2012-07-12 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "The Turkey Point Nuclear Plant will be performing the semi-annual HVAC inspection of the TSC Building on 7/12/2012. The work is scheduled to start at 0500 EDT and complete at 1500 EDT. The projected non-functional time is 10 hours. The Emergency Response Organization duty team members will be informed to respond to alternate locations if activation is required during that period. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to loss of an emergency response facility." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL COEN TO CHARLES TEAL AT 1538 EDT ON 7/12/12 * * * The maintenance on the TSC has been completed and the TSC was declared operable at 1535 EDT on 7/12/12. Notified R2DO (Calle). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-12
48095 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-07-11 15:20 | 2012-07-11 19:18 | 2012-07-11 | CABLE ASSOCIATED WITH 4KV SHUTDOWN BOARD ROUTED INCORRECTLY "On July 11, 2012, during the [National Fire Protection Association] NFPA 805 transition review process for the Browns Ferry Nuclear Plant (BFN), it was discovered that a cable associated with 4kV Shutdown Board B cross-tie breaker 1828 differential lockout contacts was not routed in accordance with the Appendix R Separation Analysis. Specifically, the cable was determined to be routed in Fire Zone 03-02 and is considered to be an unanalyzed condition. "In the event of an Appendix R fire in Fire Zone 03-02, fire damage to cables associated with 4kV Shutdown Board B cross-tie breaker 1828 and the 4kV Shutdown Board 3EB cross-tie breaker 1848 could occur. A fire induced hot short could cause spurious closure of breaker 1828. Fire damage to cable associated with 4kV Shutdown Board B cross-tie breaker 1828 differential lockout contacts could also result in the loss of the breaker trip function. This condition may result in the following two failures: "1) If breaker 1828 spuriously closed, it could close onto a fault, since the cross-tie power cables from breaker 1828 on 4kV Shutdown Board B to Breaker 1848 on 4kV Shutdown Board 3EB are routed through Fire Zone 03-02 and would be subject to a fire induced fault, if energized. This could result in the trip of Diesel Generator B output breaker 1822 and deenergization of the 4kV Shutdown Board B. "2) Breaker 1848 on 4kV Shutdown Board 3EB is also vulnerable to spurious closure in the event of an Appendix R fire in Fire Zone 03-02, as the control cable for this breaker is routed through Fire Zone 03-02. In accordance with the applicable BFN Safe Shutdown Instruction, breaker 1848 is isolated and tripped locally prior to connecting Diesel Generator 3B to 4kV Shutdown Board 3EB. If offsite power was lost and 4kV Shutdown Board B and 4kV Shutdown Board 3EB were powered from Diesel Generators B and 3B respectively, and fire damage occurred to the breaker 1848 control cable and the cable for the breaker 1828 differential lockout contacts (which are both routed in Fire Zone 03-02) prior to the completion of Safe Shutdown Instruction steps to isolate and trip breaker 1848, then the potential to parallel Diesel Generators B and 3B out of phase would exist. Paralleling the Diesel Generators B and 3B out of phase with each other or offsite power poses the potential to damage either Diesel Generator. "Therefore, this condition could result in a loss of power to credited safe shutdown equipment that would challenge the ability to provide adequate core cooling during performance of BFN Safe Shutdown Instructions. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(ii)(B). "The NRC Resident Inspector has been notified of this event." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-07-11
48094 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-07-11 16:03 | 2012-07-11 18:10 | 2012-07-11 | ANALYSIS OF INTERNAL CONTAINMENT SUPPORT BEAM EXCEEDS LOAD COMBINATION LIMIT "Fort Calhoun Station is making an 8-hour verbal report per 10CFR50.72(b)(3)(ii)(B) Unanalyzed Condition. An internal containment support beam (B-22) has been identified by the station as not passing the required load combination as stated in the USAR for at power conditions. Beam B-22 is the designation for the two beams that directly support Safety Injection Tanks 6B and 6D. "This beam was also identified as having potential loading conditions outside the allowable limits for the load combination for shutdown conditions. Specifically, it was determined that in order to bring the beam loading to within acceptable levels, the allowable floor live load would need to be reduced from the current designated load distribution of 200 pounds per square foot (psf) to 140 psf. A walkdown of the area by Design Engineering estimates the current floor live load is approximately 100 psf. "Compensatory actions are being established to remove any equipment that is contributing to current live loading of the support beam and to isolate and post the affected area to ensure no equipment is stored without engineering analysis." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-07-11
48093 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-11 11:57 | 2012-07-11 14:21 | 2012-07-11 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF AMMONIA FOUND IN GROUNDWATER "A report to the State of New Jersey was made on July 11, 2012 at 1157 EDT. The report was in accordance with Attachment 16 of the ECG (Event Classification Guide). The report was due to 4-5 ppm ammonia found in ground water on an excavation site. Samples were obtained from ground water in the hole. Estimate of leakage into hole is 2 ounces per minute." The licensee believes the ammonia is from leftover de-icing salt. An estimated 100 gallons of water was pumped from the hole into a treated system. The NRC Resident Inspector and the Lower Alloways Creek township was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-11
48092 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-05-14 09:28 | 2012-07-11 12:26 | 2012-07-11 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID EMERGENCY SERVICE WATER ACTUATION "At 0928 EDT on May 14, 2012, the 'B' Emergency Service Water (ESW) pump started during testing from the Unit 1 remote shutdown panel (RSP). The likely cause of the start was either human error in performing continuity checks or inadvertent contact with the manual start circuit in the RSP. Based on the likely cause, this was an invalid actuation of a system listed in 10 CFR 50.73(a)(2)(iv). "As indicated in 10 CFR 50.73(a)(1), in the case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv) other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. This 60-day telephone notification is being made to meet the reporting requirements instead of submitting an LER since the actuation was invalid and was not an RPS actuation with the reactor critical. "The following additional information is being provided as specified in NUREG-1022: "The specific train(s) and system(s) that were actuated: The 'B' ESW pump inadvertently started during testing from the Unit 1 remote shutdown panel. "Whether each train actuation was complete or partial: This was a partial actuation (one of four ESW pumps). "Whether or not the system started and functioned successfully: The 'B' ESW pump started successfully, operated properly, and continued running until manually secured via normal controls." At the time of the event, the licensee was performing a surveillance where control was shifted from the control room to the remote shutdown panel. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-07-11
48091 | -1 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-07-10 12:30 | 2012-07-11 12:19 | 2012-08-10 | METALLURGICAL SAMPLE PANS EXCEEDED VOLUME LIMIT The following is a redacted summary of the event report provided by the licensee: EVENT DESCRIPTION: Metallurgical samples at B&Ws NOG-L facility are contained in 'bread pans'. The bread pans are used to transport and store samples. Each bread pan has U235 quantity limits as well as spacing and volume limits for maintaining criticality controls. The volume of the bread pan is an Item Relied on For Safety (IROFS). On July 10, 2012, at approximately 1230 EDT, a Nuclear Criticality Safety (NCS) engineer identified during a routine quarterly audit that the bread pans in use exceeded the volume liter limit. At the time of discovery, the mass controls for the bread pans were not exceeded. Neither was there excess moderation between storage locations. EVALUATION OF THE EVENT: Although an IROFS was lost (the bread pan volume), other IROFS (operator control of mass, operator control of interspersed moderation) were available at the time of discovery of this condition to ensure the risk of a criticality remained highly unlikely. However, 10 CFR 70.61 (d) states in part: '...the risk of nuclear criticality accidents must be limited by assuring that under normal and credible abnormal conditions, all nuclear processes are subcritical, including use of an approved margin of subcriticality for safety.' Further evaluation of the as-found condition of the bread pans indicated the licensed keff limit may have been exceeded. Therefore, the performance requirements of 10 CFR 70.61 were not maintained. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. However, the bread pan storage area is being shutdown. NOTIFICATION REQUIREMENTS: B&W is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1) Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. STATUS OF CORRECTIVE ACTIONS: An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation. The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 0845 EDT ON 8/6/2012 FROM TONY ENGLAND TO MARK ABRAMOVITZ * * * The following is a redacted summary of the event report provided by the licensee: The event was reported in 24 hours in accordance with 10 CFR 70. Appendix A. (b)(1): 'any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61'. Upon further evaluation it was determined that keff limit in the NRC License was not exceeded. Therefore, the performance requirements of 10 CFR 70.61 were maintained. This is the basis for correcting Event Notification #48091 and withdrawing the report. A conservative approach was initially taken in evaluating the event in order to ensure compliance with the specified time periods established in the regulations. A reanalysis calculated keff less than the keff safety limit in NRC License SNM-42. Although the facility was in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, the performance requirements of 10 CFR 70.61 were maintained. In accordance with 10 CFR 70.61 (b) and FCSS Interim Staff Guidance-12, although an IROFS was lost, the situation did not pose a safety concern that is significant enough to report to NRC. Other IROFS were available at the time of discovery of the condition to ensure the risk of a criticality remained highly unlikely. In addition, the calculated keff using an approved approach described in Section 5.2.2 of NRC License SNM-42 demonstrates compliance with 10 CFR 70.61 (d). The system remained subcritical, including use of an approved margin of subcriticality for safety, during a credible abnormal condition. Therefore, in accordance with the guidance of FCSS ISG-12, Rev 0, '10 CFR Part 70, Appendix A - Reportable Safety Events,' B&W is correcting Event Notification #48091 in accordance with 10 CFR 70.74(a)(4) and withdrawing the 10 CFR 70, Appendix A, (b )(1) notification. The licensee notified the NRC Resident Inspector. Notified the R2DO (Ernstes), NMSS (Stablein), and the Fuels Group OUO (via e-mail). Contact the Headquarters Operations Officer for additional details on this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-08-10
48090 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2005-01-01 | 2012-07-11 11:36 | 2012-07-11 | AGREEMENT STATE REPORT - LOST CS-137 SOURCE USED IN DENSITY METER The following information was provided by the State of Nevada via email: "The licensee issued a report of a lost radioactive source previously in service at James Hardie's McCarran, NV manufacturing facility. The missing source material in question was a component of a Thermo Measuretech density meter, Model 5201. The radiation source housing has the serial # B4106. The source's serial # is GV-9532. The isotope is Cesium-137, and the activity is 50 mCi. "This unit was received on site in July, 2004 and put into commission in December of 2004. This particular unit was installed on the agitator feed line (a process line that transfers feed material in a mixing vessel to a production machine). At some time in 2005, the density meter in question was removed from service and replaced with an inline flow meter. "Thermo Scientific was contacted to determine if the source material in question had ever been sent back to them for recycling or disposal. They have no record of receiving the material in question. In early 2012, the McCarran facility executed a major site clean-up effort. This included taking inventory of all spare parts in the warehouse and cleaning up the 'bone yard'. "Western Metals Recycling was contacted prior to this clean-up initiative and asked if they had ever found radioactive material in a scrap metal load from James Hardie. They said that they had not. They also stated that all inbound loads are screened for the presence of radioactive material, and that they would have located the lost device had it come into their yard. No scrap metal shipments generated from the 'bone yard' clean-up initiative were found to contain radioactive material. "At this time James Hardie believes that it has done all that can be done to locate the lost source material. The facility is now easily inspected due to recent clean-up efforts, and effort will continue to be made to locate the lost radiological material. In the event that the lost material is located, the licensee will notify the State of Nevada immediately and initiate action to return the source material to Thermo Scientific for recycling or disposal. "There is currently one Thermo Measuretech density meter in service at this facility. The device is operated under a General License. In accordance with license requirements, annual training is provided to all site personnel." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2012-07-19
48089 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-02-12 14:54 | 2012-07-11 10:14 | 2012-07-11 | PART 21 - FAILED AUXILIARY CONTACTOR AFFECTING DIESEL GENERATOR "On February 10, 2012, during the monthly testing of Diesel Generator 1 (DG-1), speed was raised from 500 RPM to 900 RPM. At approximately 750 RPM, the generator field did not 'flash', a term used to describe the normal voltage buildup in the field of a generator. Initial troubleshooting identified that the auxiliary contacts on the 2CR contactor did not close. This caused the field flash failure. The failure of the auxiliary contacts on the 2CR contactor prevented the diesel generator from performing its designed safety function. The specific part which fails to comply or contains a defect is General Electric CR105X300 auxiliary contactor. The auxiliary contactor was manufactured by General Electric Company and supplied by Nuclear Logistic, Incorporated, as an auxiliary part of a General Electric CR305 contactor. "Further evaluation of the failure determined it to be reportable under 10CFR21 on June 8, 2012. The Corporate Officer was informed on June 13, 2012. The Regional Administrator was notified as required, but, due to an oversight, this report was not made to the Operations Center. The required 30 day report has been submitted (ML 121910230)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2012-07-11
48088 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-06-15 | 2012-07-11 10:02 | 2012-07-11 | AGREEMENT STATE REPORT - DAMAGED TROXLER The following information was obtained from the State of Tennessee via Email: "On June 15, 2012, Building and Earth Sciences contacted the Division of Radiological Health to report that their Troxler Moisture Density Gauge model 3430 (SN#37366) which contains 8 mCi of Cesium-137 and 40 mCi Americium-241:Beryllium had been hit by a bull dozer at a jobsite in Sevierville, TN. The gauge was visually inspected, and it was determined that the source rod was retracted and inside the gauge but the sliding block was not in place. The survey meter indicated an exposure level of 100 mRem/hr within 1 meter of the base of the gauge in its case. After speaking with Troxler, the RSO replaced the sliding door and held it in place with duct tape. This reduced the dose rate to 18 mR/hr. The gauge was secured into a truck bed and was returned to their licensed facility in Birmingham, AL. Upon arrival in Birmingham, a leak test was conducted and sent for analysis. Once the results were returned, they obtained a return authorization to ship the gauge to Troxler." Tennessee Event: TN-12-164 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-07-19
48087 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-07-10 22:25 | 2012-07-11 02:23 | 2012-07-11 | LOSS OF ERDS DUE TO COMMUNICATIONS NETWORK MODULE FAILURE "A 'Communications Network Module' failed rendering the Emergency Response Display System (ERDS) incapable of transmitting data to the NRC. ERDS is out of service for both Unit 1 and Unit 2. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. Control Room Emergency Response Organization personnel will use backup methods already captured in emergency response procedures to disseminate plant parameter data to the effected emergency response facilities and NRC during the plant data network outage. The module was removed from service and ERDS was restored at 2325 [EDT]." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-11
48086 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-06-04 | 2012-07-10 16:19 | 2012-07-10 | KENTUCKY AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING PROSTATE SEED IMPLANTS The following information was obtained from the Commonwealth of Kentucky via email: "A prostate seed implant was performed on June 4, 2012. The procedure presented with some complications related to a deficit from a TURP [Transurethral Resection of the Prostate] surgery performed on the patient over 15 years ago. When the procedure was completed cystoscopy identified no seeds in the bladder or urethra. "The patient returned for the post implant CT on July 9, 2012. During the post implant visit with the Authorized User, the patient identified he had passed what was thought to be two seeds. Further discussion with the Authorized User identified it was two strands of seeds. The patient flushed one strand into his septic system and will bring the second strand back to the licensee for proper disposal. "The post implant CT determined approximately 15 seeds were missing from the implant. It appears the two strands containing these seeds were in the deficit resulting from the earlier TURP surgery. "The licensee is preparing a report for submission to the RHB within the next 15 days." Radiation Oncologist (AU): [Deleted] Referring Physician: [Deleted] Implant Date: 6/4/2012 Prescribed dose: 108 Gy to the prostate Post implant CT dosimetry: D-90 = 54% Source: I-125 encapsulated seeds Vendor: IsoAid Model Number: IAI-125A Activity per seed: 0.24 mCi Number of seeds implanted: 85 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-07-18
48085 | 0 | ST JOHNS MACOMB OAKLAND HOSPITAL |  |  |  |  | 2012-07-10 | 2012-07-10 16:16 | 2012-07-10 | WRONG APPLICATOR USED IN PROCEDURE PREVENTING PATIENT FROM RECEIVING PROPER DOSE "The RSO received a phone call from the physicist who explained she incorrectly connected the HDR unit during a patient treatment. She explained how she connected a transfer tube to the endobronch catheter, when she should have connected the endobronch catheter directly to the HDR unit. This would add about 1 meter of distance between the intended treatment site and the HDR unit source. "It was determined that the source exited the HDR unit, but never made it to the patient. This was confirmed by a repeat test/reproduction with a dummy patient/setup in the exact format the patient treatment was performed. It was clear from observing this set up a mistaken addition of about 1 meter of transfer tube was added and that the source did not make it to the patient treatment site, or to the patient at all, and instead would be within the endobronch catheter potentially exposing a portion of patient skin (confirmed not to be in direct skin contact). We then placed a farmer chamber, a MOSfet and an Ion chamber in locations where we determined would be the highest possible patient skin dose measurements. We determined the highest potential skin dose to be 1.8cGy/1.8rem (significantly below the 50rem medical event definition) to the patient arm/shoulder area, however due to a folded blanket that was placed in that location it prevented direct skin contact. "The hospital staff has changed policy as of today, to include a time out for the physicist to verbally voice the assurance to the in room nurse of proper connection to the HDR unit. They are planning an education process for their nursing staff so they may visually assist as a secondary visual confirmation. They are also reassessing additional support staff to be present during HDR treatment in a future meeting. The RSO believes the error happened due to human error, and a rushed procedure that occurred at the end of the day. "The hospital staff is assessing the patient for potential skin burns both now and in the future (2wk, 5wks for reassessment). They do not expect to see skin burns, but will perform this patient skin burn assessment for assurance and to confirm our lower dose skin estimates. They intend on completing the patient treatment and therefore will complete this written directive dose which was scheduled for 500cGy, based upon the medical consult with the Radiation Oncologist. We are in process of follow-up with the patient, and referring physician." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-07-18
48084 | -1 | PORTSMOUTH AMERICAN CENTRIFUGE |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-07-10 08:00 | 2012-07-10 15:48 | 2012-07-18 | SAFEGUARDS REPORT - PERSONNEL ACCESS CONTROLS VIOLATED The licensee discovered a personnel failure that allowed unauthorized access to an access controlled area. Contact the Headquarters Operations Officer for details. * * * RETRACTION AT 1100 EDT ON 07/18/12 FROM CHARLES SEIDEL TO S. SANDIN * * * "Update: On 07-18-12 at 1017 the NRC Event has been retracted on the guidance of the Regulatory Organization for the following reason: "It has been determined that the two previously reported DOE IMI-3 events for 2012 did not meet the requirements for an NRC reportable event and should have been entered into the written log in accordance with 10 CFR 95.57. While they did meet the criteria for an 8-hr reportable event to the DOE they did not meet the NRC requirements for reporting to the NRC Operations Office. We hereby request that both NRC Events 48084 and 47956 be retracted." Notified R2DO (Desai) and ILTAB via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2012-07-10
48083 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-07-10 13:44 | 2012-07-10 15:47 | 2012-07-11 | SAFEGUARD SYSTEMS DEGRADED Discovered vulnerability in a safeguard system that could allow access to a controlled access area. Compensatory measures are now in place. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional information. * * * UPDATE FROM RICK LULLING TO DONG PARK ON 7/11/12 AT 0021 EDT * * * Vulnerability in a safeguard system has been corrected and compensatory measures have been secured. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Blamey) and 73.71 Group via email. * * * UPDATE FROM RICK LULLING TO JOHN KNOKE ON 7/11/12 AT 2044 EDT * * * Vulnerability in a safeguard system has been retracted based on an evaluation of available guidance documents, and verification of compensatory measures implemented. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Blamey) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-07-10
48082 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-05-19 00:06 | 2012-07-10 14:37 | 2012-07-10 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On May 19, 2012, at 0006 hours Central Daylight Time (CDT), two fuses were inadvertently contacted with a spiral notebook in panel 9-42 of the auxiliary instrument room. The two blown fuses resulted in a Primary Containment Isolation System (PCIS) partial Group 6 isolation. The partial Group 6 isolation caused the initiation of Standby Gas Treatment subsystems 'A' and 'C', the initiation of Control Room Emergency Ventilation subsystem 'A', and the isolation of the inboard Group 6 valves and ventilation dampers. "Plant conditions which initiate PCIS Group 6 actuations are Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, and Reactor Building Ventilation Exhaust High Radiation. At the time of the event, these conditions did not exist; therefore, the partial actuations were invalid. "The affected equipment responded as designed. On May 19, 2012, at 0130 hours CDT, Operations personnel reset the partial Group 6 isolation. "There were no safety consequences or impact on the health and safety of the public as a result of these events. "This event was entered into the Corrective Action Program as Problem Evaluation Report 554165. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-07-10
48081 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2012-06-28 | 2012-07-10 11:03 | 2012-07-10 | AGREEMENT STATE REPORT - LEAK FROM NUCLEAR LAUNDRY FACILITY DISCHARGE LINE The following information is provided by the State of Alabama via facsimile: "On Thursday, June 28, 2012, representatives of Eastern Technologics, Inc. (ETI) notified the Alabama Office of Radiation Control of the discovery of a leak in the sewer drain that handles the waste water discharge from ETI's nuclear laundry facility in Ashford, Alabama. At that time, ETI was determining the extent of contamination caused by the leak. ETI is authorized to possess and use the radioactive material as part of their operations under Alabama Radioactive Material License No. 947. Under the conditions of this license, ETI is required to restrict effluent releases to sewers to ten percent of the maximum permissible concentrations specified in Appendix B, Table III of Agency [Alabama Office of Radiation Control] Rule 420-3-26-.03 for all radioisotopes (except Co-60). For Co-60, the licensee is required to restrict releases to 20 milliCuries each calendar year. "ETI excavated the area and determined that the source of the leak was an elbow in the drain pipe. Access to the area identified as contaminated was restricted and controlled. Samples were taken by Alabama Office of Radiation Control personnel on July 1, 2012. The results of the analysis of those samples were made available on July 9, 2012 and identified contamination in the soil at levels greater than five times the lowest annual limit of intake (ALI) as specified in the Agency [Alabama Office of Radiation Control] rules. "ETI is currently decontaminating the site by excavating the contaminated soil. Personnel from the Alabama Office of Radiation Control are monitoring activities and taking confirmatory samples to verify clean up standards. The cause of the incident and the corrective measures by the licensee are pending at this time. The information is accurate as of 0900 CDT, July 10, 2012." Alabama Incident # 12-51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2012-07-18
48080 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-07-10 02:36 | 2012-07-10 10:30 | 2012-07-10 | INVALID GROUP 5 ISOLATION DUE TO FAILED TEST SWITCH DURING SURVEILLANCE "At 0236 CDT on Tuesday, July 10 2012, the Dresden Nuclear Power Station (DNPS) U3 Isolation Condenser System automatically isolated due to a inadvertent partial Group 5 Primary Containment Isolation System (PCIS) isolation, causing the inboard isolation valves to close. The PCIS isolation was caused during the performance of DIS 1300-07, 'U3 Isolation Condenser Steam/Condensate Line High Flow Calibration,' due to a failed test switch. The test switch failed to bypass the PCIS signal generated during the surveillance. All valves responded as expected due to this condition. "The isolation condenser was declared inoperable and Technical Specification 3.5.3, Condition A was entered. HPCI was verified to be operable to satisfy the requirements of TS 3.5.3, Condition A.2. This condition is reportable under 10 CFR 50.72(b)(3)(v)(B) due to a condition occurring that could have prevented fulfillment of a safety function needed for residual heat removal." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-07-10
48079 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-07-09 | 2012-07-09 14:17 | 2012-07-09 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was provided by the State of California via facsimile: "At 0818 [PDT] on July 9, 2012, RHB was notified by CalEMA [California Emergency Management Agency] that they had received a report of a stolen gauge. The gauge CPN MC-1DR #MD20706668) was discovered stolen this morning when the gauge user arrived at the job site in Ontario, CA. The lock on the mini storage trailer was broken and the chain that bolted the gauge (in the locked case) to the structure was broken and the gauge and case were removed. The gauge case was locked. "At 1015 [PDT] on the same morning, the licensee reported the gauge and case had been found on a dirt road in another city from where it was stolen. There was no damage to the gauge and the lock had been removed from the case. The handle of the gauge was not locked and the licensee [was] cited because of this." CA 5010 # 070912 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-07-17
48078 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-07-08 16:27 | 2012-07-08 17:50 | 2012-07-08 | COMMONWEALTH OF MASSACHUSETTS NOTIFIED THAT PILGRIM STATION WORKERS RATIFY NEW CONTRACT "On July 8, 2012, at 1627 [EDT] hours and the reactor at 100% core thermal power, the following informational statement was issued by Entergy Nuclear regarding the status of the ongoing labor action at the site: "UWUA Local 369 Pilgrim Station Workers Ratify New Contract. "UWUA Local 369 Pilgrim Station union members voted today to ratify a new, four-year bargaining union contract which is effective May 16, 2012. "'The new contract, which came to fruition as a result of a lot of hard work on both sides, reflects our commitment to our employees, is acceptable to our union workers and preserves union interests,' said Pilgrim Site Vice President, Robert Smith. 'We look forward to our employees returning to work, which has been our goal throughout this process,' he continued. "While specific details of the agreement are not being disclosed, the new four-year contract represents a substantial commitment to employees in the form of guaranteed wage increases, a comprehensive benefits package including premium health care plan options, a Company-matching 401(k) savings program, a defined benefits pension plan and a union incentive plan. "'We now turn our attention to the transition/turnover process and have initiated our Reintegration Plan which is a deliberate process to ensure the qualifications, training and other site requirements of returning employees are current and meet all NRC or procedural requirements. As employees are reintegrated, we will be phasing out our alternate staffing/contingency plan and expect to have all of our union employees back to work this week,' said Smith." The licensee notified the Massachusetts Emergency Management Agency and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-08
48077 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2012-07-08 12:02 | 2012-07-08 12:30 | 2012-07-08 | UNUSUAL EVENT DECLARED FOR A FIRE ALARM IN THE REACTOR BUILDING VC Summer operators declared an Unusual Event due to one fire detector being in alarm inside the reactor building 'B' steam generator cubicle. There are no other fire detectors in alarm nor are there any elevated containment temperatures. The licensee is making preparations to enter the reactor building to investigate. The reactor continues to operate at 100% power. The licensee contacted the NRC Resident Inspector. * * * UPDATE AT 1640 ON 7/8/2012 FROM BRUCE THOMPSON TO MARK ABRAMOVITZ * * * "On 7/8/2012 at 1202 EDT, an Unusual Event was declared. The event was [declared based on] HU 2.1 'Fire within the Protected Area not extinguished within 15 minutes of detection' and was based on a single smoke detector alarm in the Reactor Building. There were no other indications of a fire. The NRC was initially notified at 1230 EDT. "At 1542 personnel entered the Reactor Building and verified that no fire had occurred. A faulty smoke detector is suspected. "At 1634 the Unusual Event was terminated." The smoke detector was declared inoperable. The licensee notified the NRC Resident Inspector. Notified the IRD (Marshall), R2DO (Bonser), NRR (McGinty), DHS SWO, FEMA, and DHS NICC. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-07-08
48076 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-07-07 00:09 | 2012-07-07 01:51 | 2012-07-07 | OFFSITE NOTIFICATION DUE TO LOST AMERTAP BALLS "At 0009 CDT, Prairie Island Nuclear Generating Plant notified the Minnesota State Duty Officer that up to 1482 Amertap Balls had been lost from the Unit 2 Condenser Tube Cleaning System. Since the Minnesota State Duty Officer was contacted, this constitutes a 4 hour non-emergency notification per 10CFR50.72(b)(2)(xi). The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-07
48075 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-07-06 10:12 | 2012-07-06 13:55 | 2012-07-06 | LOSS OF 7 OFFSITE SIRENS DUE TO INCLEMENT WEATHER "On the evening of July 5, 2012, a severe thunderstorm warning was issued by the National Weather Service for the Tennessee Valley Authority (TVA) area. These storms included wind and tree damage to the surrounding area. "On the morning of July 6, 2012, TVA pulsed the sirens in the emergency response system by providing an electrical signal to each of the siren towers. It was determined there had been localized power outages and possible tree damage to 7 out of the total of 99 offsite sirens. While the number of sirens out does not meet the required notification, this data was given to the state for informational update. This information was provided to the Tennessee Emergency Management Agency (TEMA) at 1012 EDT. Due to the interaction with the state and local government agencies, this report is being made as a four hour notification under 10 CFR 50.72(b)(2)(xi). "The sirens will be repaired as needed and returned to service. There were no plant events that required siren actuation, and all plant systems are operating as required. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-06
48074 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-06 10:12 | 2012-07-06 13:04 | 2012-07-06 | LOSS OF 21 OFFSITE SIRENS DUE TO INCLEMENT WEATHER "At 1012 EDT on July 6, 2012, Tennessee Valley Authority (TVA) notified Tennessee Emergency Management Agency (TEMA) due to a loss of twenty-one (21) offsite sirens. Siren outages are believed to be from power supply failures caused by high winds resulting in downed trees last night. Efforts are in place to restore offsite sirens to service. "A loss of 21 of the 108 offsite sirens does not constitute a significant degradation in the Alert and Notification System. (A loss of 32 sirens constitutes a significant degradation.) "Both Sequoyah units remain at 100 percent power. "NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-06
48073 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-07-06 02:32 | 2012-07-06 08:24 | 2012-07-07 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE "Calvert Cliffs Tech Support Computer power supply failed rendering the ERDS system incapable of transmitting data to the NRC. ERDS is out of service for both Unit-1 and Unit-2. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. Control Room Emergency Response Organization personnel will use backup methods already captured in emergency response procedures to disseminate plant parameter data to the effected Emergency Response Facilities and NRC during the plant data network outage." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOE GIOFFRE TO HOWIE CROUCH AT 1528 EDT ON 7/7/12 * * * ERDS was returned to service at 1528 EDT after replacing the computer power supply. The licensee has notified the NRC Resident Inspector. Notified R1DO (Henderson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-06
48072 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-07-05 12:58 | 2012-07-05 21:24 | 2012-08-31 | UNANALYZED CONDITION DUE TO BLOCKING BOTH REACTOR BUILDING RAILROAD BAY DOORS "At 1258 CDT on 07/05/2012, Operations was notified that both panels of Door 45 (south doors for the reactor building railroad bay airlock) were blocked by a man lift. Blocking both doors represents an unanalyzed condition as a flow path through the door is assumed for pressure relief during postulated HELB events. The man lift was immediately removed correcting the situation and all work related to Door 45 was stopped. Door 45 was blocked for approximately 20 minutes. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM BART BLAKESLEY TO DONALD NORWOOD AT 1605 EDT ON 8/31/2012 * * * "The purpose of this notification is to retract the previous Event Notification Report (#48072) made by the Monticello Nuclear Generating Plant on 7/5/2012. The initial report indicated that blocking both panels of the railroad bay doors by a man lift represented an unanalyzed condition, as a flow path through the door is assumed for pressure relief during postulated HELB events, and was reported in accordance with 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition. Since the initial report, Engineering has completed an evaluation that demonstrates equipment supporting safe shutdown would have been capable of performing their specified design function during postulated HELB events. Based on this analysis, the condition initially reported in EN #48072 did not result in an unanalyzed condition that significantly degraded plant safety and is therefore retracted. "The NRC Resident Inspector has been informed of this retraction." Notified R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-07-05
48071 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-05 10:00 | 2012-07-05 17:45 | 2012-07-05 | VALVE IMPROPERLY ALIGNED FOR ACCIDENT MITIGATION "On 7/5/12 at 0307 hrs (EDT), Salem Unit 2 declared 21 Auxiliary Feedwater Pump out of service due to the failure of the 23AF21, Auxiliary Feedwater Flow Control valve to the 23 Steam Generator. 23AF21 had failed to a full open position during performance of the in-service test. Salem Unit 2 entered Technical Specification 3.7.1.2 a, Action Statement a, which requires restoring the pump to operable status within 72 hours, otherwise be in at least Hot Standby within the next 6 hrs and in Hot Shutdown within the following 6 hours. "At 1000 hrs on 7/5/12, the air supply to the 23AF21 was found isolated. Troubleshooting and repair of the 23AF21 was completed and, following in service testing, the valve was declared operable at 1349 hrs. "Review of the valve's operability concluded that the failure of the 23AF21 valve to close represented a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. The Salem UFSAR assumes that during a Category IV Main Steam break accident, a faulted Steam Generator would be identified and Auxiliary Feedwater would be isolated to the affected Steam Generator within 10 minutes. Since the valve was failed open and could not be operated from the control room, the plant would have to manually isolate 23AF21 or trip the 21 Auxiliary Feedwater Pump to ensure feedwater isolation to the affected, faulted Steam Generator. The time to perform manual isolation or tripping of the Auxiliary Feedwater Pump may have required more time than that analyzed by the plant UFSAR. "This is being reported under 10CFR50.72(b)(3)(v), the nuclear plant being in a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "There were no other safety related systems affected by this event and there were no injuries associated with this event." Maintenance was last performed on this system on May 17, 2012. The licensee will notify the NRC Resident Inspector and Lower Alloways Creek Township. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-07-05
48070 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-06-21 16:00 | 2012-07-05 14:06 | 2012-07-05 | TWO INCORE DETECTORS CONTAINING U-235 UNACCOUNTED FOR DURING INVENTORY "This is a non-emergency notification regarding an extremely small amount of Special Nuclear Material (SNM) which is unaccounted for. On 6/21/2012, it was determined that two nuclear instrumentation incore detectors could not be accounted for at Catawba. Detectors of this type are used to measure incore neutron flux (intensity of neutron radiation) inside the reactor vessel. This determination was made following the completion of a scheduled inventory of nuclear instrumentation incore detectors in storage. This is being reported under 10 CFR 20.2201(a)(1)(ii) (reports of theft or loss of licensed material). "According to Catawba documentation, there should be 54 such detectors in storage. Only 52 detectors could be physically located on site. There is no evidence of theft or diversion of these detectors. According to site documentation, one or both of the detectors may have been shipped to Barnwell in 1986. Detectors of this type contain very small amounts of Uranium-235 (0.0041 grams/detector), which qualifies them as SNM. The most likely location for the detectors is either in one bunker located on site and within the radiological controlled area or at Barnwell via a low level radioactive waste shipment. The search for these detectors was suspended based on a determination that the additional dose to plant workers involved in the search was not justified by an equivalent offsetting safety benefit. It is unlikely that these detectors could have left the site other than in a radioactive waste shipment as the radiation monitoring equipment in place would likely have identified the presence of the detectors. "This event had no effect on plant operations and no impact on public health and safety has been identified. A written report will be made in accordance with 10 CFR 20.2201(b)(1)(i-vi). The licensee will notify the NRC Resident Inspector." Usually, spent incore detectors are stored in a locked high radiation area at the facility. This was the first physical inventory of sources performed by the licensee. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2012-07-13
48069 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-07-03 17:38 | 2012-07-03 20:35 | 2012-07-03 | INADVERTENT EMERGENCY SIREN ACTUATION "This event is being reported in accordance with 10CFR50.72(b)(2)(xi). On July 3, 2012, at approximately 1738 hours, an inadvertent actuation of the Perry Nuclear Power Plant's (PNPP) alert notification system occurred. Seventy-five of seventy-six sirens sounded for three minutes, affecting Ashtabula, Geauga, and Lake Counties. Following the actuation, county agencies received calls from members of the public. "PNPP's capability to notify the public in an emergency has been retained. The siren actuation was not related to any condition or event at the PNPP. An investigation is in progress to determine the cause of the inadvertent actuation. At the time of the event, the plant was in Mode 1 at 100 percent rated thermal power. "The public was informed of the inadvertent actuation by way of the Emergency Alert System (EAS). "The NRC Resident Inspector has been notified." The licensee has notified State and Local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-03
48068 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2012-06-05 | 2012-07-03 17:26 | 2012-07-03 | LOST SEALED SOURCES The following was reported from the state via e-mail: "During a routine six-month inventory, the licensee was unable to locate four (4) sealed sources, of which one has an activity that exceeds exempt quantities. The last known person using the sources was contacted on June 5, 2012 to determine if they were in his possession. He indicated that the previous x-ray RSO had found them and returned them to the source locker. However, the former x-ray RSO indicated that in-fact he did not locate the sources. Management and the materials RSO was notified and an investigation was initiated. "All staff members were questioned and asked to check around their work areas. The assistant RSO checked all devices, pigs, the source cabinet and surveyed the entire facility, including shipping and receiving, with a micro-R survey meter. None of the sources were located on any disposal or transfer records. "The sources were used in a prototype instrument called Plombix, designed to operate with an exempt source in the shape of a washer, and were used only for in house experiments. The missing sources were designed for this prototype instrument and do not fit all other instruments at this facility. "Washington Department of Health corrective action is pending. "The Assistant RSO indicated that sufficient controls are not in place to maintain control of sources stored outside the source locker, and that a single company source custodian will be assigned for all sources. "Source Number: 1; Source/Radioactive Material: SEALED SOURCE M & D; Radionuclide: CD-109, 0.000000194 Ci, 0.000007178 GBq; Manufacturer: ISOTOPE PRODUCTS LAB; Model Number: MISC-IND; Serial Number: 1112-35. "Source Number: 2; Source/Radioactive Material: SEALED SOURCE M & D; Radionuclide: CD-109, 0.000064 Ci, 0.002368 GBq; Manufacturer: ISOTOPE PRODUCTS LAB; Model Number: MISC-IND; Serial Number: D1-472. "Source Number: 3; Source/Radioactive Material: SEALED SOURCE M & D ; Radionuclide: CO-57, 0.000005 Ci, 0.000185 GBq; Manufacturer: ISOTOPE PRODUCTS LAB; Model Number: RFQ482-3; Serial Number: C9-333. "Source Number: 4; Source/Radioactive Material: SEALED SOURCE M & D; Radionuclide: CO-57, 0.000000122 Ci 0.000004514 GBq; Manufacturer: ISOTOPE PRODUCTS LAB; Model Number: MISC-IND; Serial Number: 1096-28. "Reference Number: WA-12-047" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2012-07-11
48067 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-07-03 10:32 | 2012-07-03 16:53 | 2012-07-03 | TSC OUTAGE RESULTING FROM MAINTENANCE "Planned maintenance activities are being performed today (July 3, 2012) to remove temporary power from and restore normal power to the Technical Support Center (TSC) 480 VAC Distribution Panel 1R25-S012. This panel provides power to the TSC Emergency HVAC (TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train) rendering the TSC non-functional (TRM - Section T 3.10.1 EMERGENCY RESPONSE FACILITIES) during the performance of this work activity. This work activity is planned to be performed and completed expeditiously within about 5 hours including establishing and removing the clearances. The temporary power was installed on 6/19/12 to support work activities on the Hatch Nuclear Plant's 1R24-S026-600/208V MCC under Work Order Number 1050889203 which is the normal power supply. "If an emergency condition occurs that requires activation of the Technical Support Center, plans are to utilize the TSC during the time this work activity is being performed, as long as habitability conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution. "The TSC was returned to service today at 1645 EDT on 7/3/2012." The licensee has notified the NRC Resident Inspector. | 98 | 99 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-03
48066 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-07-03 09:40 | 2012-07-03 13:21 | 2012-07-03 | OFFSITE NOTIFICATION DUE TO A FATALITY "At 0940 hours on July 3, 2012, Detroit Edison notified the Michigan Occupational Safety and Health Administration (MIOSHA) that an employee had suffered a fatality. "On July 2, 2012, at 1504 hours, a Detroit Edison employee reported to the nurse's office with symptoms of shortness of breath and chest pain. The individual was transported offsite via ambulance to a local hospital for care. At approximately 1700 hours on July 2, 2012, notification was received that the individual had passed away. "There was no radioactive contamination involved in this event. The licensee has not notified any other government agencies besides MIOSHA. "This ENS report is being made in accordance with 50.72(b)(2)(xi). The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-07-03
48065 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-06-28 06:00 | 2012-07-03 12:55 | 2012-07-10 | DISCARDED COMPASS CONTAINING RADIUM FOUND The following was received via email from the Commonwealth of Massachusetts: "A military compass containing approximately 10 microcurie of Ra-226 was improperly discarded via trash by an unknown person and was detected at the Maine Energy Recovery Company in Biddeford, ME on June 28, 2012. The State of Maine Radiation Control Program notified our Agency [Commonwealth of Massachusetts] and transfer back to the place of origin was arranged. This was Thomson Brothers Industries. "The truck was off loaded at that site and the source was discovered by a contracted health physics consultant. We received notification of the discovery of the source from the consultant at 10:49 am on June 29, 2012. "Our Agency is currently assisting Thomson Brothers Industries in making arrangements for the proper disposal/transfer of the compass." * * * UPDATE AT 0837 ON 7/10/12 FROM TRAEGDE TO SNYDER * * "The compass was confiscated by the [Massachusetts] Radiation Control Program on 7/6/12 and given to a Massachusetts licensee for disposal. This action closes this event." Notified R1DO (Burritt) and FSME Events Resource (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-07-11
48064 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-07-02 15:05 | 2012-07-02 18:50 | 2012-07-02 | HPCI DECLARED INOPERABLE "A spurious isolation of the High Pressure Coolant Injection (HPCI) Outboard Steam Supply Valve and Outboard Torus Suction Valve occurred. Initial verifications indicate that the signal was not valid and investigations in the vicinity of the piping revealed no evidence of leaks. Troubleshooting is in progress. "HPCI declared inoperable per TS 3.5.1 Condition F which allows 14 days to restore to operable status. "All remaining ECCS and RCIC are operable and available. Grid stability has been verified." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-07-02
48063 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2012-07-02 15:51 | 2012-07-02 18:42 | 2012-08-28 | BOTH DIESEL GENERATORS DECLARED INOPERABLE "D1 and D2 Diesel Generators (DG) were declared inoperable at 1551 CDT due to exceeding the maximum outside air temperature limit of 97 degree F. This limit was based on heatup analysis for a HELB [High Energy Line Break] in the turbine building. The temperature is measured using the 15 min average of air temperature at the 10 meter meteorological tower, which approximates the intake height for room ventilation. "LCO 3.8.1 Condition B was entered for both DGs and LCO 3.8.1 Condition E was entered for two DGs inoperable on the same unit. The DGs could start and run if required at the time of entry. "This condition is reportable per 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented the fulfillment of a safety function. "During review of the analysis, two pressure switches on D2 and one on D1 were identified as being limiting and a modification was approved to replace them. Upon replacement, the limiting outside temperature would increase to 100.5 degree F. Replacement of components had been completed for D2 diesel generator prior to LCO entry; however, the temperature limit of 100.5 degree F had not yet been approved. "Shortly after D1 was declared inoperable, it was isolated to complete the component replacement which is expected to take less than four hours. D1 will return to operable once the component replacement and PMT is completed. "At 1630 [CDT] D2 was declared operable based on approval of a revised operability recommendation that raised the outside temperature limit to 100.5 degree F. "Outside air temperature peaked at 97.1 degree F and is slowly decreasing." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM GENE DAMMANN TO DONALD NORWOOD AT 1555 EDT ON 8/28/12 * * * "Event Notification 48063 reported that D1 and D2 Diesel Generators (DG) were inoperable due to exceeding the maximum outside air temperature limit of 97 degree F. "An additional approved evaluation determined that the D2 lube oil pressure switches were replaced prior to exceeding the outside ambient air temperature limit. The new lube oil pressure switches have a higher temperature rating that supports a higher outside ambient air temperature, therefore, D2 was able to fulfill its safety function and Event Notification 48063 is retracted. "The NRC Resident Inspector has been informed." Notified R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2012-07-02
48062 | 0 | NUTHERM INTERNATIONAL, INC | [5 empty] | 2012-07-02 15:31 | 2013-07-16 | PART 21 - FAULTY SWITCH RESULTING FROM A FAILED SPRING The following was received via facsimile: "This is to notify the Nuclear Regulatory Commission, in accordance of the provisions of 10 CFR Part 21 of a potential deviation identified by Nutherm International, Inc. "On June 26, 2012 one M470 Spring Return Kraus and Naimer (K&N) switch (part number CA10 USN892 - 600 FT1 S0C G211 S0 M470/D1A) failed at the Nutherm facility. "The failed switch was returned to the manufacturer for failure analysis. On July 2, 2012 the manufacturer notified Nutherm that the specific failure mechanism was spring failure on the 'spring return.' The failure was traced to a spring manufacturer supplying the manufacturing facility between November 1, 2011 and June 29, 2012. "Based on this information, M470 spring return switches manufactured during this time period have the potential for this spring failure. "Nutherm has determined that the following site has received these switches from Nutherm and is affected: Farley Nuclear Plant." * * * UPDATE ON 7/16/13 AT 1221 EDT FROM ADRIENNE SMITH TO DONG PARK * * * The following was received via facsimile: "This written final report is in response to Event/Accession Number ML121910334 reported by Nutherm International, Inc. There were a total of three (3) switches shipped to Southern Nuclear Operating Company, Farley Nuclear Plant affected by this issue. Southern Nuclear Operating Company, Farley Nuclear Plant was notified on July 2, 2012 of this issue and provided with the specific traceability numbers of all units. None of the units had been installed at the time of the notification. "Southern Nuclear Operating Company returned all three units on July 5, 2012. The units were subsequently destroyed by Nutherm International, Inc. "Corrective actions have been put in place to prevent recurrence of this issue. Corrective actions include additional testing of spring return switches of this model type." Notified R2DO (Nease) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-07-02
48061 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-07-02 08:00 | 2012-07-02 08:25 | 2012-07-03 | SPDS AND ERDS OUT OF SERVICE FOR MAINTENANCE "Beginning July 2, 2012, at approximately 0800, the Fermi 2 Integrated Plant Computer System (IPCS) will be removed from service to support installation of a Cyber Security Modification. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform and will be out of service when the IPCS is removed from service. These systems will be unavailable to the Control Room and all other Emergency Response Facilities (ERFs) for approximately 20 hours. By 0300 on July 3, 2012, it is planned to restore IPCS, including SPDS and ERDS, to the Control Room, Operational Support Center, the Technical Support Center, and alternate facilities. During this time dose assessment capability will only be available in the manual data input mode. The majority of the Control Room indications remain available to the plant staff, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems as needed. A follow-up notification will be submitted when the IPCS is completely restored. This notification is being made per the requirements of 8 Hour Non-Emergency Notification 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 7/03/12 AT 0113 EDT FROM GROFF TO HUFFMAN * * * "On July 3, 2012, at 01:00, the Fermi 2 Integrated Plant Computer System (IPCS) has been returned to service. Emergency assessment capabilities have been restored to all onsite emergency response facilities. Due to equipment problems, the Cyber Security Modification was not installed and the original IPCS configuration was restored." The licensee has notified the NRC Resident Inspector. R3DO (Daley) notified. * * * UPDATE ON 7/03/12 AT 0556 EDT FROM GROFF TO HUFFMAN * * * "At approximately 02:04 on July 3, the Fermi 2 Integrated Plant Computer System (IPCS) failed. The Safety Parameters Display System (SPDS) and Emergency Response Data System (ERDS) reside on the IPCS platform. IPCS had previously been removed from service on 7/2/12 for a Cyber Security Modification and restored at 0100 on 7/3/12. "At 0354, plant personnel were able to reboot IPCS and restore the system to normal with a Prime and Backup CPUs. Emergency assessment capabilities have been restored to all onsite emergency response facilities. "This notification is being made per the requirements of 8 Hour Non-Emergency Notification 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability." The licensee has notified the NRC Resident Inspector. R3DO (Daley) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-02
48060 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-07-02 02:00 | 2012-07-02 01:49 | 2012-07-02 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 02:00 EDT on Monday, July 2, 2012, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 15:00 EDT on Monday, July 2, 2012. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM BEN HUFFMAN TO DONG PARK AT 1727 EDT ON 7/2/12 * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1725 EDT on 7/2/12." The licensee will notify the NRC Resident Inspector. Notified R3DO (Daley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-07-02
48059 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-06-29 17:46 | 2012-06-29 21:15 | 2012-06-29 | OFFSITE NOTIFICATION DUE TO AN EMPLOYEE MEDICAL EMERGENCY "On June 29, 2012, at 1746 EDT hours and the reactor at 100% core thermal power, the following informational statement was issued by Entergy Nuclear regarding a medical emergency involving a member of the Pilgrim Station Security Department. "This afternoon, a security employee at Pilgrim Station who appeared to be in medical distress was immediately transported to the hospital for observation and professional medical care. "The individual was observing and monitoring union picket line activities and was not filling a position required by the Pilgrim Station Security Plan. "The Resident Inspector staff has been informed of this press release and notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi). "The licensee will notify the Massachusetts Emergency Management Agency." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-06-29
48058 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-02 | 2012-06-29 15:59 | 2012-12-20 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT DUE TO LEAKING I-125 SEEDS The following was received via e-mail: "On 6/28/12 Saint Joseph Hospital personnel were surveying a packing materials used to ship I-125 seeds, for a procedure conducted earlier that day, when they noted elevated readings. Further surveys revealed that the elevated readings were not coming from the packing material associated with the 6/28/12 procedure but from packing material that was used to ship I-125 seeds for a previous procedure, which was in the area of the survey. Surveys of the packing material revealed no loose contamination on the exterior or interior of the box but elevated readings of 2500-350000 cpm and .2 mrem/hr. Receipt and post procedure surveys of the procedure associated with contaminated box did not reveal any abnormal readings. The Saint Joseph RSO assumes the material is I-125 but they do not have the capability to verify this. No loose seeds were found in any of the packing material. The I-125 seeds were accompanied by the manufacturers leak test report which indicated no contamination. "The patient, whose procedure was associated with the contaminated packing material, will be evaluated on Monday 7/2/12 to determine if there was any uptake in his urine or thyroid of I-125 as a result of leaking seeds." CA Report Number: 062912 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON 7/2/12 AT 1806 EDT FROM EUGENE FORRER TO DONG PARK VIA EMAIL * * * "This is a follow up of an incident, as information only, on Friday, June 29, 2012. Radiologic Health Branch reference would be 5010 #062912. The notification was about contaminated packaging that had contained Best Medical I-125 seeds. A thyroid count was performed on the patient who had the seeds implanted in May. The thyroid count verified that there had been an uptake of iodine by the thyroid. Below is the write up and preliminary dose estimate from the licensee regarding. "Based upon this morning's patient measurements, instrument-manufacturer supplied efficiency data, and reference data for dose conversion, we estimate the patient involved received a thyroid uptake of 0.1 mCi of I-125 and a dose to the thyroid of 300 cGy. "1) Conversion of counts per minute (cpm) to activity Two[Pi] counting efficiency for I-125 (per manufacturer) is 133.5% fraction of 2[Pi] solid angle subtended by a 2 inch diameter detector at a distance of 30 cm from the thyroid is 10.13 squared cm / 5654.9 squared cm = 0.00179 overall efficiency = 1.335 x 0.00179 = 0.00239 (190493 - 30) net cpm / 0.00239 x 4.505x10-10 mCi/dpm = 0.0359 mCi present thyroid burden. Back-correcting 60 days to time of implantation (conservatively assuming that all uptake occurred at that time) with 42-day effective half-life, initial uptake given by 0.0359 / 0.3715 = 0.0967 approximately 0.1 mCi "2) Taking the value quoted by Chen et.al. (attached) from NUREG/CR-6345, we assume the dose to thyroid is 780 cGy per mCi of I-125 administered, and this value assumes 25% uptake into the thyroid. Our calculated estimated thyroid burden of 0.1 mCi then gives an estimated absorbed dose of 0.0967 mCi x 780 cGy/mCi / 0.25 (since we measured actual thyroid burden v. amount administered) = 302 cGy approximately 300 cGy (rad) to thyroid. "3) Whole body committed effective dose equivalent (CEDE) from a 300 rad dose to the thyroid (using a thyroid weighting factor of 0.04) would be 12 rem." Notified R4DO (Allen) and FSME (Einberg). * * * UPDATE FROM GENE FORRER TO CHARLES TEAL ON 12/19/12 AT 1650 EST * * * "EVENT SUMMARY: While surveying an empty brachytherapy seeds package for return to Best Medical hospital personnel discovered contamination on the interior of the package. Follow up thyroid scans of the patient who was implanted with the seeds associated with the package verified an uptake of I-125 by the patient's thyroid. The initial report to RHB was intended, by the licensee, to be a notification of a Medical Event. "REPORTING: This event was reported to the NRC, by phone, on 4/13/12, at 8:50 am via email. "HEALTH AND SAFETY: Based on surveys of the packing material all contamination was contained within the package and did not pose a threat to hospital personnel. The estimated dose to the patient's thyroid was calculated to be approximately 330 rad with a CEDE of 12 rem. "ADDITIONAL DETAILS: The RSO conducted an investigation of the incident and could not find any indication that there were any irregularities with the implantation procedures. Hospital personnel associated with the procedure indicated to the RHB inspector that there were no irregularities with the procedure. In addition receipt surveys of the package did not reveal any contamination of any of the packaging material. The RSO concluded that the cause of the contamination was due to a manufacturing error. "The RSO of Best Medical conducted an investigation of the production of the seeds implanted in the patient. All records at Best Medical indicate that all QC tests of the seeds were done satisfactorily. The RSO concluded that the seeds had been damaged in transit or that Saint Joseph personnel must have damaged the seeds either during the initial surveys or during the implantation. The Best Medical RSO was unable to explain how the seeds could have been damaged and still be implantable. The Virginia Department of Health inspected the Best Medical facility and concluded that all QC testing on the seeds had been completed satisfactorily with no abnormalities noted. "After interviewing Saint Joseph and Best Medical personnel RHB personnel concluded that the most logical explanation for the leaking seeds was a manufacturing error, however, without samples from the same lot of seeds implanted available for analysis this can not be proven conclusively. "The hospital has changed suppliers for the brachytherapy seeds. In addition they have initiated a procedure where the needles containing the seeds are wiped after they have been removed from the shipping container. "ENFORCEMENT ACTIONS: The hospital was not cited for this incident. "INVESTIGATION STATUS: This investigation is closed." Notified R4DO (Spitzberg) and FSME Event Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-07-09
48057 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-02-13 09:20 | 2012-06-29 14:00 | 2012-06-29 | MASS CONTROL LIMIT EXCEEDED "It was discovered on 2/13/12 that the mass control limit in the gadolinia pellet press operation was exceeded. An improperly installed valve allowed a total of 43 kg of uranium powder into the favorable geometry press feed tube, exceeding the 36 kg limit. This resulted in a failed item relied on for safety (IROFS) < 1 hour condition where a criticality control was not maintained. The press feed mass control is a sole IROFS for a fire accident sequence. Control indications functioned as designed and provided notification of the malfunction to the operator and the operation was secured. The other controls on geometry and moderation were maintained at all times. "At no time was an unsafe condition present. The gadolinia pellet press operation was shut down and the powder was removed by 1000 on 2/13/2012. "Additional corrective actions, extent of condition, and extent of cause have been documented. "SAFETY SIGNIFICANCE OF EVENTS: At no time was an unsafe condition present "SAFETY EQUIPMENT STATUS: Equipment was shut down and powder removed "STATUS OF CORRECTIVE ACTIONS: Additional corrective actions, extent of condition, and extent of cause have been documented. "This event is being communicated in order to administratively meet the reporting requirements of 10CFR70, Appendix A." The licensee has spoken with Region 2 (Thomas) regarding this issue, and discussed the issue in a Reply to Notice of Violation dated 6/29/2012 letter book number SPM12-030. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2012-06-29
48056 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-06-29 10:28 | 2012-06-29 13:04 | 2012-11-29 | UNANALYZED CONDITION DUE TO INCREASE IN PROBABLE MAXIMUM FLOOD LEVEL "On June 29, 2012, TVA issued an updated calculation titled 'PMF Determination for Tennessee River Watershed' The calculation resulted in an increase in the Watts Bar Nuclear (WBN) probable maximum flood (PMF) level from Elevation 734.9 to Elevation 739.2. All flood sensitive safety related systems, structures, and components have been reviewed and been determined to remain unaffected by the revised PMF surge elevation, with the exception of the Thermal Barrier Booster Pump Motors and Essential Raw Cooling Water (ERCW) equipment required for flood mode operation located on Elevation 722 of the Intake Pumping Station (IPS). The updated PMF of Elevation 739.2 could impact the ability of the thermal barrier booster pumps and the Elevation 722 IPS ERCW equipment to perform their design accident protection function. Because of the unanalyzed condition. the potential existed for WBN to exceed its PMF design basis and adversely affect plant safety. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(B). "Compensatory measures have been prepared to install a temporary flood protection barrier around the thermal barrier booster pumps and provide additional protection of Elevation 722 of the IPS in the event of a flood alert. "The potential for the increased PMF level and the associated compensatory measures were previously discussed in a public meeting between TVA and the NRC on May 31, 2012 and in correspondence between TVA and the NRC dated June 13, 2012 and June 25, 2012. "All safety related equipment is currently operable. There are no indications of conditions that might result in a flood in the near term. "The licensee notified the NRC Resident Inspector of this condition." * * * UPDATE FROM MICHAEL BOTTORFF TO VINCE KLCO AT 1435 EST ON 11/29/12 * * * "Based upon continuing engineering reviews, the chilled water circulating pump motors for the Train A and B Main Control Room and 6.9kV Shutdown Board Room, including various sub-components, would be partially submerged during a Probable Maximum Flood (PMF) event. These components were not previously considered as affected by the PMF. The affected components are located on floor elevation 737.0 of the auxiliary building. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(B). "Compensatory measures have been prepared to install temporary flood protection barrier around the chilled water circulating pump motors and provide additional protection of Elevation 722 of the IPS in the event of a flood. "All safety related equipment is currently operable. There are no indications of conditions that might result in a flood in the near term. "The licensee notified the NRC Resident Inspector of this condition. "Licensee Event Report 50-390/2012-002-00 will be supplemented to include a description of the potential PMF affects on the chilled water circulating pump motors." Notified the R2DO (Ernstes). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-06-29
48055 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-28 13:53 | 2012-06-28 20:44 | 2012-06-28 | LOSS OF ONE OF TWO OFFSITE POWER SOURCES "At 1353 EDT on 06/28/2012, Susquehanna Steam Electric Station experienced a loss of power from one of two offsite power sources when transformer 20 shutdown automatically. All ESS [Engineered Safeguards System] electrical busses fed by this transformer automatically transferred to the other offsite power source (transformer 10). Additionally, startup bus 20, which is normally fed from transformer 20, automatically transferred to transformer 10. "On each unit, multiple system containment isolation valves closed as a result of the electrical transient. Operators were able to reset and restore each system. On unit one, residual heat removal (RHR) shutdown cooling ceased operation during the transient. Shutdown cooling was restored within one hour by control room operators in accordance with off-normal procedures. Unit two remained at 100% power throughout the event. "This incident is being reported as an unplanned actuation of systems that mitigate the consequences of significant events per 10 CFR 50.72(b)(3)(iv)(A)." The licensee is in a 72 hour LCO on Unit 2 as a result of the loss of offsite power. All emergency diesels generators are available. The licensee is investigating the cause of the transformer 20 shutdown. The NRC Resident Inspector and the Pennsylvania Emergency Management Agency (PEMA) have been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-06-28
48054 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-06-28 11:30 | 2012-06-28 14:18 | 2012-06-28 | STOLEN NUCLEAR DENSITY GAUGE The following was received from the Commonwealth of MA. via fax. "An automobile with a Nuclear Density Gauge stored in its trunk was stolen from a work site in Roslindale, MA. The nuclear density gauge was manufactured by Campbell-Pacific, Model No. MC3, Serial No. M390204846, containing sealed sources of Cs-137 and Am-241, of less than 10 millicuries and 50 millicuries, respectively. The gauge is licensed with the MA Radiation control Program, with Miller Engineering & Testing of Northboro, MA under license No. 23-4571. "A police report for the stolen property is being filed with the Boston Police. "Agency [state] continues with the investigation into this matter, and has asked the licensee for a copy of the police report and subsequent findings. Thus, the investigation remains open." * * * UPDATE FROM DOUG CULLEN TO JOE O'HARA AT 1607 EDT ON 6/28/12 * * * The Boston Police Department has recovered the stolen vehicle with the gauge intact in the trunk of the vehicle. The radiation profile is normal for the gauge and the police have notified the company to come and recover the gauge. Notified R1DO (DeFrancisco) and FSME/ILTAB via e-mail THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-07-06
48053 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-06-27 20:46 | 2012-06-28 01:06 | 2012-07-06 | MANUAL REACTOR TRIP DUE TO 100% LOAD REJECT "Unit 2 Manual Reactor Trip was actuated due to indications of a 100% Load Rejection. The cause of the Load Rejection is not known at this time. All Control Rods are fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feedwater system. The auxiliary feedwater system actuated based on low steam generator level, but has since been secured. There were no unexpected (inconsistent with nature of trip) pressure or level transients. Off site power remains available. No release occurred nor is ongoing. Emergency Core Cooling Systems did not actuate. No unexpected isolations occurred. Emergency Plan entry was not required." The plant is stable at normal temperature and pressure. The electrical system is in a normal offsite power alignment. The Unit 2 Reactor Trip had no effect on Unit 1 which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ERIC SONNENBERG TO HOWIE CROUCH AT 2337 EDT ON 7/6/12 * * * "On June 27, 2012 at 2046 CDT, a Unit 2 Manual Reactor Trip was initiated in anticipation of an automatic turbine trip due to operators noticing the turbine governor valves closing and turbine load reduction. It was originally reported that the cause was not known. This notification is updated to provide information to the cause of the load reduction. "Troubleshooting has shown that the reduction of turbine load was due to a turbine speed channel card failing in the turbine control system. The card failure resulted in sending the auxiliary governor in the turbine control system an incorrect indicated overspeed condition and throttling the turbine governor valves to reduce the turbine speed. There was no actual turbine overspeed condition. "The auxiliary governor is not part of the reactor protection system. No reactor protection setpoints were exceeded. All other plant systems functioned as required, including the Reactor Protection System. All control rods fully inserted into the core due to the manual reactor trip. There was no Emergency Core Cooling System actuation. No Emergency Diesel Generators were started and power continued to be supplied from off site. The reactor coolant system had forced circulation and the condenser steam dumps were used for decay heat removal from the steam generators." The licensee has notified the NRC Resident Inspector. Notified R3DO (Daley). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-06-28
48052 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-06-27 16:30 | 2012-06-27 20:16 | 2012-06-27 | INADVERTENT ACTUATION OF AN EMERGENCY SIREN "At 1630 EST, Exelon was notified by the NJ State OEM (Office of Emergency Management) that Oyster Creek Emergency Preparedness Siren #25, located in Harvey Cedars, NJ, was inadvertently actuated at 0209 EST and sounded for a period of 2-3 minutes. The siren was inadvertently actuated by Atlantic City Electric when restoring power to the siren. No actual plant emergency existed. Siren #25 and all other of the 42 sirens remain functional. No other reportability thresholds have been met or exceeded. State and local authorities were also notified." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-06-27
48051 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-06-27 14:46 | 2012-06-27 17:10 | 2012-06-27 | SUCTION PIPE VOIDING "On 06/27/2012, it was identified that a void existed in the common suction header for Safety Injection. The void was of the size such that operability was maintained. However, this was nonconforming to the Kewaunee Power Station licensing basis. "At 1446 on 06/27/2012, the Kewaunee Power Station declared both Safety Injection Train A and Safety Injection Train B Inoperable due to venting of the common suction line to remove the void. LCO 3.0.3 was entered as directed by LCO 3.5.2. ECCS Operating. This loss of safety function is reportable under 10CFR50.72(b)(3)(ii)(B). "The void in question has been reduced to an acceptable size with the common Safety Injection suction piping full. Both Safety Injection Train A and Safety Injection Train B have been restored to Operable status and LCO 3.0.3 was exited at 1500 on 06/27/2012." The condition was detected by ultrasonic testing as part of a surveillance for RHR pump and valve testing. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-06-27
48050 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2012-06-25 13:00 | 2012-06-27 11:30 | 2012-06-27 | STATIC ELIMINATOR BAR FOUND IN SCRAP YARD "[Metro Metals] phoned that a flatbed truck with metal scrap from a recycler in WA (Paymore Recycling & Salvage, Montesano, WA) set off their portal monitor. Hand-held exposure meters were used to survey the load and levels were found at 4000 microrem/hr. This load is waiting for RPS [Radiation Protection Services] to check. "Responded to Metro Metals. Found a static bar. Wrapped and sent back to recycler. Max reading, with Ludlum 2401 EC, at front edge of bar was 6 mR/hr. Exploranium identified Am-241. Static bar was about 5 to 6 feet in length and was cut in half. Item was wrapped in plastic and placed in a drum for return to the recycler." Radiation Protection Services No: 12-0020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2012-07-05
48049 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-06-26 | 2012-06-26 16:52 | 2012-06-26 | AGREEMENT STATE REPORT - TROXLER GAUGE STRUCK BY VEHICLE AT CONSTRUCTION SITE The State of Illinois submitted the following report via email: "On the morning of June 26, 2012, the Agency's Communication Center contacted the Radiological Duty Officer about a Troxler [Model 3411-B] gauge that had been hit by a truck on the Westbound I-90 in Chicago. The licensee, Interra, Inc., reported that an asphalt truck crossed the barriers and ran over the gauge while it was in use in an inactive traffic lane. The source rod was subsequently thrown from the gauge housing. [Illinois Emergency Management] Agency inspectors were dispatched to the scene. State police were also dispatched for traffic control. "In the interim, the licensee located the source rod two lanes over near the center median using their own survey meter. With instruction from the duty officer, they were able to scoop the rod up in an asphalt shovel and put it in a 5 gallon bucket full of sand for shielding. Approximately one hour later, [Illinois Emergency Management] Agency inspectors arrived and were able to secure the source rod back into the damaged gauge housing. A leak test was done and no removable contamination was noted. The shield and shutter were intact and radiation levels were 0.5 mR/hr at a meter once secured. The device was transported back the licensees storage area for further investigation. "[Illinois Emergency Management] Agency inspectors arrived at the licensee's facility at 2:00 pm that same afternoon to inspect the gauge, the storage area, and interview the RSO. The gauge was in view of the authorized user about 5 feet away when the truck crossed the barrier so it does not appear to be a surveillance violation by the licensee. The condition of the gauge was confirmed. The gauge is secure in its Type A container and radiation levels are 0.5 TI [Transportation Index]. All records for transportation were present and correct. The licensee appears to have followed their operating procedures correctly for this type of event. Pending leak test results, film badge results and return of the device to Troxler, we are considering this matter closed." The gauge is a Troxler Model 3411-B, Serial number 40-9314, with a Cs-137 0.009 Ci and Am-241 0.04 Ci source. IL Item Number: IL12010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-07-04
48048 | -1 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2012-06-26 15:30 | 2012-06-26 17:16 | 2012-07-04 | DRUM MISTAKENLY SET ASIDE WITH NO CRITICALITY SAFETY CONTROLS During the excavation of the burial pits area the licensee has requirements that 2 people survey the excavated materials. Excavated material was placed into a 5 gallon plastic container. After placing the material into the container a reading is taken on the bottom of the container in counts per minute which is then equated to a gram level (mass) of material present. If the mass of material is less than 15 grams (about 300,000 counts per minute) then no criticality safety controls are required. One container, packed to a level of 325,000 counts per minute, was put aside briefly near a waste bin where those materials requiring no controls can be placed. Both people assigned to the work mistook this container for a container requiring no controls. A level of 325,000 counts per minutes equates to a mass of 20 grams of Uranium 235. At that level this item was far from the amount of material needed for a criticality accident but additional controls were required. When the personnel realized their mistake they took that container to another area for overpack into a drum that provides additional spacing needed to provide additional criticality safety protection. At this time the container has the appropriate level of controls. The amount of material present was small enough that it could not have caused a criticality accident. * * * RETRACTION ON 7/4/12 AT 1556 EDT FROM KEVIN DAVIS TO DONG PARK * * * "Retraction of the initial notification is appropriate since subsequent, more detailed surveys via gamma spectroscopy (ISOCS) [In Situ Object Counting System] determined that only 2.83g of U-235 were present in the 5 gallon container. The subsequent, more detailed survey was conducted on 6/28/12, after the initial notification was made. This mass quantity is below the threshold for being exempt from criticality safety controls (i.e., no more than 15 g of U-235 in a 5L or larger container). Thus, an unsafe condition was not present when the container was set aside without safety controls since no safety controls are required for 2.83g of U-235 in a 5 gallon container. Based on this retraction, a written report will not be submitted to NRC. "The container was retrieved and the container was placed in a drum with a safety collar that provides additional spacing needed to provide additional criticality safety protection. The cause of the event was personnel inattention to the procedure, which contained the correct numerical decision points and controls. Personnel were retrained, particularly on: (a) Independence of redundant surveys and reviews; (b) Use of the procedure to provide numerical setpoints and action steps. Management and independent oversight of burial pit work activities are emphasizing independence of redundant surveys/reviews and use of the procedure." Notified R3DO (Daley), R2DO (Bonser), IRD (Marshall), and NMSS (Damon) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2012-06-26
48047 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-06-25 13:30 | 2012-06-25 16:38 | 2012-06-25 | REACTOR FEED PUMP TRIP RESULTS IN MANUAL REACTOR SCRAM "At 1330 EDT on June 25, 2012, while restoring the Main Turbine Generator (MTG) to service after repairs to Main Unit Transformer 2B (MUT2B), Main Control Room (MCR) staff manually initiated a reactor scram in response to trip of both Reactor Feed Pumps (RFP). All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 154 inches and, as expected, HPCI and RCIC did not actuate. RWL was restored to normal using the Standby Feedwater (SBFW) system. RWL is currently being maintained in the normal level band with SBFW and Control Rod Drive (CRD) systems. No Safety Relief Valves (SRV) actuated. All isolations and actuations for RWL 3 occurred as expected. Investigation into the trip of RFPs continues. "At the time of the scram, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDG) were operable and no safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The plant is in a normal shutdown electrical lineup with decay heat being removed via steam to the main condenser using the bypass valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 26 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-06-25
48046 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-06-25 10:30 | 2012-06-25 12:00 | 2012-06-25 | SAFEGUARDS REPORT - VULNERABILITY IN A SAFEGUARD SYSTEM THAT COULD HAVE ALLOWED ACCESS TO SGI DRAWINGS Discovery of vulnerability in a safeguard system that could have allowed access to safeguard drawings. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-06-25
48045 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-06-22 13:45 | 2012-06-22 18:38 | 2012-06-22 | NATIONAL RESPONSE CENTER NOTIFIED OF ION EXCHANGE RESIN SHIPMENT LEAKAGE "This report is submitted pursuant 10CFR50.72(b)(2)(xi) due to a notification that was made to the National Response Center. At 1345 CDT on June 22, 2012, Waterford 3 was informed by NRC Region IV that there was a government report concerning a Waterford 3 radioactive waste shipment. A follow-up review determined that the receiver of the shipment (Energy Solutions) had notified the National Response Center of a condition stating that a shipment received at their facility in Tennessee on June 21, 2012 was spilling water. The notification was identified as Incident Report number 1015375. The container held UN 2910, Limited Quantity, low specific activity, ion exchange resin and did not exceed any reportable quantities. Waterford 3 is sending shipping personnel to Energy Solutions to validate the state of the shipment." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-06-22
48044 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-22 13:30 | 2012-06-22 17:05 | 2012-06-23 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE ACTIVITY "Planned maintenance activities are being performed today (June 22, 2012) on the Hatch Nuclear Plant's Technical Support Center's (TSC) 480V AC distribution panel (1R25-S102). This work activity is planned to be performed and completed expeditiously within about 4 hours. This maintenance activity is to provide temporary power to the 480V AC distribution panel (1R25-S102). The temporary power is needed to support implementation of DCP 1060789901 which replaces two existing Allis Chalmers LA-600 circuit breakers installed in Motor Control Center 1B (1R24-S026) the normal power for the TSC 480V AC distribution panel. The installation of the temporary power will eliminate the need to have the TSC out of service for an extended period of time. During the time in which the normal power supply is isolated until the temporary power is restored the TSC ventilation system will be out of service which will rendered the TSC non-functional under TRM T 3.10.1. "If an emergency condition occurs that requires activation of the Technical Support Center during this work activity, it will take about one hour to return the equipment back to functional status dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the TSC for any declared emergency during the time the work activity is being performed as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10 CFR 50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0245 EDT ON 06/23/12 FROM STEVE BURTON TO S. SANDIN * * * The TSC was returned to service at 0215 EDT on 6/23/12. The licensee will inform the NRC Resident Inspector. Notified R2DO(Blamey). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-22
48043 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-06-21 15:05 | 2012-06-21 15:54 | 2012-06-21 | UNUSUAL EVENT DECLARED DUE TO A LAGGING FIRE IN A FEED PUMP "On Thursday, June 21st, at 1451 hrs, a fire was detected by visual observation at one of the running reactor feedwater pumps. Reactor power was lowered to 62% and the feedwater pump was removed from service. At 1505 hrs, the Shift Manager declared an Unusual Event. The fire was extinguished at 1508 hrs. The cause of fire is unknown. The Unusual Event classification is being reported in accordance with 10 CFR 50.72(a)(1)(i)." The fire appeared to have started from oil soaked lagging. Offsite assistance was not required, and Unit 1 was not affected. The licensee notified the NRC Resident Inspector, the State, and local agencies. Notified DHS, FEMA, and NICC. * * * UPDATE AT 1617 EDT ON 6/21/2012 FROM JASON SAWYER TO DONG PARK* * * The Unusual Event was terminated at 1600 EDT. The licensee notified the NRC Resident Inspector. Notified R1DO (Holody), NRR (Lee), IRD (Gott), DHS, FEMA, and NICC. | 0 | 62 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-06-21
48042 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC. |  |  |  |  | 2012-06-14 | 2012-06-21 15:03 | 2012-06-21 | PART 21 - RELIABILITY DEGRADATION OF RESISTORS IN TRIP UNITS AND READOUT ASSEMBLIES "Certain 710DU Trip Units may not perform their intended safety function as a result of certain wire wound precision resistors experiencing a degradation of reliability. Additionally, certain 710DU Readout Assemblies used to calibrate 710DU Trip Units may experience degraded digital display accuracy during calibration due to a similar cause. Rosemount Nuclear Instruments, Inc. does not have complete information relating to specific plant applications and therefore cannot determine the potential effects of the condition on plant operation. "This notification affects certain Model 710DU Trip Units and certain 710DU Readout Assemblies shipped from Rosemount Nuclear Instruments, Inc. between March 16, 2005 and May 10, 2012." The shipments were distributed to Ginna, Nine Mile Point, Fermi, Columbia Generating Station, Fitzpatrick, River Bend Station, Grand Gulf, Quad Cities, Peach Bottom, LaSalle, Limerick, Dresden, Perry, Hope Creek, Hatch, Brunswick, Browns Ferry, and Monticello. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-06-21
48041 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-21 08:00 | 2012-06-21 08:03 | 2012-06-21 | PLANNED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER VENTILATION "This ENS is being issued in advance of a planned maintenance activity. "Today 6/21/12, the Technical Support Center (TSC) ventilation system will be removed from service to perform corrective maintenance on a ventilation damper. The emergency ventilation system will not be available and cannot be restored within the time period required to staff and activate the Emergency Response Organization (ERO). The work will complete today 6/21/12. "If an emergency is declared and the TSC activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological or other conditions. The Station Emergency Director would assess habitability in accordance with station procedures. TSC relocation of personnel would be directed as required until such time that the TSC ventilation system is returned to service." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2124 EDT ON 6/21/12 FROM MARK ARNOSKY TO DONG PARK * * * "The work planned for the TSC ventilation system was not performed and will be rescheduled to a later date TBD. The NRC Resident Inspector has been notified." Notified the R1DO (Holody). | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-21
48040 | -1 | ACUREN INSPECTIONS |  |  |  |  | 2012-05-20 | 2012-06-20 18:15 | 2012-06-21 | POSSIBLE PERSONNEL OVEREXPOSURE GREATER THAN 25 REM The RSO from the licensee's corporate headquarters called to report a possible overexposure of a radiographer working on the North Slope of Alaska. Landauer reported that for the month of May, an individual's badge read 144 Rem. * * * UPDATE FROM GAYLE STATON TO JOHN KNOKE AT 1530 EDT ON 06/21/12 * * * The following information was received from the licensee via email: "On June 20, 2012, Acuren USA reported a possible radiation overexposure of 145R to an individual working for our [Acuren USA] company under NRC License # 42-32443-01. After interviewing all individuals involved, and conducting an internal investigation, we [licensee] believe that this dose was not received by the individual. In addition, the crew did not work with a gamma source but rather with x-ray tubes the entire month. The individual in question worked reading the scanner inside of a vehicle rather than outside utilizing the x-ray tube. He was never around the radiation producing equipment while it was energized. It is apparent that this dose was not received by this person. Therefore Acuren USA respectfully requests the NRC rescind Event Notification 48040. We apologize for the inconvenience and appreciate all your help with this matter." Notified the R4DO (Geoffrey Miller) and FSME (Brian McDermott) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2012-06-20
48039 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-06-20 08:57 | 2012-06-20 17:24 | 2012-06-20 | FITNESS FOR DUTY EVENT A non-licensed contract employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-06-20
48038 | -1 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-06-19 17:00 | 2012-06-20 15:30 | 2012-07-11 | DEGRADATION OF SAFETY EQUIPMENT "It was discovered at approximately 1700 EDT on 6/19/2012 that the moderation control in the gadolinia pellet press operation had been degraded. An operator error allowed a can containing approximately 14 kg of uranium powder to be processed without the required material move transaction, a process control that ensures the container and material type are allowed at the designated location. "This resulted in a temporary degraded item relied on for safety (IROFS) condition involving a criticality control. The press moderation control is one of four IROFS to prevent a criticality accident. The gadolinia press station material control system functioned as designed and prompted the operator of an error. The other criticality controls on geometry were maintained at all times. "At no time was an unsafe condition present. The gadolinia pellet press operation has been shut down and additional corrective actions, extent of condition, and extent of cause are being evaluated. "This event is being conservatively reported pursuant to 10 CFR 70, Appendix A (b) (2)." * * * RETRACTION FROM SCOTT MURRAY TO HOWIE CROUCH AT 1359 EDT ON 7/11/12 * * * "On 6/20/12, GNF-A conservatively made a 24 hour event notification (EN 48038) due to a single missed Fuel Business System (FBS) transaction on 6/19/12 at the gadolinia press operation. After further review of the identified condition, it has been determined to be not reportable to NRC and the event notification can be retracted." Notified R2DO (Blamey) and NMSS EO (Silva). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2012-06-20
48037 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-06-19 | 2012-06-19 21:23 | 2012-06-20 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA SOURCE "On June 19, 2012, at 1935 hours the Agency [Texas Department of Health] was notified by the licensee that one of their radiography crews reported that they had lost a QSA Global model 880D camera containing 13.4 curies of iridium 192. The radiography crew stated that they were returning to their office and had traveled about 3.5 miles when an individual in a vehicle motioned for them to pull over. The individual told them that the door to the dark room [located in the back of the truck] was open. The radiographer went to the back of the truck to close the door and discovered the radiography camera and transportation container were both missing. "The radiographers went back to the work location and searched for the camera. They asked other workers at the location if they had seen the device. They did not locate the device. The radiographers stated that they walked the road from the work location to where they had discovered the camera missing, but did not find it. "The radiographer stated that the source was locked in the fully shielded position and the result of the final survey of the camera was normal. The licensee's Radiation Safety Officer stated that they had notified the local law enforcement and were to meet with them later this night. They are considering offering a reward for the return of the camera. Additional information will be provided in accordance with SA 300." Notified: DHS, FEMA, USDA, HHS, DOE, DHS NICC, and EPA EOC. Texas Incident # I-8960 * * * UPDATE AT 0120 EDT ON 6/20/2012 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The radiography camera was recovered. A motorist passing shortly after the camera was lost picked up the gauge and called the phone number on the container. The RSO reported that the container was still locked in its transport box and the radiation readings on the container matched the readings prior to the loss. Notified the IRD (Gott), ILTAB (Hahn), R4IAT (Howell), R4DO (Miller), FSME Resources Group, DHS, FEMA, USDA, HHS, DOE, DHS NICC, and EPA EOC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 1 | 2012-06-27
48036 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-06-19 17:20 | 2012-06-19 19:48 | 2012-06-19 | MODE CHANGE REQUIRED BY TECHNICAL SPECIFICATIONS "On June 19, 2012, Unit 1 was shut down due to increasing drywell unidentified leakage. At 1720 EDT on June 19, 2012, the leakage location was discovered to be a welded joint on the 'A' reactor recirculation piping where a 4 inch blank-flanged pipe for chemical decontamination connects to the 28 inch pipe. This constitutes pressure boundary leakage. The location is within the recirculation loop isolation valves on the suction side of the recirculation pump, therefore isolable from the reactor vessel. The reactor was in mode 3 at the time of discovery and LCO 3.4.4 requires entry into mode 4 within 36 hours. "As such, the change in modes is required by Technical Specifications, therefore reportable within 4 hours under 10CFR50.72(b)(2)(i). In addition, the pressure boundary leakage at a welded joint is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)A) and is therefore 8 hour reportable as well." The licensee notified the NRC Resident Inspector. A press release is planned by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2012-06-19
48035 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-01-18 12:00 | 2012-06-19 15:19 | 2012-06-19 | HISTORICAL DISCOVERY OF LEAKING SOURCES The following information was obtained from the Commonwealth of Massachusetts via email: "The licensee is a manufacturer of beta gauges used to measure the thickness and weight of materials. This event was discovered when a hired decommissioning consultant found evidence of contamination in the source storage room of the facility. Their intention was to decontaminate the storage room and release it as part of an office relocation project within the same building. "The leaking sources in this event were apparently caused by the licensee by the improper application of PVC tape to the source window upon packaging. The licensee claims that this is not a current practice, but is the likely cause of source leakage prior to November of 2009. One or more historical sources could have been involved. The licensee claims that they were sent to Thermo Fisher Scientific in Germany in 2009. The sealed sources installed in the licensee's devices contain Strontium-90, Krypton-85, and Americium-241 (1.85E-10 TBq each). "Wipe tests were conducted on all available sources on January 19, 2012 by the licensee. None were found to be leaking. "The Massachusetts Radiation Control Program has initiated an investigation of this incident and will subsequently provide a report of the findings." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-06-24
48034 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-06-15 14:15 | 2012-06-18 18:20 | 2012-06-19 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "On Friday, June 15, 2012, at approximately 3:15 p.m. MDT (Mountain Daylight Time), a portable gauge licensee (Kumar and Associates, Inc.; Colorado License No. 778-01, Amendment 14) based in Denver, Colorado notified the Colorado Department of Public Health and Environment (CDPHE) Radioactive Materials Unit on-call duty officer that a gauge being used on a construction site had been damaged by heavy equipment earlier in the day (~2:15 p.m. MDT). The licensee reported that heavy equipment backed up and rolled over the gauge and the gauge technician was unable to retrieve or move the gauge in time. According to the licensee, and based on visual observation, the source capsule area at the end of the rod appeared intact and not significantly damaged as a result of the incident. Neither the source nor source rod were separated from the body of the gauge. The source rod, however, could not be retracted back into the shielded position and was transported back to the licensee facility in that manner. "The gauge involved was a Troxler model 3440 (gauge serial number 32754), currently containing approximately 6.2 mCi (decayed from 3/1/2001 assay date) of Cs-137 (serial #750-8100) and 40 mCi (5/28/99 assay date) of Am-247:Be (serial #47-28951). "At the time of the notification by the licensee to CDPHE at approximately 3:15 pm MDT, the gauge had already been returned to the licensee's facility. CDPHE requested that a leak test be performed on the gauge sources before any further actions are taken and that the licensee consult with a licensed repair facility or manufacturer for proper shipment of the damaged gauge. "Additional information and an incident report from the licensee is pending." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-06-26
48033 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-06-15 02:30 | 2012-06-18 13:58 | 2012-06-18 | AGREEMENT STATE REPORT - BURST VIAL OF Tc99m IN NUCLEAR PHARMACY The following information was received via email: "On Friday, June 15, 2012, at approximately 0230 Mountain Daylight Time (MDT), a nuclear pharmacy licensee located in Grand Junction, Colorado, had a vial containing approximately 1.9 Ci of liquid Tc99m burst and likely volatilize following placement on a heating block as part of compounding activities for preparation of cardiac imaging (Sestamibi) radiopharmaceuticals. The pharmacist, who also serves as the Radiation Safety Officer (RSO), notified the Colorado Department of Public Health and Environment (CDPHE) Radioactive Materials Unit on-call duty officer several hours later at approximately 1000 MDT on Friday, June 15. "Following the initial notification to CDPHE, a secondary phone interview of the pharmacist was conducted. It was determined that the burst container resulted in contamination of the pharmacist, compounding area (generator room), and areas within the main pharmacy. The pharmacist was the only person in the facility at the time of the incident. Other staff - primarily courier personnel - arrived after the incident, and provided some assistance but reportedly did not enter the pharmacy lab area. As a result of the ruptured vial, radiation survey instruments in the laboratory became contaminated, which required the licensee to borrow instrumentation from a local hospital licensee. Sometime following the incident, the pharmacist initiated limited decontamination activities of himself (glove and lab coat removal/exchange) and the area. The pharmacist reportedly continued with the preparation of some radiopharmaceutical materials following the incident. Additionally, following gross decontamination activities at the pharmacy, the pharmacist left the licensee facility to shower and change clothing at his residence. "During phone interviews with the licensee, CDPHE requested that the pharmacist obtain a urine sample, prepare for the return and processing of personal dosimeter badges and arrange for a back-up pharmacist. The pharmacist was directed to not conduct work involving radioactive material, pending further evaluation of internal and external dose. "In response to the incident, CDPHE dispatched the on-call duty officer from the Denver office to the Grand Junction area on Friday afternoon. (NOTE - Grand Junction, Colorado is approximately 5.5 hours drive time from the Denver CDPHE office). CDPHE staff met with the licensee pharmacist/RSO on the morning of Saturday, June 16, 2012 to evaluate the situation and perform surveys of potentially impacted areas and personnel. A whole body scan of the pharmacist was conducted at a local hospital nuclear medicine department in the later morning of Saturday, June 16. Personnel surveys of the pharmacist and the scan did not indicate the presence of radioactive material. Further details and information are being gathered. "No members of the public were believed to have been exposed above public dose limits as a result of the incident, and radioactive materials are believed to be contained within the lab area, with the exception of minor contamination discovered near the back door to the pharmacy. "The Department continues to investigate the incident and is gathering additional information." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-06-26
48032 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-17 13:30 | 2012-06-17 13:13 | 2012-06-17 | PLANNED OUTAGE OF ERFIS, SPDS, ERDS, AND PPC "On June 17, 2012, at approximately 1400 hours EDT, the Brunswick Nuclear Plant will be restoring the normal power supply configuration to the Emergency Response Facility Information System (ERFIS) uninterruptable power supply electrical bus 'A.' This will result in a temporary loss of the site ERFIS, Safety Parameter Display System (SPDS), Emergency Response Data System (ERDS), and Plant Process Computer (PPC) functions for both Unit 1 and Unit 2. Brunswick Units 1 and 2 had established an alternate power supply to the ERFIS UPS electrical bus 'A' on June 13, 2012 (i.e., EN 48019). "During the loss of these functions, manual data transfer will be available to the NRC. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), for a loss of emergency preparedness capability. A follow-up notification will be made when the ERFIS, SPDS, ERDS, and PPC functions are restored. "The NRC Resident Inspector has been notified of these actions." * * * UPDATE FROM STUART BYRD TO PETE SNYDER AT 1757 EDT ON 6/17/12 * * * Units 1 and 2 ERFIS, SPDS and ERDS have been returned to service. The PPC is expected to be returned to service at approximately 1900 EDT. The licensee will notify the NRC Resident Inspector. Notified R2DO (Ayers). | 63 | 98 | 0 | 63 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-17
48031 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-06-14 09:00 | 2012-06-15 17:37 | 2012-06-15 | AGREEMENT STATE REPORT INVOLVING FIVE DAMAGED NUCLEAR GAUGE HOUSINGS The following information was provided by the State of Texas via email: "On June 15, 2012, the Agency [Texas Dept. of Health] was notified by a licensee that the shutters on five Berthold Technologies Model LB300ML nuclear gauges were stuck in the open position. Open is the normal operating position for the shutters. The sources were manufactured in December of 2011 and each contained an original activity of 4.0 millicuries of cobalt - 60. The licensee was not able to provide serial numbers for the gauges or sources. The gauges are used in a steel mold and protected inside of the mold housing. An electrical power failure at the facility caused molten steel to pour on the gauge protective housing and leak into the area around the gauges. The licensee contacted a service provider who inspected the gauges on June 15, 2012. The service provider stated that the shutters would not operate, but the sources did not appear to be affected. The licensee stated that there was no increased risk of exposure to their workers due to the failed shutters. The licensee stated that the sources would be leak tested on June 15, 2012. The licensee intends to replace the gauge housing and reuse the sources from the gauges. Additional information will be provided as it is received in accordance with SA 300." Texas Incident No.: I-8960 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-06-17
48030 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-04-22 19:58 | 2012-06-15 16:00 | 2012-06-15 | KEOWEE HYDRO POWER STATION AUTOMATICALLY STARTED BASED ON AN INVALID SIGNAL "At 1958 [EDT] on 4/22/2012, Oconee emergency power (Keowee Hydro Station Units 1 and 2) automatically started based upon an invalid signal. In progress at the time was the Unit 3 Keowee Emergency Start Channel B Isolations section of the Unit 3 Engineered Safety Features Actuation System Replacement Modification procedure. A step in this procedure provided direction for a jumper to be connected between links B-13 and B-14. However, this jumper was placed between links A-13 and A-14, which caused the start of the Keowee units. During the period the jumpers were inadvertently installed, the Keowee units remained operable and available to supply emergency power to Units 1, 2, and/or 3. Both Keowee units were shutdown from the inadvertent emergency start actuation and the emergency start signal was reset per procedure at 0156 [EDT] hours on 4/23/2012. "The cause for the misplaced jumper was determined to be a human performance error by the technicians. "As required per NUREG 1022, Rev.2 the following information is provided: "(a) The specific train(s) and system(s) that were actuated: In this event, both Keowee Hydro Units 1 and 2 actuated because of the emergency start signal being generated by Channel A. "(b) Whether each train actuation was complete or partial: The automatic actuation of the Keowee units was completed. "(c) Whether or not the system started and functioned successfully: No problems or issues were identified with the performance of the Keowee Hydro Units in response to the emergency start. "Therefore this condition is being reported for Oconee 1, 2, and 3 as an invalid actuation under 10 CFR 50.73 (a)(2)(iv)(A), which allows NRC notification via telephone per 10 CFR 50.73(a)(1). "Corrective Actions: "- Work was stopped on the Unit 3 Engineered Safety Features Actuation System Replacement Modification procedure; "- Immediate investigation was conducted to determine the impact of the jumper activity as well as development of a recovery plan; and "- The jumper was removed from links A-13 and A-14 and the Keowee units were shutdown." The NRC Resident Inspector was informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-06-15
48029 | 0 | HOOSIER ENERGY |  |  |  |  | 2012-06-15 | 2012-06-15 15:19 | 2012-06-15 | FIXED NUCLEAR GAUGE FELL FROM MOUNTING BRACKET DUE TO RUSTED THROUGH MOUNTING BOLTS On the morning of 6/15/12, a fixed level monitoring gauge at the licensee's Merom Generating Station (coal fired facility), fell from its mounting bracket into a cable tray. The gauge, a Kay-Ray Model 7062P, S/N 9242Q, containing an estimated 50 mCi Cs-137 source (original activity - 100 mCi approx. 30 years ago) was not in service at the time, i.e., its shutter was closed, did not result in any personnel exposures. The licensee intends to have the instrument reinstalled using an outside contractor licensed to perform the work. The licensee contacted R3DO (Dickson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-06-17
48028 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-06-15 | 2012-06-15 11:44 | 2012-06-15 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The Commonwealth of Virginia submitted the following report via facsimile: "On June 14, 2012 the licensee reported that the shutter of one of its fixed gauges could not be closed as designed. The gauge is a Ronan Model SA-1 used on a process vessel as a level indicator. It contains a 438 millicurie (decay corrected) cesium-137 source. The problem was discovered during a routine test of the shutter mechanism. The individual who performed the test indicated that forcing the shutter closed, if possible, could damage the control mechanism. The gauge is normally in the open position during operations and the licensee has take extra steps to ensure no entry into the vessel. Ronan Engineering Company, the gauge manufacturer, has been contacted by the licensee and has scheduled a site visit during the week of June 18, 2012." VA Event Report ID: VA-12-002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-06-17
48027 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-06-15 08:08 | 2012-06-15 09:52 | 2012-06-25 | SAFEGUARDS REPORT - FAILURE IN A SAFEGUARD SYSTEM THAT COULD HAVE ALLOWED UNDETECTED ACCESS Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM GENE DAMMANN TO DONG PARK AT 1847 EDT ON 6/25/12 * * * During an Extent of Condition review, additional vulnerabilities were discovered. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R3DO (Valos) and Part 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-06-15
48026 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-06-14 13:53 | 2012-06-14 18:48 | 2012-06-14 | CONTROL ROOM ANNUNCIATOR OUTAGE "During a maintenance task to replace a main control board annunciator power supply an electrical short occurred while installing a jumper. This caused two circuit breakers to trip and a loss of all control room annunciators. The cause of the short was identified and corrected. The two circuit breakers were closed and the annunciator function was restored at 1358 CDT resulting in a total out of service time of 5 minutes. The unit was at a stable 100% power during the loss of annunciators." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-14
48025 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-22 | 2012-06-14 13:04 | 2012-06-14 | AGREEMENT STATE REPORT - CAMERA SOURCE FAILS TO RETRACT The agreement State of California reported the following via email: "On 06/13/12, the RSO at Team Industrial contacted RHB to report a radiography camera incident that occurred on 05/22/12 at the Evergreen refinery in Newalk, CA. The radiographers were using a QSA 880 camera on the second deck of the unit 1 at this refinery. The radiographer cranked the 59 Ci source out into the collimator and after the exposure, he couldn't retrieve the source back into the shielded position. He immediately contacted the RSO. Per RSO's instructions, the radiographer unscrewed the crank assembly and pulled the cable back to retrieve the source into shielded position. There were no exposures to the radiographers, two assistants, and any member of the public. The licensee's Instadose dosimetry indicated 8 mR for the radiographer for the period of 5/18 - 5/22 and 7 mR and 0 mR for the two assistants for the same period. Their pocket dosimeters indicated zero exposure for all three individuals. "The crank assembly was sent to QSA and they have indicted that the worn out teeth and bearings of the crank assembly inhibited the normal retrieval of the source. "RSO will be providing a detailed report to RHB ASAP." CA 5010 Number: 061312 Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-06-22
48024 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-06-14 06:07 | 2012-06-14 09:53 | 2012-06-14 | TECHNICAL SUPPORT CENTER OUT OF SERVICE AND OFFSITE NOTIFICATION DUE TO LOSS OF POWER TO SITE EMERGENCY BUILDING "At 0607 hrs. EDT, a vehicle struck a pole on Route 9, immediately in front of the site, causing a loss of power to the Technical Support Center (TSC). At 0615 hrs., the Fire Brigade was dispatched to investigate reports of a 'smoldering' transformer behind the Site Emergency Building (SEB) and Oyster Creek Administration Building (OCAB.) At approximately 0708 hrs., the on-scene Fire Brigade Leader called the local fire department, because, in his determination, it was an event or situation that was related to the health and safety of the onsite personnel. At 0717 hrs., the local fire department came on-site in response to the call. Upon investigation, it was found that the transformer was smoking due to overheating. There was no fire and no Emergency Action Level (EAL) was applicable for this event. Due to the notification and response of the local fire department, a 4-hour report is required per 10CFR50.72(b)(2)(xi). "At 0731 hrs., power was restored to the TSC and the TSC was restored to a fully operable condition. Due to the loss of the power to the TSC for greater than one hour (time required for TSC staffing), an 8-hour report is required in accordance with 10CFR50.72(b)(3)(xiii). "The NRC Senior Resident was on-site and notified of the event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-06-14
48023 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-06-13 17:45 | 2012-06-14 00:18 | 2012-06-14 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On 6/13/12 at 1700 CDT, it was determined that valve 2-FCV-73-81 (HPCI steam line warm-up valve) was not capable of performing its intended primary containment isolation valve function. This determination was made during performance of a prompt determination of operability for a steam leak from a missing adapter on a Furmanite injection port in the valve packing area. To meet Technical Specification (TS) 3.6.1.3 action requirements for an inoperable primary containment isolation valve, 2-FCV-73-2 (HPCI inboard steam isolation valve) was closed at 1745 hrs., rendering U2 HPCI inoperable. As a result TS 3.5.1 actions were entered. "This incident is reportable as an 8-hour ENS notification under 10CFR 50.72 (b)(3)(v)(B) and (D) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat and mitigate the consequences of an accident.' "It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(v)(B) and (D). "The NRC Resident Inspector has been notified. "This event has been entered into the Licensee's Corrective Action Program as SR 565729." Technical Specification 3.6.1.3 had a 4-hour shutdown action statement which was satisfied when the HPCI inboard steam isolation valve was closed. Technical Specification 3.5.1 action statement is a 14-day shutdown LCO. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-06-14
48022 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-06-12 15:45 | 2012-06-13 16:27 | 2012-07-16 | SAFETY EQUIPMENT FAILURE - CRITICALITY AIR HORNS NOT TESTED FOR AUDIBILITY "While reviewing Maintenance Work Package 'Performance of the C-335 Annual CMS Surveillance' from April 28, 2012 an error was identified. Procedure 'C-335 CMS Maintenance And Testing' requires an audibility check if the as-found values for the regulator air pressure drift feeding the Criticality Accident Alarm System (CMS) air horns is >?12 psig. However, an audibility check was not performed as required at six locations all on the cell floor of the process building that were discovered to be out-of-tolerance. All air pressure regulators were adjusted to within acceptable-as-left tolerances prior to the system being made operable on April 28. "Without the audibility testing being performed, the audibility of the C-335 CMS was questionable prior to the April testing. On June 13, 2012, a work package was developed to recreate the pressures encountered on April 28 and to test the audibility of the CMS. Subsequent testing has shown that three of the CMS horns fed by out-of-tolerance pressure regulators may not have provided the required sound levels necessary for audibility in those areas. This is failure of safety equipment required by TSR 2.4.4.2. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2), 'An event in which equipment is disabled or fails to function as designed when: (i) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; (ii) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand; and (iii) no redundant equipment is available and operable to perform the required safety function.' "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-12-1496; PGDP Event Report No. PAD-2012-03; Responsible Division: Operations" * * * RETRACTION FROM BILLY WALLACE TO JOHN SHOEMAKER AT 1641 EDT ON 07/16/2012 * * * "Subsequently, the C-335 CAAS air horns have been tested in the as-found conditions from April 28, 2012. Using the original design audibility criteria in the most limiting condition, the CAAS horn audibility was found to be acceptable. Therefore, the system would have been able to perform its intended safety function in the April 28, 2012, as-found condition. Based on the testing and an engineering evaluation, the event notification is being retracted." The licensee has notified the NRC Resident Inspector. Notified R2DO (Calle) and NMSS (Silva). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2012-06-13
48021 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2012-06-13 13:43 | 2012-06-13 14:22 | 2012-06-13 | UNUSUAL EVENT AFTER AN AMMONIUM HYDROXIDE SPILL IN THE ADMIN BUILDING "Seabrook declared an Unusual Event [HU3 - hazard or other conditions affecting plant safety] due to a spill of one gallon of ammonium hydroxide in the stockroom area of the Administration Building. No reports of injured individuals [were received] at this time. No plant or equipment damage occurred. The lower level of the Administration Building is evacuated. Personnel in SCBAs [Self Contained Breathing Apparatus] are mitigating the spill." The Administration Building is in the Protected Area adjacent to the Turbine Building. The licensee notified the NRC Resident Inspector and the State. Notified DHS, FEMA, NICC, DOE, USDA, and HHS. * * * UPDATE AT 1747 ON 6/13/2012 FROM ED LYONS TO MARK ABRAMOVITZ * * * "At 1343 [EDT] on 6/13/12 an Unusual Event was declared due to a reported Ammonium Hydroxide spill in a storeroom on the first floor of the Administration Building. At 1357 [EDT] the State of NH was notified and at 1401 the State of Massachusetts was notified of the Unusual Event using the State Notification Fact Sheet. The delay to the State of Massachusetts notification was due to issues with the dedicated phone system. "At 1422 the NRC was notified of the Unusual Event using the Event Notification Worksheet. This initial notification reported a one gallon spill of Ammonium Hydroxide. Additionally there were no reported injuries and no impact to plant equipment. "Further investigation revealed that the spill amount is 1-2 pints out of a 1 gallon container and the initial report of no injuries was validated. The concentration of the Ammonium Hydroxide is 25.5%. The spill was confined to a small area of the store room on the first floor of the Administration Building. The spill had no impact on plant equipment used for normal operation. Initial cleanup by plant personnel is complete and external services have been notified to complete the final spill cleanup. "Seabrook Station is terminating the Unusual Event. Seabrook Station will continue to investigate and resolve the issues with the dedicated state notification phone system. Currently we have a troubleshooting team which has verified backup communications via the commercial phone lines is available." The Unusual Event was terminated at 1730 EDT. The licensee notified the NRC Resident Inspector and State. Notified R1DO (Gray), NRR ((Howe), IRD (Grant), DHS, FEMA, NICC, DOE, USDA, and HHS. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-06-13
48020 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-13 | 2012-06-13 12:44 | 2012-06-13 | SAFETY PARAMETERS DISPLAY SYSTEM OUT OF SERVICE "At 1032 [EDT], on June 12, 2012, the Unit 2 Safety Parameter Display System (SPDS) system ceased valid data transmission to the control room computer terminals. Remote terminals were unaffected. The loss was discovered on the morning of 6/13/12 and the connection was restored at 0945 [EDT] on 6/13/12. This was a duration of greater than 8 hours which was not discovered until after the fact. This condition affected unit 2 only. ERDS was unaffected. "Since the Unit 2 SPDS computer system was unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-13
48019 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-12 17:57 | 2012-06-13 01:38 | 2012-06-14 | LOSS OF THE PLANT PROCESS COMPUTER SYSTEM "At 1757 EDT on 6/12/12, Brunswick Nuclear Plant experienced a fault on the Emergency Response Facility Information System (ERFIS) uninterruptible power supply (UPS) electrical bus 'A'. This resulted in a loss of site Safety Parameter Display System (SPDS), Emergency Response Data System (ERDS) and Plant Process Computer (PPC) for both Unit 1 and Unit 2. The cause of the fault is not yet understood and under investigation. No other major plant effects occurred and no major plant evolutions are planned. "During the loss of SPDS, the emergency response capability of that system was lost to the site. During the loss of ERDS, the automatic data transfer feature of that system was lost for transmissions to the NRC, however manual data transfer is still available. During the loss of the PPC, automatic core thermal power averaging and automatic core thermal limit monitoring was lost. Manual calculations are available for these functions. "Unit 1 SPDS was restored to the Emergency Operations Facility (EOF) at 1949 EDT. Unit 2 SPDS was restored to the EOF at 2030 EDT. ERDS and PPC remain unavailable with troubleshooting in progress. Both units reduced power to 98% as a conservative measure. "The NRC Resident Inspector has been notified." * * * UPDATE FROM JOHN MILLER TO JOE O'HARA AT 0257 ON 6/14/12 * * * "The Unit 1 and 2 ERFIS, SPDS, and ERDS functions were restored by approximately 0630 hours on June 13, 2012, after an alternate power supply configuration was established. In addition, the PPC functions were restored by approximately 1630. Compensatory actions will be maintained until the UPS 'A' bus is restored and returned to normal configuration. The Brunswick Emergency Response Organization (ERO) Site Emergency Coordinator and Emergency Response Manager have been briefed on the compensatory actions in place. "Investigation of this condition will be documented in the corrective action program in Condition Report (CR) 542704. "The NRC Resident Inspector was notified." Notified R2DO(Ayres) | 98 | 98 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-13
48018 | 0 | PALISADES | 1 |  |  | [1] CE | 2012-06-12 14:56 | 2012-06-12 17:27 | 2012-08-07 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 1456 hours on June 12, 2012, the plant commenced a shutdown due to water leakage from the SIRW [Safety Injection Refueling Water] tank exceeding the operational decision-making issue process trigger point of 31 gallons per day causing it to be declared inoperable and requiring entry into Technical Specification (TS) 3.5.4, Condition B. TS 3.5.4 Condition B requires the SIRW Tank to be returned to operable status within one hour or entry into Condition C that requires the plant to be in Mode 3 within 6 hours and Mode 5 within 36 hours. "Actual leakage from the SIRW Tank was measured at approximately 31.4 gallons per day. This event had no impact on the health and/or safety of the public. "The NRC Senior Resident Inspector has been notified." The licensee believes that the tank is leaking from several locations. However, at this time, they cannot determine exact locations. The refueling water has minor tritium contamination. The refueling water is being collected in a reservoir and then pumped into a holding tank. The licensee will be shutting down to cold shutdown. * * * RETRACTION ON 8/7/12 AT 1219 EDT FROM TERRY DAVIS TO DONG PARK * * * "Subsequent review concluded the condition did not meet reporting criteria. The rate of water leakage from the Safety Injection Refueling Water Tank had reached an administrative limit. Shutdown was not required by the Technical Specifications. The plant shutdown commenced in accordance with normal plant operating procedures. At 1849 hours on June 12, 2012, the reactor was manually tripped. This event is not reportable as the reactor trip was part of a normal shutdown for corrective maintenance. Mode 5 was reached at 1745 hours on June 13, 2012. The NRC Resident Inspector has been notified." Notified R3DO (Lipa). | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-06-12
48017 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-06-05 | 2012-06-12 14:49 | 2012-06-12 | AGREEMENT STATE REPORT - LAB AREA CONTAMINATED The following report was received via fax: "On 06/06/12, the ARSO [Assistant Radiation Safety Officer] at UC Berkeley contacted the RHB [Radiological Health Branch] to report an event that occurred on 06/05/12. This event involved contamination caused by a Cs-137 source that is not a sealed source per manufacturer's statement. This source has a very thin window to permit transmission of betas. This source was used in a vacuum chamber and the contamination occurred and was detected when researchers were changing the flange. The licensee cordoned off a 6' x 10' area within a much larger lab. No floor contamination was detected, however, the bench and some equipment within the cordoned off area are still being cleaned. Access to this area was restricted for over 24 hours. The current activity of the source is 950 microCuries. Applying conservative assumptions to convert the detected contamination counts into activity, the licensee has come up with a total activity on the order of 10 microCuries (summed over the contaminated spots). "The licensee notified the RHB within 24 hours, since the area was cordoned off for more than 24 hours, however, the activity detected is minimal per 30295(b)(1)(B) where the involved quantity is less than 5 times the lowest ALI specified in Appendix B 10 CFR 20 incorporated by reference in section 30253. Also, since this is not a sealed source, the reporting criteria for leakage of more than 0.005 microCuries does not apply. Based on these criteria, no reporting is required." California incident: 060612 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-06-20
48016 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-06-12 11:21 | 2012-06-12 14:45 | 2012-06-12 | TECHNICAL SUPPORT CENTER TAKEN OUT OF SERVICE FOR MAINTENANCE "On June 12, 2012, at approximately 1121 hours [CDT], the Kewaunee Power Station Technical Support Center (TSC) ventilation system was removed from service to allow TSC electrical distribution system repairs. The removal of the ventilation system potentially affects the TSC habitability during a declared emergency requiring activation. The Emergency Response Organization [ERO] team has been notified of the maintenance and the possible need to relocate during an emergency. If an emergency is declared and TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location. "The ventilation system is expected to be out of service for approximately 2 hours. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that resulted in a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." TSC work was completed and the TSC was returned to service at 1326 CDT. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-12
48015 | 0 | CARIBBEAN MARINE CONTRACTORS, CORP |  |  |  |  | 2012-06-05 | 2012-06-12 08:33 | 2012-06-12 | PREVIOUSLY STOLEN SOURCE HOLDER LOCATED IN A SCRAP YARD The following information was received by facsimile: "On June 5, 2012, US NRC Region I communicated with [Caribbean Marine Contractors, Corp] to notify that Ronan Measurement RLL-1 SN #206762A registered on behalf of Caribbean Marine Contractors had been found in a scrap yard in Taiwan. Immediately, we started doing our investigations to verify whether the RLL-1 found in Taiwan was ours. We proceeded to look in our storage container for the RLL-1. Noticing the absence of RLL-1, we talked to company personnel who regularly entered the storage container and everyone questioned arrived at this conclusion. "Approximately two years ago, Caribbean Marine was doing work of dredging in the town of Guayama, PR. We stopped the work of dredging and we were doing preventive maintenance to the marine equipment (washing with fresh water, removing rust, paint, etc.). [A manager] who at that time was in charge of the project gave the order to take the RLL-1 that was not working out of the dredge and store it in the storage container of the project. Weeks later, thieves broke in the container and stole the metals that were inside. Usually metals lead them to recycling centers and sold by weight. These recycling centers in turn sold the material to Taiwan or India. That [is the] way we understand that you found the RLL-1 #206762A in Taiwan. "The Ronan ultra-low level series of source holders (RLL) use very small quantities of radioactive materials. The RLL-1 is permitted to contain to a maximum of 900 microCuries of cesium-137 or 200 microCuries cobalt-60. The radioactive material is completely encapsulated in a stainless steel capsule, which is then heli-arc or laser welded closed. Due to high structural integrity, these source capsules qualify as special material form; virtually eliminating the possibility of the spread of radioactive contaminant. The sealed capsules are loaded into the RLL-1 device. This is a stainless steel tube that is welded shut at both ends and installed inside a shielded, steel housing. The general licensee is not permitted to repair, modify, or otherwise tamper with the device or its shielding. The combination of high structural integrity and low source quantity permits the general licensee to install and commission the device without special training or certification. The general licensee is required to install and operate the gage in accordance with the instructions provided by Ronan Engineering. The RLL-1 device is not required to be wipe tested and there is no shutter or moving parts that have to be periodically inspected or maintained. Important Exception The RLL-1 device is required to be tested every three years if it contains a single wipe capsule in excess of 100 microCuries. If a leak test is required, to stainless steel tag will be permanently affixed to the device stating. 'Leak Test Required'. "Iso distance curves are provided in this manual for various applications as specified in the table below: Application Drawing Number Weight Gages C-16307-K and C-16310-K Continuous Level Gages B-16306-K and C-16309-K Density / Point Level Gages B-16305-K and B-16308-K "These curves indicate that the maximum dose rate, at one foot, from any device is less than 0.5 mR/h. Most of these devices require (as a conservative estimate) less than 1 hour of handling to install. Based upon these low dose rates and the short period of time required for handling/installation it is unlikely that any personnel would receive a significant exposure. In fact, it can be safely assumed that working personnel will receive considerably less than 10 percent (10%) of the dose limits specified in column IV of 10 CFR 32.24, for the appropriate organs, and less than ten percent of the dose limits specified in 10 CFR 20.1201(a)." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2012-06-20
48014 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-06-11 10:15 | 2012-06-11 16:08 | 2012-06-11 | FITNESS FOR DUTY A non-licensed contractor refused a random fitness for duty test. The individual's access to the site has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 60 | 0 | 100 | 60 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2012-06-11
48013 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-06-11 08:52 | 2012-06-11 14:41 | 2012-06-11 | HIGH PRESSURE CORE SPRAY INOPERABLE "On June 11, 2012, at 0845 hours, an unexpected Division 3 battery DC system trouble alarm was received in the control room along with indication of lowering battery voltage. As a result of this condition, the plant operators declared the Division 3 DC electrical power subsystem inoperable at 0852 hours and entered the applicable Technical Specifications which require the High Pressure Core Spray System (HPCS) be declared inoperable. HPCS is a single-train safety system and its inoperable status is considered a loss of safety function. The cause of the trouble alarm was failure of the normal battery charger. Following a walkdown inspection of the Division 3 DC electrical bus with no abnormalities noted, the reserve charger was placed in service at 0858 hours to supply the bus. At 1245 hours, the HPCS system was declared operable following restoration of the Division 3 DC electrical power subsystem to operable status. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D). The NRC Resident Inspector has been notified." | 73 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-06-11
48012 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-06-11 05:45 | 2012-06-11 11:53 | 2012-06-11 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of North Carolina via email: "The [North Carolina] Branch Manager received a call June 11, 2012 from a radioactive materials licensee S. T. Wooten Corporation (license number 098-0792-1) based out of Wilson, NC. "An individual was on a worksite late. After completing his work, he stored the gauge, as well as other construction material, outside his residence at [redacted] in Sanford, NC. The licensee contact confirmed that the individual followed the 'two barrier' rule. "At 5:45 a.m. on June 11, 2012, the individual reported the gauge and the additional construction material missing to the local law enforcement and to the Radiation Protection Section. He last saw the gauge at 11:30 p.m. on June 10, 2012. "The truck was investigated by local law enforcement at the site and is on its way back to the headquarters office in Wilson, NC. [The North Carolina] regional inspector will meet the truck there for an onsite inspection. [The North Carolina] Increased Controls Coordinator has a good relationship with local law enforcement and has contacted them as well as informed emergency management. The proper notifications will be made to FBI, etc. "The gauge is a Troxler model 4060B, it can contain up to 9 millicuries of Cs-137 (a beta/gamma emitter)." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-06-19
48011 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-05-04 13:25 | 2012-06-11 10:03 | 2012-06-11 | REFUELING WATER STORAGE TANK CONNECTED TO NON-SEISMICALLY QUALIFIED SYSTEM "On May 4, 2011, at approximately 1325 Eastern Daylight Time (EDT), with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, it was determined that over the last 40 years, HBRSEP, Unit No. 2 periodically performed cleanup of the Refueling Water Storage Tank (RWST) by aligning the non-seismically qualified refueling water purification system to the safety related and seismically qualified RWST without recognizing that the action rendered the RWST inoperable. As a result, on multiple occasions, the RWST was inoperable for a period longer than allowed by Technical Specification (TS) Limiting Condition for Operation 3.5.4, Emergency Core Cooling Systems Refueling Water Storage Tank. 'The cause of this event was that regulatory requirements for the separation of seismically qualified and non-qualified systems, structures, and components were not adequately incorporated into the Design Basis Document (DBD) and Updated Final Safety Analysis Report (UFSAR). "A clearance order has been placed in effect to ensure restrictions for piping that could affect the operability of the RWST remain in place. "This event was described in Licensee Event Report 2011-001-00 and was initially reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. However, further reviews determined at 0800 on June 11, 2012, that the event is also reportable under 10 CFR 50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a safety function. "During the three year period prior to May 4, 2011, it is estimated that the purification loop was in service aligned to the RWST while on-line nine times, totaling 297 days." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-06-11
48010 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-06-11 03:35 | 2012-06-11 03:56 | 2012-06-18 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "On June 11, 2012, at approximately 0335 hours, the Hope Creek Technical Support Center (TSC) ventilation system was removed from service to perform planned maintenance to the system. The maintenance consists of a 12-year preventative maintenance overhaul of the ventilation supply fan and emergency filtration unit. The removal of ventilation potentially affects the TSC habitability during a declared emergency requiring activation. Appropriate compensatory measures are in place while ventilation is out of service. The Emergency Response Organization duty team has been notified of the maintenance and the possible need to activate the TSC in an alternate location. The ventilation system is scheduled to be out of service for approximately 60 hours." The licensee has notified the NRC Resident Inspector. The local township will be notified. * * * UPDATE FROM TOM FOWLER TO DONALD NORWOOD AT 1225 EDT ON 6/18/2012 * * * "The planned maintenance was completed and the TSC ventilation was returned to an operable status as of 0245 EDT on June 13, 2012. The TSC was not activated during the planned maintenance." The licensee notified the NRC Resident Inspector. Notified R1DO (DeFrancisco). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-11
48009 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-06-10 03:00 | 2012-06-10 10:00 | 2012-06-10 | HPCI DECLARED INOPERABLE DUE TO LEAKAGE "On Sunday June 10, 2012 at 0112 (Central Time), a through-wall leak was discovered on a piping elbow upstream of the High Pressure Coolant Injection (HPCI) Inlet Drain Pot Inboard Drain valve to the Main Condenser, AOV 3-2301-29. This piping elbow is safety-related, ASME Code Class 2 piping. Dresden Technical Requirements Manual 3.4.a, Condition B requires the leak to be isolated which renders the HPCI system inoperable. The Unit 3 HPCI system was isolated and declared inoperable at 0300 (Central Time), and Technical Specification 3.5.1 Condition G has been entered. The HPCI system is a single train system. "The event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-06-10
48008 | -1 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2012-05-10 12:00 | 2012-06-08 18:23 | 2012-06-26 | AGREEMENT STATE REPORT - SOURCE SHUTTER NOT FULLY CLOSING The following information was received by e-mail: "Licensee notified DRH [Mississippi Department of Radiological Health] about a Ronan X92 Continuous Level Gauge, Serial No. 9479GG with source Holder Model SA1-F37. Licensee suspects the source shutter may not be closing 100% due to elevated readings of 7 mR/hr with the shutter in the closed position." * * * RETRACTION FROM JASON MOAK TO PETE SNYDER ON 6/26/12 AT 1558 EDT * * * This report is retracted based on the fact that the gauge "did not fail to function as designed. No maintenance was performed on the gauge. The service representative did not find a problem with the gauge shutter or radiation fields." Notified R4DO (Clark), FSME (e-mail). Mississippi Incident Number: MS-12002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2012-06-18
48007 | 0 | SUMMER CONSTRUCTION | 2 | 3 |  |  | 2012-06-07 19:44 | 2012-06-08 13:43 | 2012-06-08 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM A non-licensed, contract employee supervisor had a confirmed positive for alcohol during a "for cause" fitness-for-duty test. The individual's site access was revoked, and he was removed from the site. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 0 | SC | POW |  | 26.719 |  |  |  | 0 | 2012-06-08
48006 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-04-11 15:15 | 2012-06-08 11:32 | 2012-06-08 | INVALID SYSTEM ACTUATION RESULTING FROM POST MAINTENANCE TESTING "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On April 11 , 2012, at 1515 hours Central Daylight Time (CDT), Operations personnel attempted to transfer the 3B 480V Reactor Motor Operated Valve (RMOV) Board to its alternate power supply for post maintenance testing on the alternate feeder breaker. The 3B 480V RMOV Board failed to transfer to the alternate power supply. Power to the 3B Reactor Protection System (RPS) Bus was lost resulting in a half-scram and actuation of Primary Containment Isolation System (PCIS) Group 6 with the initiation of all three trains (A, B, and C) of Standby Gas Treatment and the initiation of Train 'A' of the Control Room Emergency Ventilation System. "Plant Conditions, which initiate PCIS Group 6 actuations, are Low Reactor Vessel Water Level, High Drywell Pressure, High Reactor Building Vent Radiation, or High Refuel Zone Radiation. At the time of the event, these conditions did not exist; therefore, the partial actuations were invalid. "The affected equipment responded as designed. On April 11, 2012, at 1520 hours CDT, Operations personnel reset the half-scram from the loss of the 3B RPS Bus. "This condition is the result of a bad connection of the breaker to panel contacts due to alignment and/or infrequent manipulation. "There were no safety consequences or impact to the health and safety of the public as a result of these events. "This event was entered Into the Corrective Action Program as Problem Evaluation Report 535537. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-06-08
48005 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-09-17 12:00 | 2012-06-07 19:16 | 2012-06-07 | MAJOR LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO DEGRADED DOSE PROJECTION "On September 17, 2011, a root cause analysis identified that errors in the dose projection software gain factor associated with the high range stack monitor were introduced in 2000 and had the potential to produce inaccurate dose projection results. The resulting condition could have impacted the ability to accurately assess ongoing releases and determine appropriate protective measures for the public. The gain factors were corrected in October 2011 and dose projection capabilities have been restored. "This condition was not originally recognized as being reportable in accordance with 10 CFR 50.72(b)(3)(xiii) due to the limited nature of the impact to a small portion of the radiological effluent EALs, however, it has been recently determined to be reportable. This late identification of reportability has been entered into our corrective action program." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-07
48004 | 0 | FLOWSERVE |  |  |  |  | 2012-05-25 | 2012-06-07 14:19 | 2012-06-07 | PART 21 REPORT - PUBLISHED FLOW COEFFICIENTS FOR PILOT OPERATED RELIEF VALVES GREATER THAN ACTUAL "This is to notify the US Nuclear Regulatory Commission, in accordance with the provisions of 10CFR-Part 21 of a potential deviation identified by Flowserve Corporation. "On May 25, 2012, Flowserve Corporation notified Exelon - Byron and Braidwood Nuclear Power Stations of the results of a Steam flow test performed by Wyle Labs to confirm steam flow capacity against that specified for WKM PORVs. A refurbished size 6 class 900 WKM model 70-19-9 angle pattern control valve with 4" linear trim had been tested to determine its maximum steam flow capacity. The maximum steam flow was approximately 74% of the anticipated flow rate based on the original published WKM rated Cv for the valve. "Background and Discussion: As part of their power up rate project, Exelon Braidwood Station procured larger 4" linear valve trim from Flowserve, Raleigh for their steam generator PORVs to increase the valve's steam flow capacity. The original valves were supplied by ACF Industries, WKM Valve Division in the mid to late 1970's with 3" linear trim. The designs for the WKM PORV valves were subsequently acquired by Flowserve. The larger trim was installed in a site spare PORV and tested for steam flow capacity. "CFD analysis performed by Flowserve on the tested valve with the 4" trim, determined a Cv value that would yield steam flows similar to the test results. Analysis of the valve with the original 3" trim produced similarly reduced Cv values. "Based on this testing and subsequent CFD analysis it appears that the originally published WKM rated Cv values for WKM angle control valve model 70-19-9 for sizes greater than size 2 are higher than actual values. The actual Cv's are believed to be 65% to 75% of the original WKM ratings. "Conclusion: Based on the above, the Nuclear Industry needs to be notified concerning this deviation so that an evaluation may be performed to determine if this constitutes a defect that could create a substantial safety hazard. "Although Flowserve subsequently acquired the rights to the WKM PORV designs, it does not have the historic sales records from ACF industries (WKM Valve Division). The total number of WKM valves potentially affected and their installed locations are not known." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-06-07
48003 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-07 | 2012-06-07 14:18 | 2012-06-07 | AGREEMENT STATE REPORT - LOST TRITIUM SIGNS The following information was received by facsimile: "A biannual tritium sign inspection during the week of 5/7/2012 disclosed four tritium signs had been removed during a renovation of Mendocine Hall during the third week of January 2012 by the contractor. All attempts to locate the signs have been exhausted. "The missing signs are as follows: Serial # 263374 Model # BX1711OWHSGN 7.5 curies Serial # 263373 Model # BX1711OWHSGN 7.5 curies Serial # 263387 Model # BX1711OWHSGN 7.5 curies Serial # 263388 Model # BX1711OWHSGN 7.5 curies "Date of manufacture for all signs is 5/2/2004." California 5010 Number: 060712 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-06-15
48002 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-06-07 01:29 | 2012-06-07 11:56 | 2012-06-07 | BOTH TRAINS OF LOW TEMPERATURE OVERPRESSURE SYSTEM INOPERABLE "On June 7, 2012, at 0129 PDT, both trains of the low temperature overpressure (LTOP) system were rendered inoperable when the vital 120 VAC panel PY-13 was de-energized due to a human performance error. DCPP Unit 1 was in Mode 5, reactor coolant system loops not filled. Technicians were troubleshooting an existing de-energized vital 120 VAC panel PY-14 that had resulted from the supply breaker tripping open. The technician incorrectly opened the supply breaker to panel PY-13 instead of PY-14. With PY-14 de-energized, one train of LTOP was inoperable due to loss of signal from Reactor Coolant System (RCS) wide range pressure transmitter PT-405A. With PY-13 de-energized, the second train of LTOP was rendered inoperable due to loss of signal from RCS wide range pressure transmitter PT-403A. Operations immediately recognized the error and had the technician reclose the PY-13 supply breaker, thereby re-energizing panel PY-13, returning one train of LTOP back to its operable condition. "Plant personnel notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-06-07
48001 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-06-07 09:47 | 2012-06-07 09:47 | 2012-06-07 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM MAINTENANCE "This ENS is being issued in advance of a planned activity. Today, 6/7/12, the (TSC) Technical Support Center Emergency Ventilation system will be removed from service to support preventive maintenance activities. The emergency ventilation system will not be available and cannot be restored within the time period required to staff and activate the Emergency Response Organization (ERO). The work will complete today, 6/7/12. "If an emergency is declared and TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-07
48000 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2012-06-06 19:56 | 2012-06-07 02:39 | 2012-06-07 | DEGRADED CONDITION DUE TO DISCOVERY OF PRESSURE BOUNDARY LEAKAGE "On June 6, 2012, at 1956 EDT, with the Unit shutdown for refueling, leakage was identified from a 3/4-inch weld during Reactor Coolant System (RCS) walkdown inspections. The leakage amount was approximately 0.1 gpm pinhole spray. "During the performance of MODE 3 engineering walkdown inspections in accordance with procedure DB-PF-03010 (ASME Section III, Class 1 and 2), with the RCS at Normal Operating Temperature and Pressure, a pressure boundary leak was identified on the Reactor Coolant Pump (RCP) 1-2 1st seal cavity vent line upstream weld of 3/4 inch small bore pipe socketweld at a 90 degree elbow between the RCP pump and valve RC-407 (1st Seal Cavity Vent Isolation). The plant was in MODE 3 at Normal Operating Pressure and Normal Operating Temperature (NOP/NOT) for the inspections. "The plant entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.13, 'RCS Operational Leakage,' Condition B and procedure DB-OP-02522. 'Small RCS Leaks,' abnormal operating procedure. Plant cooldown to comply with LCO 3.4.13, Condition B, Required Action B.2 is in progress. The cause and resolution are under evaluation. "This event is reportable within 8 hours under 10CFR50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified. This condition has been documented in the Davis-Besse Corrective Action program as Condition Report 2012-09381." The plant is required to be in MODE 5 within 36 hours. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-06-07
47999 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-06-06 06:12 | 2012-06-06 09:38 | 2012-06-06 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP ON TURBINE MAIN GENERATOR TRIP "On June 6, 2012, at approximately 0612 hours, Indian Point Unit 2 reactor automatically tripped from 100% steady state power due to a turbine-main generator electrical trip. All rods fully inserted. Investigation into the generator trip is in progress. All systems responded as expected. The Auxiliary Feedwater system actuated and responded as expected and is maintaining steam generator levels. Decay heat removal is via the steam generators to the main condenser. Offsite power and plant electrical lineups are normal. No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. Unit 3 was unaffected and remains at 100% power." The NRC Resident Inspector has been notified, and the licensee issued a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-06-06
47998 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2012-06-06 03:27 | 2012-06-06 05:19 | 2012-06-06 | INADEQUATE COOLING AVAILABLE TO SUPPORT ELECTRICAL POWER SYSTEMS "Wolf Creek commenced a nuclear plant shutdown in accordance with Technical Specifications. Engineering analysis has determined that with one non-functional Class IE A/C unit, there is inadequate cooling available to support electrical power systems required by Technical Specifications (TS) 3.8.4, 3.8.7, 3.8.9, during all postulated conditions. Actions are currently underway to restore the non-functional Class IE A/C unit to a functional status." The non-functional Class IE A/C unit had a clogged oil pump strainer. Per TS 3.0.3, Wolf Creek began reducing power and was at 89% power at the time of the report. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM WARREN BRANDT TO DONG PARK AT 0700 EDT ON 06/06/12 * * * "The A Class IE A/C unit was restored to functional at 6/6/2012 0505 CDT. The plant shutdown was terminated at 87 percent power. Actions are underway to restore the unit to 100 percent power." Notified R4DO (Gepford). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-06-06
47997 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-06-06 00:45 | 2012-06-06 00:47 | 2012-06-06 | OFFSITE NOTIFICATION REGARDING LABOR NEGOTIATIONS "On June 6, 2012, at 0045 EDT hours and the reactor at 100% core thermal power the following press release being issued by Entergy Nuclear regarding the status of the ongoing labor negotiations. "Plymouth, Mass. - Entergy Nuclear, the company that owns and operates the Pilgrim Nuclear Power Station is implementing a contingency staffing plan after weeks of negotiations between the Company and the Utility Workers Union of America Local 369 leadership were unsuccessful in reaching an agreement for a new union contract. "Local 369 has stated flatly that while its members are not on strike, they reserve the right to walk off the job at any time, without any notice, and leave the nuclear power plant critically understaffed and in violation of the plant's operating license. This disregard for public safety is unacceptable. Accordingly, the company's contingency plan is being implemented. "The contingency plan for temporary alternate staffing is consistent with Nuclear Regulatory Commission regulations and is in the interest of safety and maintaining formal organizational controls on the plant site. Highly qualified individuals from within Pilgrim's management team as well as the Entergy nuclear fleet will be filling the necessary positions. "The NRC Resident Inspector staff has been informed of this press release and notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi)." The licensee will be notifying the Massachusetts Emergency Management Agency. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-06-06
47996 | 0 | INBERG-MILLER ENGINEERING |  |  |  |  | 2012-06-05 16:00 | 2012-06-05 18:24 | 2012-06-05 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The gauge operator finished with a density reading and left the Troxler device at the measurement area when he was storing his tools in his truck. When he was returning to the measurement area, an end-loader drove over the Troxler, destroying the hand operating pad. At the time of the accident, the source was retracted into the shield. Immediately after the accident, the operator covered the gauge with shielding and established a boundary zone. No overexposures or contaminations are expected as the sources were retracted into the shielded position. The Troxler is a model 3430 which contains 40 mCi of Am-241 and 8 mCi of Cs-137. The licensee is conferring with Troxler to determine whether the gauge will be repaired or returned for disposal. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-06-13
47995 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2012-06-05 05:02 | 2012-06-05 13:37 | 2012-06-05 | TECHNICAL SUPPORT CENTER FILTER TRAIN INOPERABLE "At approximately 5:02 a.m. CDT on June 5, 2012, during scheduled test of the Technical Support Center (TSC) ventilation system, it was determined that the system would not function in the emergency mode. The plant is currently in cold shutdown for a maintenance outage. "The activity was terminated and the TSC ventilation system was restored to its normal configuration. This failure caused the TSC to be potentially uninhabitable, and thus it could not have been relied upon for the purposes of the site Emergency Plan. Repairs and retest of the system were successfully completed at approximately 11:30 a.m. CDT. "This condition is being reported in accordance with 10CFR50.72(b)(3)(xiii) as an event that resulted in a major loss of emergency assessment capability. The NRC Resident Inspector has been notified." The suction damper to the filter train failed to open which led the licensee to declare the filter train inoperable. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-06-05
47994 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-06-05 | 2012-06-05 13:14 | 2012-06-05 | FLORIDA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following information was obtained from the state of Florida via email: "First quarter 2012 whole body dosimeter badge for a nuclear med tech indicated a 10.5 Rem dose. Badge was recounted and the dose remained the same. Dose is not confirmed by ancillary ring dosimeters. Ring dosimeters indicate a typical 100 mR/month. Because the ring dosimeters do not confirm the badge dose, the consulting health physicist does not think this is a valid dose and the med tech is still working. Florida is investigating." The isotope used by the medical technician is Tc-99, 30 mCi. Florida Incident Number: FL12-049 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-06-13
47993 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-06-04 | 2012-06-05 12:47 | 2012-06-05 | TENNESSEE AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED GAUGE The following information was obtained from the state of Tennessee via fax: "On June 4, 2012 Eastman Chemical Company contacted the [Tennessee] Division of Radiological Health concerning an incident that had just occurred. A shutter on a fixed level gauge was difficult to operate and could not be completely closed. In an attempt to close the shutter, a viscous polymer material which had leaked onto the top part of the gauge was removed. However, removal of the polymer still did not allow for complete closing of the shutter. Surveys have confirmed that radiation levels around the gauge are normal. The vessel manway is posted and procedures are in place to prevent entry into the vessel prior to the gauge being repaired or replaced." The level gauge contained 173 mCi of Cs-137. No personnel overexposures were reported. Tennessee Event: TN-12-148 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-06-13
47992 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-06-04 15:14 | 2012-06-04 21:59 | 2012-08-03 | REACTOR COOLANT SYSTEM IN A DEGRADED CONDITION DUE TO AN INSTRUMENT RACK SEISMIC DESIGN ISSUE "During a review of plant installed instrumentation racks inside containment, two instrument racks were identified that were over the analyzed weight for the seismic analysis. The instruments on these racks are used for reactor coolant pressure transmitters that are part of the Reactor Coolant System (RCS) pressure boundary, as they are connected via instrument lines to the RCS with no remote closure capabilities. A failure of these racks during a seismic event due to the excessive weight could result in an unisolable leak from the RCS within containment based on engineering judgment. This results in the RCS principal safety boundary being in a degraded nonconforming condition as the Updated Safety Analysis Report (USAR) specified Class 1 requirement is not being met for the current seismic design. Further engineering analysis is in progress to address the weight issue for these racks and mounting requirements. The plant is shutdown and in Mode 5 with the reactor vessel head removed, so RCS is not intact and not required to be for current plant conditions. This report is being made in accordance with 10CFR72(b)(3)(ii)(A) for a degraded condition." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 8/3/12 AT 1708 EDT FROM JULIE BISSEN TO DONG PARK * * * "On June 4, 2012, at 2059, Fort Calhoun Station made an 8-hour non-emergency notification for a degraded condition. Subsequent internal review has determined that the initial reporting criterion for degraded condition, 10 CFR 50.72(b)(3)(ii)(A), was incorrect. The instrument racks were identified as being over the analyzed weight for the seismic analysis. This is an unanalyzed condition, not a degraded condition. The report made on June 4, 2012 should have been made under 10 CFR 50.72(b)(3)(ii)(B), unanalyzed condition." The licensee has notified the NRC Resident Inspector. Notified R4DO (Werner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-06-04
47991 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2012-06-01 08:00 | 2012-06-04 16:45 | 2013-01-09 | AGREEMENT STATE REPORT - LOST NI-63 ELECTRON CAPTURE DETECTOR On June 1, 2012, the licensee reported a lost Ni-63 electron capture detector (ECD) to the state of Oregon. The source is an Agilent Technology model 19233, serial number L5286 and was used in a gas chromatograph (GC) device. The source was obtained in April of 2006. The last time the source was known to be in possession of the licensee was during a 6-month wipe test performed on November 1, 2011. The gas chromatograph was sent to Far West Fiber Metal Recycling around the first of the year and it is possible the source was in the machine at the time of disposal. The licensee will continue to search for the source. The state of Oregon will follow-up with the licensee. * * * UPDATE ON 1/9/13 AT 1218 EST FROM DARYL LEON TO HUFFMAN * * * The following update was received from the State of Oregon Radiation Protection Services via facsimile: "Inspection/investigation at TestAmerica Analytical Testing Corporation (TAATC) site performed on June 14, 2012. Missing ECD device not located, believe to have been housed inside a gas chromatograph (Hewlett-Packard model 5890, serial number 3033A30613) that was turned over to Far West Fiber Metal Recycling on December 5, 2011. All other ECD devices (25) were accounted for during the inspection. "Discussion with Far West on June 4, 2012 indicates that metal items received are held for downstream customers for two weeks and then turned over to them for stripping/smelting. Far West had no record of receipt of the GC/ECD or which customer it may have gone to. Checks were made with local firms (Schnitzer Steel and Metro Metals) but no record of the GC/ECD unit receipt was located. TAATC continued to search for ECD unit for several months but it was not found. Believe ECD was smelted with GC at this time. "Cause of this event due to management deficiency. RSO was moved to new position in November 2011 and out of room where ECD unit located and was training replacement person to perform some RSO duties (6-month leak testing/inventory) for ECD's. Missing ECD was housed in GC unit that was not used for 4 years and GC was used for spare parts. An employee of TAATC not listed on the materials license and unfamiliar with GC/ECD's removed 3 GC units from the room on December 5th and delivered to Far West Fiber for recycling, including the GC unit that normally housed the ECD in question. The other GC's did not house ECD's. The RSO and his trainee were unaware of the missing ECD until June 1, 2012 during routine 6-month leak testing nor was the RSO aware of the GC transfer since RSO works in a different area on site and do not routinely monitor ECD locations anymore. "No other actions available at this time. The State of Oregon is closing this event." Notified the R4DO (Gaddy) and e-mailed FSME Events Resource. OREGON NMED REPORT NUMBER 120345 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2012-06-12
47990 | 0 | MITSUBISHI HEAVY INDUSTRIES, LTD. |  |  |  |  | 2012-02-13 | 2012-04-19 12:33 | 2012-09-07 | PART 21 - STEAM GENERATOR TUBE WEAR ADJACENT TO RETAINER BARS The following information was obtained from Mitsubishi Heavy Industries, LTD on April 19, 2012 was inadvertently added to Event Notification #47833 as an update to that event. The vendor's intent was to issue two interim reports; one for San Onofre Nuclear Generating Station (SONGS) Unit 2 and one for SONGS Unit 3. The information was obtained via fax: "On January 31, 2012, San Onofre Unit 3 shut down due to indications of a steam generator tube leak. Steam generator tube inspections confirmed one small leak on one tube in one of the two steam generators. Continuing inspections of 100% of the steam generator tubes in both Unit 3 steam generators discovered unexpected wear, including tube to tube as well as tube to tube support structural wear. Inspection, testing, and analysis of SG tube integrity in both Unit 3 SGs is ongoing. In-situ pressure testing identified eight Unit 3 SG tubes that did not meet the target performance criteria in Technical Specification for tube integrity. One of the failed tubes was the leaking tube that required the Unit 3 shutdown. "Discovery date: February 21, 2012 "Evaluation completion schedule date: August 31, 2012" Interim Report: U21-019-IR Reference Document: UET-20120105 Original notifications (per EN# 47833) were made to R1DO (Joustra), R2DO (Nease), R3DO (Peterson), R4DO (O'Keefe), and Part 21 Group via email. Notified R1DO (Cahill), R2DO (Vias), R3DO (Passehl), R4DO (Gepford) and Part 21 Groups via email. * * * UPDATE FROM MITSUBISHI HEAVY INDUSTRIES, LTD VIA FAX ON 6/4/12 AT 1145 EDT * * * The vendor reported that eight Unit 3 SG tubes did not meet the target performance criteria in Technical Specifications for tube integrity. Notified R1DO (Cahill), R2DO (Vias), R3DO (Passehl), R4DO (Gepford) and Part 21 Groups via email. * * * UPDATE FROM MITSUBISHI HEAVY INDSUSTRIES, LTD VIA FAX ON 9/7/12 AT 1539 EDT * * * "MHI evaluated that the deviation contains a reportable defect for San Onofre Nuclear Generating Station Unit 2 and 3." Notified R4DO (Gaddy) and Part 21 Reactor Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-06-04
47989 | 0 | NUCLEAR REGULATORY COMMISSION R-I |  |  |  |  | 2012-05-08 | 2012-06-01 15:09 | 2012-06-04 | MISSING CHECK SOURCE "On May 8, 2012, Region I identified that a survey instrument check source containing approximately 2.64 microCuries of strontium-90 was missing. The source is believed to have been inside of a metal cabinet that was inadvertently discarded on May 2, 2012, during the removal of excess property in preparation for relocation of the regional office. The source is not considered to be a hazard to public health and safety due to its low activity level and beta emission decay path. Upon discovery, the Region implemented several immediate actions including: attempts to locate and retrieve the source; confirmation that the remaining instrument check source was properly secured; and, a courtesy notification regarding this issue to the Commonwealth of Pennsylvania. In addition, a review of this event, consistent with the NRC's Management Directives, was initiated to identify and implement appropriate follow-up actions to prevent recurrence. "This report is being submitted in accordance with NRC MD 10.131, Part V for missing material in a quantity greater than 10 times the quantity specified in 10 CFR 20 Appendix C." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2012-06-12
47988 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2012-06-03 02:39 | 2012-06-03 06:07 | 2012-06-03 | AUTOSTART OF "B" EDG DUE TO LOSS OF OFFSITE POWER CIRCUIT 767 "At approximately 0239 hours on June 3, 2012 the 'B' Emergency Diesel Generator (EDG) automatically started when offsite power circuit 767 was de-energized. The EDG started and re-energized Safe Guards busses 16 and 17. The selected Service Water (SW) pump 'B' automatically started to supply cooling to the EDG. "The operators responded to the loss of circuit 767 using abnormal operating procedure AP-ELEC.1 'Loss of 12A and/or 12B Busses'. "Offsite power was restored to 12B bus using ER-ELEC.1 'Restoration of Offsite Power' on circuit 7T at 0318 hours. The 'B' EDG was shutdown at 0445 hours. "The initial investigation of the loss of circuit 767 indicates that the likely cause was due to wildlife, e.g., raccoon." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-06-03
47987 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2012-06-02 19:35 | 2012-06-02 21:52 | 2012-06-02 | REACTOR TRIP DUE TO A TURBINE CONTROL SYSTEM FAILURE "At 1935 during normal full power operations, Unit 1 automatically tripped due to a loss of load caused by an instantaneous failure of the turbine control system. The trip was uncomplicated and all CEAs [control rods] fully inserted when the reactor was tripped. No automatic safety system actuations were required and none occurred. The cause and details of the turbine control system failure are under investigation. The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Main Feedwater and Steam Bypass Control Systems with condenser vacuum. The offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to RPS actuation with the reactor critical." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-06-02
47986 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-06-01 09:00 | 2012-06-01 17:26 | 2012-06-01 | CABLE ROUTING ERROR COULD FAIL DC CONTROL POWER TO SHUTDOWN BOARD IN A FIRE "During NFPA 805 transition reviews, a cable routing error has been identified that would fail the DC control power to credited 4kV Shutdown Board 3EA for an Appendix R fire in Fire Area 23. "Cable 3B181 provides alternate DC Control Power to 4kV Shutdown Board 3EA from Battery Board 2. Cable 3B181 is routed in Fire Area 23. However, cable 3B181 is not identified as being in Fire Area 23 in Browns Ferry Nuclear Plant (BFN) calculation EDQ099920030037, Appendix R Computerized Separation Analysis. This error allowed the analysis to credit alternate DC Control Power to 4kV Shutdown Board 3EA. The normal DC Control Power to 4kV Shutdown Board 3EA is not available in the event of an Appendix R fire in Fire Area 23. The routing error results in the credited 4kV Shutdown Board 3EA being unable to perform its function for Fire Area 23 Appendix R fires due to both the associated normal and alternate DC Control Power cables being routed In Fire Area 23. The failure of 4kV Shutdown Board 3EA could result in a loss of power to credited safe shutdown equipment that would challenge the ability to provide adequate core cooling during performance of BFN Safe Shutdown Instructions. "Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the BFNP Fire Protection Report. "This event is reportable as an 8 hour notification to the NRC in accordance with 10CFR 50,72(b)(3)(ii)(B). This is also reportable as a 60 day written report in accordance with 10CFR 50.73(a)(2)(ii)(B)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-06-01
47985 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-06-01 12:47 | 2012-06-01 13:21 | 2012-06-01 | UNUSUAL EVENT DUE TO A BOMB THREAT Two individuals (one male and one female) drove up to the site security gate and stated they had a bomb in the vehicle (Jeep Cherokee). LLEA was notified and responded to the site. The two individuals are in custody and the Raleigh Police bomb squad is enroute to the site. The site is in a heightened level of security. Notified DHS, NICC, and FEMA. * * * UPDATE AT 1544 EDT ON 6/1/2012 FROM ALLISON HARKEY TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 1530 EDT on 6/1/2012. The vehicle search did not find a bomb and the two individuals are in custody. Notified the R2DO (Vias), NRR EO (Chernoff), DHS, NICC, and FEMA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-06-01
47984 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-05-31 23:37 | 2012-06-01 06:36 | 2012-06-01 | TRANSPORT OF POTENTIALLY CONTAMINATED PERSON OFFSITE "At 11:11 PM on May 31, 2012, the Harris main control room was notified that a contract employee in a radiation controlled area was in need of medical assistance. The individual was transported by ambulance to the hospital, accompanied by Harris radiation protection personnel. The individual was considered potentially contaminated because a complete survey to confirm the absence of contamination was not completed prior to transport of the person off site for medical treatment. The individual and the ambulance used to transport the individual were surveyed and released after arrival at the hospital." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-06-01
47983 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-05-29 | 2012-05-31 18:18 | 2012-05-31 | AGREEMENT STATE REPORT - PROSTATE SEED MEDICAL EVENT The following report was received via fax: "Patient underwent Iodine 125 surgical prostate seed implants (total dose 145 Gy). Initial post operative X-ray film revealed complete seed count. Day zero computed tomography revealed all seeds inferior to true base and resulted in placement in the penile bulb vs. the prostate gland. There were no instrument malfunctions to include the ultrasound. Urologist notified and in-turn patient was immediately notified. Risk to urethra was discussed. Further investigation to occur from NC RPS [North Carolina Radiation Protection Section] Inspectors on Tuesday, June 12, 2012 awaiting the return of the authorized user/physician." North Carolina incident: 12-37 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-06-08
47982 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2012-04-17 | 2012-05-31 15:37 | 2012-05-31 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILED IN THE OPEN POSITION The following report was received via fax: "On May 31, 2012 at 1530 hrs [EDT], the SC Department of Health and Environmental Control was notified by phone that during a routine shutter check on April 17, 2012, an Automation and Control Technology (ACT) Model TG-7 gauging device containing 100 mCi of Sr-90, had a shutter mechanism that was harder to operate than normal. An ACT Model TG-7 technician was evaluating the operation of the shutter when it failed and was unable to be moved into the closed position. The ACT technician was able to replace the shutter assembly and switch on April 19, 2012. A survey, as well as a shutter check was performed to insure proper function. A report was sent from ACT to Samuel Strapping Systems on April 30, 2012." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2012-06-08
47981 | 0 | SHAW NUCLEAR SERVICES |  |  |  |  | 2012-05-31 | 2012-05-31 16:17 | 2012-05-31 | PART 21 - DUCTILITY OF REINFORCING STEEL FOR EMBEDMENTS NOT IN ACCORDANCE WITH CODE REQUIREMENT "The reporting organization provided information pertaining to the identification of a noncompliance associated with the steel reinforcing material (rebar) attached to embedments being supplied as basic components for the Vogtle Units 3 and 4, nuclear project, based on reinforcing bar that exceeded the limit for yield strength. "The results of the evaluation of this condition as documented by Shaw Nuclear and conducted in accordance with the procedure for performing evaluations required by 10 CFR 21.21, has concluded that the noncompliance could potentially create a substantial safety hazard, if it were to remain uncorrected. Therefore, it has been determined that this noncompliance is reportable under the requirements of 10 CFR Part 21." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-06-01
47980 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2009-06-04 | 2012-05-31 15:20 | 2012-06-05 | AGREEMENT STATE REPORT - THREE MEDICAL EVENTS DISCOVERED DURING AN INSPECTION The following report was received via e-mail: "During a routine inspection, three unreported [prostate brachytherapy] medical events were identified. "Case One: Implant Date: 6/4/2009 Prescribed dose: 145Gy to the prostate Post implant CT dosimetry: V100 (the volume of the prostate receiving 100% of the prescribed dose) totaled 69.71% Source: I-125 encapsulated seeds Vendor: IsoAid Model Number: IAI-125A Activity per seed: 0.330 mCi Number of seeds implanted: 69 "Case Two: Implant Date: 6/19/2009 Prescribed dose: 145Gy to the prostate Post implant CT dosimetry: V100 (the volume of the prostate receiving 100% of the prescribed dose) totaled 62.77% Source: I-125 encapsulated seeds Vendor: IsoAid Model Number: IAI-125A Activity per seed: 0.330 mCi Number of seeds implanted: 80 "Case Three: Implant Date: 10/29/2009 Prescribed dose: 145Gy to the prostate Post implant CT dosimetry: V100 (the volume of the prostate receiving 100% of the prescribed dose) totaled 65.34% Source: I-125 encapsulated seeds Vendor: IsoAid Model Number: IAI-125A Activity per seed: 0.330 mCi Number of seeds implanted: 84 * * * UPDATE FROM CURT PENDERGRASS TO HOWIE CROUCH VIA EMAIL ON 6/5/12 AT 1018 EDT * * * "D90 is defined as minimum dose received by 90% of CT-defined prostate volume Case 1 D90 = 72.80% of 145Gy Case 2 D90 = 58.86% of 145Gy Case 3 D90 = 54.00% of 145Gy" Notified R1DO (Cahill) and FSME Events via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-06-08
47979 | 0 | UNIV OF FLORIDA |  |  |  | 100 KW ARGONAUT | 2012-05-30 17:00 | 2012-05-31 15:00 | 2012-05-31 | TRAINING REACTOR MODIFICATIONS NOT REPORTED "On 5/30/2012, during preparation of a supplemental license submittal in support of LAR#27, an apparent violation of 10 CFR 50.54(p)(2) was discovered. This is a reportable event under UFTR [University of Florida Training Reactor] Technical Specification 6.6.2(3)(g). "Contrary to 10 CFR 50.54(p)(2), over a period of several years, the UFTR made several changes to the facility, as described in the approved Security Plan, without documentation of a security effectiveness evaluation, and without submitting a report containing a description of the change within the required timeframe. "An initial review indicates that these changes have no negative impact on security effectiveness. Investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 2 | FL | NPR | [5 empty] | 0 | 2012-05-31
47978 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-05-30 11:20 | 2012-05-31 09:58 | 2012-05-31 | UNPLANNED MEDICAL TREATMENT OF WORKERS "On 05/30/12, approximately at 1120 CDT, five employees working in the Feed Materials Building received first aid precautionary treatment for chemical inhalation in the on-site dispensary. The employees were found to have contamination on their boots and plant coveralls. The highest reading found on the employees was 53,300 dpm/100cm2 on the employee's boots. The employees were not transported to an off-site facility. The employees were released to go back to work and appropriately exit monitored at the end of their shift. There was no detectable contamination on the employees when they left the site." The licensee has notified NRC Region 2 (Calle). The chemical was Uranium Ore Concentrates. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-05-31
47977 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2012-05-31 03:04 | 2012-05-31 04:47 | 2012-05-31 | OFFSITE NOTIFICATION CONCERNING LOSS OF AMERTAP BALLS "At 0304 CDT, Prairie Island Nuclear Generating Plant notified the Minnesota State Duty Officer that 1000 Amertap balls were lost from the Unit 1 condenser tube cleaning system. Since the Minnesota State Duty Officer was contacted, this constitutes an 4 hour non-emergency notification per 10 CFR 50.72(b)(2)(xi). "The licensee has notified the NRC Resident Inspector." The licensee will notify local and other government agencies. | 100 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-31
47976 | 0 | RSCC WIRE & CABLE LLC |  |  |  |  | 2012-05-30 | 2012-05-30 16:26 | 2012-05-30 | PART 21 NOTIFICATION - FIREZONE 3HR 600V CABLE MAY NOT FUNCTION AS TESTED AND QUALIFIED The following information was received via fax: "Nature of Defect: RSCC Wire & Cable LLC's Firezone 3HR 600V cables may have been installed in a configuration not tested by RSCC. RSCC has only tested the Firezone 3HR 600V cable while installed in a tray with no additional cables. The actual installation at the Comanche Peak Nuclear Power Plant of the Firezone 3HR 600V cable was in a tray with other non-fire rated cables. The guidelines given by UL in FHIT.Guide Info and FHIT.31 are not specific enough to cover this case. RSCC Wire & Cable LLC conservatively concludes this may be a potential defect. "Potential Hazard: Under fire conditions in a tray with other non-fire rated cables, Firezone 3HR 600V cables may not function as tested and qualified in accordance with UL 2196. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: RSCC has issued a Corrective Action Report (CAR 12-19) to address requirements that include documented installation procedures for Firezone 3HR 600V cables. Robert Gehm, Applications Engineering Manager for RSCC Wire & Cable LLC, has been designated as the responsible individual for action(s) to be taken. Completion of the corrective action is expected by June 29, 2012. "Notification will be made to Comanche Peak Nuclear Power Plant and the Dresden Nuclear Power Plant for their evaluation regarding the condition as described. Notification will be made by May 31, 2012." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-05-30
47975 | 0 | ABB INC |  |  |  |  | 2012-03-29 | 2012-05-29 17:07 | 2013-04-01 | PART 21 NOTIFICATION - PROTECTIVE RELAYS MAY NOT BE QUALIFIED FOR HARSH ENVIRONMENTS The following report was received via fax: "During the commercial grade dedication process for a unit that was returned for repair, the unit was found to be in nonconformance with ABB specifications. The ABB specifications require that two (2) particular components, integrated circuits (ICs) of plastic construction, are replaced with 2 ICs of ceramic construction during the assembly process. The chips found on the harmonic filter circuit board (HF Board) of the relays were of plastic construction. While plastic ICs are approved for use in commercial relays, they have not been qualified for safety-related applications. Relays in this condition will function normally in mild environments, but have not been qualified for harsh environments, or for elevated radiation environments." The affected solid state relays are 27N and 59G shipped between August 1, 2010 and October 15, 2010. "Eighteen (18) Relays (Material number: 211T4175-HF-1E) were sold to ABB Florence who in turn shipped the same to Detroit Edison's Fermi 2 Power Plant." * * * UPDATE FROM TAUZER TO SNYDER AT 1730 EDT ON 4/1/13 * * * The supplier has concluded that the solid state relays with the plastic encapsulate are qualified for Class 1E applications. "ABB Coral Springs is providing this letter to close the interim report and notice of deviation from specification requirements associated with Solid State Relays 27N and 59G dated May 29, 2012 (Event ML12153A030). "As stated in the interim report, one of the actions to be completed was the qualification and testing of representative plastic ICs to confirm acceptability and use in safety-related applications. "This letter is a follow-up notification that the plastic IC qualification and testing is complete, and based upon the results, we have concluded that the ICs with the plastic encapsulate are qualified for Class 1E applications specific to the subject relays. "Affected customers have been notified." Notified R3DO (Daley) and Part 21 Reactors (Email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-05-29
47974 | 0 | 3M CORPORATION |  |  |  |  | 2012-05-21 13:30 | 2012-05-29 16:40 | 2012-05-29 | INDUSTRIAL GAUGE INOPERABLE DUE TO BENT SHUTTER "On May 21, 2012, the shutter on an industrial thickness gauging device (NDC Infrared Systems model 102) was discovered to be bent so that when closed, it did not adequately attenuate the radiation beam from the device. The facility Radiation Safety Officer removed the gauging device from the production line and secured plate steel over the radiation source to provide supplemental shielding to the same degree as the undamaged shutter. The device was placed in secure storage pending shipment for repair. "The device was shipped to 3M Corporate Health Physics in St. Paul, MN, on May 25, 2012. On May 29, 2012, the device was received and the shutter assembly replaced with an undamaged, spare shutter assembly. The repair was performed by [corporate radiation safety staff] under US NRC Radioactive Materials license no. 22-00057-03. The device was then returned to 3M Springfield. "Conversations between 3M Corporate Health Physics and US NRC Region III (Geoffrey Warren) on May 29, 2012, indicated that this event is reportable under 10 CFR 30.50(b)(2). "Location of event: 3M Springfield, 3211 East Chestnut Expressway, Springfield, MO 65802 "Isotope, quantity, chemical and physical form: Am-241, 150 milliCuries on February, 7, 1997, double encapsulated solid source (special form). "The event resulted in no additional exposure to any individual." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-06-06
47973 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2011-09-21 11:22 | 2012-05-29 14:44 | 2012-05-29 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM INOPERABLE "On Sept. 20, 2011, with the reactor at 100% power in mode 1, a scheduled test of the technical support center ventilation system revealed that the adsorber stage leak test did not meet acceptance criteria. The system was returned to service on Sept. 21, 2011, following corrective maintenance and a satisfactory test. It was not recognized at the time that the condition met 10 CFR 50.72(b)(3)(xiii) reporting criteria for the emergency filtration function. "The system was returned to service within approximately 30 hours of discovery. Investigation of Condition Report 526951 in the Harris Corrective Action Program determined that this event should have been reported upon discovery. "The NRC Resident Inspector has been Informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-29
47972 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-05-29 03:31 | 2012-05-29 07:22 | 2012-05-29 | AUTOMATIC REACTOR SCRAM DUE TO MAIN GENERATOR LOAD REJECT SIGNAL "On 5/29/2012 at 0331 [CDT] the Unit 3 reactor scrammed due to turbine control valve fast closure initiated by a load reject signal on the Main Generator. The cause of the load reject signal is Main Transformer differential relay 387T. Reactor power at the time of the SCRAM was approximately 75%. All systems responded as expected to the load reject signal. Main Steam Isolation Valves remained open and reactor pressure is being controlled on the Main Turbine Bypass Valves. No Main Steam Relief Valves lifted during the transient. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation setpoints were reached. Primary Containment Isolation Signals (PCIS) Groups 2, 3, 6 and 8 were received. The lowest reactor water level observed was -41 inches. Reactor water level was restored to and is being controlled by the Feedwater system in the normal band. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B), 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10CFR50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR50.73(a)(2)(iv)(A). "This event is documented in the station corrective action program on SR# 557947. "The NRC Resident Inspector has been notified." All control rods inserted into the reactor core. Electrical power is being back fed from offsite power through the 161 KV feeder line. The reactor is being cooled down within the Technical Specification rates. | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-05-29
47971 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-05-28 05:49 | 2012-05-28 06:46 | 2012-05-28 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO A PROTECTED AREA Attempted introduction of contraband into protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM K. ROBINSON TO JOE O'HARA AT 1452 ON 5/28/12 * * * The licensee retracted the event and notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-05-28
47970 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-05-26 21:30 | 2012-05-27 15:45 | 2012-05-27 | FITNESS FOR DUTY RULE NOT MET "At 2130 EDT on 5/26/2012, a condition was reported identifying that the 10 CFR Part 26 requirement for performing waiver evaluations was not met for three security officers held over for compensatory measures after lightning strikes impacted security equipment at PPL Susquehanna, LLC. "Granting a waiver under Subpart I, 'Managing Fatigue,' of Title 10 of the Code of Federal Regulations (10 CFR) Part 26, 'Fitness for Duty Programs,' involves a process that, once completed, allows individuals who are subject to the Subpart I work hour controls to not meet one of the work hour requirements. "Contrary to the above, waivers were not processed for three security officers as required by the regulation and the officers worked hours exceeding the 16 hour limit. "This event is reportable under 10 CFR 26.719(b)(4) requiring a 24-hour ENS notification." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2012-05-27
47969 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2012-05-27 11:22 | 2012-05-27 14:24 | 2012-05-27 | OFFSITE NOTIFICATION CONCERNING LOSS OF AMERTAP BALLS "At 1122 CDT, Prairie Island Nuclear Generating Plant notified the Minnesota State Duty Officer that up to 1,500 Amertap balls were lost from the Unit 1 condenser tube cleaning system. Since the Minnesota State Duty Officer was contacted, this constitutes an 4 hour non-emergency notification per 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector in addition to state and local government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-27
47968 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-05-26 02:00 | 2012-05-26 02:28 | 2012-05-26 | PRESS RELEASE REGARDING STATUS OF ONGOING LABOR NEGOTIATIONS "On May 26, 2012, at 0200 EDT with the reactor at 42% core thermal power, the following press release is being issued by Entergy Nuclear regarding the status of the ongoing labor negotiations. "Pilgrim Station Negotiation Team Agrees to Present Proposed Package to Union Membership for Ratification Vote. "Plymouth, Mass. - Entergy Nuclear and the Utility Workers Union of America (UWUA), which have been negotiating a four-year Pilgrim Station labor contract, agreed early Saturday to present a proposed package of pay and benefits to the membership for a vote on Saturday, June 7. "Additionally, the parties have agreed to a 10-day [contract] extension that will expire at midnight on Tuesday, June 5. The previous contract for the approximately 240 workers will remain in effect during the extension. "Pilgrim's Site Vice President Robert Smith said, 'We appreciate the hard work of both parties to get to this point and believe this proposal represents fair and equitable terms both for our employees and the company.' "Entergy owns and operates power plants with more than 30,000 megawatts of electrical generating capacity and has about 14,000 employees. Entergy's nuclear businesses comprise six reactors at five sites in Massachusetts, New York, Vermont and Michigan and five reactors at four locations in Arkansas, Mississippi and Louisiana. Entergy Nuclear also manages operations at a nuclear generating plant in Nebraska. "The [NRC] Resident Inspector staff has been informed of this press release and notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi)." The licensee will notify the Massachusetts Emergency Management Agency. | 42 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-26
47967 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2012-05-25 13:22 | 2012-05-25 21:17 | 2012-05-25 | DE-ENERGIZATION OF BOTH DIVISIONS OF RHR SUCTION LINE PRIMARY CONTAINMENT ISOLATIONS VALVES DURING TESTING "On Friday, May 25th 2012 at 1322 EDT, Nine Mile Point Unit 2 experienced a loss of power to 600V 2EJS*US1 emergency load center while performing scheduled surveillance testing of the Division 1 Remote Shutdown System disconnect switches. Disconnect switch SW 1-2CESA20 was taken to the actuate position which isolated main control room control, bypassed the housing limit switches and aligned the trip test switch for local breaker control of 2EJS*US1 supply breaker 1-3B. Contacts in the trip test switch for 2EJS*US1 supply breaker 1-3B were found to be closed which energized its trip coil. This resulted in a loss of motive power to Division 1 Residual Heat Removal (RHR) system primary containment isolation valve 2RHS*MOV113 on the shutdown cooling suction line from the reactor vessel. At the time of the event, the Division 1 RHR shutdown cooling system was in-service with the Division 2 shutdown cooling suction line primary containment isolation valve 2RHS*MOV112 de-energized open to prevent inadvertent or spurious closure, which would interrupt the shutdown cooling decay heat removal function. "The result of the event was that both the Division 1 and Division 2 isolation valves on the common RHR shutdown cooling suction line (2RHS*MOV112 and 2RHS*MOV113) were open with no motive power. Thus, neither valve was capable of automatically closing in the event of a reactor level low (level 3) signal due to a leak in the RHR shutdown cooling system. The loss of this isolation function is being reported in accordance with 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented fulfillment of a safety function of a system that is needed to (D) mitigate the consequences of an accident. "Technical Specification 3.6.1.3 Condition G was entered and actions to restore the valves to operable status were immediately initiated in accordance with Required Action G.2. Power to 2RHS*MOV113 was restored at 1824 hrs, re-enabling its automatic isolation capability." The licenses has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-05-25
47966 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-04-26 | 2012-05-25 16:33 | 2012-05-25 | AGREEMENT STATE REPORT - LEVEL/DENSITY GAUGE SHUTTER MALFUNCTION The following information was obtained from the State of Louisiana via fax: "On April 26, 2012, the Louisiana Department of Environmental Quality (LDEQ) received notification that a shutter malfunctioned on an Ohmart Corporation Level/Density gauge at BASF Corporation. BASF Corporation has a RAM License LA-2304-L01 and Agency Interest Number 2049. The gauge was a Model SH-F1, containing a Cs-137 sealed source, serial number 6274GK with 50 mCi of activity. Ohmart sent out a field engineer to repair the following devices: 1) Ohmart Model SH-F1 level/density gauge, serial number 67471 to replace shutter and rotor; 2) Ohmart Model SH-F1 level/density gauge, serial number 6292GK to lubricate and restore proper shutter function; 3) Ohmart Model SH-F1 level/density gauge, serial number 6247GK, source holder remains stuck in the open position and the gauge is scheduled to be replaced and disposed of at a licensed facility. This incident is reference by LDEQ T139229." LA Report ID No.: LA120001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-06-04
47965 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-20 | 2012-05-25 14:19 | 2012-05-25 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING IODINE-125 PROSTATE SEEDS The following information was obtained from the Commonwealth of Pennsylvania via fax: "A patient was undergoing treatment with I-125 prostate seeds on January 20, 2012. The patient was prescribed to receive 110 Gy for a determined prostate volume of 21.08 cc. On March 16, 2012 the patient had a follow up CT scan where the prostate volume was determined to be 47 cc and the D90 to the prostate to be 75 Gy. The oncologist questioned the results and ordered an additional CT scan. On May 16, 2012, a second CT scan was performed to confirm the first CT scan. On May 21, 2012, the radiology oncologist calculated the prostate volume to be 33.59 cc and confirmed the D90 to be 75 Gy. The radiation oncologist has no explanation for the edema. "Cause of the Event: Implant performed using ultrasound, post implant verification via CT. "Actions: There will be a reactive inspection [by the Commonwealth of Pennsylvania]. The radiation oncologist ordered external beam radiation therapy and feels that the total dose is sufficient. Additional follow up with the patient will occur." PA Report ID No.: PA120018 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-06-04
47964 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-05-18 | 2012-05-25 13:29 | 2012-05-25 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was obtained from the Commonwealth of Pennsylvania via fax: "Alcoa was doing some renovations and had a previous inventory of nine (9) general license [GL] tritium exit signs. During the renovation it was discovered that only seven (7) were accounted for. "Details of the two missing exit signs: Evenlite, Inc. Model #201, serial numbers 1388F and 389F, each containing 10.5 Ci of tritium. "CAUSE OF THE EVENT: Though these GL tritium exit signs comply with NRC regulations for labeling to alert the user that they contain radioactive material, the size of the label is woefully inadequate to prevent unintentional loss of the GL device. This event is another example. "ACTIONS: No reactive inspection is planned at this time. It is expected these two tritium exit signs have or will end up in an unlicensed Commonwealth of Pennsylvania landfill." PA Report ID No.: PA120015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-06-04
47963 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2012-05-25 | 2012-05-25 11:32 | 2012-05-25 | AGREEMENT STATE REPORT - URANIUM SOURCE FOUND AT METAL CHECK RECYCLING FACILITY "On May 22, 2012 we [Oklahoma Department of Environmental Quality (OKDEQ)] were contacted by the Director of Radiology at INTEGRIS Southwest Medical Center in Oklahoma City. The Director informed us that an individual had presented at their Emergency Room complaining that he had been exposed to radiation at the Metal Check, Inc. scrap metal yard located at 5700 South High Avenue, Oklahoma City, OK. According to [the Director], the individual was a heavy equipment mechanic who had been sent to Metal Check to repair a piece of their equipment. While working there he was told by some of the Metal Check employees not to enter a certain part of the facility because it contained radioactive pipe. The mechanic immediately left Metal Check and went to the Medical Center." "That afternoon [an inspector with OKDEQ] went to Metal Check and spoke with the owner and the manager. They agreed to allow [the inspector] to survey the pipe in question and showed [the inspector] the area where it was stored and where the mechanic was working. It appeared to [the inspector] that the pipe was located approximately 40 feet from where the equipment was being repaired, making it impossible for the mechanic to receive any significant dose from this material. [The manager] showed [the inspector] a small bin approximately six feet long by four feet high by four feet deep filled with miscellaneous pieces of scrap metal. The top of the bin was surveyed with a Ludlum Model 19 microR meter (S/N 70537, cal. Aug. 18, 2011) which produced a reading of approximately 1100 microR/hr. This was very high for NORM [naturally occurring radioactive material] pipe and [the inspector] also noted that the radiation level was not uniform along the length of the bin, having a definite spike approximately two feet from the left end. This led [the inspector] to conclude that there was a localized source somewhere in the bin at that point. [The inspector] then contacted [his supervisor] and related what [he] had found at the facility. [The inspector] suggested returning the next day with an additional person and additional instruments, and attempting to locate the postulated radiation source. "The following morning [the inspector and an associate] returned to Metal Check and began to unload the bin. Almost immediately [they] found what appeared to be a badly corroded metal bucket which had been crushed around an object inside it. A survey of the object with the same Model 19 used the previous day produced a reading of 2.2 mR/hr on contact with the bucket. A Thermo Fisher Interceptor portable gamma spec was used to collect a gamma spectrum from the object, which the instrument identified as shielded Uranium. A second spectrum was collected through a hole in the bucket surrounding the object; this was identified as natural Uranium. A portion of the object was wiped through a hole in the bucket; analysis of the wipe by the DEQ Environmental Lab confirmed the presence of U-235 and U-238, and their daughters. The object was roughly disk-shaped, approximately 12 inches in diameter and one inch thick. One side had a second, smaller disk, approximately 10 inches in diameter, centered on the larger and approximately 2 inches thick. No markings or labels were visible. [The inspectors] estimate the weight of the object at approximately 40 lbs. Three pieces of NORM pipe were also found with high radiation levels (1 mR/hr). All four objects were removed from the bin which was then surveyed again, producing readings of approximately 300 to 400 microR/hr. Rachel Browder and Michelle Hammond of the NRC were informed of the situation later that day by phone. The uranium object was placed in a locked room at the Metal Check facility pending further guidance from NRC." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2012-06-04
47962 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2012-05-24 16:30 | 2012-05-24 21:59 | 2012-05-24 | MISSING FLOOD BARRIER INSIDE EAST SWITCHGEAR ROOM "On 5/24/12, it was identified that a conduit flood seal was missing between an outside manhole and the interior of the switchgear rooms. The missing flood seal compromised the interior flooding design for both East and West Switchgear Rooms. Repairs were made by procuring and installing a 4" flood seal so that the flood path has been plugged. The conduit plug seal is now functional. "The event is being reported under 10CFR 50.72(b)(3)(v) as internal flooding of both Switchgear Rooms could possibly affect (a.)safe shutdown, (b.)removal of decay heat, (c.)control of release of radioactive material and (d.)mitigating an accident." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2012-05-24
47961 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2012-05-23 | 2012-05-24 19:04 | 2012-05-25 | AGREEMENT STATE REPORT - MANUFACTURER RECEIVED AN ANALYZER WITH AN OPEN SHUTTER The following was reported from the state via e-mail: "A Kennewick licensee who manufactures and distributes hand-held devices used to analyze metal alloys notified the Materials Section of an incident that occurred with one of their General License customers in California. The shutter in the device which shields the radioactive material remained in the open position even after disengaging the trigger mechanism to close the shutter. This allowed radiation to stream from the device unabated. The California customer packaged the device for shipping knowing the shutter was open with nothing shielding the radiation and sent it back to the manufacturer in Kennewick for repairs. When the manufacturer received the device, a radiation reading in excess of the package limitations was noted and promptly reported to us. The licensee informed us this is the first shutter malfunction ever for this device model, which has been in service without any similar problems for many years. The Materials staff is working with the licensee to identify compliance issues and to prevent recurrence." The Bruker AXS hand held XRF analyzer contains 5.9 milliCuries of Co-57. Incident Number WA-12-037 * * * UPDATE FROM CRAIG LAWRENCE (VIA EMAIL) TO HOWIE CROUCH AT 1125 EDT ON 5/25/12 * * * The XRF device is owned by Benchmark Environmental. Benchmark Environmental shipped the device to Bruker on May 22, 2012. "Based on the dose rate measurement taken by Bruker prior to opening the package and removing the instrument, the Washington State Department of Health doesn't believe there were exposures to any member of the public in excess of regulatory limits. A dose rate measurement at 3 feet was 0.3 mR/hr as measured by their Bicron Surveyor 50 (cal date 1/19/12). Reading at approximately six inches from the surface pegged the dose rate meter on the 0 to 0.5 mR/hour scale. Bruker did not take measurements on higher scales. "At that point, Bruker's shipping and receiving took the MAP FA4C1 analyzer out of the case and carried it at arm's length to the shielded source exchange pit. The instrument was evaluated inside the pit and the shutter was found partially open. The Co-57 source was removed from the analyzer and put into a shielded pig. Bruker examined the analyzer and found the source block was defective and [the analyzer was] sent to production for a replacement source block. The licensee provided corrective actions in the NMED data entry form. Notified R4DO (Spitzberg) and FSME (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2012-06-01
47960 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2012-05-24 13:48 | 2012-05-24 18:04 | 2012-05-24 | MANUAL REACTOR SCRAM DUE TO LOSS OF FEEDWATER "At 1348 CDT on 5/24/12 with the Reactor at 33% power, River Bend Station operators inserted a manual reactor scram based on loss of high pressure feed to the reactor following a loss of a 13.8 Kv switchgear. "The Control Room team observed an electrical transient in the Control Room concurrent with the start of Reactor Feed Pump "B". "The crew identified that no high pressure feed was aligned to the reactor and inserted a manual scram. Based on the configuration of the electrical plant during startup, all circulating water and Normal Service Water (NSW) was supplied from NPS-SWG1B. MSIVs were closed based on loss of circulating water and Standby Service Water (SSW) initiated automatically based on loss of NSW. "EOP-0001, 'RPV Control' was entered on reactor high pressure and reactor low water level. EOP-0002, 'Primary Containment Control' was entered based on primary containment pressure high and suppression pool level high. EOP-0003, 'Secondary Containment Control', was entered on annulus pressure high. "Reactor water level control is being maintained with Reactor Core Isolation Cooling (RCIC). High pressure core spray was manually started but was not required and was subsequently shut down. Pressure control is via RCIC and Safety Relief Valves (SRVs). Safety related busses are aligned to offsite power as normal. They were not affected by the electrical transient. "Immediately after the scram at 1350, a report from the Turbine Building indicated smoke was seen around the Reactor Feed Pump 'B' termination cabinet. The Fire Brigade was activated. At 1358, the Fire Brigade reported that there was no fire. A review of the Emergency Action Levels (EALs) was performed. No emergency declaration was required. "Initial investigation shows damage to cabling and circuit boards associated with Reactor Feedpump 'B' in the Turbine Building, but no fire was ever observed. "In addition, the Technical Support Center (TSC) and Operations Support Center (OSC) lost power. At the time, both facilities continued to be in a state of readiness and emergency functions could be performed. At 1526, power was restored to both facilities, including the ventilation systems." All rods inserted into the core. The unit is stable at 230 psi and 391 degrees F. Reactor pressure is maintained by RCIC and decay heat removal via safety relief valves to the suppression pool. The unit is in a technical specification for suppression pool high level. There were no safety system failures. There is one non-safety related 13.8 switchgear out of service due to this event and NNS-Switchgear 2A out of service from an event three days ago. Offsite assistance was not required. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 33 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  | 0 | 2012-05-24
47959 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-05-24 15:41 | 2012-05-24 17:31 | 2012-05-24 | OFFSITE NOTIFICATION DUE TO OIL SHEEN ON THE RIVER "On 5/24/2012 at 1541 EDT, a notification to the National Response Center was made after the discovery of a visible oil sheen on waters of the U.S. (the Tennessee River side of Sequoyah's intake forebay skimmer wall). The source of the oil appears to be a tipped or overflowing catchpan located in the Essential Raw Cooling Water (ERCW) pumping station. All catchpans in the pumping station have been emptied to eliminate them as immediate potential source of oil released to the environment. "The following agencies have also been notified: EPA Region 4, and the Tennessee Emergency Management Agency (TEMA). The Tennessee Department of Environment and Conservation (TDEC) will be notified. "Cleanup is in progress. Measures to prevent recurrence are being taken." The NRC Resident Inspector will be notified. | 75 | 100 | 0 | 75 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-24
47958 | 0 | DOW CORNING |  |  |  |  | 2012-05-24 14:00 | 2012-05-24 15:29 | 2012-05-24 | DENSITY GAUGE SHUTTER FAILURE During a routine bi-annual periodic inspection, a density gauge with a 4 milliCurie Cs-137 source was identified to have a stuck shutter. The gauge was an Ohmart Vega Model SHF1-A, S/N 0964C0. The instrument is permanently installed in an isolated tower area, and this event did not result in exposure to any personnel. The licensee plans on having the gauge repaired by the manufacturer. The licensee notified R3 (Bramnik). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-06-01
47957 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-05-23 17:00 | 2012-05-24 15:21 | 2012-05-24 | CONTRABAND FOUND INSIDE THE PROTECTED AREA "On May 23, 2012, at approximately 1700 hours, a beer bottle was discovered in a trash can inside the protected area. The bottle was discovered during trash collection by housekeeping personnel who reported the discovery to their supervision. The bottle was determined to contain remnants of moisture and had an odor of beer, constituting the potential presence of alcohol. This report is submitted pursuant to 10 CFR 26.719 (b)(1) based on the presence of alcohol in the protected area. The NRC Senior Resident Inspector has been notified. "We do not know if it was consumed in the Protected Area. It was found in the Construction Support Building, not in a Vital Area. This has been entered into the Corrective Action Program and investigation has been in progress." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2012-05-24
47956 | -1 | PORTSMOUTH LEAD CASCADE |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-05-24 08:33 | 2012-05-24 13:14 | 2012-07-18 | UNAUTHORIZED INDIVIDUAL GAINED ACCESS TO FACILITY "At 0833 on 05/24/2012, an uncleared vendor employee was piggybacked by a cleared vendor employee through a security gate into the x3012 Security Area. The uncleared employee was removed from the area. There is no known compromise of classified information. "This incident is reportable to the Nuclear Regulatory Commission as an 8 hour Security Event in accordance with American Centrifuge Administrative Procedure ACD2-RG-044, Nuclear Regulatory Event Reporting, Appendix B, Section K2, IMI-3#14, which states, 'Circumvention of established access control procedures into a security area (excluding Property Protection Area)." The licensee notified NRC Region 2 (Hartland). * * * RETRACTION AT 1100 EDT ON 07/18/12 FROM CHARLES SEIDEL TO S. SANDIN * * * "Update: On 07-18-12 at 1017 the NRC Event has been retracted on the guidance of the Regulatory Organization for the following reason: "It has been determined that the two previously reported DOE IMI-3 events for 2012 did not meet the requirements for an NRC reportable event and should have been entered into the written log in accordance with 10 CFR 95.57. While they did meet the criteria for an 8-hr reportable event to the DOE they did not meet the NRC requirements for reporting to the NRC Operations Office. We hereby request that both NRC Events 48084 and 47956 be retracted." Notified R2DO (Desai). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2012-05-24
47955 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-05-24 06:39 | 2012-05-24 11:10 | 2012-05-24 | REACTOR SCRAM DURING STARTUP "At 0639 CDT on 5/24/2012. Unit 3 initiated a manual scram due to multiple rods inserting. At 0637 CDT during Unit 3 start-up Intermediate Range Monitor (IRM) 'H' was ranged down instead of up resulting in half scram on Reactor Protection System (RPS) 'B' trip system. The half scram was being reset after IRM 'H' was properly ranged. The operator placed the scram reset switch in Group 2/3 position. As the operator reset groups 2 and 3, a spike on IRM 'A' was received on the RPS 'A' trip system, resulting in rod insertion for groups 1 and 4. When the operator identified multiple rods inserting, the actions of procedure 3-AOI-l00-1 were followed and a manual scram was inserted. Investigation is ongoing. "All safety systems remained in standby readiness configuration. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary Containment lsolations Systems did not received actuation signals and performed as designed. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of systems listed in paragraph (b)(3)(iv)(B) 'Reactor Protection System (RPS) Including reactor scram and reactor trip.' This event requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Startup; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-05-24
47954 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2012-05-23 20:02 | 2012-05-23 20:49 | 2012-05-24 | SAFEGUARDS REPORT - DISCOVERED VULNERABILITY There was a discovered vulnerability in a safeguards system that could allow access to a vital area for which compensatory measures were not employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM W. MARTIN TO J. O'HARA AT 1438 ON 5/24/12 * * * This event is being retracted. The licensee determined that compensatory measures were adequate. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-05-23
47953 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-05-23 16:00 | 2012-05-23 19:54 | 2012-05-23 | CRACK IDENTIFIED IN PRESSURIZER HEATER "During inspections to determine the physical integrity of a failed pressurizer heater it was determined that the heater (number 26) was cracked. Due to the location of the pressurizer heater crack, this is considered a degradation of the RCS Barrier. The initial visual inspection of heater 26 in November of 2011, did not identify the cracking. During efforts to remove the heater, a crack was observed on May 21, 2012. The crack is above and below the heater support plate. The crack is an axial crack showing some branching. The crack is about an inch above and inch below the heater support plate. These inspections were being performed as a result of the operating experience at the Sizewell B reactor in the United Kingdom." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-05-23
47952 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-04-10 | 2012-05-23 16:38 | 2012-05-23 | AGREEMENT STATE REPORT - STUCK SOURCE IN CATHETER The following the received via e-mail: "On May 23, 2012, the Agency [State of Texas] was notified by the licensee that on April 10, 2012, while the licensee was performing a routine quality assurance test using a beta catheter system device, the 50.2 milliCurie Strontium-90 source train jammed as it began to move from the transfer device to the test catheter. The source train was lodged near the transfer device exit port and could not be returned to the home position. After a few failed attempts to retract the source train, the applicator and phantom were covered with a lead apron, and the manufacturer's Radiation Safety Officer was notified. A manufacturer's technician arrived at the licensee's Hot Lab the morning of April 11, 2012. The technician was not able to return the source to the shielded position. The device was returned to the manufacturer's facility for analysis. Since this fault occurred during routine quality assurance testing, no patient was involved in the procedure. The manufacturer inspected the catheter and found a deformation in the catheter that would have interfered with the source movement. The source was leak tested, and the results indicated that the source was not leaking. The source train has been removed from service. "Additional information will be provided as it is received in accordance with SA - 300." TX Incident # I-8956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-05-31
47951 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-05-22 10:13 | 2012-05-23 09:34 | 2012-05-23 | FITNESS FOR DUTY - PERSONNEL ACCESS DENIED "On May 22, 2012, at approximately 1013 hours CDT, access was denied to an individual who is licensed under Part 10 CFR Part 55 to operate a power reactor. The denial was due to the individual violating the company's Fitness for Duty policy. "This condition is being reported pursuant to 10 CFR 26.719(b)(2)(ii)." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2012-05-23
47950 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-05-22 17:32 | 2012-05-22 22:31 | 2012-05-22 | FIFTY-EIGHT SIRENS WERE NOT FUNCTIONAL IN WRIGHT COUNTY MINNESOTA "On May 22, 2012 at 1732 [CDT] Monticello Nuclear Generating Plant [MNGP] was notified by the Wright County siren vendor of an equipment malfunction with the siren activation system. Due to this issue, they are unable to activate any sirens in Wright County. The vendor discovered the issue during the completion of siren work in the county today. The vendor requested the dispatcher to issue a cancel test. The cancel test did not work. The issue is affecting both the primary and back up activation systems. The vendor will be following up until the issue is resolved. 58 sirens are impacted. The vendor anticipates investigation and repairs to be completed this evening. A compensatory measure, route alerting, is in place. The NRC Resident Inspector has been notified. "MNGP was notified by the vendor at 2120 [CDT] on 5/22/2012 that the issue had been resolved and the sirens are now functional." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-22
47949 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-05-22 16:30 | 2012-05-22 22:29 | 2012-07-19 | UNANALYZED CONDITION IDENTIFIED DURING A FIRE PROTECTION REVIEW "During a review of non-compliances with Appendix R that are being resolved as part of the NFPA 805, Risk Informed Fire Protection Transition, it was identified that a non-compliant operator manual action to manually backwash the cooling water strainers was identified in several fire areas, but the need to manually backwash the strainers may be required in other fire areas not previously identified. For Fire Areas 25, 30, 31, 38, 66, 109, and 117 power to the cooling water strainer central control panel could be affected which could require the need to perform a manual backwash of the strainers. Manual backwash of the cooling water strainers has not been established as an alternate compensatory measure for Fire Area 25, 30, 31, 38, 66, 109 and 117. "Manual operator actions that are required to recover functionality of a system that is credited to achieve and maintain hot safe shutdown for a fire in a III.G.1 or III.G.2 fire area are indicative of a missing fire barrier. "The lack of established alternate compensatory measures is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). "Compensatory measures have been established by verifying fire detection in the affected areas is functional with an hourly fire watch established in accordance with site procedures." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1708 EDT ON 7/19/12 FROM STEVE SCHMIDT TO HUFFMAN * * * "An eight hour report per 10 CFR 50.72(b)(3)(ii)(B) was reported on May 22, 2012 for a non-Compliant manual operator action to backwash the cooling water strainers in several fire areas not previously identified. "Subsequent analysis determined that the process of removing sufficient decay heat to achieve and maintain cold shutdown does allow the use of repair actions. Since Prairie Island Nuclear Generating Plant (PINGP) can be in the process of removing sufficient decay heat to reach cold shutdown conditions in much less than 15 hours there is significant margin to show this action is acceptable as a cold shutdown action and is in compliance with the requirements of Appendix R, Section III.G. "Therefore, the action is not a non-compliant operator manual action and EN 47949 is retracted. "The NRC Resident Inspector has been informed." R3DO (Kozak) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-05-22
47948 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-05-22 17:13 | 2012-05-22 19:22 | 2012-05-22 | OFFSITE NOTIFICATION DUE TO LOSS OF AMERTAP BALLS "On May 22, 2012 it was determined that more than 20% (3 of 8 barrels) of the Amertap balls used for condenser cleaning on May 18, 2012 were not able to be recovered by normal means. Observers were stationed at the discharge structure during the process and it is not believed that balls were released to the river. The current agreement with the Minnesota Pollution Control Agency dated September 12, 2008, requires XCEL Energy to make a report to the MPCA whenever more than 20% (1.5 barrels or approximately 7,500 balls) of the Amertap balls are not recovered. The MPCA was notified May 22, 2012." Approximately, 15,000 Amertap balls have not been recovered by the normal strainer system and may be in the discharge canal. The licensee is investigating the cause of the event. The NRC Resident Inspector, Wright County Sheriffs Department, and Sherburne County Sheriffs Department have been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-22
47947 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2012-05-22 10:55 | 2012-05-22 17:53 | 2012-05-22 | HPCI DECLARED INOPERABLE "At 1055 hours [CDT] on 5/22/2012, a through-wall leak was discovered on the Unit 2 High Pressure Coolant Injection (HPCI) inlet drain pot piping. This is a safety-related, ASME Code Class 2 piping. Dresden Technical Requirements Manual 3.4.a, Condition B requires the leak to be isolated which renders the HPCI system inoperable. The Unit 2 HPCI system was isolated and declared inoperable at 1141 CDT and Technical Specification 3.5.1 condition G was entered. "The event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-05-22
47946 | 0 | UNIVERSITY OF MICHIGAN HOSPITAL |  |  |  |  | 2012-05-17 08:00 | 2012-05-22 16:35 | 2012-05-22 | MEDICAL EVENT - PATIENT INJECTED WITH WRONG RADIOPHARMACEUTICAL AND QUANTITY A patient scheduled for a lymphoscintigraphy procedure was incorrectly injected with 25 milliCuries of Tc-99M Medronate instead of the prescribed 3 milliCuries of Tc-99 Sulphur Colloid. The cause of the event was human error. The patient and physician have been notified. The physician believes there will be no long term adverse effects due to this error. In order to prevent reoccurrence, the nuclear medicine staff will add this event to staff training to ensure that staff double check the label and the dosage and drug. Other options are still being assessed. The licensee also notified NRC Region 3 (Bob Gattone). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-05-30
47945 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-05-22 13:11 | 2012-05-22 16:33 | 2012-05-22 | MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "On Tuesday, May 22, 2012 at 1311 hours [EDT], with the reactor at approximately 35% core thermal power, during a planned power reduction to support thermal backwash of the main condenser, a manual reactor scram was inserted due to degrading main condenser vacuum. The cause of the degraded vacuum is currently under investigation. "Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. Standby Gas Treatment System Train 'B,' which is designed to shutdown 65 seconds after the Group II signal is received if the Standby Gas Treatment Train 'A' is in service, continued to operate until manually secured. With this exception, all other plant systems responded as designed. "Currently reactor pressure is being maintained at 920 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-Site power is being supplied to the station by the Start-up Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The NRC Senior Resident Inspector has been notified." The licensee has notified the Massachusetts Emergency Management Agency. | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-05-22
47944 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-04-29 | 2012-05-22 15:58 | 2012-05-30 | AGREEEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following notification was received via e-mail: "On May 21, 2012, the Arkansas Department of Health received email notification regarding a possible overexposure. The Radiation Safety Officer (RSO) for International Testing & Inspection Services, Inc. (ARK-773-03320) in Little Rock, Arkansas was reporting a 43.2 Rem exposure to a radiographer. "The licensee believes that on April 29, 2012, while performing radiographic operations at the permanent storage location, the radiographer may have lost or misplaced his personal dosimeter while setting up for the second exposure. Pocket dosimeter readings for the day of operations were negligible for the radiography crew. "The licensee was notified on May 16, 2012 by email by Landauer Inc. of the possible overexposure. The RSO opened the email and notified the Department by email on May 20, 2012. "The radiographer has been suspended from licensed activities pending the completion of an investigation by the licensee. The radiographer has been sent to his personal physician for a physical and blood work. "Radioactive Material Information: "Camera: Industrial Nuclear Company "Model: IR-100 "Serial Number: 4353 "Source Serial Number: R984 "Iridium-192 52.0 Curies "The Department will conduct an investigation. The licensee will provide an incident report. "Arkansas Incident Number: AR-2012-002" * * * UPDATE VIA EMAIL FROM JARED THOMPSON TO JOE O'HARA AT 1552 ON 5/30/12 * * * "On May 22, 2012, the Arkansas Department of Health conducted an investigation of the potential overexposure at International Testing & Inspection Services (ARK-773-03320) in Little Rock, Arkansas. "The investigation consisted of a review of statements made by the 3 man radiography crew, interview with the affected radiographer, review of equipment, and the results of the medical lab report. A review of the safety equipment issued to the radiography crew indicated that there had not been a significant exposure to the individual. The highest reading on the self reading dosimeters worn by the crew was 2 mRem. "A review of the medical lab results indicated normal white blood and red blood cell counts. The Department consulted with RE/ACTS concerning the medical lab results on May 25, 2012. "Based on the statement of the radiographer, the exposure measurement of self reading dosimeters, no abnormal surveys observed and the medical lab results, the Department has concluded that this is an overexposure to the personal monitoring device. "On May 25, 2012, the Department authorized the assignment of 500 mRem radiation dose for this radiographer for the wear period of April 2012. "The Department considers this incident to be CLOSED." Notified R4DO (Pick) and FSME EO (McDermott) THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 1 | 2012-05-30
47943 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-03-23 | 2012-05-22 13:02 | 2012-05-22 | AGREEMENT STATE REPORT - POTENTIAL OVER EXPOSURE DURING GAUGE REMOVAL The following information was received via email from the State of Colorado: "On May 21, 2012, the Colorado Department of Public Health and Environment was notified of an incident which occurred at Public Service Company of Colorado, Colorado License 032-01. The event occurred at the Hayden Station located in Hayden, CO on March 23, 2012. During boiler repairs, two contract workers removed six radiation level detector fixed gauges from an ash hopper without authorization. The gauges were discovered the following day by plant personnel, and it was noted that the shutters were in the open position. Each gauge, Texas Nuclear Model 5197, contained 100 mCi of Cesium-137. Based on dose reconstruction estimates provided by the licensee, it is likely that at least one of the contract workers received an exposure in excess of 2.0 mrem in one hour and up to 6.0 mrem in one hour. No other details are available at this time. "Event Report ID No.: CO12-I12-09" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-05-30
47942 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-05-22 02:49 | 2012-05-22 07:38 | 2012-05-22 | AUTOMATIC SCRAM DUE TO REACTOR PROTECTION SYSTEM BEING DE-ENERGIZED "At 0249 CDT on 5/22/2012, Unit 3 reactor automatically scrammed due to de-energization of Reactor Protection System (RPS) from actuation of 3A Unit Station Service Transformer (USST) differential relay 387SA, which resulted in a loss of 500KV power to Unit 3. This relay was picked up during a transfer of 4KV Unit Board 3C from alternate power (161KV) to normal power (3A USST). Investigation is in progress as to the cause of relay actuation. 500KV power was restored through the alternate feeder breakers from 161KV to all Unit 3 4KV Unit Boards successfully. 161KV remained available during the entire event. Loss of 500KV power lasted less than 30 seconds and power has been restored to all safety related boards. All Unit 3 diesel generators successfully started and tied to their respective 4KV Shutdown Boards. "All safety systems responded as expected to the loss of 500KV power. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. RCIC was manually started to control reactor water level. Primary Containment Isolation System (PCIS) and PCIS initiation signals for groups 1, 2, 3, 6 & 8 were received as designed. At the time of the scram, High Pressure Coolant Injection (HPCI) system was tagged out for removal of temporary instrumentation following planned maintenance. "This event is reportable within 4 hours per 10CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation'. It is also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-05-22
47941 | -1 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-05-22 06:35 | 2012-05-22 07:24 | 2012-05-22 | EMERGENCY PLANNING ZONE SIREN MALFUNCTION "The MCR [Main Control Room] at Limerick Generating Station was informed by PEMA [Pennsylvania Emergency Management Agency] that EPZ [Emergency Planning Zone] siren #129 located at Maryland and Western avenues in Chester County was sounding. The siren maintenance contractor was contacted to silence and repair the siren. No plant emergency exists. The siren activation was caused by an equipment malfunction. The remaining sirens in the EPZ remain functional. An 'Event of Potential Public Interest' will be issued for this problem." The NRC Resident Inspector, the State, and local officials will be notified of the siren malfunction. The state is expected to issue a press release. * * * RETRACTION AT 0758 ON 5/22/2012 FROM MARK ARNOSKY TO MARK ABRAMOVITZ * * * The siren was not an EPZ siren but rather a local fire house siren. Therefore, the licensee is retracting this event. Notified the R1DO (Trapp). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-22
47940 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2012-05-21 14:52 | 2012-05-21 18:35 | 2012-05-21 | AUTOMATIC REACTOR SCRAM RESULTING FROM A LOW CONDENSER VACUUM-TURBINE TRIP "At 1452 CDT on 5/21/2012 with the reactor at 100% power, River Bend Station experienced a reactor scram resulting from an RPS actuation. Following the scram, reactor water level briefly lowered below level 3. The reactor is stable with pressure and temperature being controlled by the feed water system and main steam bypass valves, respectfully. The cause of the scram was due to a turbine trip/low condenser vacuum. The low vacuum condition resulted from a loss of non-safety related 4160V switchgear that powers two of four circulating water pumps. "A suspected spurious Division II isolation of Reactor Core Isolation Cooling (RCIC) was observed. Restoration of RCIC to standby is in progress. "A report of a fire in a manhole was received shortly after the scram . Fire Brigade was dispatched and noted a small active fire in a cable tray. The fire was extinguished with fire extinguishers. Power cables are routed through this manhole. "The plant is conducting causal investigations to fully understand the cause of the turbine trip. As information becomes available, River Bend Station will provide additional information." All rods are inserted, and the plant is in a normal shutdown electrical lineup with the exception of NNS-Switchgear 2A being deenergized. Offsite assistance was not required to extinguish the fire. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-05-21
47939 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-05-21 15:30 | 2012-05-21 16:44 | 2012-05-21 | TSC TEMPORARILY OUT OF SERVICE FOR PLANNED MAINTENANCE "The Technical Support Center (TSC) fire protection sprinkler system was isolated and tagged out to perform planned maintenance. In conjunction with the sprinkler system being isolated, the charcoal filtered fan unit for the TSC ventilation was isolated. This prevents placing the TSC ventilation system in 'incident' mode; that is, the air cannot be re-directed through the charcoal filter in an event requiring the TSC atmosphere to be filtered due to an on-site release. The TSC ventilation system remains in service providing proper temperature control to maintain the facility habitable during normal operation; however with the 'incident' mode being unavailable, it may not remain habitable during all postulated scenarios and is, therefore, considered non-functional." The licensee notified the NRC Resident Inspector and will notify the Public Service Commission. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-21
47938 | 0 | HEMLOCK SEMICONDUCTOR, CORP |  |  |  |  | 2012-05-18 15:00 | 2012-05-18 22:34 | 2012-05-25 | STUCK OPEN SHUTTER ON FIXED MOUNTED PROCESS GAUGE The Radiation Safety Officer (RSO) reported a stuck open shutter on a fixed mounted process gauge. The gauge is Ohmart Vega American, Model SHLG2, with a Cs-137 5,000 mCi source. It was discovered that the shutter would not close during a routine shutter check. The shutter is normally open to support the manufacturing process and the failure of the shutter to close does not pose any personnel risk. The gauge will remain in service until a representative from the gauge manufacturer can repair the shutter. This repair should take place on May 30, 2012, when the manufacturer's representative is scheduled to repair other equipment at the site. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 1 | 2012-05-25
47937 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-05-18 14:15 | 2012-05-18 16:04 | 2012-05-18 | DISCOVERED A VULNERABILITY IN A SAFEGUARDS SYSTEM "On Friday, May 18, 2012 at 1415 [CDT], Monticello Nuclear Generating Plant discovered a vulnerability in a safeguards system. Appropriate measures are being taken by the site to compensate for the vulnerability under all conditions. Presently the condition does not exist. "The [NRC] Resident Inspector has been notified of the issue." The licensee will contact the State of Minnesota. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-05-18
47936 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-05-17 20:42 | 2012-05-18 15:57 | 2012-05-18 | FITNESS FOR DUTY A licensed operator employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access has been suspended. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2012-05-18
47935 | 0 | NEBRASKA DEPARTMENT OF HEALTH |  |  |  |  | 2012-05-17 14:31 | 2012-05-18 13:38 | 2012-05-18 | AGREEMENT STATE - POOL IRRADIATOR ROOF PLUG SENSOR FAULT "The RSO [Radiation Safety Officer] for the licensee said that an Assistant RSO called him after a [pool irradiator] roof plug fault had occurred and the source rack dropped to the shielded position. It was confirmed that the roof plug and roof cap were still in place, but the plug sensor located between the cap and plug had failed. There are two sensors that alarm if the plug was removed. One sensor is located inside the vault and the second sensor is between the cap and plug. The second sensor is the one that failed. The plant is installing a new sensor, located on the cap of the roof plug that will alarm if the roof cover is removed dropping the source rack." Nebraska State Report No. - NE-09-00X | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2012-05-28
47934 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-23 01:00 | 2012-05-18 12:50 | 2012-05-18 | ULTRASONIC EXAMINATION RESULTS IN AN INDICATION ON THE REACTOR PRESSURE VESSEL HEAD PENETRATION "On April 23, 2012, during the Braidwood Station Unit 1 refueling outage, it was determined that the results of planned ultrasonic (UT) examinations performed on one penetration (Penetration No. 69) did not meet the applicable acceptance criteria, requiring repair prior to returning the reactor pressure vessel head to service. A portion of the indication was conservatively assumed to be within the J-groove weld. At the time of the examination, the Braidwood Station Unit 1 reactor pressure vessel head was classified as a low susceptibility head. The cause of the recordable indication is attributed to Primary Water Stress Corrosion Cracking. The examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to ensure the structural integrity of the reactor pressure vessel head pressure boundary. All of the remaining penetrations have been examined during the current refueling outage. Repairs to Penetration No. 69 were completed prior to commencing startup. No other repairs were required. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as found indication did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." As a result of a follow-up review, at 0600 CDT on 05/18/12, the licensee determined this was an 8 hour reportable event while Unit 1 was in Mode 4. The licensee did not determine this was a reportable event immediately after the UT was conducted on April 23, 2012. The unit is currently in Mode 3. Reactor Vessel Head Penetration No. 69 is a control rod penetration. Reactor Coolant Leakage test are satisfactory and there are no indications of boron buildup on the Reactor Vessel Head. Control rod testing has not yet been performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-05-18
47933 | 0 | ND DEPARTMENT OF HEALTH |  |  |  |  | 2012-05-16 | 2012-05-18 10:19 | 2012-06-19 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA CRANKOUT GEARS LOCKED WITH SOURCE EXPOSED "On Wednesday May 16, 2012 at 1900 MDT, two Midwest Industrial X-Ray, Inc. radiographers had a reportable incident involving a radioactive material exposure device. The exposure device involved was a SPEC 150 SN:386 loaded with an Ir-192 sealed source model G-60 SN: TC1301. The activity level on 5/16/12 was 56 Ci (2072 GBqs). A SPEC Double Gear Control Assembly with red conduit was used for the drive cable. "The radiographers had made previous exposures during the day without incurring any equipment malfunction. At approximately 1900, the radiographers had 'cranked out' the source to make an exposure and upon retraction were unable to retract the source. The radiographers removed the cover plate of the control assembly and manually pulled the drive cables in order to retract the source back into the locked and shielded position. The sealed source was exposed for approximately 3 minutes. Caution Radiation Area cones were posted at 95 ft. from the source and no persons were inside the 2mR/hr zone. The drive cable was disconnected and no further exposures were made that day. The exposure device was inspected and was found to be in good working condition. "Corrective Actions: A set of SPEC single gear control assembly, yellow conduit drive cables were brought to the radiographers to replace the malfunctioning drive cables. The set of malfunctioning drive cables will be sent back to SPEC and traded in for a set of single gear control assembly/yellow conduit drive cables." * * * UPDATE FROM STATE OF NORTH DAKOTA VIA EMAIL AT 1046 EDT ON 6/15/12 * * * Source Production & Equipment Company (SPEC) was unable to replicate the failure using the returned gears. They did note that the gears offered a large amount of resistance, had impurities and that the drive cable was out-of-tolerance. Notified R4DO (Lantz) and FSME Events via email. * * * UPDATE FROM STATE OF NORTH DAKOTA VIA EMAIL AT 1148 EDT ON 6/19/12 * * * The final closeout report of event notification 47933 was provided. Notified R4DO (Miller) and FSME Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2012-05-25
47932 | 0 | BOEING LTS |  |  |  |  | 2012-05-16 16:00 | 2012-05-17 20:23 | 2012-05-17 | LOST IONIZER DEVICES During a review of records on May 10, 2012, the licensee was unable to account for 4 NRD Nuclecel In Line Ionizer model number P-2021 1000. A thorough sweep of the facilities was completed on May 16, 2012 at 1600 HST. The sweep failed to locate these devices and they were declared lost. The materiel involved were four devices, each containing 10mCi of Polonium-210 and encased in a steel pressure welded cylindrical case, each approximately 2.3 inches long and .5 inches in diameter. The circumstances under which the loss occurred were that one shipment of 2 devices (Serial Numbers: A2HE600A/A2HE601A) were last known to have been delivered to the licensee logistics center in August 2010 and there were no record of those two items having been returned to NRD, LLC. These two items were received from NRD on 7/8/2010. A second set of two devices (Serial Numbers: A2HT541/A2HT540) were last known to have been in a sealed package in the possession of a Boeing employee in March, 2012. These items were received from NRD on 7/14/2011. All devices are presumed lost and potentially disposed of as ordinary waste. The casing of all devices were known to be intact at the time of loss and no exposure has occurred. A thorough review of shipping records and site wide physical search have been conducted and failed to account for the devices. In the future, all such devices will be subject to the accountability rules, requirements, and procedures established by the USAF Bio-Environment office, Hickam Air Force Base, Honolulu, Hawaii. Internal company procedures will be updated to conform to the requirements of the USAF Bio-Environmental Office, Hickam Air Force Base. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-05-25
47931 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-17 11:26 | 2012-05-17 17:06 | 2012-05-17 | AREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State of California submitted the following information via email: "On May 17, 2012, at 1126 [PDT], [the licensee Assistant Radiation Safety Officer] ARSO of Ninyo and Moore, contacted the California Emergency Management Agency with a report of a theft of a Troxler Model 3430 moisture/density gauge, S/N 38771 (9 mCi Cs-137, 44 mCi Am:Be-241) in Moreno Valley, CA. This occurred between 1000 and 1030 [PDT]. The ASRO stated that the gauge operator arrived at the construction site and unlocked and opened the tailgage/hatch on their Nissan Armada SUV and then walked away approximately 15 feet to speak with the site manager to find out where to make the measurements. The gauge was still inside the gauge transport case with two locks and a trigger lock. The case was tied down to the inside of the vehicle, but was not secured to the frame of the vehicle. While the gauge operator was speaking with the site manager, an older model black sedan (make and model unknown and did not have a license plate) stopped next to SUV and an unknown individual exited the sedan, grabbed the gauge case out of the SUV, placed the gauge case in the sedan and then left the scene before anyone could stop the theft. The gauge operator then contacted their office to report the theft. The Moreno Valley Police and Cal EMA were also notified. The Moreno Valley Police then arrived to investigate (Police report #MZ121380120). "At approximately 1215 [PDT], [the California State Department of Public Health, Senior Health Physicist] spoke with the ASRO about the incident. [The ASRO] confirmed the information in the previous paragraph. [The ASRO] also stated that the measurements were to be taken of the asphalt/concrete of the sidewalk on the side of the road, which allowed the public easy access to the vehicles at the site. When asked about the security of the gauge, [the ASRO] stated that the gauge case had two locks and a the gauge had a handle lock. The gauge case was tied down inside the vehicle, but was not locked or secured otherwise. During transport, the tailgate is locked, securing the gauge inside the SUV. When asked if the vehicle had an alarm, [the ASRO] stated that he was not sure, but the vehicle did have a Lojack tracking device installed. The ASRO was informed that a written report was required within 30 days and that a newspaper ad with a reward and description of the stolen item be placed in a local paper. The ASRO was also informed that the gauge operator should be writing a statement and that the most current leak test should be submitted to [State] office. [The ASRO] stated that his [Radiation Safety Officer] RSO was currently working on those items. When asked if anyone had attempted to search the immediate area in an attempt to locate the gauge or the vehicle, [the ASRO] stated that they were going to have some of their employees search the local neighborhood in the afternoon. "The licensee will be cited for leaving the gauge unattended. Any other citations will be deferred until the licensee has submitted the 30-day report and the investigation has been completed by this office. As of the time of this report, the gauge has not been recovered." California Incident 5010 Number - 051712 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-05-25
47930 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-05-17 04:38 | 2012-05-17 12:11 | 2012-05-17 | EMERGENCY OPERATIONS FACILITY NON-FUNCTIONAL DUE TO FAILED RETURN FAN "At 0438 [CDT] on Thursday, May 17, the Callaway Plant Emergency Operations Facility (EOF) was declared non-functional when the building's return fan was found not running. Loss of the EOF return fan, results in an inability to maintain a positive pressure on the facility. Efforts are underway to return this fan to service. "If an emergency is declared requiring EOF activation while the EOF is non-functional, EOF emergency response personnel will report to their backup locations in accordance with Callaway Plant emergency planning procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the unavailability of an emergency response facility. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BRANDON LONG TO JOHN SHOEMAKER ON 05/17/12 AT 1704 EDT * * * At 1330 (CDT) on 05/17/12, the Callaway Plant EOF was been returned to service. The licensee will notify the NRC Resident Inspector. Notified R4DO (Powers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-17
47929 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-05-11 00:40 | 2012-05-17 09:25 | 2012-05-17 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-05-17
47928 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-05-16 22:10 | 2012-05-17 01:05 | 2012-05-17 | STATE NOTIFICATION OF POTENTIAL CHLORINE DISCHARGE TO THE DELAWARE RIVER "At 2210 [EDT] it was reported to the State of New Jersey that a permitted discharge exceeded Total Residual Chlorine permit level of 0.3 ppm. Actual Total Residual Chlorine discharged was 3.0 ppm. Currently the amount of the discharge is unknown and the event is under investigation. The discharge has been terminated and no personnel injury resulted form this event. The discharge originated from a tank overflow from the Chemical Treatment Building that entered the storm drain system that discharges to the Delaware River via a permitted outfall. "No safety related equipment was impacted by this event. "The report to the State of New Jersey Department of Environmental Protection was made in accordance with the Salem Station Spill/Discharge Reporting Plan." The licensee estimates that the discharge occurred between 2010 and 2135 EDT on 5/16/2012 and that less than 1000 gallons overflowed the clarifier. The licensee will notify the NRC Resident Inspector and has notified the State and Lower Alloways Creek Township. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-17
47927 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-05-16 21:00 | 2012-05-16 21:06 | 2012-05-16 | PRESS RELEASE REGARDING STATUS OF ONGOING LABOR NEGOTIATIONS "On May 18, 2012, at 2100 [EDT] hours and the reactor at 100% core thermal power the following press release is being issued by Entergy Nuclear regarding the status of the ongoing labor negotiations. "Plymouth, Mass -- Entergy Nuclear, the owner and operator of the Pilgrim Nuclear Power Station in Plymouth, Mass. said today that the company remains focused squarely on plant safety as a negotiating team works toward a four-year contract with plant workers that reflects the realities of the competitive electric power business and fairly compensates the workforce. The contract with the Utility Workers Union of America Local 369 covers approximately 240 production and maintenance/office technical and professional workers out of a total workforce of about 650 employees at the plant. The contract expired May 15 without final resolution. Plant management directed workers covered by the contract in non-essential positions to remain at home Wednesday with full pay with benefits and insurance pending further progress on the contract. It is not a lockout. The management decision to temporarily limit the workforce at the plant is in the interest of safety. The company remains prepared to implement contingency plans in the event of a strike by the union members. Those plans assign routine tasks to other pre-qualified workers in roles that ensure continued safe operations. "The Resident Inspector staff is onsite and has been informed of this press release and notification. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi)." The company feels they have adequate numbers of pre-qualified workers available to fill necessary positions to ensure continued safe operations. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-16
47926 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-05-05 | 2012-05-16 19:15 | 2012-05-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA POTENTIALLY FAILED TO FUNCTION CORRECTLY The State of California submitted the following information via email: "On May 9, 2012 [a licensee employee] reported that on May 5, 2012, the RSO of Testing Engineers. Inc. (TEI) had damaged the pigtail attachment of an INC IR100 radiography camera. The incident took place at Apple in Cupertino. In addition [the licensee employee] indicated that [name withheld] did not remove the camera from service and told TEI personnel to go ahead and use the camera on 5/7/12 even though the pigtail failed the go no go gauge test. On Tuesday May 8, 2012, [the licensee employee] red tagged the camera out of service when it failed the go no go test." CA 5010 number: 050912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 1 | 2012-05-25
47925 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2012-05-11 | 2012-05-16 17:45 | 2012-05-16 | AGREEMENT STATE REPORT - FRONT END LOADER RAN OVER A PORTABLE NUCLEAR GAUGE The following information was received from the State of Washington via email: On 5/11/2012 a front end loader ran over a Troxler moisture density gauge. The gauge contained a 0.37 GBq Cs-137 source and a 1.85 GBq Am-241 source. The cause was identified as inattention to detail. WA Item: WA12034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2012-05-25
47924 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-05-15 07:20 | 2012-05-15 10:39 | 2012-05-15 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "The Farley Nuclear Plant Technical Support Center (TSC) has been rendered non-functional due to a pre-planned and scheduled maintenance period to perform PMs [Preventive Maintenance] on the TSC ventilation system. The TSC ventilation maintenance will be worked with high priority to include around the clock support. Pre-planned compensatory measures are in place in accordance with site procedures to include the conditional relocation of the TSC staff should the Emergency Director deem the TSC to be uninhabitable. "This report is being generated per Technical Requirements Manual TRM section 13.13.1 condition B for the TSC emergency response facility being out of service for greater than 30 minutes. The projected return to service is on 5/15/12 at 16:30 CDT." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-15
47923 | 0 | SHAW GROUP INC. |  |  |  |  | 2012-05-14 | 2012-05-14 14:46 | 2012-05-14 | THREADING DEVIATIONS ON STEEL REINFORCING BAR SUPPLIED TO CONSTRUCTION PROJECTS This report was supplied for informational purposes. The threaded ends of some of the reinforcing bar supplied to the V.C. Summer Units 2 and 3 and the Vogtle Units 3 and 4 nuclear projects were found to have threads too long or too short, double threaded areas, voids in threads, or an incorrect thread profile. "The results of evaluations of this condition as documented by Shaw Nuclear and conducted in accordance with the procedure for performing evaluations required by 10 CFR 21.21, have concluded that the deviations in the rebar would not create a substantial safety hazard, if they were to remain uncorrected. Therefore, it has been determined that these deviations are not reportable under the requirements of 10 CFR Part 21. This information is being provided for industry awareness of the occurrence of these types of deviations in reinforcing steel being provided as a basic component." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-05-14
47922 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-05-14 10:24 | 2012-05-14 13:45 | 2012-05-14 | OFFSITE NOTIFICATION DUE TO OIL SHEEN OBSERVED ON DIFFUSER POND "On 05/14/2012 at 1024 EDT, a notification to the National Response Center was made as a result of an oil sheen on waters of the U.S. (Sequoyah's Diffuser pond). The discharge from an onsite pond was isolated stopping what appears to be the source of oil to the diffuser pond. The source of leakage is still under investigation. "The following additional agencies have also been notified: "EPA Region 4, "Tennessee Department of Environment and Conservation (TDEC), and "Tennessee Emergency Management Agency (TEMA). "Oil is maintained onsite, [and] no oil has been discharged to the river. Cleanup is in progress. The licensee notified the NRC Resident Inspector. Notified DOE (Turner), EPA (Post), USDA (Beverly), HHS (Emerson), and FEMA (Casto). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-14
47921 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-05-14 03:00 | 2012-05-14 11:02 | 2012-05-14 | TECHNICAL SUPPORT CENTER OUT-OF-SERVICE DUE TO PLANNED MAINTENANCE "At 0300 PDT on 5-14-2012, planned maintenance was started on the Technical Support Center (TSC) HVAC system. The scope of work is to replace the carbon tray gaskets and perform carbon filter testing. The duration of this scheduled maintenance is planned for 26 hours. "This condition represents a major loss of emergency preparedness capability per 10 CFR 50.72(b)(3)(xiii) in that the TSC habitability might not be sustainable during events due to the inability of the filtration system to maintain a habitable atmosphere. Station procedures provide instructions to relocate the TSC if monitoring during an emergency event indicates habitability cannot be maintained. Compensatory measures are in place to heighten awareness of responsible TSC staff following ERO activation to monitor TSC habitability in accordance with procedures and to consider TSC relocation as necessary as described in the station emergency plan." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-14
47920 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-05-12 20:15 | 2012-05-13 01:00 | 2012-05-13 | HVAC FOR TECHNICAL SUPPORT CENTER OUT OF SERVICE "The facility Technical Support Center (TSC) was rendered non-functional due to the TSC HVAC Air Handling Unit (AHU) ventilation system being out of service. Investigation into the cause of the failure of the TSC ventilation AHU found a tripped supply breaker. The supply breaker was subsequently reset and the TSC HVAC unit placed back in service. "This report is being generated per TRM bases 13.13.1 condition B for the TSC emergency response facility being out of service for greater than 30 minutes. The total out of service time was 44 minutes." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-13
47919 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-05-11 16:03 | 2012-05-11 21:27 | 2012-05-11 | LOSS OF CONTROL ROOM FLOOR COOLING "At 16:03 hours on 5/11/12, Susquehanna Steam Electric Station Unit 2 entered LCO 3.0.3 due to two control room floor cooling systems being inoperable. "A discharge damper for the 'A' train of control room floor cooling had failed earlier during the same day at 05:23 hours, rendering the associated 'A' fan inoperable. The redundant 'B' train fans and associated Control Structure Chiller automatically started as a result of a fan low flow interlock. The 'A' train logic was left in 'Start' and the 'B' train logic was left in 'Auto' as directed by an alarm response procedure. "During application of a clearance order for repair of the failed 'A' fan damper, the 'A' control room cooling fan switch was placed in 'Stop' position. This resulted in an automatic start of the 'A' Control Structure Chiller and all the associated 'A' fans except for the control room cooling fan, and a trip of the 'B' train fans and chiller. This condition caused a loss of both control room cooling fans. "The control room operators immediately recognized the loss of cooling and took manual action to restart the 'B' train. "LCO 3.0.3 was exited at 16:18 hours without a reactor power reduction. This condition is reportable as loss of entire safety function under 10CFR50.72(b)(3)(v) & (vi)." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-05-11
47918 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2012-05-09 | 2012-05-11 12:34 | 2012-05-11 | MISSING TRITIUM EXIT SIGN The following report was received via email from the State of Nebraska Division of Radioactive Materials: "Adams Land and Cattle reported that they have a missing [tritium] exit sign. The sign was purchased in January of 2007 from SRB Technologies. We do not have the serial number at this time. "They discovered that it was missing when doing the annual inventory. The sign may have been broken several months ago and was likely disposed of in the regular trash. The trash is taken to the Custer County landfill. The general licensee is checking with the employee who disposed the sign and trying to find out additional details. "We will report additional information once the general licensee has additional information. "Source/Radioactive Material: SEALED SOURCE LUMINOUS "Manufacturer: SRB TECHNOLOGIES INC "Model Number: BX-10-WH "Radionuclide: H-3 "[Activity]: 9.21 Ci, 340.77 GBq" Incident Number: NE120001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2012-05-21
47917 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2012-05-11 05:15 | 2012-05-11 09:20 | 2012-05-11 | BRIEF LOSS OF THE EMERGENCY NOTIFICATION SYSTEM PHONE "At approximately 0515 EDT today, Seabrook experienced a brief loss of the Emergency Notification System (ENS). The ENS was inoperable for approximately four minutes due to an unknown cause. During this time, commercial telephone lines were available as a means of communication with the NRC. A subsequent communications check using the ENS phone was satisfactory. "This event is being reported as an eight-hour notification in accordance with 10CFR50.72(b)(3)(xiii) for a loss of offsite ENS communications capability. Investigation into the cause continues and will be documented via the corrective action process." The licensee has notified the NRC Resident Inspector. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-11
47916 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-05-10 10:20 | 2012-05-11 09:21 | 2012-05-11 | UNPLANNED MEDICAL TREATMENT OF WORKER "On 05/10/12, approximately at 1020 CDT, a person working in the Feed Materials Building injured his foot while drumming off green salt. The employee received first aid treatment in the on-site dispensary. The individual was found to have contamination on his plant coveralls and boots. The employee was decontaminated and transported to an off-site medical facility. The employee was appropriately exit monitored and there was no detectable contamination on the employee when he left the site. Contamination on the employees right boot was 26,664 dpm/100cm2." The chemical was Uranium Ore Concentrate. The licensee has notified NRC Region 2 (Richard Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-05-11
47915 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2012-05-11 03:55 | 2012-05-11 07:07 | 2012-05-11 | MANUAL REACTOR TRIP DUE TO FEEDWATER CONTROL VALVE FAILURE "On May 11, 2012, a failure of the High Power Feed Regulating Valve FCV-9011 resulted in '2A' S/G water level lowering. Manual operator control of the Main Feed Regulating system was unsuccessful in stabilizing S/G water level. '2A' S/G level lowered to the procedurally required manual reactor trip criteria. The crew inserted a manual trip. All CEAs fully inserted into the core. Following the trip, Auxiliary Feedwater actuated as designed and decay heat removal was via Auxiliary Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently, Unit 2 is maintaining pressurizer pressure at 2250 psia, temperature at 532 degrees F on Main Feedwater (using Low Power Feed Regulating Valves LCV-9005/9006) and Steam Bypass Control. 'Unit 1 was unaffected and remains in Mode 1 at 29% power. "This event is reportable pursuant to 10CFR50.72(b)(2)(iv)(B) for the Reactor Trip, as well as 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Auxiliary Feedwater)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-05-11
47914 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-11-01 | 2012-05-10 15:48 | 2012-05-10 | FLORIDA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO PATIENT "Patient presents in May, 2012 with a 1 cm x 3 cm oval necrotic tissue [on the] inner thigh consistent with radiological overexposure. Patient received radiation treatment in November, 2011 at the incident hospital. Hospital physicist and the RSO [are] investigating the incident and calculating whole body/skin dose based on assumption of released source scenario." Incident Number: FL12-043 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-05-18
47913 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-05-10 11:00 | 2012-05-10 10:29 | 2012-05-10 | SAFETY PARAMETER DISPLAY SYSTEM AND EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE "Beginning at approximately 1100 hours EDT on May 10, 2012, plant personnel will be taking the plant integrated computer system (ICS) out-of-service for planned maintenance. During the time ICS is out-of-service, the Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. The computer outage is scheduled for two hours. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up by the Private Branch Exchange, Off Premise Exchange, and various redundant intrafacility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out-of-service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). A follow-up notification will be made when the maintenance activities are completed and the equipment is restored. The NRC Resident Inspector has been notified." * * * UPDATE AT 1245 EDT ON 5/10/12 FROM MORSE TO HUFFMAN * * * The maintenance activities were completed as scheduled and the integrated computer system and associated systems SPDS, ERDS and CADAP has been returned to service as of 1238 EDT. The licensee will notify the NRC Resident Inspector. R3DO (Giessner) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-10
47912 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2012-05-09 | 2012-05-10 10:25 | 2012-05-10 | AGREEMENT STATE REPORT - STOLEN RADIOACTIVE GAUGE The following information was received from the State of New York via fax: "As required by 10NYCRR16.15(a)(1)(ii), Callanan Industries in Ravena, NY called to report a stolen gauge. The gauge is a BSI Instruments model NW-201 gamma gauge. It contains 0.3 mCi of Cesium 137 in sealed form. The gauge was removed from its location above a conveyor line and stored in a container in a warehouse in 2011. At some point in October of 2011 several items of copper were stolen from that warehouse. It is now believed that the gauge was also stolen at that time. Callanan Industries will submit a written report as required under 16.15(a)(2). NYS BERP [Bureau of Environmental Radiation Protection] will review recent reports of scrap metal yard monitor trips. Local police have been notified. A press release has not been issued. A reward has not been offered. NYS BERP internal tracking number for this incident is #970." NY Event Report ID No. NY-12-01 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2012-05-18
47911 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2012-05-08 16:16 | 2012-05-09 08:42 | 2012-05-15 | AUTOCLAVE HIGH PRESSURE ISOLATION SYSTEM FAILURE "At 1616 CDT, on 05-08-12 the Plant Shift Superintendent (PSS) was notified that C-360 (Toll Transfer & Sampling Building) Autoclave #2 had a failure in the Autoclave High Pressure Isolation System [AHPIS]. [AHPIS] is designed to: 1) prevent a cylinder failure inside the autoclave as a result of overheating; and 2) mitigate releases to the atmosphere from releases inside the autoclave. Autoclave containment is required to be operable per TSR 2.1.3.1 while the autoclave is in TSR modes 3 (containment), 4 (autoclave closed), and 5 (autoclave heating). On 5/08/12 at 1610 CDT an operator noticed water flowing from the autoclave head to shell sealing surface on the #2 autoclave in C-360 while a cylinder was being heated (TSR mode 5 - autoclave heating). The PSS was notified of the loss of containment at 1616 CDT and the [AHPIS] was declared inoperable. The steam cycle was interrupted and the autoclave was placed in a non-applicable TSR mode at 1657 CDT. No release of UF6 occurred due to the failure of the [AHPIS]. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand; and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-12-1195; PGDP Event Report No. PAD-2012-02; Responsible Division: Operations" * * * UPDATE FROM BILLY WALLACE TO DONALD NORWOOD AT 1640 EDT ON 5/9/2012 * * * After further review the licensee determined that additional reportability criteria were met as described below: "At 1616 on 05/08/2012, the PSS was notified that C-360 Autoclave #2 had water flowing from the autoclave head to shell sealing surface indicating a potential failure in the Autoclave High Pressure Isolation System (AHPIS) containment, which is relied on as an engineered control in NCSE 042 (SRI 5.5.3). The AHPIS is designed to minimize leaks to atmosphere from the autoclave under maximum pressures resulting from a UF6 release from the cylinder, valve or pigtail in the autoclave. The maximum acceptable leak rate for the autoclaves is 12 SCFM at a minimum test pressure of 90 psig or a 10 psi pressure drop in 1 hour. In order to determine if the AHPIS would have met its safety function, a pressure decay test will be performed. However, the pressure decay test will not be performed within 24 hours of discovery. Therefore, it is conservatively assumed that the leak discovered is greater than 12 SCFM or greater than 10 psi pressure drop in 1 hour; resulting in a 24 hour NCS reportable event. When the leak was noticed, the heat cycle was interrupted and the autoclave placed in a safe configuration. No release of UF6 had occurred in the autoclave when the leak out the autoclave was found. "This event is reportable as a 24 hour event in accordance with 24-Hr. NRC BL 91-01 Supp. 1. This is a criticality safety event in which violations involving operations that comply with the double contingency principle and do not meet the criteria for a 4-hr report, but still result in a violation of the double contingency principle, such as, events where the double contingency principle is violated but control is immediately reestablished. "Safety Significance of Events: --While an NCSA control was not maintained resulting in the potential autoclave leak rate being exceeded, a release of fissile material from a cylinder in the autoclave did not occur and therefore a criticality was not possible. "Potential Criticality Pathways Involved: --In order for a criticality to be possible, a cylinder, valve, or pigtail of a fissile cylinder would have to fail and release greater than a safe mass of fissile material into the autoclave and the autoclave containment would have to fail allowing a large release to atmosphere of uranium and settle out in an unfavorable geometry with sufficient moderator present. "Controlled Parameters: --The first leg of double contingency is based on mass. --The first leg of double contingency is based on administrative and design controls to ensure that it is unlikely to have a large release of UF6 from the cylinder, valve or pigtail in the autoclave while healing the cylinder. --The second leg of double contingency is based on geometry moderation. "Estimated Amount, Enrichment, Form of Licensed Material: --No leakage of UF6 occurred. "Nuclear Criticality Safety Control(s) or Control System(s) and Description of the Failures or Deficiencies: --The first leg of double contingency is based on mass. --The first leg of double contingency is based on administrative and design controls to ensure that it is unlikely to have a large release of UF6 from the cylinder, valve or pigtail in the autoclave while heating the cylinder. This control was maintained. --The second leg of double contingency is based on geometry / moderation. --Small leaks out of the autoclave to atmosphere are considered normal case and the Autoclave High Pressure Isolation System ensures containment to minimize a significant release to atmosphere if a release occurs in the autoclave during heating. The AHPIS ensures that the maximum leak rate from the autoclave will not exceed 12 SCFM or a maximum acceptable pressure drop of 10 psi in 1 hour. If the containment leak rate is maintained, only a small amount of uranium could leak to atmosphere and the uranium would form in thin layers on surfaces in a geometrically safe configuration. Also there would be insufficient uranium to leak outside of the building; therefore there would not be a sufficient source of moderation. Since this control is assumed to have failed, uranium could leak out of the autoclave to atmosphere if a large release of UF6 occurred in the autoclave and potentially deposit in geometrically unfavorable configurations in areas where sufficient moderators exist. Since the leak rate cannot be confirmed within 24 hours, it is conservatively assumed that the geometry moderation parameter was lost and double contingency was not maintained. "Corrective Actions To Restore Safety Systems and When Each Was Implemented: --Perform a pressure decay test on Autoclave #2 according to procedures and if the leak rate is determined to be greater than 12 SCFM or 10 psi in one hour, repair AHPIS prior to heating another cylinder containing uranium. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-12-1195; PGDP Event Report No. PAD-2012-03; Responsible Division: Operations." Notified R2DO (Freeman) and NMSS EO (Campbell). * * * RETRACTION FROM DAVID PETTY TO DONG PARK AT 1403 EDT ON 5/15/2012 * * * "Subsequent to the above notifications on May 10, 2012, autoclave no. 2 was subjected to a pressure decay test in the as-found condition. The test indicated that the High Pressure Isolation Safety System would have been capable of performing its intended safety function if called upon on May 8, 2012, during the heat cycle subject of the event reports. Thus, the event was not required to be reported under 10CFR 76.120(c)(2)(i) and the notifications may be retracted. "Subsequent to the above notifications on May 10, 2012, autoclave no. 2 was subjected to a pressure decay test in the as-found condition. The test indicated that the High Pressure Isolation Safety System would have been capable of performing its intended safety function if called upon on May 8, 2012, during the heat cycle subject of the event reports. The pressure drop from the as-found test was less than the maximum allowable pressure drop for the system required for criticality safety. Thus, the event did not meet the criteria to be reported under 24-Hr. NRC BL 91-01 Supp. 1." The NRC Senior Resident Inspector has been notified of this event. Notified R2DO (Shaeffer) and NMSS EO (Guttmann). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | RESPONSE-BULLETIN | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2012-05-09
47910 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-05-08 11:14 | 2012-05-08 19:09 | 2012-05-08 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "On 5/8/2012 at 1114 EDT, maintenance informed the Control Room that a fan blade on one of the Technical Support Center (TSC) ventilation compressors had failed, causing the fan and motor to become unstable. As a result, Operations secured TSC ventilation and declared the TSC non-functional. "The on-call Emergency Response Manager and Site Emergency Coordinator were notified and the alternate TSC remains available. "The affected unit has been isolated and TSC ventilation re-started and declared functional as of 1900 EDT on 5/8/2012." The license will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-08
47909 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-05-08 09:00 | 2012-05-08 17:06 | 2012-05-08 | AN UNANALYZED CONDITION COULD DELAY TRANSFER TO EMERGENCY DIESEL GENERATORS UNDER CERTAIN POSTULATED CONDITIONS "At 0900 [CDT] on May 8, 2012, it was determined that Monticello Nuclear Generating Plant did not meet Technical Specification Limiting Condition for Operation 3.3.8.1 because the requirement of Table 3.3.8.1-1 for the 4.16 KV Essential Bus Degraded Voltage time delay transfer to the Emergency Diesel Generators [EDGs] of 9.2 seconds could not be met under all postulated conditions. The degraded transfer scheme has the ability to transfer to an intermediate offsite source (1AR) which under a degraded voltage condition, coincident with an accident, would delay the transfer to the EDGs an additional 5 seconds. Both EDGs were subsequently declared inoperable." As an interim action 1AR transformer has been removed from service. This eliminates the unanalyzed condition, restores Technical Specification compliance, and restores both EDGs to an operable condition. Additionally this event is being reported under criteria 10 CFR 50.72(b)(3)(v)(D) - Accident Mitigation. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2012-05-08
47908 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2012-05-08 07:30 | 2012-05-08 15:55 | 2012-05-08 | IMPROPERLY ANALYZED CONDITION "This plant condition is being reported under 10CFR70, Appendix A criterion (b)(1), 'Any event or condition that results in the facility being in a state that ... was improperly analyzed ... and which results in a failure to meet the performance requirements of 10CFR70.61.' "AREVA's conclusion that such a condition exists at the AREVA Richland facility is based on an NRC issued letter dated May 7, 2012 from John D. Kinneman to Janet R. Schlueter which among other things states: "'It is not acceptable, however, to conclude that a process does not need IROFS because an event is 'not credible' due to the characteristic provided by some other controls or features of the plant that are not IROFS.' "Based on this NRC position, AREVA did not adequately analyze the facility (in accordance with the May 7th position) because unacceptable consequences resulting from some process upsets were determined to be 'not credible' based on plant conditions or features that were not declared as IROFS. "For example, an accidental criticality accident resulting from a solution leak onto the floor was declared not credible because gravity would cause the leak to spread out on the floor into a safe geometry. However, the floor was not declared an IROFS. Another example is that accidental criticality in a 1-inch diameter pipe was declared 'not credible' due to the geometry of the pipe and no credible mechanism being identified that could cause the pipe to balloon into an unfavorable geometry, yet the pipe diameter was not declared an IROFS. Other similar conditions exist at the Richland facility. "Therefore, AREVA Richland has concluded that the NRC approved ISA does not meet the performance requirements of 10CFR70.61(e). However, the safety significance of this technical non-compliance is considered to be low because all proposed changes to the facility are evaluated for potential impact to the facility ISA before they are made. These changes are reviewed and approved by a diverse group of people including staff who is familiar with the safety basis for each process system and the 10CFR70.72 change control requirements and will not authorize changes that could invalidate the safety basis. "Additionally, although these items are not individually identified as IROFS, the ISA summary on pg. 7-9 states: "'... the following general criticality safety program elements are considered IROFS, albeit that they differ from other listed IROFS in that although they are key to safety, they are not always individually identified and used in specific accident sequences: "-- equipment dimensions and materials forming the basis for a nuclear criticality safety analysis (NCSA); and "-- bounding assumptions used in an NCSA'." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-05-08
47907 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2012-03-13 16:04 | 2012-05-08 12:33 | 2012-05-08 | 60-DAY OPTIONAL REPORT - INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Unit 2 Primary Containment Isolation System (PCIS). On 3/13/12, at approximately 1604 hours, Unit 2 experienced an invalid PCIS partial isolation. An equipment operator was in the process of making an adjustment to the Reactor Protection System (RPS) MG Set output voltage during daily rounds. As the rheostat was beginning to be rotated to increase the voltage, output voltage quickly dropped below the MG Set undervoltage trip setpoint. The BC757B and BC757D MG Set output breakers opened, resulting in the loss of the 2B RPS bus causing a half scram. The half scram signal resulted in closure of the instrument nitrogen primary containment isolation valve, secondary containment normal ventilation isolation valves and start of the 'B' Standby Gas Treatment supply fan. "The invalid PCIS isolation was a result of the failure of the voltage adjustment rheostat for the MG Set output voltage. "This issue has been entered into the site Corrective Action Program (AR 1340452) for evaluation and implementation of further corrective actions. The NRC Resident Inspector has been informed of this notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-05-08
47906 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-05-07 12:12 | 2012-05-08 08:49 | 2012-05-08 | CONTAMINATED INJURED PERSON "An employee received a laceration on the bridge of his nose when removing a respirator. He went into the onsite medical dispensary where the nurse cleaned the wound and applied a bandage. The employee had been working in the Feed Materials Building. He was donning PPE [Protective Personal Equipment] in the cooling shack on the 6th floor. There was approximately 33,000 dpm/100cm? contamination on the bottom of the employee's plant issued shoes. The employee returned to work following the treatment." The licensee notified the Senior NRC Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-05-09
47905 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-05-07 23:57 | 2012-05-08 08:16 | 2012-05-08 | PRESSURE BOUNDARY LEAKAGE "On May 7, 2012, at 2357 CDT, with the plant in MODE 3 at normal operating temperature and pressure, leakage from a transmitter manifold test valve diaphragm seal was determined to be pressure boundary leakage per TS 3.4.13. The manifold test valve is associated with pressurizer pressure transmitter PT-430. It has been determined that the most likely cause of the leakage is a cracked manifold diaphragm and that this is classified as part of the Reactor Coolant System Pressure Boundary per 10 CFR 50.2. "This condition is being reported under 10 CFR 50.72(b)(3)(ii)(A) because the defect is associated with the Reactor Coolant Pressure Boundary. "Isolation and repair of the leakage is being pursued. "The licensee has notified the NRC Resident Inspector." The licensee closed the root isolation valves for the pressure transmitter to allow repair of the diaphragm, however there is still leakage past these valve. This leakage is quantified as a few drops per minute. * * * RETRACTION FROM MIKE TERRY TO DONALD NORWOOD AT 1552 EDT ON 5/8/2012 * * * "On May 8, 2012, EN #47905 provided notification of leakage from a pressurizer manifold valve that was potentially pressure boundary leakage. Since the leak could not quickly be determined to be otherwise, it was conservatively reported as pressure boundary leakage. "Subsequent investigation and evaluation determined that the identified leakage originated from the mechanical components of the valve and not the pressure boundary. "The leak has been isolated and the affected manifold valve is being repaired. "Therefore, the leakage did not constitute pressure boundary leakage and this condition did not meet the reportability criteria identified in 10CFR50.72. "As a result, the notification made on May 8, 2012 is hereby retracted. "The NRC Resident Inspector has been notified." Notified R3DO (Giessner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-05-08
47904 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-05-07 08:47 | 2012-05-07 20:50 | 2012-05-07 | VIOLATION OF FITNESS FOR DUTY PROGRAM A non-licensed contractor employee supervisor was found in violation of the Fitness for Duty Program. The individual's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2012-05-07
47903 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-05-07 12:39 | 2012-05-07 16:31 | 2012-05-07 | TONE ALERT RADIO SYSTEM OUTAGE "At approximately 1239 CDT on 5/7/2012, Cooper Nuclear Station was informed by the National Weather Service that the Shubert radio transmission tower was not working. This affected the tone alert radios Cooper Nuclear Station provides to members of the public to notify them of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10 CFR 50.72(b)(3)(xiii). "Local county authorities within the 10 mile EPZ have been notified of the condition of the tower and the affect on the tone alert radios and will utilize Local Route Notification (backup notification method). "At approximately 1356 [CDT], the National Weather Service reported that the Shubert radio transmission tower had been restored to service." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-07
47902 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-05-07 12:33 | 2012-05-07 16:16 | 2012-05-07 | INADVERTENT EMERGENCY SIREN ACTUATION "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi). On May 7, 2012, at approximately 1233 hours [EDT], an inadvertent actuation of the Perry Nuclear Power Plant's alert notification system occurred. Twenty of the seventy-six total sirens sounded for three minutes affecting Ashtabula, Geauga, and Lake Counties. Following the actuation the county agencies received calls from members of the public. "A successful quiet test of the sirens had been conducted earlier in the day (at approximately 0830 hours [EDT]). At this time, all sirens are functioning correctly. The siren actuation was not related to any condition or event at the Perry Nuclear Power Plant. The actuation signal originated from the Lake County Emergency Operations Center while thunderstorms were passing through the area. Additional investigation is in progress to determine the cause of the inadvertent actuation. At the time of the event, the plant was in Mode 1 at 100 percent rated thermal power. "Lake County officials plant to issue a press release. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-07
47901 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-05-06 09:35 | 2012-05-06 20:53 | 2012-05-06 | OFFSITE NOTIFICATION MADE FOR NPDES NONCOMPLIANCE "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi). On May 6, 2012, during daily chlorination activities, it was identified that the National Pollutant Discharge Elimination System (NPDES) permit limit for Total Residual Chlorine was exceeded between approximately 0935 hours [EDT] and 0947 hours [EDT] when the noncompliance was corrected. The maximum measured value was 0.29 mg/L, which exceeded the NPDES Maximum Concentration Limit of 0.2 mg/L. "On May 6, 2012, at approximately 1930 hours [EDT], a 'Noncompliance Notification for Exceedance of a Daily Maximum Discharge Limit' was made to the Ohio Environmental Protection Agency. The cause of the NPDES permit noncompliance is under investigation. Chlorination evolutions have been suspended pending investigation results. At the time of the event, the plant was in Mode 1 at 100 percent rated thermal power. "This event is also being reported in accordance with the plant's operating license, appendix B, Environmental Protection Plan, which states, in part, that any occurrence of an unusual or important event that indicates or could result in environmental impact causally related to plant operation shall be recorded and reported to the NRC within 24 hours followed by a written report." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-06
47900 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-05-04 10:00 | 2012-05-04 16:20 | 2012-05-04 | CONTAINMENT EQUIPMENT NOT ANALYZED FOR ENVIRONMENTAL CONDITIONS OF RECORD "While evaluating the station environmental equipment qualification for equipment inside the containment it was determined that a number of different pieces of equipment were not analyzed for the environmental conditions associated with the current analysis of record. The equipment is subject to adverse conditions for a time frame longer than currently accounted for (220 verses 60 seconds). In addition, the equipment is subject to potentially different temperature effect than that to which it is currently analyzed. This affects a variety of equipment in containment." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-05-04
47899 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-05-04 | 2012-05-04 12:44 | 2012-05-04 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED AT JOBSITE The State of Texas supplied the following information via email: "The RSO for Rone Engineering contacted the Texas Radiation Program by phone on 4 May 2012 at approximately 10:15 AM CDT. The RSO reported a gauge had been damaged when run over by a water truck on a highway construction site in San Antonio. The RSO requested a radiation program inspector to conduct a radiation survey of the device because there was no radiation detection equipment immediately available. "An inspector was dispatched to the site and reported that the device was severely damaged, but the radioactive sources were still shielded. However, the source rod was broken and radiation levels at the point where it broke were measured to be 86 millirem per hour. The licensee contacted a company licensed to recover and ship radioactive sources. The recovery company packaged the gauge and will return it to the manufacturer. "The gauge was a Troxler 3430 plus, Serial number 60001. The gauge contained two sources; one 0.696 GBq Cs-137 and one 1.48 GBq Am-241 The Cs-137 source serial number was 77-7272 and the Am-241 source serial number was 78-4445." Texas Incident #: I - 8951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-05-14
47898 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-05-03 10:15 | 2012-05-04 10:02 | 2012-05-04 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "An employee complained of feeling dizzy. He was taken into the onsite medical dispensary for observation. The employee had been working at the Uranium Ore Concentrates Sampling area when he began to feel ill. There was approximately 18,000 dpm/100cm2 contamination on the bottom of the employee's plant issued shoes. After the employee recovered sufficiently, he was released [to] the care of his personal physician. The employee was free of contamination before being transported to the offsite medical facility." The licensee notified the Region II Senior Fuel Facility Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-05-04
47897 | -1 | WATERFORD | 3 |  |  | [3] CE | 2012-05-03 16:13 | 2012-05-03 21:07 | 2012-06-29 | BOTH TRAINS OF THE CONTROLLED VENTILATION AREA SYSTEM INOPERABLE "This is a non-emergency 8 hour notification being made in accordance with 10CFR50.72(b)(3)(ii) Degraded or Unanalyzed Condition and 10CFR50.72(b)(3)(v) Prevented Safety Function. Both trains of the Controlled Ventilation Area System (CVAS) were considered inoperable from 1613 to 1641 CDT on 5/3/2012. "Waterford 3 was performing planned maintenance on CVAS Train A with the train declared inoperable. Operations supervision was informed by maintenance personnel that an electrical conduit near the work area and not related to the work in progress had been found with a conduit connection unthreaded and separated. The contained wires could be seen and appeared intact. Investigation by engineering personnel determined that the conduit was associated with CVAS Train B. Operations declared CVAS Train B inoperable and entered Technical Specification (TS) 3.0.3 at 1613 hours. "Operations personnel were already restoring CVAS Train A following completion of maintenance. After performing the planned retest, Operations declared CVAS Train A operable and exited TS 3.0.3 at 1641 hours. No actions were taken to commence a power reduction or reactor shutdown. "The CVAS is required following a design basis accident to draw all exhaust air from the CVAS areas of the Reactor Auxiliary Building through HEPA and charcoal filters before discharge to the atmosphere. The CVAS areas contain equipment such as the shutdown cooling heat exchangers, safety injection pumps and other areas with containment penetrations. The CVAS is credited in accident analysis for limiting the radiological release under a Loss of Coolant Accident condition. "Following repair of the conduit connection, Operations declared CVAS Train B operable at 1956 hours. "Waterford 3 remained stable at 100% power during the condition. Both trains of offsite and onsite electrical sources, ECCS, and Containment Cooling safety systems remained operable during the condition." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM WILLIAM HARDIN TO VINCE KLCO ON 6/29/2012 AT 1515 EDT * * * "This is a non-emergency notification from Waterford 3 retracting a previous notification. "On 5/3/2012 at 2107 EDT, Waterford 3 communicated Notification Message EN 47897, pursuant to 10 CFR 50.72(b)(2)(ii), Degraded or Unanalyzed Condition and 10 CFR 50.72(b)(3)(v), Prevented Safety Function, stating that both trains of the Controlled Ventilation Area System (CVAS) were considered inoperable from 1613 to 1641 CDT on 5/3/2012. "Subsequent engineering evaluation has determined that the as-found condition would not cause the inoperability of CVAS Train B. With one train operable, the plant remained within analyzed conditions and capable of fulfilling safety functions. As such, no condition existed which required reporting. "Based on this information, Waterford 3 is retracting notification message EN 47897." The licensee has notified the NRC Resident Inspector. Notified the R4DO (Clark). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2012-05-03
47896 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-05-03 08:31 | 2012-05-03 18:12 | 2012-05-03 | OPERATOR FAILS FITNESS FOR DUTY TEST "A licensed operating supervisor tested positive in a for-cause test for alcohol. The operator was not on shift during the day of the test. The operator's access to the plant has been suspended. A review of the operators work is being performed." The license has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2012-05-03
47895 | 0 | ENERGYSOLUTIONS |  |  |  |  | 2012-05-03 | 2012-05-03 11:02 | 2012-05-25 | SHIPPING CASKS TAKEN OUT OF SERVICE FOR ACCIDENT SCENARIO NOT PREVIOUSLY ANALYZED "This serves as notification of a regulatory compliance issue with the 10-160B Type B Cask (Certificate of Compliance #9204) and the 8-120B Type B Cask (Certificate of Compliance #9168). This notification is being made in accordance with 10 CFR Part 21.21(d)(3)(i). These casks have been administratively placed out of service as Type B Packages until a complete determination can be made by Energy Solutions and the Nuclear Regulatory Commission (NRC). "As part of the relicensing of new 8-120B Casks, EnergySolutions identified a hypothetical accident scenario required by 10 CFR 71 which was not previously analyzed as part of the original or ongoing licensing activities. This analysis confirmed that the current cask design does not comply with the Type B package requirement for this specific accident scenario. The 10-160B has a similar design. As such, the casks have been placed out of service. EnergySolutions initiated Condition Report ENG-CR12-018 to track this issue. "In accordance with 10 CFR Part 21.21(d)(4), EnergySolutions will provide written notification to the NRC within 30 days with additional information including corrective actions." * * * UPDATE AT 1644 EDT ON 5/25/12 FROM SHRUM TO HUFFMAN * * * The licensee provided a 30-day written follow-up report to the condition described above: "Pursuant to the requirements of 10 CFR 21, EnergySolutions is providing this thirty day written report as required by 10 CFR 21.21(d)(3)(ii). "On May 3, 2012, the Senior Vice President, Regulatory Affairs, of EnergySolutions provided written notification to the NRC Operations Center of a regulatory compliance issue with the 10-160B Type B Cask (Certificate of Compliance #9204) and the 8-120B Type B Cask (Certificate of Compliance #9168) as required by 10 CFR 21.21(d)(3)(i). "Information required to be reported by 10 CFR 21.21(d)(3)(ii) is provided as follows: (4) The written report required by this paragraph shall include, but need not be limited to, the following information, to the extent known: (i) Name and address of the individual or individuals informing the Commission. "Dan Shrum, EnergySolutions Senior Vice President, Regulatory Affairs 423 West 300 South, Suite 200 Salt Lake City, UT 84103 (ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. "Model 8-120B Package, USA/9168B(U) "Model 10-160B Package, USA/9204B(U)F-96 (iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "The basic component is supplied by EnergySolutions (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "A Hypothetical Accident Condition was identified that had not been previously analyzed. Evaluation of this accident scenario found that during the thermal test the package secondary lid seals might reach a temperature exceeding the temperature limit for the seal material. If the temperature exceeds the limit, the seals may fail. Failure of the seals could result in a release of radioactive material exceeding the limits of 10 CFR 71.51. (v) The date on which the information of such defect or failure to comply was obtained. "Confirmatory calculations of the engineering analysis issue were completed on May 26, 2012. (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "The packages, as currently designed, meet the requirements of a Type A or IP-2 package and some are being used in that capacity. The package location listed below is as of 5/23/12. MODEL NUMBER LOCATION(S) 8-120B 4 120B-1 Cooper Nuclear Station in Nebraska; 120B-2 in transit to Tennessee; 120B-1S in to transit to Tennessee; 120B-2S in transit to Tennessee 10-160B 6 160B-1 Bremerton, WA; 160B-2 Columbia, SC; 160B-3 Portsmouth, MA; 160B-4 Canada; 160B-5 Canada; 160B-6 Kittery, ME; 160B-7 Carlsbad, NM; 160B-8 Columbia, SC (vii) The corrective action which has been, is being, or will he taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action, "EnergySolutions issued a Condition Report, ENG-CR12-018, on 4/26/12 identifying the issue and beginning the internal investigation process to determine the cause of the defect and identify corrective action(s); this internal investigation is in progress. The packages were taken out of service as of 4/27/12. EnergySolutions has submitted a request for NRC approval to continue use of the packages for a limited time. EnergySolutions will submit a request to the NRC before the end of May 2012 for approval of a change to the package design supported by a revision to the SAR demonstrating compliance with the requirements of Part 71. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "Owners and users of the packages have been informed of the defect and have concurred with EnergySolution's action to remove the packages from service. Any action by the NRC on continued use will be communicated to the package users and owners. Once NRC has approved the design change, users and owners will be notified and modifications to the packages will be made to conform with the approved design. (ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "Not applicable" The R1DO (Trapp), R2DO (Sykes), R3DO (Dailey); R4DO (Spitzburg) & NMSS EO (Smith) were notified. Copies of this report were sent to the Part 21 Reactors and Materials Group and FSME Event Resource via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-05-03
47894 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-05-03 08:30 | 2012-05-03 07:59 | 2012-05-03 | PREPLANNED MAINTENANCE ON TSC VENTILATION SYSTEM "At approximately 0830 EDT on 5/3/12, preplanned maintenance will be performed on the Technical Support Center (TSC) ventilation system. This maintenance will be performed for TSC Fan OA-2 for a motor replacement. This maintenance is planned to be performed and completed within 8 hours. If an emergency condition should occur that would require evacuation of the TSC, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TIM ENGLISH TO DONALD NORWOOD AT 1713 EDT ON 5/3/2012 * * * Maintenance work has been completed and the TSC is considered operable as of 1713 EDT. The licensee notified the NRC Resident Inspector. Notified R2DO (Seymour). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-05-03
47893 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-05-02 17:58 | 2012-05-02 22:12 | 2012-05-02 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO ERRATIC GOVERNOR OPERATION "On 5/2/2012 at 1758 EDT, the Unit 1 High Pressure Coolant Injection (HPCI) System was declared inoperable in accordance with Technical Specification 3.5.1 due to the flow controllers inability to maintain stable system flow and discharge pressure. This failure was discovered during the high steam pressure operability run (i.e., within 48 hours of achieving adequate test pressure following a scheduled refueling/maintenance outage) required by Technical Specification Surveillance 3.5.1.7 following refueling outage B119R1. "This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The Reactor Core Isolation Cooling (RCIC) system, Automatic Depressurization System (ADS) and Low Pressure Emergency Core Cooling Systems (ECCS) remain operable at this time. Actions have been taken to protect redundant safety systems. "The NRC Resident Inspector has been notified." | 37 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-05-02
47892 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-05-02 11:55 | 2012-05-02 19:02 | 2012-10-19 | POTENTIAL UNANALYZED CONDITION WITH CONTAINMENT PRESSURE INSTRUMENTS "While investigating operating experience from another station it was determined that Fort Calhoun Station (FCS) is subject to similar conditions. The operating experience involved setpoint drift of safety related pressure switches beyond what had been accounted for in the station's safety analyses. "Following investigation and evaluation, it was determined that pressure switches that provide safety related signals for high containment pressure to the reactor protection system (RPS) and engineered safeguards actuation circuitry may be similarly affected at FCS. The impact of the potential drift was evaluated, and it was determined that neither RPS nor the engineered safeguard circuitry may actuate at the required containment pressure of 5 psig. An evaluation determined that the actuation may not occur until slightly higher than the required pressure. Other systems are currently being evaluated to see if this same condition applies. "The station is in MODE 5, refueling shutdown condition, and there is no immediate safety concern." The pressure instruments are located in the penetration area which is subject to elevated temperatures. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1616 EDT ON 10/19/2012 FROM LUKE JENSEN TO MARK ABRAMOVITZ * * * "The condition was initially determined to be reportable under 10CFR50.72(b)(3)(ii)(B), plant in unanalyzed condition, based on a conservative assumption that the error introduced violated not only the Technical Specification limit (5.0 psig) but also the safety analysis limit of 5.4 psig, USAR Table 14.1-1. Subsequent evaluation of actual data concluded that the safety analysis limit was not exceeded and therefore not reportable under 10 CFR 50.72(b)(3)(ii)(B). "LER 2012-004-1 reported this condition under 10CFR50.73(a)(2)(i)(B), 10CFR50.73(a)(2)(ix)(A), and 10CFR50.73(a)(2)(v)(A,B,C,D). Revision 2 of the LER will correct the reporting criteria." The NRC Resident Inspector was notified by the licensee. Notified the R4DO (Pick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-05-02
47891 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2012-05-01 15:00 | 2012-05-02 14:15 | 2012-05-02 | AGREEMENT STATE REPORT - RADIOACTIVE SPILL DURING MEDICAL TREATMENT "The SC Department of Health and Environmental Control was notified on Wednesday, May 2, 2012, at 1400 hrs, that a nurse's aide was attempting to empty a Foley bag containing I-131 at 1500 hrs on May 1, 2012, when she inadvertently spilled 200-300 cc of the contents of the bag on the floor, her shoe and sock. The patient had received 203 mCi of I-131 for in-patient treatment. The Supervisor, Nuclear Med, was notified and the nurse's aide's foot was decontaminated. Surveys after the decontamination did not indicate the presence of any radioactive material on her skin. The nurse's aide had a bioassay on May 2, 2012, and no uptake was indicated. Absorbent paper had been placed on the floor prior to the in-patient procedure and most of the spill was contained on the absorbent paper. A 12 x 100 inch area of the floor under the patient bed may have contamination and the area will be cleaned and surveyed once the patient has been released. "[The Nuclear Med Supervisor] was advised by [South Carolina] to submit a written report detailing this event to the [South Carolina] Department within 30 days. The event is open and pending the licensee's investigation and report to the [South Carolina] Department. Updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2012-05-10
47890 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-04-30 | 2012-05-02 15:08 | 2012-05-02 | AGREEMENT STATE REPORT - DENSITOMETER DISLODGED The following report was received via fax: "On April 30, 2012, while on location in North Eastern, PA, an incident occurred which indirectly involved a nuclear density device. While pumping at a well site at 7200 psi, a large section of 4 inch pipe became dislodged at a joint, sending the pipe in the direction of the gauge. This caused a piece of iron to collide with the densitometer which in turn, knocked the in-line densitometer off of the 4 foot, 4 inch piece of iron it was attached to. Gauge Information: Material: Cs-137 Manufacturer: Thermo MeasureTech Sealed Source Model: 57157C Activity: 250mCi "The density gauge showed no signs of damage. The device was immediately secured and a trained employee was dispatched to retrieve and properly package and transport the device back to the Blacklick, PA facility. The device was leak tested in the field and surveyed with a Ludlum Model 3. The densitometer is currently in secure storage at the Blacklick facility and is awaiting repair from a licensed service provider. The Department [PA Bureau of Radiation Protection] plans to conduct a reactive inspection on Tuesday, May 8, 2012." PA Event: PA-120014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-05-10
47889 | 0 | ESCANABA PAPER COMPANY |  |  |  |  | 2012-05-02 | 2012-05-02 14:16 | 2012-05-02 | DENSITY GAUGE SHUTTER STUCK OPEN The shutter on a Kay Ray model 7063PS, S/N S99F1501, was determined to be stuck open during its annual shutter check. The gauge shutter was last tested satisfactorily on 5/6/2011. The gauge measures density in a line kiln and the shutter is normally open. The area is not normally accessible to personnel i.e. the open shutter does not pose a risk to the operators. The source is a 50 mCi Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-05-02
47888 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-05-02 07:24 | 2012-05-02 13:15 | 2012-05-02 | MANUAL INITIATION OF SECONDARY CONTAINMENT ISOLATION "In response to a trip of Unit 1 reactor enclosure [secondary containment] HVAC and subsequent loss of reactor enclosure delta-p, a Unit 1 manual secondary containment isolation was initiated per station procedures. This manual initiation also resulted in an isolation signal to containment atmosphere control (CAC) system valves and primary containment instrument gas (PCIG) system valves. System responses were as expected. "Unit 1 secondary containment delta-p was restored via standby gas treatment system (SGTS), and Unit 1 secondary containment integrity remains intact and operable. "Investigation of the trip of Unit 1 reactor enclosure HVAC is ongoing. "This is being reported under 50.72(b)(3)(iv) for containment isolation signal affecting containment isolation valves in more than one system." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-05-02
47887 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-05-02 10:05 | 2012-05-02 12:18 | 2012-05-02 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE "On 5/2/2012 at approximately 0914 hours, a Duke Energy contract worker performing activities in the Unit 3 reactor basement (currently defueled in a planned refueling outage), experienced dizziness and subsequently experienced a loss of consciousness. Upon discovery, the plant emergency medical team was dispatched to aid the individual. The individual soon regained consciousness but was immediately transported, via ambulance, to a local hospital for treatment. Accompanying the individual were two (2) radiation protection and one (1) Duke energy Public Affairs individuals. The individual was transported out of the protected area at approximately 1005 hours. Because the potentially contaminated individual's back could not be surveyed prior to being transported offsite, the individual was considered potentially contaminated. As such, this event is being reported as an 8-hour prompt report pursuant to 10CFR50.72(b)(3)(xii). "On 5-2-2012 at approximately 1100 hours, the radiation protection personnel that accompanied the individual to the medical facility reported that the individual was determined not to be contaminated. As a result, no follow-up status report is planned. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Power Operation | Power Operation | Refueling Shutdown | Power Operation | Power Operation | Refueling Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-05-02
47886 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-04-19 | 2012-05-02 11:00 | 2012-05-02 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received from the State of Texas Department of Health Radiation Branch (via e-mail): "On May 1, 2012, the Agency (Texas Radiation Branch) was notified by a licensee that the shutter on a Ronan SA-1 nuclear gauge containing 50 millicuries of cesium-137 was stuck in the open position. This is the normal position for the gauge shutter. "The licensee contacted the gauge manufacture and the gauge shutter was repaired by the manufacturer on May 1, 2012. The shutter failure did not create an exposure risk to any individual. Additional information will be provided as it is received in accordance with SA - 300." Texas Report I-8950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-05-10
47885 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-05-01 13:00 | 2012-05-01 22:01 | 2012-05-31 | FLOOR DRAIN BLOCKAGE ADVERSELY AFFECTS ASUMPTIONS OF PIPE BREAK ANALYSIS FOR ELECTRICAL SWITGHEAR ROOMS "At 1300 on May 1, 2012, as a result of fire water flushing operations, it was observed that the floor drains in the 'A' and 'B' ESF (Engineered Safety Features) 4160 VAC switchgear rooms were draining extremely slow. Engineering was consulted and it was identified that the floor drains in these rooms are credited with preventing any water accumulation in these rooms as a result of internal flooding due to a pipe break. It is expected that the floor drains in the 'A' ESF switchgear room can drain approximately 134 gallons per minute (gpm) and the floor drains in the 'B' ESF switchgear room can drain approximately 208 gpm. With the floor drains partially blocked, a break in the 'A' Essential Service Water pipe in the 'B' ESF Switchgear Room would result in flood levels in the 'B' ESF Switchgear Room to exceed the maximum levels calculated in the current flooding analysis. The higher flood level may result in the inoperability of 'B' train Electrical Switchgear. The 'A' train Essential Service Water supplied equipment would be adversely affected due to the reduced flow. Consequently the pipe break would result in both ESF trains being adversely affected. "Compensatory measures have been taken to restore system operability. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM KEITH DUNCAN TO JOHN KNOKE AT 1534 ON 05/31/12 * * * "On May 1, 2012, Callaway Plant made an ENS notification in accordance with 10 CFR 50.72(b)(3)(ii)(B) to report the discovery of partially blocked floor drains in the safety-related 4160 V switchgear rooms. At the time of the initial notification, preliminary information indicated that the partially blocked floor drains could have caused a postulated flooding event to adversely affect independent trains of safety-related equipment inside these rooms. "Upon further analysis, Callaway Plant staff determined that the pipe break assumed in the flooding calculation of these rooms was overly conservative. Specifically, based on seismic qualifications, the guillotine break of Essential Service Water piping that was originally assumed is not required to be postulated. Instead, a much smaller, through-wall crack of fire protection system piping is the most severe break that must be postulated in the safety-related 4160 V switchgear rooms. "An analysis of a postulated flood hazard in these rooms was performed based on the correct water source. Even if considering a complete blockage of the floor drains in these rooms, this analysis demonstrates that a postulated fire protection system piping crack would not have adversely affected safety-related equipment. "Based on the results of this analysis, the partially-blocked floor drain condition described in EN 47885 did not meet the criteria for reportability as an unanalyzed condition that significantly degrades plant safety. Event Notification 47885 is hereby retracted." The licensee has notified the NRC Resident Inspector. Notified the R4DO (Greg Pick) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-05-01
47884 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-03-02 08:41 | 2012-05-01 17:46 | 2012-07-17 | POTENTIAL DEGRADATION OF REACTOR CONTAINMENT ELECTRICAL PENETRATION SEALS "During a review of environmental qualification records for reactor containment building electrical penetrations, six penetrations were identified that may not provide an adequate seal during worst case (Design Basis Accident (DBA)) conditions as required. These penetrations are through wall from the containment into the auxiliary building. The conditions that could cause degradation of the electrical penetration seals are not applicable to this operating mode. The station is currently in a refueling mode. This event was identified on March 2, 2012. The reportability was confirmed on May 1, 2012 at 1502 CDT." The current penetration configuration has existed since the plant was built. The area of concern is that the Teflon connections may degrade under conditions of high radiation and high temperature during a DBA event. The licensee is investigating the extent of the condition and repair techniques. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ROBERT KROS TO PETE SNYDER AT 1523 ON 6/26/12 * * * "On review of CR 2012-01947 by a new Project Manager, who was brought in as a subject matter expert on HELB/EEQ, and issue was identified with the 530 primary containment electrical penetration feed-throughs used for non-CQE devices. The CR [Condition Report] correctly notes that under the original accident testing, the Teflon seals failed, and water was noted leaking from these penetrations. "On further review, the following was noted: Due to the design of the penetration feed-throughs, when the inboard Teflon seal fails (as it is expected to, due to high level of radioactivity in the primary containment, following a Loss of Coolant Accident (LOCA)), the atmosphere of the primary containment will be introduced to the penetration assembly, first through the failed seal or seals, and then through the weep hole between the inboard and outboard seals of the feed-through. This will put the same high level of radioactivity in direct contact with the outboard seals, resulting in the failure of its Teflon Seal. This would result in approximately 530 breaches of the Primary Containment during post LOCA conditions. The existing vendor analysis does not assume any contribution to the outboard seal exposure from the mixing of containment atmosphere with the penetration air after the failure of the inboard seal. This is probable, as each feed-through has a weep hole. Once the inboard seal fails, the penetration will be filled with containment atmosphere to equalize the pressure, which will bring the associated noble gas and Iodine fraction in proportion, into the penetration." The licensee notified the NRC Resident Inspector. Notified R4DO (Clark) * * * UPDATE AT 1748 EDT ON 7/17/12 FROM MOECK TO HUFFMAN * * * "During the extent of condition review for CR 2012-01655 and 2012-01947 additional penetration feed-through assemblies were identified that are subject to the same failure mechanism. These penetrations are associated with the containment sump recirculation isolation valves, and also associated with the personnel air lock." The licensee notified the NRC Resident Inspector. Notified R4DO (Walker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-05-01
47883 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2012-01-25 | 2012-05-01 14:11 | 2012-05-01 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER FAILED IN CLOSED POSITION The following report was received via fax: "The SC [South Carolina] Department of Health and Environmental Control was notified in writing on January 25, 2012, that during a routine shutter check, a Vega Americas Corporation Model SHRD gauging device containing 20 Ci of Cs-137, had a shutter mechanism that was harder to operate than normal. Vega Americas Corporation was contacted and on January 24, 2012, a Vega Americas Corporation technician arrived and was evaluating the operation of the shutter when it failed in the closed position. The metal operating handle broke off and the shutter cannot be moved. The source holder was surveyed and [it was] verified that the shutter is in the closed and safe position. "Following further correspondence with the licensee on May 1, 2012, the licensee stated that Vega Americas Corporation will not repair the source holder. Vega Americas Corporation will be handling the proper disposal of the SHRD fixed gauge. "Even though this event is being reported, the Department of Health and Environmental Control does not feel that this is a reportable event since the shutter is closed and radiation exposure in excess of regulatory limits is not possible." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2012-05-09
47882 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-05-01 12:05 | 2012-05-01 12:33 | 2012-05-01 | FAA NOTIFIED OF REMOVAL OF STACK AVAITION OBSTRUCTION LIGHTS "On May 1, 2012 at 12:10 EDT, Indian Point Unit 2 notified the Federal Aviation Administration that the Unit 1 Ventilation Stack Aviation Obstruction Lights were removed from service at 12:05 EDT on May 1, 2012. This is a planned evolution as Indian Point no longer requires the Unit 1 ventilation stack and plans to dismantle the stack to an approximate elevation of 167 feet which will remove the obstruction to air navigation and its associated aviation obstruction lights. "The NRC Resident Inspector has been notified." The licensee estimates that the job will be completed September 6, 2012. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-05-01
47881 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-30 23:28 | 2012-05-01 02:34 | 2012-05-01 | AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "On 30 April, 2012, at 2328 [EDT], DC Cook Unit 2 Reactor automatically tripped due to a trip of the main turbine. The cause of the main turbine trip is still under investigation. "The electrical grid is stable and Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via Steam Generator PORVs to atmosphere. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post trip review. No radioactive releases were experienced as a result of this event. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The DC Cook Resident NRC Inspector has been notified." The licensee stated that the trip was uncomplicated and the reactor is stable in mode 3 at no load temperature and pressure. The unit is on steam generator atmospheric relief valves because the secondary steam load on the plant was causing too much of a cool down. There is no primary to secondary steam generator leakage for the unit. The trip had no impact on Unit 1 which continues to operate at full power. | 0 | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-05-01
47880 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-04-30 18:01 | 2012-04-30 22:34 | 2012-04-30 | WELD DEFECT INDICATION FOUND IN RESIDUAL HEAT REMOVAL SYSTEM TO REACTOR PRESSURE VESSEL NOZZLE "Grand Gulf Nuclear Station is currently in Mode 4 (less than 200 degrees F) executing Refueling Outage 18 (RF-18) including in-service inspections. "General Electric notified Entergy of a weld indication that was detected by automated ultrasonic testing. The indication is in the weld root area of N06B-KB Reactor Coolant System Pressure Boundary weld. The N06B nozzle connects Residual Heat Removal System 'C' to the Reactor Pressure Vessel. The dimension of the indication is approximately 0.9 inches in length, approximately 0.5 inches in depth and with no discernible width. Nominal wall thickness is 1.3 inches. "The indication does not penetrate the entire thickness of the pipe wall and there is no leakage at the indication. There has been no release of radioactive material due to the indication. No systems were actuated due to this event. There are currently no other systems affected. The cause is under investigation and corrective action plans are being explored. "The weld defect has been evaluated by Entergy Engineering and determined to meet the criteria for reporting identified in NUREG-1022: Welding or material defects in the primary coolant system that cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws,' or ASME Section XI, Table IWB-3410-1, 'Acceptable Standards'." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-04-30
47879 | -1 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-03-31 | 2012-04-30 18:34 | 2012-07-17 | AGREEMENT STATE REPORT - FILM BADGE INDICATES RADIOGRAPHER OVEREXPOSURE "KY RHB [Kentucky Radiation Health Branch] was notified on April 27, 2012, by the corporate RSO (CRSO) of Mistras Group, Inc. (license 201-699-05), that on the morning of April 27, 2012 he received a notice from Landauer that [an employee] received an extremely high dose reading on his film badge for the month of March 2012. The report stated that 'Dosimeter has exceeded the reporting capabilities of 1000 Rads, dosimeter reprocessed, second read agrees with reported dose.' The representative with Landauer told the CRSO that the image blinded the camera and was too blurry to read. She also stated that the reading was so high they could not get a reading. The CRSO conducted a telephone interview with [the employee] and he was told that his dosimeter never went off scale during that period and his film badge was on him at all times while performing radiography procedures. He did say his film badge may have been stored in his work bucket in the dark room of his transport vehicle. The CRSO has instructed [the employee] to turn in his [the employee's] current film badge to the office manager and is not to participate in radiographic operations until this matter has been resolved. According to a telephone conversation with the RSO early this evening, [the employee] is not experiencing any signs or symptoms of radiation exposure and he will be calling Oak Ridge tomorrow morning (5/1/12) to schedule blood work for [the employee]." Kentucky Report: 120008 * * * THE RETRACTION FROM CURT PENDERGRASS TO JOHN SHOEMAKER AT 1538 EDT ON 7/17/12 * * * The following retraction was received from the State of Kentucky via email. The Kentucky Department of Radiation Control provided dose reconstruction results and corrective actions for EN 47879 purported overexposure of industrial radiographer. The Kentucky Department of Radiation Control wishes to retract this event due to the results in documents showing that, while this person's badge received a dose of 1,000 R, the individual received a dose of less than 200 mrem for the reporting period. Notified R1DO (Dimitriadis) and FSME Events Resource (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-05-08
47878 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2011-03-03 | 2012-04-30 16:01 | 2012-04-30 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA The following report was received via fax: "World Testing reported a 3.66 TBq (99 Ci) Se-75 radiography source (QSA Global model A-424-25W) disconnect from the exposure device (QSA Global model 880 Delta, serial #D1120) that occurred on 3/3/2011. The lead radiographer determined that the source remained in the collimator at the end of the guide tube following retraction attempts. The work area was surveyed and the barricade was appropriately adjusted. A manned lift was used to detach the exposure device from overhead piping and lower it to the ground. A six-foot retrieval tool was used to grasp the collimator and elevate it until the source fell out of the end of the guide tube. Using concrete and lead for shielding, personnel were able to place the source back into the exposure device and secure it. Inspection of the source drive cable revealed that the crimped connection, which attaches to the source pigtail, detached from the drive cable. QSA Global was notified of the failure." Tennessee Report Number: TN-11-038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-05-08
47877 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2011-01-18 | 2012-04-30 16:01 | 2012-04-30 | AGREEMENT STATE REPORT - SR-90 CATHETER STUCK WHILE BEING CALIBRATED The following report was received via fax: "K&S Associates were attempting to perform a routine calibration of a Beta-Cath system, when the Sr-90 source train became stuck in the 'out' position. They believed they could cut the catheter and isolate the source train and subsequently place the train and housing unit into a pig and send the system back to the manufacturer. While cutting the plastic catheter, they misjudged where the source train was located and severed the train. Approximately 10 mL of water spilled out onto a table, along with the train. Paper toweling was used to wipe up the water. A survey was performed to account for the seeds. The total leaking activity was under 3.5 milliCuries. The entire source train of 4 cm contained 16 seeds with a total activity of 56 milliCuries. After the Division received the notification from K&S, two members of our staff from the Nashville Field Office responded to the incident to investigate. The Division found that K&S Associates were performing work they were licensed to do. However, when the catheter was cut, an unlicensed task was performed. A Notice of Noncompliance was issued. K&S responded to the noncompliance letter with the actions that were implemented as a result of this incident." Tennessee Report Number: TN-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-05-08
47876 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2009-01-23 | 2012-04-30 16:01 | 2012-04-30 | AGREEMENT STATE REPORT - RADIOACTIVE SOURCE FOUND IN DRUM FROM PREVIOUS OWNER The following report was received via fax: "Studsvik contacted The Division of Radiological Health (DRH) regarding an incident that occurred on January 23, 2009. Studsvik was going through 18 drums from the previous owner (RACE) that were identified as legacy lead. The drums were scheduled for segregation for potential free release, reuse and disposal. These drums were scheduled for processing in a specific order based on radiological data. When they reached the final drum, they suspected that package SPFM 2008 04 40 (30-gallon drum) contained more than just lead based on the fact that it was stored in the high radiation room. It contained a 10 gallon drum. Between the space of the inner and outer drum were several empty lead pigs. The inner drum was wrapped in a lead blanket, containing 3 pigs, 2 empty and the third one contained a sealed source. The outer surface of the pig containing the sealed source read 2.5 R/hr. A shielded enclosure was constructed and the source was removed with proper handling devices. The dose rate at one inch from the source was 850 R/hr. The source was immediately returned to the pig. The 10 gallon drum was lined with lead blankets and the pig was placed in the middle. Ends of the blankets were folded over the pig. More blankets were placed inside the drum and it was closed. Blankets were then used to cover the drum. Duct tape was used to secure the blankets in placed. Approximately 700 lbs of blankets were shielding the pig and source. The dose rate was at 61 mR/hr on contact of the blankets. The 30 gallon drum, the small lead pigs and the original lead blankets were removed from the high radiation room. No contamination was found on the pig, blankets or drum. The Health Physicists received 16 mrem and 11 mrem on their electronic dosimeters. No extremity dosimeters were used but are being purchased for future remote source handling. The source was shipped through Northwest NARM Services and arrived on July 1, 2010 at US Ecology for disposal." Tennessee Report Number: TN-09-015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-05-08
47875 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2012-03-24 19:36 | 2012-04-30 13:38 | 2012-04-30 | INVALID PROTECTION SYSTEM ACTUATION DURING STATION ELECTRICAL TRANSIENT "The purpose of this report is to provide a telephone notification for an invalid actuation. On March 24, 2012, following the completion of switch yard work, the Control Room received switching orders to open Bus Tie 9-10 Bus 9 disconnect and close Bus Tie 9-10 Bus 10 disconnect. Operations was unaware that a grounding device, installed for personnel protection during the work activities, had not been removed. Consequently, when the Bus Tie 9-10 Bus 10 disconnect was closed the switchyard was grounded resulting in an electrical transient. Protective relaying operated as designed to clear the fault, and there were no injuries. "During the electrical transient, the voltage depression tripped the Unit 1 "A" Reactor Protection System (RPS) bus which caused a 1/2 scram and certain protective logic systems to de-energize by design. The following invalid actuations occurred as a result of the loss of power to the RPS bus: partial Group 11 Isolation (Primary Containment); Group III Isolation (Reactor Water Cleanup); Reactor Building Ventilation Isolation; Control Room Ventilation Isolation; and Standby Gas Treatment Initiation. "The electrical transient also tripped the Unit 1 ECCS keepÀfill pump, resulting in the Core Spray (CS) discharge pressure decreasing to the alarm setpoint. Both CS subsystems were conservatively declared inoperable and entry into Technical Specifications (TS) 3.0.3 occurred at 1936 hours. Subsequent fill and vent activities confirmed no air existed in the discharge headers of the CS subsystems (no loss of safety function) and both subsystems were declared operable with TS 3.0.3 being exited at 2017 hours. Following the electrical transient, the Unit 1 generator was temporarily limited to approximately 90% load due to elevated vibration on Turbine Bearing No. 10. In-plant walk-downs identified no other equipment concerns. Unit 1 returned to full power on April 2, 2012, following confirmation the bearing vibration is acceptable for long-term operation. Unit 2 was in a scheduled refueling outage during the event and was unaffected by the electrical transient. A Root Cause Investigation is ongoing." The licensee notified the NRC Resident Inspector. | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-04-30
47874 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-30 10:18 | 2012-04-30 10:45 | 2012-04-30 | UNUSUAL EVENT DUE TO A POTENTIAL FIRE IN CONTAINMENT "Performing an I&C functional [test] caused an inadvertent Safety Injection signal resulting in a reactor trip/safety injection. All safety systems responded as designed for a safety injection. Electrical systems are aligned to normal offsite power sources. All fire alarms have been validated by the Fire Protection Department as invalid alarms and confirmed that no fire event in the protected area. "The reactor trip was successful and all rods [fully] inserted. Decay heat removal is via auxiliary feedwater through the atmospheric [steam] dumps. Unknown at this time is the cause of the inadvertent safety injection signal. No injuries occurred as a result of this event." The licensee believes that the trip/safety injection may have caused piping to shake resulting in dust near the fire detection equipment resulting in the invalid fire indication. The instrument being tested was the high steam flow channel-1 bistable for PT505. The maximum pressurizer level during this event was 95%. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1400 EDT ON 4/30/2012 FROM JOHN KOKOVALCHICK TO MARK ABRAMOVITZ * * * "At 1003 hours on April 30, 2012, Salem Unit 1 experienced a reactor trip and safety injection (SI) signal due to a high steam flow coincident with a low steam pressure signal. At the time of the safety injection signal, function testing of the 1PT505 turbine inlet pressure channel was in progress. This testing required the tripping of the high steam flow bistables. "As a result of the reactor trip and safety injection signal, the Emergency Diesel Generators started but did not load, the ECCS system (high head safety injection pumps actuated and injected into the reactor vessel, intermediate head safety injection pumps and low head (RHR) safety injection pumps) actuated. All 4 main steam isolation valves closed along with feedwater isolation and start of the auxiliary feedwater pumps. All control rods fully inserted following the reactor trip. Following the main steam line isolation, the atmospheric relief valves opened along with the lifting of several main steam safety valves. "The unit is currently in Mode 3 and will be cooling down to Mode 4. Train A SSPS [Solid State Protection System] is currently out of service and suspected of causing the safety injection signal. Train B SSPS has not been reset due to the standing safety injection signal. With Train A SSPS inoperable and Train B SSPS not reset, TS 3.0.3 was entered and a shutdown required by TS 3.0.3 was commenced at 1345 hours. "This report is being made in accordance with 10CFR50.72(b )(2)(iv)(B), 50.72(b)(3)(iv)(A), 50.72(b)(2)(i) and 50.72(b)(2)(iv)(A)." The licensee exited the Unusual Event at 1249 EDT. The licensee notified the NRC Resident Inspector. Notified the R1DO (Conte). The NRC Operations Center notified other Federal Agencies (DHS SWO, FEMA Ops, DHS NICC, and NuclearSSA via e-mail). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | ECCS INJECTION | PLANT S/D REQD BY TS | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(i) | 0 | 2012-04-30
47873 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-04-30 06:00 | 2012-04-30 10:55 | 2012-04-30 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL SYSTEM DECLARED INOPERABLE "At 1742 CDT on 04/27/2012, while in Mode 5, both trains of Residual Heat Removal were declared inoperable due to a through wall leak in a 3/4-inch pipe socket weld connection. The leak developed in an ASME Section XI, Code Class 2 weld upstream of a sample isolation valve. The leak is not isolable from the common 10-inch Residual Heat Removal discharge piping. However, the leakage is isolable from the Reactor Coolant System and is therefore not considered RCS pressure boundary leakage per Technical Specification LCO 3.4.13, RCS Operational Leakage. Currently, with both trains of RHR in service for decay heat removal, the leakage impacts redundant equipment required to fulfill a safety function. In the current condition, both trains are required to be operable to meet Technical Specification LCO 3.4.7, RCS Loops - Mode 5, Loops Filled. This event was reported per EN #47871. "At 0600 CDT on 04/30/2012 during the subsequent repair of the leaking weld a second leak of approximately 0.03 gallons per minute developed. The second leak occurred down stream of the original leak while welding a temporary clamp to the 3/4-inch sample line. The cause of the second leak is being directly attributed to the welding activity and not degradation of the pipe. The structural integrity of the pipe in the area of the second leak was verified to be acceptable. Both trains of Residual Heat Removal remain in service removing decay heat from the core. No other equipment is being affected by the leak. Repair options are currently being evaluated. "The new leak is being reported under 50.72(b)(3)(v)(B), 'Any event that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat.' "Actions continue in accordance with Technical Specification LCO 3.4.7 Required Action C.2 to restores one RHR loop to operable status." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-04-30
47872 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-29 | 2012-04-29 17:35 | 2012-04-29 | PART 21 REPORT - CONTROLLERS DID NOT MEET EMI / RFI GUIDELINES "This report constitutes a 10 CFR Part 21 notification. On March 23, 2012, Scientech (a business unit of Curtis Wright Flow Control), sent a 10 CFR Part 21 report (Letter Number 12-09-BB) to Pacific Gas & Electric Company. Diablo Canyon Nuclear Plant (DCPP) entered this report into its corrective action program on April 23, 2012. This Part 21 report identified that eight AMS286 and AMS287 hand controllers supplied to DCPP had a deviation from the purchase specification. DCPP specified the controllers to be qualified to meet electromagnetic interference (EMI) / radio frequency interference (RFI) emissions and susceptibility in accordance with NRC Regulatory Guide 1.180, Rev. 1. Contrary to this requirement, Scientech did not perform the EMI / RFI testing on the AMS286 controllers shipped to DCPP with a Certificate of Conformance to DCPP's specification. Scientech tested the AMS287 controllers, which failed some of the required testing, but were shipped to DCPP with a Certificate of Conformance nonetheless. DCPP accepted the controllers based on the Certificates of Conformance, but did not install them. Following acceptance of the controllers, DCPP identified the nonconformance with its specification, and had another vendor modify the controllers to subsequently pass required testing. "DCPP determined the deviation could have potentially created a substantial safety hazard if the controllers were installed at DCPP. The controllers were intended to control auxiliary feedwater from the Unit 1 control room and the hot shutdown panel as part of an upcoming process control system modification. Following a postulated fire in the control room, plant shutdown would be managed from the hot shutdown panel. In this instance, radios would be used to communicate with operators at the panel. The controllers would be susceptible to EMI/RFI interference and could potentially affect the operators' ability the safely shut down the plant and maintain it in a safe shutdown condition. DCPP notified Scientech of this conclusion on 4/27/12." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2012-04-29
47871 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-04-27 17:42 | 2012-04-27 22:23 | 2012-04-27 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL DECLARED INOPERABLE "At 1742 EDT on 04/27/2012, while in Mode 5, both trains of RHR (Residual Heat Removal) were declared inoperable due to a through wall leak on a socket welded connection of ASME code class piping. Currently, with both trains of RHR in service for decay heat removal, the leakage impacts redundant equipment required to fulfill a safety function. In the current condition, both trains are required to be operable to meet Technical Specification [TS] 3.4.7, 'RCS Loops - MODE 5, Loops Filled'. "The leakage is isolable from the reactor coolant system and is therefore not considered RCS pressure boundary leakage per LCO 3.4.13, 'RCS Operational Leakage'. "This event is being reported under 50.72(b)(3)(v)(B), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) remove residual heat'. "Action has been initiated in accordance with TS 3.4.7 required action C.2 to restore one RHR loop to operable status." The licensee is performing engineering analysis to determine the most appropriate repair method. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-04-27
47870 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-04-27 13:45 | 2012-04-27 16:02 | 2012-04-27 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ILLEGAL DRUGS A non-licensed supervisory employee was determined to be under the influence of illegal drugs during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2012-04-27
47869 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2012-04-27 08:00 | 2012-04-27 13:19 | 2012-04-27 | FITNESS FOR DUTY - NON-LICENSED CONTRACT SUPERVISOR TESTED POSITIVE FOR DRUGS A non-licensee contract supervisor tested positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-04-27
47868 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-04-26 10:12 | 2012-04-26 14:55 | 2012-04-26 | VALID ACTUATION OF THE REACTOR PROTECTION SYSTEM DURING TESTING "At 1012 EDT on April 26, 2012, during the Reactor Pressure Vessel Hydrostatic Test, a valid high pressure reactor scram occurred due to issues related to controlling pressure near rated values. This actuation of the Reactor Protection System was not part of the pre-planned testing sequence. All control rods were fully inserted at the time of the scram. This report is being made in accordance with 10CFR50.72 (b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' The reactor scram was reset after reactor pressure was lowered." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-04-26
47867 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-03-14 | 2012-04-26 14:02 | 2012-04-26 | MASSACHUSETTS AGREEMENT STATE REPORT - MISSING THALLIUM-201 SHIPMENT The following information was obtained from the Commonwealth of Massachusetts via email: "On 4/5/12, [the] licensee reported as missing a 1.78 GBq (48.1 mCi) Thallium-201 package that was shipped from its site on 3/12/12, was scanned in at the carrier's Nashville, TN, transportation hub on 3/13/12 and reported to the licensee as missing by the carrier on 3/13/12. Licensee in communication with the carrier in ongoing effort to locate missing package. After a reasonable search time had passed, licensee reported missing package to this Agency [MA Radiation Control Program]. "Last known location was in Nashville, TN. The subject radioactive material is 7 ml of liquid solution held within a vial inside a lead pig inside a sealed plastic container inside a styrofoam insert within a corrugated cardboard box. Subject radioactive material has a 73 hour (~3 days) half-life and has decayed well past 10 half-lives since its original shipping date. "Licensee remains in communication with carrier in ongoing effort to locate missing RAM and has requested return of package to licensee if found. "The Agency considers this event to be CLOSED." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-05-04
47866 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-04-26 09:55 | 2012-04-26 13:50 | 2012-04-26 | OFFSITE NOTIFICATION DUE TO DEATH OF A BALD EAGLE "At 0955 [EDT] on April 26, 2012, a bald eagle (bird of prey) caused a phase to phase fault on the Station's 428 power line (power to buildings outside the protected area). The fault temporarily de-energized the 428 line. The bald eagle was found dead beneath the power lines. "Two outside agencies, The Virginia Department of Game and Inland Fisheries and The U.S. Fish and Wildlife Service will be notified. "This is being reported pursuant to 10 CFR 50.72(b)(2)(xi) for an event that required notification of other government agencies. "The NRC Resident has been informed." | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-04-26
47865 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-25 22:27 | 2012-04-26 04:20 | 2012-04-26 | PRESS RELEASE ISSUED FOR SHUTDOWN OF UNIT 2 DUE TO SALP INFLUX "On April 25, 2012, at 2227 PDT, Diablo Canyon Power Plant (DCPP) U2 was manually taken offline and the reactor shut down due to an influx of sea salp - a small, jellyfish-like organism - in the intake structure. Operators manually started the auxiliary feedwater pumps in accordance with the plant operating procedures. "PG&E will not restart Unit 2 until conditions improve at the intake structure. As previously announced, Unit 1 was safely shut down for a planned refueling and maintenance outage. "All systems operated as designed and no unexpected equipment performance issues were noted. "The licensee notified the NRC Resident Inspector." The licensee plans on issuing a press release. | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-04-26
47864 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-25 22:46 | 2012-04-26 01:21 | 2012-04-26 | NOTIFICATION TO OFFSITE AGENCIES DUE TO OIL SPILL "At 2246 EDT on April 25, 2012, D.C. Cook notified the State of Michigan and local authorities of an oil spill from the Unit 2 [Main Generator] Seal Oil system at 2110 EDT which resulted in a portion of this oil entering the absorption pond, which is in the owner controlled area. An oil sheen is present on the absorption pond which has a surface area of approximately 2 acres (87,000 square feet) and it is estimated that five to ten gallons of oil are on the absorption pond. "The NRC Resident Inspector was notified." The licensee has contained the oil leak and clean up efforts are ongoing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-04-26
47863 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-04-25 21:06 | 2012-04-25 22:42 | 2012-08-02 | ALERT DECLARED DUE TO TOXIC GAS BUILD UP FOLLOWING AN EMERGENCY DIESEL GENERATOR TEST RUN On April 25, 2012 at 2106 CDT, Point Beach Nuclear Plant declared an Alert under EAL HA3.1 due to toxic gas in a vital area. During a maintenance run on the plant's emergency diesel generator, diesel exhaust caused the concentration of carbon monoxide in an adjacent vital area room (Plant Instrument Air Compressor Room) to exceed OSHA IDLH (Immediately Dangerous to Life and Health) levels. The diesel was immediately secured and the room was ventilated. There were no personnel injuries and no public health and safety issues associated with this event. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, USDA, DOE, DHS NICC, HHS AND EPA. * * * UPDATE FROM JOHN RODGERS TO JOHN SHOEMAKER AT 0022 EDT ON 04/26/12 * * * The Alert at Point Beach was terminated at 2314 CDT on 04/25/12. The licensee notified the NRC Resident Inspector. Notified R3DO (Lara), NRR EO (Lubinski), IRD (Scott via email only). Notified DHS SWO, FEMA, USDA, DOE, DHS NICC, HHS, EPA, and Nuclear SSA (email only). * * * RETRACTION FROM MARY SIPIORSKI TO CHARLES TEAL AT 1650 EDT ON 8/2/2012 * * * "On April 25, 2012, at 2106 CDT, Point Beach Nuclear Plant declared an Alert under EAL HA3.1 (EN #47863) due to toxic gas in a vital area. During a maintenance run on the plant's emergency diesel generator, diesel exhaust caused the concentration of carbon monoxide in an adjacent vital area room (Plant Instrument Air Compressor Room) to exceed OSHA IDLH (Immediately Dangerous to Life and Health) levels. The diesel was immediately secured and the room was ventilated. There were no personnel injuries and no public health and safety issues associated with this event. "This retraction is based on the fact that station personnel incorrectly used an Alert trigger value for toxic gas concentration that was well below the actual value which would pose an immediate danger to life and health. In a subsequent evaluation, NextEra concluded that the station used the carbon monoxide (CO) OSHA limits (OSHA Permissible Exposure Limit 8-hour time weighted average of 50 ppm to 200 ppm short term exposure limit) that are normally monitored for confined spaces. The recommended CO limit value of 1200 ppm was determined to be the correct IDLH for the plant air compressor room, the actual reading in the room was 124 ppm. The plant air compressor room is not a confined space, and is not required to be monitored to the same limits as a confined space. "Therefore, the Emergency Notification made on April 25, 2012, documenting an Alert due to toxic gas in a vital area is retracted." The NRC Resident Inspector has been notified. Notified R3DO (Kunowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-04-25
47862 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-04-25 09:00 | 2012-04-25 17:22 | 2012-04-25 | UNANALYZED CONDITIONS RESULTING FROM A NON-CONSERVATIVE ERROR IN CALCULATIONS "A non-conservative error was identified in the Proto-Flo input calculation FC06644 for LPSI (Low Pressure Safety Injection) flow post-RAS [recirculation actuation signal]. The calculation used an incorrect (non-conservative) input for LPSI pump performance. Also, the associated procedure (EOP/AOP Attachment 11) as written does not provide adequate direction during the Alternate Hot Leg Injection mode of operation. "EOP/AOP Attachment 11 (Alternate Hot Leg Injection) used 140 psia as the entry point. The LPSI pumps may not be able to meet minimum flow requirements at this pressure, affecting core cooling and possibly resulting in pump damage. Also the EOP/AOP attachment directs the operator to verify that flow is approximately 400 gpm as indicated on FIC-326. If 400 gpm cannot be achieved the contingency is to open any LPSI loop injection isolation valve. This step would not depressurize the RCS low enough to allow the 400 gpm flow rate to be achieved which would cause insufficient flow. "Therefore, it is reasonable to conclude that the referenced procedural guidance may not be able to complete the safety function of providing adequate core cooling during the Alternate Hot Leg Injection mode of operation under a worst case scenario. "Therefore, this condition is an unanalyzed condition and reportable under 10CFR50.72(b)(3)(ii)(B)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-04-25
47861 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2012-04-23 22:00 | 2012-04-24 13:48 | 2012-04-24 | CONTAMINATED INDIVIDUAL REQUIRED MEDICAL TREATMENT "Westinghouse Environmental Health and Safety (EH&S) staff responded to an operator who was exposed to dilute nitric acid (30%) on the left forearm and left foot. Employee was cleaning scrubber piping in the conversion area of the plant when exposed to the nitric acid solution containing uranium. The employee was treated within the onsite medical facility where decontamination was performed. Medical, emergency response and health physics procedures were followed. Upon completion of the decontamination efforts, the smearable alpha reading was < 50 dpm/100 cm2 and alpha direct reading on forearm was 818 dpm/100 cm2, on foot direct alpha reading was 280 dpm/100 cm2. Medical staff recommended transfer to the hospital for further treatment. Westinghouse followed contaminated injury protocols and had the employee transported to the hospital emergency room via ambulance. A Westinghouse health physics (HP) technician accompanied the employee to the hospital. Surveys were conducted of the ambulance and all results were below established limits. Material Safety Data Sheets for the nitric acid and uranium were provided to the hospital in accordance with procedures. Hospital report describes injury as, 'irritation noted over the left forearm as well as over the left anterior part of the foot and dorsal part of the foot ...some mild orange discoloration noted to these areas.' Employee was monitored for a period of time, given treatment for pain, and then released from the hospital. "Immediate Actions: Initial investigation into the event is ongoing. This event has been entered into the Facility Corrective Action Process Issue # 12-115-001. Local county authorities and state authorities are aware of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2012-04-24
47860 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-04-06 | 2012-04-24 14:03 | 2012-04-24 | FLORIDA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RADIOGRAPHER The following information was obtained from the State of Florida via email: "On April 16, [a licensee] employee notified [the] RSO that his 0-200 pocket detector had gone off scale ten days earlier. His film badge was immediately sent to Rad Detection Services for processing. It was reported to have 25 Rem whole body exposure. This office [Florida Bureau of Radiation Control] was informed on 24 April. The RSO has tried to recreate the scenario but he can't come up with a 4.5 minute exposure scenario. RSO is considering a blood test. Licensee will provide a written report. Florida is investigating." FL Incident No. FL 12-039 The camera involved was an INC IR-100 Model 32, serial number R887, with a 65 Ci Ir-192 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-05-02
47859 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-02-25 01:38 | 2012-04-24 07:52 | 2012-04-24 | INVALID ACTUATION OF STANDBY GAS TREATMENT SECONDARY CONTAINMENT ISOLATION VALVES (SCIVs) "During restoration of Unit 1 reactor protection system (RPS) following preventive maintenance (PM), a link was closed on February 25, 2012 at 0138 EST that resulted in the automatic actuation of the standby gas treatment (SGT) trains for Units 1 and 2 and the automatic isolation of the associated SCIVs (Secondary Containment Isolation Valves). The instruments that input to the actuation logic were in the tripped condition during the performance of the PM with links opened to preclude the automatic response of the SCIVs. The PM procedure did not contain the necessary steps to ensure that the associated instruments that input into the actuation logic were reset prior to reclosing the links that were previously opened to disable their input to the logic. Reclosing the first link associated with a Unit 1 reactor building high radiation monitor trip resulted in an actuation signal that caused the Unit 1 and 2 SGT trains to automatically start as designed, Unit 1 and 2 reactor building normal ventilation to shut down and the Unit 1 and 2 SCIVs to automatically close. This actuation was therefore not the result of a valid signal. The automatic actuation of the SGT system and the isolation of Unit 1 and 2 SCIVs are considered an invalid actuation since the parameters that cause this actuation to occur had not been exceeded. For this reason the actuation is considered invalid and a report to the NRC is not required by 10CFR50.72(b)(3)(iv); however, because the secondary containment isolation signals affected containment isolation valves in more than one system (Unit 1 and 2 components affected) the event is reportable as required by 10CFR50.73(a)(2)(iv)(B)(2). A licensee event report (LER) is required, but a telephone notification is allowed by 10CFR50.73. In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. The affected procedure(s) will be revised to ensure the affected instruments are reset prior to returning the system to service to preclude recurrence during the performance of future RPS PM activities. "The four Standby Gas Treatment (SBGT) fans auto started and both Unit 1 and Unit 2 reactor building and refueling floor normal ventilation systems automatically shutdown and isolated as designed. The SBGT initiation and the ventilation system shutdown were both complete actuations." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-04-24
47858 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-21 16:15 | 2012-04-22 02:50 | 2012-04-25 | APPARENT PHASE IMBALANCE BETWEEN NORMAL AND ALTERNATE POWER CIRCUITS "On April 21, 2012, at 1615 PDT, Diablo Canyon Power Plant (DCPP) operators identified that an attempted manual transfer of the Unit 1 AC power sources from the normal offsite circuit (500 kv) to the alternate offsite circuit (230 kv) failed. "The attempted manual transfer of the offsite power source from the normal 500 kv to the alternate 230 kv was a planned activity to shut down Unit 1 for its 17th refueling outage. The failure to manually transfer was concluded to be caused by an indicated out of phase condition between the 500 kv and 230 kv system. DCPP control transfer systems prevent paralleling and transferring the power supplies from the normal to alternate offsite circuit with an out of phase condition. The offsite AC power sources remain capable of being manually transferred from the normal to the alternate source by way of transferring to diesels as an intermediate step. "The 230 kv system ability to perform its accident mitigation safety function following a reactor trip or safety injection was not affected by the inability to perform a direct manual transfer from the 500 kv offsite power system. "DCPP staff are currently troubleshooting the out of phase indication and will provide an update when the cause is concluded. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM MIKE QUITTER TO HOWIE CROUCH AT 2013 EDT ON 4/25/12 * * * "This is an update to EN #47858 reported on April 22, 2012, where Pacific Gas & Electric Company (PG&E) reported that an attempt to manually transfer the DCPP Unit 1 AC power sources from the normal offsite circuit (500 kV) to the alternate required offsite circuit (230 kV) failed. "PG&E determined that the out-of-phase condition between the 500kV system and the 230 kV system resulted from the offsite power system configurations and conditions existing at the time of the attempted transfer. PG&E established alternate operating guidance to allow operators to perform bus transfers between the 500kV source and the 230 kV source in the event that an out-of-phase condition exists when bus transfer is desired. "PG&E personnel informed the NRC Resident Inspector." Notified R4DO (Proulx). | 20 | 100 | 0 | 82 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2012-04-22
47857 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-21 05:15 | 2012-04-21 12:45 | 2012-04-24 | MAIN STEAM ISOLATION VALVES FAIL TO SHUT "At approximately 0515 EDT on April 21, 2012, the Harris Nuclear Plant [HNP] was in the process of a normal plant shutdown for a refueling outage. HNP was at 0% power in Mode 4. During OST-1046, MSIV Operability Test, 'B' and 'C' Main Steam Isolation Valves (MSIV), failed to close from the main control board. "At 0648 EDT an April 21, 2012 'B' MSIV shut immediately after the instrument air supply was isolated. "At 0938 EDT an April 21, 2012 'C' MSIV shut after the instrument air supply was isolated. "The cause of the equipment failure is not yet known but is currently being investigated. This report is being made in accordance with 10 CFR 50.72 (b)(3)(v)(C), inability to isolate and mitigate a radioactive release, and 10 CFR 50.72 (b)(3)(v)(D), a condition which could have prevented the fulfillment of a safety function to mitigate the consequences of an accident. The plant continues to remain shutdown at 0% power. Other equipment functioned as expected including the turbine isolation valves." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOHN CAVES TO HOWIE CROUCH AT 1258 EDT ON 4/24/12 * * * "Investigation into the condition revealed the instrument air supply to the MSIVs was isolated at 0530 EDT and 'B' MSIV indicated [drifted] shut at 0607 EDT. The plant is currently in Mode 6, Refueling, and the investigation is ongoing." The licensee notified the NRC Resident Inspector. Notified R2DO (Musser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-04-21
47856 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2012-04-20 12:49 | 2012-04-20 16:29 | 2012-04-20 | UNUSUAL EVENT DECLARED DUE TO ELECTRICAL PANEL FIRE IN TURBINE BUILDING San Onofre Unit 2 declared an Unusual Event at 1249 PDT today due to an electrical fire within a fire detection panel (2L319) in the Unit 2 turbine building. The fire was declared extinguished at 1314 PDT after the panel was de-energized. The location of the fire had no impact on plant operation, equipment, or personnel safety. No offsite assistance was necessary. The licensee exited the Unusual Event at 1341 PDT after the licensee confirmed that the fire was terminated and there was no ongoing risk to the plant. The licensee notified state and local authorities and the NRC Resident Inspector. The NRC Operations Center notified other Federal Agencies (DHS SWO, FEMA Ops, DHS NICC, and NuclearSSA via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-04-20
47855 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-19 17:24 | 2012-04-19 22:32 | 2012-04-19 | TSC VENTILATION INOPERABLE "At approximately 1724 EDT on April 19, 2012 with the Harris Nuclear Plant operating at 90% power in mode 1, Air Handler 17 was discovered not operating. Air Handler 17 provides ventilation supporting environmental habitability to the Technical Support Center (TSC) to keep ambient temperatures habitable for personnel and to ensure communications and assessment equipment remains functional. This degrades the heating and cooling capacity of the TSC by approximately one third. Due to the cool weather in the forecast, the remaining cooling systems will be operating more efficiently than they would in the hot summer months, which mitigates the impact of the degraded ventilation system. The system has been repaired as of 1950 EDT on April 19, 2012. The cause of the equipment failure was a broken belt and a condition report has been entered into the site's corrective action program. This report is being made in accordance with 10 CFR 50.72, criterion (b)(3)(xiii) as a condition that may impair the functionality of an Emergency Response Facility. The plant continues to operate at 90%. Other equipment functioned as expected. The on call Emergency Response Manager and Site Emergency Coordinator (TSC) have been notified and the alternate TSC is available." The licensee notified the NRC Resident Inspector. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-19
47854 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-19 17:45 | 2012-04-19 22:07 | 2012-04-19 | POTENTIAL FIRE INDUCED SPURIOUS OPERATION OF STEAM GENERATOR PORV BLOCK VALVES "On March 22, 2012, McGuire Nuclear Station notified the NRC of a condition which could result in fire induced spurious operation of the block valves for the Unit 2 Steam Generator (SG) Power Operated Relief Valves (PORVs). This potential condition could adversely affect the ability to achieve and maintain a cold shutdown of Unit 2. This represented a condition reportable as per the requirements of 10 CFR 50.72(b)(3)(ii)(B). Reference Event #47764 [for Unit-2]. "In accordance with 10 CFR 50.72(c)(2)(i), McGuire is reporting results of ensuing cause and extent of condition evaluation of Event #47764, which has identified a similar condition on McGuire Unit 1. This condition could result in a fire induced spurious operation of the block valves for the Unit 1 SG PORVs. This spurious operation could potentially damage these valves and render them inoperable. Since these valves are unisolable, they could not be repaired to allow the Unit 1 SGs to be used for Unit cool down if needed. This potential condition could adversely affect the ability of the plant to achieve and maintain a cold shutdown of Unit 1. This represents a condition reportable as per the requirements of 10 CFR 50.72(b)(3)(ii)(B). This potential condition is mitigated by existing compensatory measures (i.e. fire watches) which have been in place as part of McGuire's transition to NFPA 805." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-04-19
47853 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-04-19 14:30 | 2012-04-19 20:58 | 2012-04-19 | HPCI FAILED TRIP TESTING SURVEILLANCE "On 04/19/12 at 1430 while performing 1-SR-3.5.1.7, HPCI [High Pressure Coolant Injection] Main & Booster Pump Set developed head & flow rate at rated reactor pressure. The HPCI turbine failed to trip using the manual trip pushbutton. This manual trip pushbutton should have caused the 1-FCV-73-18, HPCI TURBINE STOP VALVE, to go closed. HPCI was secured by taking the 1-FCV-73-16, HPCI TURBINE STEAM SUPPLY VALVE, to close. The 1-FCV-73-18, HPCI TURBINE STOP VALVE, also failed to go closed locally using the 1-XCV-73-18, HPCI TURBINE MECHANICAL TRIP, nor did it go closed when the auxiliary oil pump was secured. "With the 1-FCV-73-18, HPCI TURBINE STOP VALVE, open, the HPCI ramp generator is no longer in the circuit therefore, should an initiation occur and cause the 1-FCV-73-16, HPCI TURBINE STEAM SUPPLY VALVE, to open there is the potential for the HPCI turbine to over speed. Therefore, HPCI was isolated using 1-FCV-73-3, HPCI STEAM LINE OUTBD ISOL VALVE. This incident is reportable as an 8-hour ENS notification under 10CFR 50,72 (b)(3)(v) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(vii). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-04-19
47852 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-04-19 11:58 | 2012-04-19 17:47 | 2012-04-19 | OFFSITE TRANSPORT OF POTENTIALLY CONTAMINATED INJURED WORKER "At approximately 1156 EDT on 4/19/2012, a craft contractor worker was transported to an off-site medical facility due to a work-related injury. The injured individual was partially surveyed by a Health Physics technician in their anti-contamination clothing prior to leaving the site and no radioactive contamination was detected. The injured individual was then transported by ambulance accompanied by a Health Physics technician to the local hospital for medical treatment. "At the hospital, the individual and applicable areas and equipment were surveyed by the Health Physics technician and no radioactive contamination was detected. The individual's anti-contamination clothing was returned to the site. "This notification is being made under the 10CFR50.72(b)(3)(xii) reporting requirements since a complete survey of the injured individual was unable to be made and he was considered to be potentially contaminated prior to being transported offsite. "The site NRC Resident Inspector has been notified." The worker was in containment on a polar crane platform when injured. He was subsequently released from the hospital and cleared to work. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-04-19
47851 | -1 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-04-18 13:45 | 2012-04-19 13:30 | 2012-05-17 | LOCAL ALARM HORN WAS FOUND TO BE INAUDIBLE DURING ROUTINE TESTING "At approximately 1345 EDT on 4/18/12, during routine testing on an outdoor Criticality Accident Alarm System (CAAS) Data Acquisition Module (DAM #22), the local alarm horn in the Wilmington Field Services Center (WFSC) building #3 inspection records area was found to be inaudible. The cause and extent of the condition is under investigation. "Personnel were removed from the inspection records area until compensatory measures were established. There are no active fissile material operations impacted by this discovery, thus no unsafe condition existed. "This event is being reported pursuant to the requirements of 10CFR70.50 (b)(2)." The licensee notified the NC Division of Radiation Protection and the New Hanover County Emergency Response Center. * * * RETRACTION FROM SCOTT MURRAY TO JOHN SHOEMAKER ON 05/17/2012 AT 1641 EDT * * * "Upon further review, GNF-A has determined that the reported condition (EN 47851) was not required to be reported by the plain letter of the regulation (10 CFR 70.50(b)(2)) and the filing of the report was inconsistent with industry practice. As such, this report is being retracted. GNF-A has entered the condition identified in the course of the monthly tests (i.e., areas where audibility of the CAAS should be enhanced) into its corrective action program and is addressing them accordingly." The licensee will notify NRC Region II (Thomas). Notified R2DO (Shaeffer) and NMSS (Stablein). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2012-04-19
47850 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-04-19 07:53 | 2012-04-19 11:10 | 2012-04-20 | MANUAL REACTOR SCRAM FOLLOWING LOSS OF RECIRCULATION PUMPS "Limerick Unit 1 was manually scrammed from 100% power at 0753 hours on 4/19/12 in accordance with plant procedure OT-112 'Recirculation Pump Trip' when both 1A and 1B Recirculation Pump Adjustable Speed Drives (ASDs) tripped due to an electrical fault affecting the 144D and 114A non-safety related 480V Load Centers. The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass valves to the main condenser and normal level control using feedwater. The manual RPS actuation is reportable under 10 CFR 50.72(b)(2). "The Technical Support Center (TSC) Normal Air conditioning systems shut down due to loss of power from the 144D Load Center. The loss of power also affects the flow indication for the Emergency Ventilation system. This is considered a Loss of Emergency Assessment Capability, and reportable under 10 CFR 50.72(b)(3)(xiii). The Emergency TSC Ventilation system is available but flow cannot be verified. During a required activation the TSC, responders would report to the TSC. If conditions required use of the Emergency Ventilation system, the Station Emergency Director would assess habitability in accordance with Station procedures. TSC relocation of personnel would be directed as required until such time that the TSC ventilation system is returned to service" The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1726 ON 4/20/2012 FROM BRANDON SHULTZ TO MARK ABRAMOVITZ * * * "The Technical Support Center (TSC) 144D load center has been re-energized, restoring the emergency ventilation flow indication and emergency assessment capability to its normal stand-by condition." The switchgear was inspected for any potential grounds and then reenergized at approximately 0800 EDT on 4/20/2023. The licensee notified the NRC Resident Inspector. Notified the R1DO (Joustra). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-04-19
47849 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-04-18 19:55 | 2012-04-18 22:46 | 2012-04-18 | FITNESS FOR DUTY A non-supervisor licensed operator had a confirmed positive result for alcohol during a random fitness-for-duty test. The operator's access to the plant has been suspended. Contact the Headquarter Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2012-04-18
47848 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-10-06 13:44 | 2012-04-18 18:53 | 2012-09-26 | WASTE DISPOSAL SYSTEM CLASS ONE SEISMIC SUPPORT INOPERABLE "The Waste Disposal System [WDS] Class 1 piping requires operable seismic supports downstream of the isolation valve class break. Currently, eight (8) INC [International Nuclear Safety, Corp.] snubbers have been degraded to [Non Nuclear System] NNS Class 4 ridged struts. The snubbers original design function was to allow thermal motion but restrain seismic motion. "The snubbers have been identified as potential to create an unanalyzed condition that over stresses the safety class 1 drain pipe upstream of the isolation valve if the snubbers on the drain pipe downstream of the isolation valve were in a locked condition (acting as a strut). Per NRC bulletin 81-01, these snubbers are assumed to be frozen and do not allow movement of the pipe; thus, they have been degraded to rigid struts as they are not in the snubber program and are not tested. They still provide a seismic safety function for [class] II/I issues and act as a strut to provide horizontal restraint to the WDS piping. "The snubbers were removed from the piping system and tested to determine their performance and if they would have moved to allow thermal growth. Six snubbers failed the test and were either in a locked condition or their movement was dimensionally small relative to the required movement. The [Reactor Coolant System] RCS is within acceptable stress values with the snubbers removed. "The 8-hour regulatory reporting time has been exceeded." An initial Reportability Evaluation was completed on March 26, 2012 and had determined the supports were operable. A second Reportability Evaluation later determined the supports have been inoperable since October 6, 2011. The WDS is used to drain the RCS. The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 9/26/12 AT 1949 EDT FROM ROBERT KROS TO DONG PARK * * * "Additional review and testing demonstrated that [there was] no degradation of the RCS from thermal fatigue. The analysis demonstrates adequate past performance of the snubbers with regard to thermal fatigue. The impact of the snubber has been analyzed and determined to have not resulted in an unanalyzed condition that significantly degraded plant safety. Therefore, this event is being retracted. The failure to retract this notification in a timely fashion has been entered into the corrective action system." The licensee will notify the NRC Resident Inspector. Notified R4DO (Werner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-04-18
47847 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2012-04-18 15:11 | 2012-04-18 18:07 | 2012-04-18 | UNIT TWO AUTOMATIC REACTOR SCRAM ON HIGH REACTOR PRESSURE "On April 18, 2012, at 1511 hours (CDT), an automatic scram occurred on high reactor pressure. The pressure increase occurred during post-modification testing on the main generator automatic voltage regulator, which had been upgraded during the recent refueling outage. "Following the reactor scram, reactor water level decreased to approximately zero inches, which resulted in automatic Group II and III isolations (Reactor Water Clean Up and Secondary Containment Isolation) as expected. All systems responded properly to the event. The cause of the event is still under investigation. "Unit 1 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." All Control Rods fully inserted, decay heat is being removed through the bypass steam valves to the main condenser, and the plant remains in a normal shutdown electrical alignment. The high reactor pressure appears to have been caused by a load rejection associated with the main generator voltage regulator testing. The licensee has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-04-18
47846 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2012-04-18 | 2012-04-18 14:46 | 2012-04-18 | FISHER TYPE 9500 BUTTERFLY VALVES CONTAIN NON DEDICATED PARTS "While reviewing an incoming order for a Type 9500 Butterfly Valve, it was discovered that two parts, namely the Thrust Plate and Thrust Plate Cap Screws, were not called out for Commercial Grade Dedication per Fisher Manufacturing Procedure (FMP) 2K27. These parts are considered an essential-to-function part in order for the valve to perform an active safety function. "Upon discovery of this possible failure to comply, an investigation was performed on all Safety-Related Type 9500 Butterfly Valves that have been shipped, are in active service or inventory, and are required contractually to be dedicated and it was determined that the Thrust Plate and Thrust Plate Cap Screws in these valves were supplied commercial grade and had not been dedicated per FMP 2K27. "The Thrust Plates retain the Thrust Sleeve Assemblies which provide a bearing surface for the Valve Shaft. The Thrust Sleeve Assemblies also provide adjustment to the Valve Body Liner. The Thrust Plate Cap Screws retain the Thrust Plates. Without the Thrust Plates or the Thrust Plate Cap Screws, there is a risk that the Thrust Sleeve Assemblies will disengage from the Valve Body, preventing the valve from performing its active safety-related function. "It is Fisher's opinion that while the Thrust plates and Thrust Plate Cap Screws were not dedicated, the failure to dedicate does not pose an inherent safety risk given the materials used. "Fisher will revise its procedures to ensure that this issue is corrected and does not happen in the future. "Action Required: Fisher will supply properly dedicated Thrust Plates and Thrust Plate Cap Screws for the affected valves that are in inventory or service, at no cost to the affected customers. Notification has been made to plants with the Type 9500 Butterfly Valves for; Cooper Plant (NPPD), Vogtle Plant (Georgia Power), Ft. Calhoun Plant (OPPD), and Millstone Plant (Dominion) and specific valve order numbers and serial numbers were provided. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-04-18
47845 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-17 21:30 | 2012-04-17 23:12 | 2012-05-15 | PLANT PROCESS COMPUTER REMOVED FROM SERVICE FOR PLANNED REPLACEMENT "At 2130 (CDT) on April 17, 2012, the Unit 1 Plant Process Computer (PPC) was removed from service for a planned replacement in the current Unit 1 Refueling Outage. The Unit 1 PPC feeds the Safety Parameter Display System (SPDS) used in the Main Control Room (MCR) and the Technical Support Center (TSC). The Unit 1 PPC also feeds the Emergency Response Data System (ERDS). The Unit 1 and Unit 2 PPCs also feed the Plant Parameter Display System (PPDS) used in the MCR, TSC and Emergency Operations Facility (EOF). Meteorological data will remain available in the MCR but not through ERDS for either Unit 1 or Unit 2. The dose assessment program will remain functional as the Unit 2 Plant Process computer will be capable of providing the necessary data through PPDS to run the program. The dose assessment program is not affected by the Unit 1 PPC being out of service. As compensatory measures, a proceduralized backup method to fax or communicate via a phone circuit applicable data to the NRC, TSC, and EOF exists. There is no impact to the Emergency Notification System (ENS) or Health Physics Network (HPN) communication systems. "The new Unit 1 PPC is scheduled to be functional on April 21, 2012. However, based on the mode Unit 1 will be in, this will limit the number of points that would provide usable data. The Unit 1 PPC will be tested as mode changes occur. The Unit 1 PPC is planned to be declared functional by Mode 2. A follow-up ENS call will be made once the Unit 1 PPC is declared functional. "The loss of SPDS and ERDS is a 'major loss of assessment capability' and is reportable under 10CFR50.72(b)(3)(xiii). "The NRC Senior Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS call." * * * UPDATE FROM JOE KLEVORN TO JOHN KNOKE AT 1035 EDT ON 05/15/12 * * * "As of 1035 EDT on May 15, 2012, the Unit 1 PPC is considered operational with respect to the Safety Parameter Display System (SPDS), Plant Parameter Display System (PPDS) and Emergency Response Data System (ERDS). Therefore, a Major Loss of Assessment Capability no longer exists on Unit 1. The EP Manager will contact the NRC Computer Center for Unit 1 to ensure the ERDS data is being satisfactorily sent to the NRC. "The NRC Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS update." The R3DO (Patty Pelke) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-17
47844 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-17 15:40 | 2012-04-17 21:02 | 2012-06-07 | UNIT 2 SECONDARY CONTAINMENT AFFECTED BY VIOLATION OF UNIT 1 SECONDARY CONTAINMENT INTEGRITY DURING OUTAGE "At 1540 (EDT) on 4/17/12, with Unit 1 in mode 5 and Unit 2 in mode 1, the Work Control Center was notified that the U1 #2 Main Stop Valve (MSV) was disassembled. The U1 #2 MSV was required to be intact to maintain Unit 1 Secondary Containment. Ongoing work on the D Main Steam Line Outboard Valve created a pathway that violated Unit 1 secondary containment integrity. Unit 1 Secondary Containment is required to be operable for Unit 2 while Unit 1 Zone 1 is aligned to the Recirculation Plenum. Unit 1 Zone 1 was isolated from the recirculation plenum and Unit 2 Secondary Containment was restored at 1643 (EDT) on 4/17/12. Unit 2 Secondary Containment differential pressures were maintained throughout the event. "This is considered a loss of an entire safety function and requires an 8 hour report per 10CFR50.72(b)(3)(v)(C)." The licensee is still investigating the cause but it appears to be associated with recent administrative changes to the Reactor Vessel draining definition and work process procedures. The licensee has notified the NRC Resident Inspector. *** RETRACTION FROM RON FRY TO S. SANDIN ON 6/7/12 AT 0205 EDT *** The licensee is retracting this report based on the following: "On April 17, 2012, work on the Unit 1 'D' Main Steam Line Outboard Valve with the Unit 1 #2 Main Stop Valve disassembled created a pathway that violated Unit 1 secondary containment integrity. Since Unit 1 Secondary Containment is required to be operable for Unit 2 while Unit 1 Zone 1 would be aligned to the Recirculation Plenum in the event of a secondary containment isolation signal, the condition impacted Unit 2 Secondary Containment. Susquehanna considered the impact a loss of safety function and reported the impact in accordance with 10CFR50.72(b)(3)(v)(C). "Following the ENS report, Susquehanna analyzed the impact of the opening. Calculations were performed that show secondary containment would have maintained the dose consequences to the public and control room operators within regulatory limits (10 CFR 50.67) assuming a Unit 2 design basis accident (Unit 1 was in a refueling outage at the time of the condition). "Based on the above information, Susquehanna has determined that there was no loss of safety function and this ENS report is retracted." The licensee informed the NRC Resident Inspector. Notified R1DO(Cahill). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-04-17
47843 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-17 09:00 | 2012-04-17 16:45 | 2012-05-22 | TECHNICAL SUPPORT CENTER HAD ONLY ONE POWER SOURCE DURING PREPLANNED MAINTENANCE "On April 16, 2012, at 0738 hours, the Harris Nuclear Plant notified the NRC Operations Center (i.e., Event Number 47838) of preplanned maintenance on the Technical Support Center (TSC) normal power supply. "Following completion of the power transfer, it was discovered that in the current alignment, the TSC is only powered from one power source, which is the backup power supply. "A backup diesel generator is stationed near the TSC which can be connected if necessary during an emergency. "Activities are in progress to modify the existing procedure to allow the TSC to be connected to the offsite power source which will restore two sources of power to the TSC. This normal power arrangement is expected to remain in place while maintenance is performed on the TSC normal power supply for approximately two months. "The NRC Resident Inspector has been informed. "This report was made in accordance with 10 CFR 50.72(b)(3)(xiii)." * * * UPDATE FROM JOHN CAVES TO JOE O'HARA AT 1211 EDT ON 5/22/12 * * * "On April 19, 2012, the power configuration was revised to restore the availability of two sources of power to the TSC. An extent of condition review identified two similar conditions in 2009 and 2010 where the TSC had only one source of power for approximately two months each time. The backup diesel generator described in the initial report was not available during these two periods; providing an alternate power source in the event it was needed would have required lifting a clearance and closing a breaker. These conditions might be of generic interest or concern and are therefore provided as a follow-up report." The NRC Resident Inspector has been notified. Notified R2DO (Shaeffer). | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-17
47842 | 0 | SWAGELOK COMPANY |  |  |  |  | 2012-04-17 | 2012-04-17 13:51 | 2012-04-17 | PART 21 REPORT - SWAGELOK U SERIES BELLOWS VALVES LOOSENING OF STEM TIPS "Swagelok received a return from Duke Energy (Oconee) for two 8U series bellows valves for investigation of stem tips that had loosened during performance testing of equipment. "Our evaluation confirmed loosening of the stem tips and determined the root cause to be higher than normal torque being applied to the valve handle during closure. (Please note that we did not specify a minimum or maximum torque for our operating instructions). This caused the stem and the stem insert interface to loosen, but not fully disengage. Our tests show that closure to catalog specification of 4.0 x 10-9 atm. cc/sec of helium can still be achieved with this condition. "Therefore, it is the opinion of Swagelok that there is no inherent safety risk associated due to this condition, however lower than expected flow through the valve, or erratic flow, can occur if the stem tip loosens. If utilities consider full flow as a safety function, they should evaluate the valves currently in service for this condition. "Applicability - There have been no other field returns for this condition. The possible condition extends to the Swagelok 4U, 6U and 8U series bellows valves. Only hand operated valves are susceptible; air operated valves are excluded, as are the 12U series valves supplied by Swagelok." Callaway may also be affected and will be notified by the Supplier. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-04-17
47841 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-04-13 | 2012-04-17 10:53 | 2012-04-17 | AGREEMENT STATE REPORT - RADIOTHERAPY UNDERDOSE The following report was received via fax: "On April 13, 2012, a patient was to receive a prescribed dose of 100 mCi of iodine-131 (I-131) for thyroid cancer. Two capsules of I-131 were received from the radiopharmacy in a single vial which was assayed to assure proper dose prior to administering to the patient. The patient was given the contents of the vial for treatment and the treatment was considered complete. The Nuclear Medicine staff prepared the remaining container for return to the radiopharmacy on Monday April 16, 2012. The radiopharmacy picked up the I-131 container and returned it to their facility. Upon inspection of the returned package, the radiopharmacy discovered that one of the two capsules intended for the treatment remained lodged in the vial. The radiopharmacy informed Tristan and the RSO at 12:30 EDT on Monday April 16, 2012. The patient received 50 mCi of the intended 100 mCi dose. "Patient and referring physician are in the process of being notified. The [PA] Department [of Radiation Protection] plans to do a reactive inspection on April 17, 2012." PA Event ID: PA120013 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-04-23
47840 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-16 09:32 | 2012-04-16 17:11 | 2012-04-16 | UNAVAILABILITY OF TECHNICAL SUPPORT CENTER RADIATION MONITOR "At 0932 EDT on April 16, 2012, the Harris Nuclear Plant (HNP) Technical Support Center (TSC) normal power feed was removed from service for scheduled maintenance. "Upon restoration of power to the TSC, it was identified that the TSC radiation monitor (RM-3653C) did not return to service as expected. Following discovery, Radiation Protection technicians were dispatched to investigate the cause of RM-3653C not operating properly. "At 1627 EDT, the TSC radiation monitor has been returned to service and is operable. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREGÀ1022, Rev. 2 due to the loss of the TSC radiation monitor. "The NRC Senior Resident Inspector has been informed" The cause of the radiation monitor failure was related to a dead back-up battery which did not allow the radiation monitor to properly re-boot after power was restored. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-16
47839 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-04-13 07:00 | 2012-04-16 14:22 | 2012-04-16 | LOST STATIC ELIMINATOR The licensee notified the Kentucky Department of Public Health and Safety, Radiation Health Branch on April 16, 2012 at 1135 (CDT) of a missing static eliminator. The static eliminator was discovered to be missing by an oncoming operator on April 13, 2012 at 0700 (CDT). An operator on the previous shift reported the device to be in place. The Director of Facility Operations was not in the office on April 13, 2012 and was not made aware of the missing device until April 16, 2012 at 0715 (CDT). The licensee initiated a search for the device on April 16, 2012 at 0715 (CDT) but has been unsuccessful in locating the device. The licensee plans to continue searching for the device. The licensee does not suspect tampering or theft and no exposures to personnel have occurred or are expected at this time. The device is a Model P-2021 Static Eliminator, Serial # A2HU670, with a 10 mCi Po-210 source. Kentucky Radiation Health Branch Report number KY120007. No other notifications have been made by the licensee. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-04-19
47838 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-04-16 08:00 | 2012-04-16 07:38 | 2012-04-16 | PLANNED MAINTENANCE ON THE TECHNICAL SUPPORT CENTER NORMAL POWER SUPPLY "At approximately 0800 [EDT] on April 16, 2012, the Harris Nuclear Plant (HNP) Technical Support Center (TSC) normal power feed will be removed from service for scheduled maintenance. "The maintenance will consist of first switching the TSC to the TSC backup power supply. The normal supply will be disconnected and replaced with another offsite power source which is independent of the Harris switchyard. This power arrangement will remain in place while maintenance is performed on the TSC normal power supply and is expected to last approximately two months. A backup diesel generator is stationed near the TSC which can be connected if necessary during an emergency. "An update will be provided when the TSC normal power supply has been returned to its normal alignment "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2, since this work activity affects an emergency response facility for the duration of the maintenance. "The [NRC] Senior Resident Inspector has been informed." | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-16
47837 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2012-04-15 12:20 | 2012-04-15 17:13 | 2012-04-15 | MANUAL REACTOR TRIP DUE TO CONTROL ROD DEVIATION DURING STARTUP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 15, 2012 at approximately 1220 Mountain Standard Time (MST), Palo Verde Unit 3 was manually tripped during low power physics testing. "While conducting low power physics testing following a refueling outage, Regulating Group 1 rods were being inserted while simultaneously diluting to maintain a constant power level below the Point of Adding Heat. While inserting rods one rod deviated from its subgroup when it stopped moving. The Reactor Operator immediately ceased rod motion and the dilution was stopped. The residual positive reactivity in the core caused a corresponding reactor power increase that approached procedural power limits set forth in the low power physics testing procedure. Based on these indications, operators initiated a manual reactor trip. "Following the reactor trip, all CEAs inserted fully into the core. All systems operated as expected and this event was diagnosed as an uncomplicated reactor trip. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 3 is stable and in Mode 3 feeding Steam Generators with Auxiliary Feedwater Pump 'N'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 3 reactor trip." The electrical lineup remained normal. Decay heat is being removed via the steam bypass to the main condenser. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Startup; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-04-15
47836 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-04-14 13:46 | 2012-04-14 16:12 | 2012-04-14 | MANUAL REACTOR TRIP DUE TO LOW MAIN FEEDWATER FLOW "At 1346 EDT, Vogtle Unit 1 reactor was manually tripped from 100% power due to Main Feedwater Pump 'B' discharge flow lowering unexpectedly. All control rods fully inserted. AFW system automatically actuated as expected. System responses allowed for an uncomplicated reactor trip response. Plant is stable in Mode 3 during cause investigation." The electrical lineup remained normal. No safety valves lifted due to the trip. Decay heat is being removed via the steam dumps to the main condenser. The licensee has notified the NRC Resident Inspectors. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-04-14
47835 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2012-04-11 | 2012-04-13 20:37 | 2012-04-13 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DETECTED IN LOAD OF SCRAP METAL The following information was provided by the State of Nevada via email: On 4/11/12 a report was received [by Nevada State Health Division] that a truckload of radioactive scrap metal belonging to Top Dollar Recycling was refused in Southern California. This scrap steel originally came from a mine in Utah. On 4/12/12, the 40 foot semi-truck of scrap metal returned to Top Dollar Recycling and a site visit by the State Radiation Control Program (RCP) was conducted. RCP staff took measurements of the semi-truck's scrap metal. Background reading was <10uR/hr, and the highest readings of 50uR/hr on contact were near the back of the truck on the driver's side. The truck was unloaded using a small bobcat loader, spread out and surveyed. One piece of scaffolding, about 4 foot long and bent roughly in half, had elevated readings of 180 uR/hr on contact and identified as Ra-226. The scaffold, which was tubular steel and hard packed with soil type debris, was the source of radiation. The remainder of the semi-truck was unloaded, and all scaffolding metal was segregated and surveyed individually. No additional sources of radiation were identified. The other metal on the truck was also surveyed with no elevated readings. The outside of a very large pile (12' x 20') of metal from the same mine was scanned and no elevated reading were found. Top Dollar Recycling took possession of the item, wrapped it in a plastic garbage bag before moving it to a sturdy container in the storage/control location. Item Number: NV120011 . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2012-04-18
47834 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-04-13 15:25 | 2012-04-13 19:31 | 2012-04-13 | UNANALYZED CONDITION IMPACTING EMERGENCY DIESEL GENERATOR LOADING "On March 14, 2012, it was determined that in the event of an Appendix R fire, fire damage to cables in certain fire areas could cause a Residual Heat Removal Service Water System (RHRSW) pump to spuriously start, overload EDG A and B, and render them inoperable during certain Appendix R fires. This was reported as an unanalyzed condition (Ref. EN #47764). "An extent of condition analysis was completed on April 13, 2012. From this analysis it was determined that EDG A, D, 3EC, and 3ED could exceed the maximum rated loading due to the potential for an automatic or spurious start of RHRSW Pumps B3 and D3 that supply Emergency Equipment Cooling Water (EECW) to essential safety equipment. "The following are the Fire Areas (FA) affected: EDG A in FA 21 EDG D for FA 2-3 and 9 EDG 3EC in FA 1-1, 1-3, and 20, and EDG 3ED in FA 1-1, 1-3, 1-4, and 20. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). This is also reportable as a 60 day written report IAW 10 CFR 50.73(a)(2)(ii)(B). This event was entered into the licensee's Corrective Action Program as PER 536176. "The NRC Resident Inspector has been notified of this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-04-13
47833 | 0 | MITSUBISHI HEAVY INDUSTRIES, LTD. |  |  |  |  | 2012-02-21 | 2012-04-13 15:58 | 2012-09-07 | PART 21 INTERIM REPORT - STEAM GENERATOR TUBE WEAR This interim Part 21 is in regard to San Onofre Nuclear Generating Station, Unit 2, Steam Generator replacement. "During the first refueling outage following steam generator replacement, eddy current testing identified ten total tubes with depths of 90 to 28 percent of the tube wall thickness. Some of the affected tubes were located adjacent to retainer bars. The retainer bars are part of the floating anti-vibration bar (AVB) structure that stabilizes the u-bend region of the tubes. "Other tubes in the two steam generators had detectable wear associated with support points elsewhere in the AVB structure. Each steam generator has 9727 tubes with an 8 percent (778 tubes) design margin for tube plugging. "Discovery Date: February 13, 2012 "Evaluation completion schedule date: May 31, 2012" "Those Mitsubishi Heavy Industries customers potentially affected by this issue have been notified and will receive a copy of this interim report." Reference Document: UET-20120089 Interim Report No: U21-018-IR (0) Notified R1DO (Joustra), R2DO (Nease), R3DO (Peterson), R4DO (O'Keefe), and Part 21 Group via email. * * * UPDATE FROM MITSUBISHI HEAVY INDUSTRIES, LTD VIA FAX ON 6/4/12 AT 1145 EDT * * * The vendor changed the number of tubes identified with wear depths of 90 to 28 percent from ten tubes to six tubes and only some of the tubes were adjacent to retainer bars. Notified R1DO (Cahill), R2DO (Vias), R3DO (Passehl), R4DO (Gepford) and Part 21 Groups via email. * * * UPDATE FROM MITSUBISHI HEAVY INDUSTRIES, LTD VIA FAX ON 9/7/12 AT 1539 EDT * * * "MHI evaluated that the deviation contains a reportable defect for San Onofre Nuclear Generating Station Unit 2 and 3." Notified R4DO (Gaddy) and Part 21 Reactor Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-04-15
47832 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-04-11 | 2012-04-13 13:35 | 2012-04-13 | AGREEMENT STATE REPORT - UNDERDOSE TO PATIENT RECEIVING YTTRIUM-90 MICROSPHERES TREATMENT The following information was sent by the State of Texas via email: "On April 13, 2012, the Agency [Texas Department of Health] was notified by the licensee that a therapy event had occurred on April 11, 2012. A patient was prescribed 105 grays using Yttrium-90 microspheres. The patient received only 77.4 grays. The licensee stated that the reduced exposure was because a flow clamp was not in the fully opened position allowing microspheres to plate out in the flow tube instead of being administered to the patient. The licensee stated that there were no adverse effects on the patient. "Additional information will be provided as it is received in accordance with SA-300." Texas Report No: I-8948 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-04-19
47831 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-04-04 | 2012-04-13 11:50 | 2012-04-13 | AGREEMENT STATE REPORT - TC-99M GENERATOR INADVERTANTLY SENT TO NON-LICENSED RECIPIENT The following information was received from the State of California by email: "The hospital had sent a depleted Tc-99m generator to an incorrect recipient, a non-licensee. They had intended to return it to Mallinckrodt in St. Louis, [Missouri]. He [RSO] thought the generator still contained about 100 mCi. The package was shipped on 4/4/12, and was retrieved on 4/6/12 after the mistake was discovered." The package was returned to Saint Joseph Hospital and the following week the hospital resent the package to the correct recipient, Mallinckrodt. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-04-18
47830 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-04-11 | 2012-04-13 10:07 | 2012-04-13 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "On April 11, 2012, a technician performing compaction tests using a CPN MC portable moisture density gauge (10 millicuries cesium-137; 50 millicuries americium-241), left the gauge during a test to prepare the next test location 20 to 30 feet away. A compaction roller ran over the gauge and shattered the gauge housing. The technician cordoned off the area and contacted the Radiation Safety Officer. The RSO contacted the Virginia Emergency Operations Center and returned the gauge to its storage area after ensuring the sources were inside their shields. Based on an onsite investigation by members of the Virginia Radioactive Materials Program, it was determined that no individual was likely to have received a radiation dose and that the gauge sources were secured in their shields. The licensee has contacted the gauge distributor to return the gauge." Virginia Report No.: VA-12-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2012-04-18
47829 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-04-12 08:00 | 2012-04-12 18:30 | 2012-04-12 | INTERNAL REPORTING REQUIREMENT FOR CRITICALITY SAFETY CONTROLS "At approximately 8:00 am on April 12, 2012, a criticality safety engineer was notified that waste in the Dry Conversion Process (DCP) area was improperly placed into a designated storage location. Upon investigation, it was determined that waste in the designated location contained materials with a total of less than 5 kg of uranium. As a result, no unsafe condition existed. "An operator placed a bag of waste adjacent to a partially filled receptacle instead of placing the bag into the receptacle. This resulted in a portion of one of the documented administrative controls for criticality safety, requiring 24 inches separation between waste storage locations, to be degraded. This event is being conservatively reported per internal procedural requirements. "As an immediate corrective action, the material was removed and transferred to the waste processing area. In addition, a shop wide communication to Fuel Manufacturing Operations is underway to inform operators of the issue. "Additional corrective actions and extent of condition are being evaluated. "At no time was an unsafe condition present." Notifications were sent to state and local agencies and NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2012-04-12
47828 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-04-12 09:30 | 2012-04-12 09:42 | 2012-04-13 | TSC AND EOF OUT OF SERVICE DUE TO MAINTENANCE "At approximately 0930 hours EDT on Thursday, April 12, 2012, the H. B. Robinson Steam Electric Plant, Unit No. 2, Technical Support Center (TSC)/Emergency Response Facility (EOF) air conditioning and charcoal filtration systems will be removed from service to facilitate the replacement of the charcoal filtration media. The duration of work is expected to be approximately 11 hours. Since the unavailability will last greater than 8 hours, this is considered a Loss of Emergency Assessment Capability, and reportable under 10 CFR 50.72(b)(3)(xiii). "Due to the inability of the TSC/EOF ventilation system to maintain a habitable atmosphere, as a compensatory measure, Emergency Responders assigned to these facilities have been informed to report to the alternate facilities until such time that the TSC/EOF ventilation system has been returned to service. "TSC/EOF ventilation system maintenance and post maintenance testing is scheduled to be completed by 2030 hours EDT on Thursday April 12, 2012. "The NRC Resident Inspector has been informed." * * * UPDATE FROM WARREN WONKA TO HOWIE CROUCH AT 0435 EDT ON 4/13/12 * * * At 1814 EDT on 4/12/12, maintenance on the TSC/EOF ventilation system was completed and the TSC/EOF was returned to service. Notified R2DO (O'Donohue). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-12
47827 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2012-04-11 10:48 | 2012-04-12 07:28 | 2012-04-12 | FITNESS FOR DUTY - A CONTRACT SUPERVISOR TESTED POSITIVE ON A DRUG TEST A non-licensed contract supervisor tested positive for illegal drugs on a random fitness-for-duty test. The individual's access has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2012-04-12
47826 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-04-11 18:07 | 2012-04-11 22:38 | 2012-04-11 | BRIEF LOSS OF RHR PUMP DUE TO VOLTAGE TRANSIENT "On 4/11/12 at 1807 EDT, with the plant shutdown in Mode 5 during Refueling Outage 15, the 'A' Residual Heat Removal pump tripped while operating in the Shutdown Cooling Mode. The pump trip was due to an isolation of the E1150F009 'Division 1 RHR Shutdown Cooling Inboard Isolation Valve.' This resulted in an interruption of primary decay heat removal for approximately 11 minutes. Approximate calculated time to boil was 23.1 hours. This is being reported under 10CFR50.72(b)(3)(v)(B) 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.' "At the time of the pump trip, the station was attempting to restore power to Division 2 Bus 65E from the 64T cross tie bus. A voltage transient occurred due to a fault and caused a Group 4 (Shutdown Cooling/Head Spray) isolation signal. Abnormal Operating Procedure 20.205.01 'Loss of Shutdown Cooling,' was entered, the Group 4 isolation was reset and Shutdown Cooling was restored at 1818 EDT. "An investigation is in progress to determine the cause of the bus fault." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2012-04-11
47825 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-04-11 18:26 | 2012-04-11 20:03 | 2012-04-11 | UNUSUAL EVENT DUE TO A FIRE IN THE 'A' MAIN CONDENSER "At 1811 [CDT] hours a fire was reported inside the 'A' Main Condenser. The fire brigade was dispatched to combat the fire and the area was evacuated. "An Unusual Event (HU4) was declared at 1826 [CDT] hours due to the fire being in the Protected Area boundary and not extinguished within 15 minutes of detection. "The Claiborne County, Mississippi Fire Department was notified to provide assistance. "At 1847 [CDT] hours the fire was reported to be extinguished. "The Unusual Event was terminated at 1900 [CDT] hours." The source of the fire is still under investigation. There were no personnel injuries. The licensee notified the NRC Resident Inspector, Mississippi Emergency Management, Governor Office of Homeland Security, Claiborne County Sheriffs Department, Tensas Sheriffs Office, Mississippi Highway Patrol, and the Louisiana Department of Environmental Quality. Notified DHS SWO, FEMA, NICC and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | MS | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2012-04-11
47824 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2012-04-11 12:40 | 2012-04-11 17:02 | 2012-04-11 | DRILL MESSAGE INADVERTENTLY MISTAKEN FOR ACTUAL EVENT "As part of a planned NRC Emergency Plan Exercise on 04/11/2012, local radio and television stations were given access to drill exercise messages to facilitate public awareness of the drill. These messages were plainly marked as 'drill' activity. At 12:40 p.m. CST, an email was sent to Entergy Executive Management showing the contents of a web page that stated in part 'A site area emergency was declared Wednesday at Arkansas Nuclear One, Unit 1, today at 10:18 a.m. by Entergy Operations Inc. officials...' A Little Rock, Arkansas local television station had posted a story on their internet web page at 10:53 a.m., indicating a real event, not a drill activity. The television station News Director stated that once the error was identified, the story was removed from their web page within a matter of minutes. This unplanned media event is being reported in accordance with 10CFR 50.72.(b)(2)(xi)." The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-04-11
47823 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-03-19 03:00 | 2012-04-11 16:32 | 2012-04-11 | OFFSITE NOTIFICATION TO STATE AND LOCAL AGENCIES DUE TO NPDES DISCHARGE "The following ENS is being submitted late. "On Monday, March 19, 2012 at 3 a.m. a manhole overflowed during a scheduled and permitted radiological release through the cooling tower blow down outfall. As a result, several thousand gallons of water overflowed briefly, formed puddles in the area, and was discharged through a different National Pollutant Discharge Elimination System (NPDES) permitted outfall. "The overflow was terminated, water samples were collected from the impacted areas, and the area was remediated in keeping with the Station's environmental monitoring program. Several samples showed increased levels of tritium that were well below permitted Commonwealth and Federal effluent limits. "There were no public health risks associated with this event. The NRC Resident Inspector was notified, and courtesy notifications were made to all appropriate government agencies and local stakeholders in accordance with NEI 07-07, Industry Groundwater Protection Initiative, on March 20, 2012. Due to notification of government agencies, this event is being reported under 10CFR50.72 (b)(2)(xi)." The licensee informed the Commonwealth of Pennsylvania, and Berks, Montgomery and Chester counties. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-04-11
47822 | 0 | SABIC INNOVATIVE PLASTICS |  |  |  |  | 2012-03-22 09:30 | 2012-04-11 16:02 | 2012-04-11 | SIX TRITIUM EXIT SIGNS UNACCOUNTED FOR AFTER SHIPPING TO MANUFACTURER On 1/16/12, the licensee replaced the tritium exit signs in their facility. These exit signs were installed in the late 60's. They put the signs back into the original packaging to return them to the manufacturer. Gexpro [exit sign distributors] picked up the signs with the understanding that they would be shipped to SRB Technologies Inc. (the sign manufacturer). SRB technologies did not receive the signs. A search of the Gexpro warehouse did not locate the signs. Additionally, SRB Technologies had no record of receiving the signs. A total of 6 tritium exit signs are unaccounted for. The serial numbers of the signs are 600275, 600276, 600277, 600278, and 600279. The remaining exit sign did not have a serial number attached any longer. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-04-11
47821 | 0 | SINAI-GRACE HOSPITAL |  |  |  |  | 2012-01-31 | 2012-04-11 11:15 | 2012-04-12 | PATIENT BURIED WITH PLUTONIUM-238 PACEMAKER A former patient at St. John Macomb-Oakland Hospital expired on 1/31/12 and the body was released to the family for burial. The patient had a Medtronic pacemaker with a radionuclide of Plutonium-238. The RSO at Sinai-Grace Hospital notified the NRC of this event. There is no planned action to recover the pacemaker from the buried patient. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-04-11
47820 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-10 21:48 | 2012-04-11 01:18 | 2012-04-14 | SPDS AND ERDS REMOVED FROM SERVICE DUE TO PLANNED MAINTENANCE "At 2148 EDT, on April 10, 2012 the Unit 1 and Unit 2 Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service to support a planned maintenance outage on the 1A Engineered Safeguards System (ESS) Bus as part of the U1 17th Refueling and Inspection outage. The Bus Outage is expected to have a duration greater than 8 hours, but less than 72 hours. During this time, required control room hardwire indications will be available from the unaffected ESS buses. An update will be provided when SPDS/ERDS becomes available. "Since the Unit 1 and Unit 2 SPDS/ERDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10 CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM RON FRY TO JOHN KNOKE AT 2313 EDT ON 04/14/12 * * * "As of 1800 hours EDT on 04/13/12, Unit 1 and Unit 2 ERDS and SPDS were restored to normal operation. Operation of these systems has been monitored since that time and operation has been determined to be reliable." The licensee has not notified the NRC Resident Inspector. Notified the R1DO (Blake Welling) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-11
47819 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-12-04 | 2012-04-10 12:42 | 2012-04-10 | HABITABILITY REQUIREMENT NOT MET DUE TO MAINTENANCE ON THE TSC "Portions of the Turkey Point Technical Support Center (TSC) Heating Ventilation and Air Conditioning System (HVAC) were deenergized for maintenance for the periods of 12/4/10 to 7/13/11 and 10/10/11 to 10/28/11 (prior Event Notification 47387, made on 10/28/11, for the 10/10-28/11 period was retracted by FPL on 12/14/11). "For the period 10/10/11 to 10/28/11, an Equipment Clearance Order (ECO) deenergized the TSC HVAC dampers in the non-emergency position while the ECO was in effect. The ECO was put into effect on 10/10/11. The ECO was released at 1630 [EDT] on 10/28/2011 and functionally tested restoring TSC ventilation recirculation capability. "For the period 12/4/10 to 7/13/11, a similar ECO deenergized all but one of the TSC HVAC dampers in the non-emergency position while the ECO was in effect. The normal air inlet damper was stuck in the closed (emergency) position during this period. The ECO was put into effect on 12/4/10 and released on 7/13/11. "Compensatory measures were not put into effect during either period that the TSC HVAC dampers were deenergized. Accordingly, FPL [Florida Power and Light] cannot conclude that the TSC would have remained continuously habitable for 30 days under every postulated design basis accident scenario as required by NRC standards. However, the alternate Turkey Point TSC remained available at all times." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-10
47818 | 0 | ABB INC |  |  |  |  | 2012-04-09 | 2012-04-09 17:06 | 2016-12-16 | PART 21 REPORT - HK CIRCUIT BREAKER STUDS FAILED TO MEET SPECIFICATION "This letter is submitted in accordance with 10 C.F.R. 21.21(d)(3)(ii) with respect to a failure to comply with the specifications associated with two studs P/N 163392A00 and 192247A00 used in medium voltage HK circuit breakers that may be subject to failure due to hydrogen embrittlement due to incorrect processing during plating. These studs were manufactured at the ABB Medium Voltage Service facility in Florence, SC from steel rod, heat treated in-house, and then sent to Surtronics for zinc plating with chromate treatment, including hydrogen embrittlement relief baking immediately following plating. A total of 51 pieces of P/N 163392A00 and 104 pieces of P/N 192247A00 were plated by Surtronics." * * * UPDATE FROM DAVID BROWN VIA FAX AT 1309 EDT on 4/27/12 * * * The vendor has notified the affected licensees, removed all remaining studs from inventory and will be auditing Surtronics established process during the next finishing production run. The licensees affected include EFH/Luminant, Progress Energy and TVA. Notified R1DO (Jackson), R2DO (Musser), R3DO (Lara) and R4DO (Proulx). * * * UPDATE FROM DAVID BROWN TO DONG PARK VIA FAX AT 1318 EST on 12/16/16 * * * "This [update] amends the previous 10CFR Part 21 Notification of 27 April 2012 that reported failed studs on 7.5 and 15 kV HK circuit breakers. This amendment is required to encompass a wider time period during which the stud (PIN: 163392A00) was sold for use in medium voltage HK circuit breakers. The previous report addressed orders between September 2011 and March 2012, but based upon a recent notification reported by TVA, our notification should have extended further in the past. Further research indicates that a shift in plating vendors in November 2010 is the likely starting point for this issue." Notified R1DO (Schroeder), R2DO (Michel), R3DO (Dickson), R4DO (Kellar), and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-04-09
47817 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-09 05:29 | 2012-04-09 09:15 | 2012-04-09 | VALID EMERGENCY DIESEL GENERATOR ACTUATION "On April 9, 2012, at 0529 hours, electrical power was lost to the 4160 V emergency bus E1. Activities to support testing of emergency bus E1 were in progress when technicians connected a recorder across the terminals of an under-voltage relay on emergency bus E1 and caused the normal supply breakers for emergency bus E1 to open. "The power loss to emergency bus E1 affected both Unit 1 and Unit 2. Emergency diesel generator #1 automatically started and re-energized the E1 emergency bus. "Unit 1 was in Mode 5 and electrical systems were aligned to support testing of emergency bus E1. As a result, no other safety system isolations or actuations occurred. Per design, no Unit 2 safety system isolations or actuations occurred. "The safety significance of this event is minimal. Safety systems functioned as designed when emergency bus E1 de-energized. There was no interruption of Unit 1 shutdown cooling as a result of this event. Normal power supply was restored to emergency bus E1 and emergency diesel generator #1 was shutdown at 0701 hours. "Reporting requirements met by this notification: 10CFR50.72(b)(3)(iv)(A) with specified system in 10CFR50.72(b)(3) (iv)(B)(8). The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-04-09
47816 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-09 01:02 | 2012-04-09 02:07 | 2012-06-07 | BOTH CONTROL STRUCTURE CHILLERS DECLARED INOPERABLE WHILE SWITCHING POWER SUPPLIES "On 4/9/2012, starting at 0102 EDT, the 'A' and 'C' Emergency Diesel Generators (EDG) were sequentially and briefly declared inoperable to switch their DC control power back to their normal supplies. Switching power to the normal supply is required by Unit 2 technical specification 3.8.4 following maintenance work on the U1 power supplies. Previously, at 18:35 EDT on 4/4/2012, the 'B' Control Structure Chiller was declared inoperable due to an unrelated problem. With the 'B' Control Structure Chiller inoperable coincident with the 'A' EDG or 'C' EDG inoperable, neither Control Structure Chiller would be available to perform its design function on a loss of offsite power. This is a condition that, at the time of discovery, could have prevented fulfillment of a Safety Function and is reportable under 50.72(b)(3)(v)(D) as an 8 hour notification. "Switching the power supplies was a planned evolution. The duration of the loss of safety function was a total of eight minutes. As a mitigating action, operators were continuously available with communication to the control room. The associated diesel generator could have been returned to an operable condition promptly if required. "Note that Technical Specifications allows four hours to correct the condition before further actions are required, i.e. declare the features ('A' Control Structure Chiller) supported by the inoperable diesel inoperable." The licensee notified the NRC Resident Inspector. ***RETRACTION FROM RON FRY TO S. SANDIN ON 6/7/12 AT 0205 EDT*** The licensee is retracting this report based on the following: "On April 9, 2012, Susquehanna reported that the 'A' and 'C' Emergency Diesel Generators (EDGs) were sequentially and briefly declared inoperable to switch their DC control power back to their normal supplies while the 'B' Control Structure Chiller was inoperable. The basis for the 8 hour notification, which was reported under Reporting Requirement 50.72(b)(3)(v)(D), was the conclusion that neither Control Structure Chiller would be available to perform its design function on a loss of offsite power. "The reporting guidance in NUREG-1022, Revision 2 identifies events or conditions that are generally not reportable in accordance with 50.72(b)(3)(v). One of the identified conditions is 'removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function).' After further review, Susquehanna has determined that an ENS report was not required for this event since the EDGs and the associated 'A' Chiller were removed from service as part of a planned evolution in accordance with approved procedures and the plant Technical Specifications and no condition was discovered that could have prevented the EDGs and associated 'A' chiller from performing their function. "Based on the above information, this ENS report is retracted." The licensee informed the NRC Resident Inspector. Notified R1DO(Cahill). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-04-09
47815 | 0 | PALISADES | 1 |  |  | [1] CE | 2012-04-08 05:01 | 2012-04-08 05:01 | 2012-04-08 | OFFSITE NOTIFICATION OF NOISE ASSOCIATED WITH PLANT SHUTDOWN "Notified Van Buren County Sheriff of atmospheric steam dump valve usage for cooldown of Palisades Nuclear Plant for start of refueling outage." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2012-04-08
47814 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-07 13:54 | 2012-04-07 15:27 | 2012-04-18 | TRANSPORT OF POTENTIALLY CONTAMINATED WORKER "On 04/07/2012 at 1354 [EDT], Susquehanna Steam Electric Station requested an offsite ambulance via the 911 system for medical assistance. The individual was in the radiologically controlled area and was treated as contaminated. An offsite ambulance arrived on site at 1413 hrs. and the ambulance departed the site at 1424 hrs. enroute to the Berwick Hospital. "This is considered a transport of a contaminated individual requiring an 8 hour ENS Notification per 10CFR50.72(b)(3)(xii)." Licensee health physic technicians accompanied the individual to the hospital. The licensee notified the NRC Resident Inspector and the Pennsylvania Emergency Management Agency. * * * RETRACTION FROM DARVIN DUTTRY TO JOHN SHOEMAKER ON 04/18/2012 AT 1522 EDT * * * "On 04/07/2012, PPL Susquehanna reported that a potentially contaminated individual was transported offsite via ambulance for medical assistance. The individual had been in the radiologically controlled area when the event occurred, and for medical reasons could not be completely surveyed for radioactive contamination prior to transport to the hospital. Therefore the event was considered transport of a contaminated individual. "Health Physics personnel accompanied the individual to the hospital and conducted surveys of the individual, ambulance and hospital equipment and facilities. The results of these surveys indicated that no contamination was detected and the individual, ambulance and all hospital facilities and equipment were non-contaminated. "Based on the above information, reporting pursuant to 10CFR50.72(b)(3)(xii) described in the referenced Event Notification is retracted." The licensee has notified the NRC Resident Inspector. Notified R1DO (Joustra). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-04-07
47813 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-04-06 14:44 | 2012-04-06 22:18 | 2012-04-06 | VALID LOAD SHED SIGNAL OCCURRED DUE TO LOSS OF THE 1B STARTUP TRANSFORMER "At 1444 [CDT] on April 6, 2012, during a planned refueling outage on Unit 1, maintenance activities in the high voltage switchyard caused feeder breaker 820 to inadvertently trip. With the second feeder breaker, 924, already out of service, power was lost to the 1B startup transformer. An undervoltage condition was then experienced on the 1G 4160 V emergency bus. As a result, the B1G Sequencer initiated a valid load shed of the 1G 4160 V emergency bus. Due to outage conditions, the B-Train, 1B Emergency Diesel Generator (EDG) was tagged out and did not automatically start but did receive a valid start signal. None of the ESF loads supplied by the 1G bus started automatically since the 1B EDG was out of service. With a B-Train equipment outage in progress, the 1A RHR pump (A-Train) remained in service for shutdown cooling throughout the event. Although the bus safety function was not needed for plant conditions a valid load shed signal occurred and therefore this event is considered reportable. "The 1G 4160 V emergency bus was restored to service at 1542 on April 6, 2012. Investigation revealed a technical inaccuracy in the instructions used during the maintenance activity in the high voltage switchyard that caused feeder breaker 820 to trip." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-04-06
47812 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-04-06 17:57 | 2012-04-06 20:33 | 2012-04-06 | LOCAL LEAK RATE TEST RESULTS EXCEED PATHWAY TECHNICAL SPECIFICATION LIMITS "Appendix J local leak rate testing has determined that secondary containment bypass leakage (SCBL) has been exceeded for Unit 1. During performance of leak rate test SE-159-026 for X-9A penetration it was determined the combined SCBL limit of 15 scfh [standard cubic feet per hour] for as-found minimum pathway was exceeded as specified in Tech Spec SR 3.6.1.3.11. "Acceptance criteria test results were within acceptance criteria for the 10CFR50 Appendix J limits of 0.6 La. "This event is being reported as a degraded or unanalyzed condition pursuant to 10CFR50.72(b)(3)(ii)." Licensee corrective actions are to repair the identified valve seats. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-04-06
47811 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-06 04:43 | 2012-04-06 08:41 | 2012-04-06 | LOSS OF TONE ALERT SYSTEM "On Friday April 6, 2012, at 0443 EDT, the National Weather Service (NWS) Jacksonville Florida office notified Hatch Nuclear Plant (HNP) of a loss of the NWS Tone Alert Weather Radio System. Site Emergency Procedures define a loss of Tone Alert System for greater than 15 minutes as a significant loss of Emergency Communications. "The NWS Tone Alert Weather Radios are utilized as the Prompt Notification System (PNS) for HNP. This loss impacts the ability to notify the Emergency Planning Zone (EPZ) population for the HNP. This failure meets NRC 8 hour reporting criteria 10CFR50.72(b)(3)(xiii). "The State of Georgia Department of Homeland Security / Georgia Emergency Management Agency (GEMA) 24-hour warning point and the '911' dispatch centers of Appling, Jeff Davis, Tattnall and Toombs counties were notified so compensatory measures would be available should the Prompt Notification System be needed. This consists of utilizing route alerting and the 'Code Red' system, which is a reverse 911 feature available from the county 911 center. This notification meets the 4-hour notification reporting criteria 10CFR50.72(b)(2)(xi). "On Friday April 6, 2012, at 0503 EDT, the NWS Jacksonville Florida office notified HNP that the NWS Tone Alert Weather Radio System had been returned to service." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2012-04-06
47810 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-04-05 22:38 | 2012-04-06 03:57 | 2012-04-13 | STANDBY SHUTDOWN FACILITY (SSF) NOT ANALYZED FOR ALL OPERATING CONDITIONS "On 3/29/2012 Duke Energy identified that unanalyzed conditions exist for SSF mitigated events since associated thermal and hydraulic analyses do not consider all initial operating conditions, especially lower operating modes and lower decay heat. Specifically there are four (4) conditions where the SSF is not currently analyzed: "1. SSF operating at less than 525 degrees F and less than normal operating pressure (approximately 2155 psig), 2. SSF operation before four (4) Effective Full Power Days (EFPDs), 3. SSF reactor coolant make up at low Reactor Coolant System (RCS) pressure. 4. A reactor trip from less than 85 percent power and less than 579 degrees F. "On 4/4/2012, an immediate determination of operability concluded that for the first three (3) conditions the SSF was operable but degraded/nonconforming (OBDN). For the 4th issue, there was reasonable assurance that 1% delta k/k shutdown margin would be maintained if T average. remained above 500 degrees F. Based on a lack of analysis and an increased likelihood of reducing T average. below 525 degrees F during a 72 hour event, the SSF was declared OBDN with a separate operability determination required to validate the Unit 3 power coastdown and end of life T average. reduction analysis. Until additional analysis is performed, the SSF is inoperable on any unit where the power level is reduced below 85 percent. "A second operability determination for Unit 3 concluded that the SSF will maintain greater than or equal to 525 degrees F with an initial power level of 70 percent and a 570 degree F T average. The SSF will be declared inoperable on Unit 3 if power is reduced to less than 70 percent. Seventy percent was chosen as a conservative value to ensure the unit stayed inside the bounds of existing analyses. Unit 3 is currently at approximately 85 percent power and reducing power at approximately 1 percent per day in preparation for the Unit 2 end of core 26 refueling outage. For Unit 3, the SSF is OBDN based on preliminary calculation results. "On 4/5/2012, due to a worsening component cooling water system leak on Unit 2, it was necessary to bring the unit down to Mode 3 to implement repairs. Upon down power, when Unit 2 transitioned below 85 percent power, the ability of the SSF to perform its design function, in consideration of the information above, could not be confirmed and the SSF was declared inoperable for Unit 2. "Currently, there is no conclusive information that would support SSF operability while Unit 2 is below 85 percent power. As such, this event is being conservatively reported under 50.72(b)(3)(ii)(B), 'The nuclear plant being in an unanalyzed condition that significantly degrades plant safety.' Due to their current power levels, this condition does not affect Units 1 and 3. "Initial Safety Significance: Until confirmed by analysis, the lack of decay heat may result in an initial over cooling of the RCS and potentially an interruption of natural circulation or inadequate shutdown margin. Consequently, the SSF was declared inoperable. "Corrective Action(s): Additional analyses are being completed to reestablish SSF operability to bound the unanalyzed entry conditions. "The NRC Resident Inspector has been informed." * * * UPDATE FROM DEAN PORTER TO JOHN KNOKE AT 1403 EDT ON 04/13/12 * * * "Update to ENS Notification Number 47810: ENS Notification number 47810 identified an unanalyzed condition for Oconee Unit 2. This update includes Oconee Units 1, 2 and 3 because the condition of the SSF affects all three units during certain plant conditions. "The Standby Shutdown Facility (SSF) serves as a backup for existing safety systems. Currently the events that rely upon the SSF for mitigation are unanalyzed on Units 1 and 2 when the power level is reduced below 85 percent and on Unit 3 when the power level is reduced below 70 percent, or for any unit operating with less than 4 Effective Full Power Days (EFPDs) at 100% full power since its most recent shutdown. Since the SSF events are unanalyzed for these conditions and until further analysis and evaluation can be completed, Duke Energy is conservatively calling the SSF inoperable when in these conditions. "For these conditions, this event is being reported for Oconee Units I, 2, and 3 under 50. 72(b )(3)(ii)(B), that is, the nuclear plant being in an unanalyzed condition that significantly degrades plant safety. Based on current analyses, the SSF will be declared inoperable, and action statements entered on Units 1 or 2 if power is reduced below 85% power and on Unit 3 if power is reduced below 70% power, or for any unit operating with less than 4 EFPDs since its most recent shutdown. "Initial Safety Significance: Until confirmed by analysis or evaluation, the lack of decay heat may result in an initial over cooling of the RCS and potentially fail the various acceptance criteria of the events required to be augmented by the SSF. Consequently, the SSF will be declared inoperable for the conditions stated above. Unit 3 is being shut down for a routine refueling outage. Units 1 and 2 continue to operate at 100% power with no problems. "Corrective Action(s): Additional evaluations are being completed to establish whether the existing analyses are applicable to the conditions outside of which they were performed and, if not, there is a reasonable assurance that successful mitigation can be accomplished with the existing procedure. If not, further licensing action may be required. These evaluations were initiated on April 4, 2012, and are ongoing." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Kathleen O'Donohue). | 0 | 85 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-04-06
47809 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-04-05 12:20 | 2012-04-05 18:21 | 2012-04-05 | UNPLANNED SYSTEMS ACTUATIONS WHILE PERFORMING A SURVEILLANCE TEST "Unit 1 was performing a planned refueling outage surveillance test, FNP-1-STP-40.0, 'Safety Injection with Loss of Off-Site Power [LOSP].' The systems were being returned to normal following the actuation portion of the test. When the B1F Sequencer Test Trip Override Switch was taken to the 'ON' position, the 1-2A Diesel Generator output breaker opened, which caused a loss of power to the 'A' Train 4 kV busses. Prior to the event, the 1-2A Diesel Generator was running at normal speed and voltage carrying the 'A' Train 4kV busses. When the diesel generator output breaker opened, it then reclosed upon receipt of the LOSP signal causing the LOSP sequencer loads to automatically start. This included the 1C Component Cooling Water Pump, the 1A High Head Safety Injection Pump (discharge isolation was closed prior to the event), and the 1A and 1B SW pumps. Therefore, during the test, the system actuated in a way that was not part of the planned surveillance testing. The 1A RHR pump was in shutdown cooling mode at the time of the event and was load shed. RHR was restarted manually by the operating crew approximately 1 minute later (no auto start [signal] present due to a loss of site power - LOSP signal without a safety injection signal present). "The investigation revealed that a step in the procedure sequence was not performed during the restoration portion of the test. The operator did not parallel the diesel with off-site power prior to operating the B1F Sequencer Test Trip Override Switch which opened the diesel output breaker without off-site power aligned to the 'A' Train 4kV busses. The 1-2A Diesel Generator was subsequently paralleled to the grid and properly shutdown per the test procedure restoration." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-04-05
47808 | 0 | BUREAU OF INDIAN AFFAIRS |  |  |  |  | 2012-04-05 09:00 | 2012-04-05 10:45 | 2012-04-05 | TROXLER MOISTURE DENSITY GAUGE FOUND ON INDIAN RESERVATION The Bureau of Indians Affairs Great Lakes Agency (License #48-32735-01) reported that a Troxler Moisture Density Gauge has been found on the Bad River Indian Reservation. The gauge was delivered to the Radiation Safety Officer for the Bureau of Indian Affairs. The gauge is currently stored in a safe location and the source rod is in the locked position. The licensee and owner of the gauge is not known at this time. The Troxler Gauge is a model 3411B, S/N 8975, and contains an Am-241 40 mCi and a Cs-137 7.5 mCi source. The RSO contacted the Troxler Corporation for more information. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | WI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-04-05
47807 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-04-04 18:35 | 2012-04-04 22:59 | 2012-04-04 | INOPERABLE ACCIDENT MITIGATION EQUIPMENT "On 4/4/2012 at 1517 EDT, the 'A' Emergency Diesel Generator (EDG) was declared inoperable for performance of a maintenance surveillance. At 1835 EDT on 4/4/2012 the 'B' Control Structure Chiller was declared inoperable due to an unrelated problem. [With] the 'B' Control Structure Chiller inoperable coincident with the 'A' EDG inoperable, the 'A' Control Structure Chiller would not be available to perform its design function on a loss of offsite power. This is a condition that, at the time of discovery, could have prevented fulfillment of a Safety Function and is reportable under 50.73(a)(2)(v) as an 8 hour notification. Note that Technical Specifications allows four hours to correct the condition before further actions are required, i.e. declare the features ('A' Control Structure Chiller) supported by the inoperable diesel inoperable. The 'A' EDG was restored to operable at 2200 which restored safety function capability for the 'A' Control Structure Chiller." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-04-04
47806 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2012-04-04 17:16 | 2012-04-04 21:32 | 2012-04-04 | DEGRADED CONDITION DUE TO IDENTIFIED REACTOR PRESSURE VESSEL TEST LEAKAGE "On April 4, 2012, at 1716 [CDT], with Unit 2 shutdown for refueling, leakage was identified from a 2-inch vessel nozzle during a Reactor Pressure Vessel (RPV) pressure test. The leakage amount was approximately one drop per second. The penetration (N-11B) is a reference leg used for reactor vessel instrumentation. The leakage originates from the area where the nozzle penetrates the vessel wall. The nozzle is welded on the inside of the vessel, so the actual attachment weld could not be examined at the time of this report. The RPV pressure test has been stopped and the reactor vessel depressurized. The cause and resolution are under evaluation. The condition is being reported under 50.72(b)(3)(ii)(A) given the defect was associated with the primary coolant system pressure boundary." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-04-04
47805 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-04 20:03 | 2012-04-04 20:25 | 2012-04-05 | NOTICE OF UNUSUAL EVENT DUE TO DUAL UNIT LOSS OF OFFSITE POWER At 2003 EDT on 4/4/12 Catawba Unit 1 automatically tripped due to a loss of offsite power. The licensee declared a Notice of Unusual Event due to entry into EAL 4.5.U.1, 'AC Electrical Power from All Offsite Sources Has Been Lost for Greater Than 15 Minutes.' Power is still available from onsite sources. All four Emergency Diesel Generators [EDG] started and powered their respective safety buses. "The EAL poses no threat to the safety of the public." The Unit 1 control rods fully inserted, there is no known primary to secondary leakage, and the auxiliary feedwater water system automatically started. The licensee notified the NRC Resident Inspector Notified: DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, EPA, and Nuclear SSA via email. * * * UPDATE AT 0150 EDT ON 04/05/12 FROM DARRYL HELTON TO S. SANDIN * * * Catawba Nuclear Generating Station exited the Unusual Event at 0137 EDT after restoring offsite power at 0135 EDT to the Unit 1A and Unit 2B essential busses. The EDGs powering these busses have been secured and returned to Standby. The Unit 1B and Unit 2A essential busses remain energized by their respective EDGs. The licensee does not have an estimate as to when offsite power will be restored for these busses. Additional information provided as follow-up includes: 4-hour notification per 10CFR50.72(b)(2)(iv)(B) due to the Unit 1 Reactor Protection System [RPS] actuation (Rx Trip), 4-hour notification per 10CFR50.72(b)(2)(xi) for offsite notifications to the States of North and South Carolina and the counties of York, Gaston and Mecklenburg, 8-hour notification per 10CFR50.72(b)(3)iv)(A) due to the Unit 1 Rx Trip, Unit 1 Auxiliary Feedwater automatic start, Unit 1A and 1B and Unit 2A and 2B EDG auto starts. 8-hour notification per 10CFR50.72(b)(3)(v)(B) due to the loss of Residual Heat Removal [RHR] cooling on the initial loss of power. Unit 2 RHR was restored in less than three (3) minutes when the essential busses were re-energized by the EDGs. The licensee informed the NRC Resident Inspector. Notified R2IRC, EO (Nelson), IRD (Gott) and FEDS (DHS SWO, DOE Ops Center, FEMA, HHS Ops Center, DHS NICC, USDA Ops Center, EPA EOC) and NuclearSSA via email. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Cold Shutdown |  | Hot Standby | Cold Shutdown |  | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-04-04
47804 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2012-04-03 17:15 | 2012-04-04 09:00 | 2012-04-04 | SECURITY REPORT INVOLVING DEGRADATION IN A SAFEGUARDS SYSTEM Discovered vulnerability in a safeguards system that could allow access to a controlled access area. Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | KS | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2012-04-04
47803 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-04-04 05:00 | 2012-04-04 05:15 | 2012-04-04 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE STATIC INVERTER "Indian Point 2 commenced a Technical Specification required shutdown in accordance with Limiting Condition of Operation 3.8.7, Condition B at 0500 hours on 04/04/2012 due to the inoperability of '24' Static Inverter - a component in the 118VAC Distribution System. Indian Point 2 is required to be in Mode 3 by 0802 hours. Repair of the '24' Static Inverter is in progress. "The NRC Resident Inspector has been notified." The licensee also notified the NY State Public Service Commission. * * * UPDATE FROM P. SCHOAN TO DONALD NORWOOD AT 1053 EDT ON 4/4/2012 * * * At 0538 hours, the Technical Specification shutdown was stopped following the repair and return to service of the '24' Static Inverter. The licensee notified the NRC Resident Inspector. Notified R1DO (Caruso). | 43 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-04-04
47802 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-04-02 15:20 | 2012-04-03 11:29 | 2012-04-03 | CONTAMINATED INDIVIDUAL TREATED IN THE ON-SITE DISPENSARY FOR INJURED FINGER "On 4/2/12 approximately at 1520 CDT a person working in the Feed Materials Building injured his finger between a drum lid and drum ring. The employee received first aid treatment in the on-site dispensary. The individual was found to have contamination on his boots. The employee was not transported to an off-site facility. The employee was released to go home at the end of his shift and appropriately exit monitored. There was no detectable contamination on the employee when he left the site." The contamination was uranium ore concentrates. The licensee informed NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-04-03
47801 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-03 08:00 | 2012-04-03 07:36 | 2012-04-03 | UNIT 2 PLANT PROCESS COMPUTER OUT-OF-SERVICE FOR PLANNED MAINTENANCE "The Unit 2 DC Cook Nuclear Plant (CNP) Plant Process Computer (PPC) will be removed from service on Tuesday, April 3, 2012 at 0800 EDT to support scheduled maintenance. This will cause the entire Unit 2 PPC, including the ERDS [Emergency Response Data System] to be unavailable to the NRC Operations Center. The planned maintenance also affects the Safety Parameter Display System (SPDS), the Real Time Data Repository (RDR), and PPC data to Emergency Response Facilities at CNP. "The scheduled maintenance, returning of equipment to service, and post maintenance testing is expected to be completed by 0000 EDT on Wednesday, April 4, 2012. "Compensatory measures exist within the DC Cook Emergency Response procedures to provide plant data via the Emergency Notification System to the NRC Operations Center until the ERDS can be returned to service. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to any event that results in a major loss of emergency assessment capability, offsite response capability, offsite communications capability (e.g. significant portion of control room indication, Emergency Notification System, or offsite notification system)." * * * UPDATE FROM BRAD LEWIS TO CHARLES TEAL ON 4/3/12 AT 1536 EDT * * * At time 1500 EDT, the Plant Process Computer and ERDS system has been restored to service. The licensee has notified the NRC Resident Inspector. Notified R3DO (Dickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-03
47800 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-04-03 05:24 | 2012-04-03 05:57 | 2012-04-06 | SPDS AND ERDS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On 4/03/12 at 0524 EDT, the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 80 hours. During this time, the majority of the control room indications remain available to the plant staff, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems, if needed. The plant is currently in Mode 5, and will remain in Mode 5, for the duration of the SPDS and ERDS unavailability. Since the unavailability will last greater than 8 hours, this is considered a Loss of Emergency Assessment Capability, and reportable under 10 CFR 50.72(b)(3)(xiii). "Follow up notification will be made when SPDS and ERDS have been restored." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM GEORGE PICCARD TO VINCE KLCO ON 4/6/2012 AT 1227 EDT * * * "At 0702 EDT on April 6, 2012, Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were restored, following restoration of the associated power bus." The licensee notified the NRC Resident Inspector. Notified the R3DO (Bloomer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-03
47799 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2012-04-02 14:52 | 2012-04-02 23:32 | 2012-04-02 | INITIATION OF REACTOR SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS (TS) 3.8.1.F "On April 2, 2012, at 1452 hours, Unit 1 received Panel 901-8 A7 U1 Emergency Diesel Generator (EDG) Trouble alarm. Equipment Operators were dispatched and the Unit 1 EDG was found running unloaded, without a generator field flash, and no auto start signal received. Troubleshooting identified that a 125 VDC ground had caused the Unit 1 EDG to start. As a result, the Unit 1 EDG was declared inoperable. "At this time Unit 2 is in a refueling outage and the Unit 2 EDG is currently inoperable for repairs. Due to the inoperability of the Unit 1 and Unit 2 EDGs, at 2000 hours a Reactor Shutdown was initiated on Unit 1 in accordance with TS 3.8.1.F. "In addition, since the EDGs supply emergency power to both Unit's Standby Gas Treatment Systems (SBGTS), emergency power was unavailable to SBGTS; however, normal power supplies remained available. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(i), and in accordance with 10 CFR 50.72(b)(3)(v)(D). "At 2151 hours, the Unit 1 EDG was declared operable following repairs and successful operability testing." The NRC Resident Inspector has been informed. | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-04-02
47798 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-04-02 15:11 | 2012-04-02 22:56 | 2012-04-02 | AUTOSTART OF DIVISION 3 DIESEL GENERATOR FOLLOWING 4160 VOLT LINE OUTAGE "On 4/2/12 at 1511 [CDT], GGNS [Grand Gulf Nuclear Generating Station] received a valid ESF actuation for emergency AC power to Division 3 4160V bus due to degraded voltage. "One of the two 500KV offsite feeders (Tech Spec Offsite Power Source) tripped causing a drop in grid voltage which resulted in a trip of the ESF feeder breaker for 4160 Volt Division 3 bus. The HPCS (High Pressure Core Spray) Diesel Generator automatically started and energized the bus. The HPCS system was not running and no ECCS initiation occurred during this event. The plant was in Mode 5 with RHR A in shutdown cooling. Divisions 1 and 2 ESF power monitoring instrumentation responded to the grid voltage transient but no actuation setpoints were reached. Division 1 and 2 ESF 4160V buses remained energized and shutdown cooling remained in service. The 500KV offsite feeder (Tech Spec Offsite Power Source) and additional 115 KV feeder (Tech Spec Offsite Power Source) remained in service. The 500KV feeder that tripped was restored by the dispatcher at approximately 1515 CDT. The Division 3 bus was subsequently transferred back to offsite power and the HPCS Diesel Generator was secured. This event is reportable per 10 CFR 50.72(b)(3)(iv). "A lightning strike resulted in a voltage transient on the GGNS electrical distribution system. Due to this transient, the 'A' Control Room Air Conditioning Unit (CRAC 'A') tripped and had to be manually restarted. CRAC 'A' was not running for approximately two minutes. During this timeframe CRAC 'B' was tagged out of service. This was evaluated and determined to not be a loss of safety function." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-04-02
47797 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2012-04-02 19:33 | 2012-04-02 20:40 | 2012-04-02 | UNUSUAL EVENT - FIRE FROM HYDROGEN SUPPLY TO VOLUME CONTROL TANK "At 1933 EDT on 4/2/12, a fire was discovered on top of the Auxiliary Building Roof coming from a one inch hydrogen supply header to the U-3 Volume Control Tank. "At 1948 EDT [Turkey Point] declared an Unusual Event due to a fire greater than 15 minutes in the protected area (HU2). "At 1949 EDT [operators] closed the hydrogen isolation valve and hydrogen header pressure began to lower. "At 1956 EDT a second isolation valve was closed. Header pressure continued to lower. "At 2018 EDT the fire is out. No damage to plant equipment or adverse effect to safe shutdown systems. [Turkey Point] is currently working on a de-escalation process." The licensee notified the NRC Resident Inspector, State and local agencies. Notified DHS SWO, FEMA, NICC and Nuclear SSA. * * * UPDATE FROM JOSE VASQUEZ TO PETE SNYDER T 2139 EDT ON 4/2/12 * * * After the fire was out the pipe became cool to the touch. At 2110 EDT Turkey Point terminated the Unusual Event for Unit 3. The licensee notified the NRC Resident Inspector, State and local agencies. Notified DHS SWO, FEMA, NICC and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-04-02
47796 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-03-30 | 2012-04-02 17:38 | 2012-04-02 | AGREEMENT STATE REPORT - THERASPHERES FOUND IN DELIVERY EQUIPMENT AFTER PROCEDURE The following information was received from the State of Illinois via email: "On April 2, 2012 the licensee contacted the [Illinois Emergency Management] Agency [IEMA] to provide a preliminary notification that they believed a medical event had occurred as a result of a Therasphere treatment the previous workday. On March 30, 2012 a patient had been administered Y-90 for the treatment of liver cancer according to their standard protocol. No unusual anomalies took place during the treatment and no shunting of the dose was observed. The treatment was completed as expected including initial agitation of the vial, 'tapping' of the system during administration and repeated flushing of the delivery system upon completion of the five minute process. "However, when post-treatment measurements were conducted of the delivery system and vial, a measurable amount of activity was determined to still be present. Analysis of the associated microcatheter, tubing, vial and the rest of the delivery system resulted in an assessment that only 92 of the prescribed 130 Gy [71%] of dose had been delivered. Additional measurements and imaging identified that an aggregate of microspheres remained in the vial and at the hub of the microcatheter where it connects to the delivery system. No other activity or contamination was noted in associated equipment. "The patient was advised the next day of the substantial lowering of the dose delivered. No immediate effect on the patient is expected at this time and no determination has been made as to any corrective action or additional dose to supplement the partial treatment. A follow up with the patient is pending. Similarly, the licensee is unaware of any corrective action necessary for future treatments pending additional evaluations and assessments. Consideration is being given to having the delivery system returned to the manufacturer for an engineering analysis once the radioactivity present has decayed. An investigation by IEMA is pending." IL Item Number: IL12007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-04-08
47795 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-02 06:24 | 2012-04-02 11:45 | 2012-04-02 | INFORMATION ONLY - FIRE IN PLANT VITAL BATTERY ROOM AREA "At 0624 EDT on 04/02/2012 the control room was notified by a plant operator that there was a fire in the plant vital battery room area on Unit 2. The fire was located in the lower compartment of inverter 2KUI. This equipment supplies power to 120V AC non-safety related components. The fire brigade captain was dispatched along with the site fire brigade. When the fire brigade captain arrived the operator was staged near the inverter with a CO2 [carbon dioxide] fire extinguisher. The fire brigade captain instructed the NLO [non-licensed operator] to extinguish the fire with the extinguisher. The fire was immediately extinguished once the CO2 was applied from the extinguisher. At 0633 EDT the fire brigade captain reported to the control room that the fire was extinguished. Upon further investigation it appears that transformer in the lower compartment of the inverter had caught fire. The fire was confined to the lower compartment of the inverter and did not affect any other components in the area. Due to the loss of the inverter the loads automatically swapped to the alternate AC source as designed and no indications or equipment were lost due to the loss of the inverter. "At the time of this event Unit 1 was at 100% power and Unit 2 was shutdown in Mode 6 with reactor coolant system drained to 8% level with 2B Residual Heat Removal pump supplying core cooling. There was no impact to either unit as a result of this event. All equipment required to maintain core cooling, AC and DC power, and reactor coolant inventory on Unit 2 was maintained during this event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2012-04-02
47794 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-04-01 04:26 | 2012-04-01 04:26 | 2012-04-01 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0445 EDT on Sunday, April 1, 2012, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance and post maintenance testing is scheduled to be completed by 1900 EDT on Sunday, April 1, 2012. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM DEAN BRUCK TO PETE SNYDER ON 4/1/12 AT 1633 EDT * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1620 EDT on 4/1/12." The licensee will notify the NRC Resident Inspector. Notified R3DO (Dickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-04-01
47793 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2012-03-31 00:22 | 2012-03-31 03:42 | 2012-03-31 | MANUAL REACTOR TRIP DUE TO UNCONTROLLED COOLDOWN "At 0022 (EDT) on 03/31/12 while maintaining power stable at 10% for Steam Bypass Control System testing, Unit 1 was manually tripped due to an uncontrolled cooldown caused by PCV-8802 (Steam Bypass Control Valve) unexpectedly opening. Following the trip, PCV-8802 closed and the secondary was isolated by closing the Main Steam Isolation Valves per Standard Post Trip Actions. Following isolation of the steam demand, the trip was uncomplicated with all CEAs fully inserted. No automatic safety system actuations were required and none occurred. The cause of the unexpected opening of the Steam Bypass Control System valve is under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Auxiliary Feedwater and Atmospheric Dump Valves. The Offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation with the reactor at power." The RCS cooled down from 532 degree to 515 degrees over a period of approximately 2 minutes and 40 seconds. The reactor was manually tripped when RCS temperature reached 515 degrees and the lowest RCS temperature observed after the trip was 505 degrees. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-03-31
47792 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2012-03-28 13:35 | 2012-03-30 16:36 | 2012-03-30 | AGREEMENT STATE REPORT - A MOISTURE DENSITY GAUGE WAS FOUND IN BUILDING The following information was received from the State of Arizona via email: "At approximately 10:00 AM on March 28, 2012, the Agency [Arizona Radiation Regulatory Agency (ARRA)] was informed that radioactive material had been detected by the Tempe, AZ Fire Department in an old flour mill. The Agency [ARRA] dispatched a response team to the site to locate and confirm information. The response team determined that the isotope involved is Cesium-137 and based on the label information approximately 25 millicuries remain in the device. The device is labeled on the accessible surfaces as a Kay Ray Model 7107 gauge and also as a Model 7519B gauge assembly SN 13454. Based on the site history and the labels, it appears that the device was transferred to Bay State Milling in the 4th quarter of 1980 or the 1st quarter of 1981. The Agency [ARRA] did not issue a specific license for this site. We assume that the device was transferred as a GL (Generally Licensed) device and remained in use into 1998. Only about 10% of the site has been surveyed thus far. The site security is being maintained by the Tempe FD (Fire Department). "The Agency [ARRA] is now searching historical records for information, including any other devices on site. "The Agency [ARRA] continues its investigation." Arizona Report #: 12-008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2012-04-04
47791 | -1 | US ARMY |  |  |  |  | 2009-12-16 | 2012-03-30 15:31 | 2012-04-05 | MISSING CHEMICAL AGENT DETECTOR When returning from deployment a Virginia National Guard unit discovered that they had lost a M43A1 Chemical Detector containing 250 uCi of Am-241. The unit searched the facility as well as a storage warehouse located in Richmond, VA for the device, but they were unable to locate it. * * * RETRACTION FROM THOMAS GIZICKI TO VINCE KLCO ON 4/5/2012 AT 1201 EDT * * * Retraction due to the detector found in the same location in a different Army unit. Notified the R1DO (Caruso), R3DO (Bloomer) and the FSME (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2012-03-30
47790 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-03-08 | 2012-03-30 08:07 | 2012-03-30 | AGREEMENT STATE REPORT - GAMMA KNIFE MEDICAL OVEREXPOSURE The following information was received from the State of Florida via email: "Licensee reported a possible medical event on 8 March which was confirmed in a written report received on 22 March. Patient was being treated by Gamma Knife with 8 shots at four sites when the fifth shot was interrupted for a bathroom break. While in the bathroom the patient fell and dislodged the stereotactic frame. The frame was reapplied and treatment plan recalculated. However, the computer did not start the treatment at the correct site resulting in an increase in dose of 22.2% at site 2, 14.8% at site 3 & 15, and 7% at site 4. The doses are well within clinical practice. A conservative dose prescription had been elevated to a moderate prescription. The referring physician and patient have been notified. No medical consequences are expected. The cause is human error. Any further investigation referred to Licensing and Materials. No further action will be taken on this incident by this office." Device: Leksell Perfexion Serial Number: 6130 Florida Incident: FL-12-034 "A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-04-05
47789 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-03-29 21:05 | 2012-03-30 01:11 | 2012-03-30 | LOSS OF TONE ALERT SYSTEM "At 2235 (EDT) on 3/29/12, James A. FitzPatrick (Power Station) was notified by the Oswego County Emergency Management Office (OCEMO) that the Tone Alert System had been out-of-service for greater than one (1) hour. This condition is considered a significant loss of offsite communication capability and is therefore a 50.72 8-hour non-emergency reportable condition per 10 CFR 50.72(b)(3)(xiii). "The Tone Alert System failed at 2105 (EDT) on 3/29/12, and was subsequently restored to service at 2245 (EDT) on 3/29/12. The cause of the system loss is still being investigated by the OCEMO. "During the time the Tone Alert System was unavailable the county emergency sirens, the Hyper-Reach system which is a reverse 911 feature was available from the county 911 center, and 'Route Alerting' where Local Law Enforcement Personnel are able to assist in alerting affected areas of an (Emergency Planning Zone) EPZ were available as alternate mechanisms to provide emergency offsite notifications." The licensee has notified the NRC Resident Inspector. This Tone Alert System also services the Nine Mile Point Power Station. * * * UPDATE FROM RICHARD SULLIVAN TO MARK ABRAMOVITZ AT 1023 EDT ON 3/30/2012 * * * "At 0335 [EDT] on 3/30/12, James A. FitzPatrick was notified by the Oswego County Emergency Management Office (OCEMO) that the Tone Alert System had been out of service for greater than one (1) hour. This condition is considered a significant loss of offsite communication capability and is therefore a 50.72 8-hour non-emergency reportable condition per 10CFR50.72(b)(3)(xiii). "The Tone Alert System failed at 0211 on 3/30/12 and was subsequently restored to service at 0328 on 3/30/12. This failure was the second such failure in a 24 hour period. The first failure occurred at 2105 on 3/29/12 and was restored at 2245 on 3/29/12. The first failure was reported to the US Nuclear Regulatory Commission Operations Center at 0111 on 3/30/12. "The cause of the Tone Alert System loss is being investigated by the OCEMO. Oswego County reported that the National Weather Service had verified the system was broadcasting as designed at 0540 on 3/30/12. "During the time the Tone Alert System was unavailable, the county emergency sirens, the Hyper-Reach system which is a reverse 911 feature available from the county 911 center, and 'Route Alerting' where Local Law Enforcement personnel are able to assist in alerting affected areas of the EPZ were available as alternate mechanisms to provide emergency offsite notifications." The licensee notified the NRC Resident Inspector. Notified the R1DO (Newport). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-30
47788 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-03-29 22:42 | 2012-03-30 00:59 | 2012-03-30 | LOSS OF TONE ALERT SYSTEM "On Thursday, March 29, 2012, at 2242 EDT, Oswego County notified Nine Mile Point (NMP) via the land line of a loss of the Tone Alert System as of 2105 (EDT). Site Emergency Procedures define a loss of Tone Alert System for greater than one hour as a significant loss of Emergency Communications (EPIP-EPP-30). "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the NMP and (James A. FitzPatrick) JAF Nuclear Power Plants. This failure meets NRC 8-Hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the Hyper-Reach system, which is a reverse 911 feature available from the county 911 center. "The County Alert Sirens, which also function as part of the Public Prompt Notification System, remain operable. "At 2300 EDT, Nine Mile Point received notification from Oswego County 911 that the Tone Alert System has been restored and is fully functional as of 2245 EDT." The licensee has notified the NRC Resident Inspector. The cause of the loss is still being investigated. * * * UPDATE AT 1035 EDT ON 3/30/2012 FROM RYAN HAMILTON TO MARK ABRAMOVITZ * * * "At 03:33 [EDT] on 3/30/12, Nine Mile Point was notified by the Oswego County Emergency Management Office (OGEMO) that the Tone Alert System had been out of service for greater than one (1) hour. This condition is considered a significant loss of offsite communication capability and is therefore a 50.72 8-hour non-emergency reportable condition per 10 CFR 50.72(b)(3)(xiii). "The Tone Alert System failed at 0211 on 3/30/12 and was subsequently restored to service at 0328 on 3/30/12. This failure was the second such failure in a 24 hour period. The first failure occurred at 2105 on 3/29/12 and was restored at 2245 on 3/29/12. The first failure was reported to the US Nuclear Regulatory Commission Operations Center at 0059 on 3/30/12. "The cause of the Tone Alert System loss is being investigated by the OCEMO. Oswego County reported that the National Weather Service had verified the system was broadcasting as designed at 0540 on 3/30/12. During the time the Tone Alert System was unavailable, the county emergency sirens, the Hyper-Reach system which is a reverse 911 feature available from the county 911 center, and 'Route Alerting' where Local Law Enforcement personnel are able to assist in alerting affected areas of the Emergency Planning Zone were available as alternate mechanisms to provide emergency offsite notifications." The licensee notified the NRC Resident Inspector. Notified the R1DO (Newport). | 100 | 97 | 0 | 100 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-30
47787 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-03-29 17:00 | 2012-03-29 21:20 | 2012-03-29 | UNANALYZED CONDITION IMPACTING APPENDIX R SEPARATION REQUIREMENTS "At the Browns Ferry Nuclear Power Plant (BFN), exclusion 'Red Zones' are established for compliance with the 20-foot separation requirements of Appendix R section III.G.2.b as modified by the associated NRC approved exemption for BFN issued on March 29, 2007. On March 28, 2012, it was determined that intervening combustible materials, i.e., cables, found in exclusion 'Red Zones' were not in conformance with Appendix R Section III.G.2.b and the associated NRC approved exemption issued for BFN. As a result of the intervening combustible material found in the exclusion 'Red Zones,' the degree of separation for redundant Appendix R safe shutdown trains is lacking. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." The NRC Resident Inspector has been informed. | 100 | 100 | 95 | 100 | 100 | 95 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-03-29
47786 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2012-03-29 04:00 | 2012-03-29 04:04 | 2012-03-29 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUTAGE "At 0400 (EDT) on Thursday March 29th, the Peach Bottom Atomic Power Station (PBAPS) Technical Support Center (TSC) supply and exhaust fans will be removed from service for planned preventative maintenance activities on the exhaust fan. This maintenance is scheduled to be worked continuously until completion to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 14 hours. If TSC staffing is required, it will take a maximum of 4 hours to return the ventilation system back to an operable status." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JEREMY HITE TO CHARLES TEAL ON 3/29/12 AT 1949 EDT * * * The planned maintenance is complete and the TSC was restored back to service at 1530 EDT. The NRC Resident Inspector has been informed. Notified R1DO (Newport). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-29
47785 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2012-03-24 18:10 | 2012-03-29 00:02 | 2012-03-29 | SEWAGE SPILL IN THE TURBINE BUILDING THAT DISCHARGES TO THE KEOWEE RIVER "On 3/24/12 at 1810 hrs EDT, a four inch sewage line in the turbine building failed. This allowed sanitary wastewater to spill into the turbine building basement. An estimated 100 gallon entered into trench drains and then to the station sump which discharges into the conventional wastewater system. This conventional wastewater system is discharged to the Keowee River from NPDES [National Pollutant Discharge Elimination System] outfall 002. The discharge of outfall 002 is into the Keowee River below the Keowee River Hydro Station. The normal discharge path for sanitary wastewater is to the City of Seneca. South Carolina DHEC [Department of Health and Environmental Control] was notified of the spill on 3/24/12 at 2259 hrs EDT. After further review, this was determined to be reportable under 10CFR50.72(b)(2)(xi)." This event was determined to be reportable at 2150 EDT on 3/28/2012. The event was entered into the corrective action program. There was no impact on plant operations and the cleanup has been completed. The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-29
47784 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-03-28 16:15 | 2012-03-28 22:44 | 2012-03-28 | UNANALYZED CONDITION DISCOVERED DURING NFPA 805 TRANSITION IMPACTING EMERGENCY DIESEL GENERATOR LOADING "On March 14, 2012, it was determined that in the event of an Appendix R fire, fire damage to cables in Fire Area 2-4, 3-3, or 25-1 could cause a Residual Heat Removal Service Water System (RHRSW) pump to spuriously start. This unanalyzed condition was originally determined to be not reportable. However, during subsequent review on March 28, 2012, this condition was determined to be reportable since the additional load from the spurious start of the RHRSW pump on the associated Emergency Diesel Generator (EDG) could result in the design maximum loading of the EDG being exceeded. As a result of the EDG maximum loading being exceeded, the EDG credited in the Appendix R fire analysis to supply required Appendix R safe shutdown loads could fail. The issue has significant safety impact since the capability to supply power to the Appendix R safe shutdown equipment for the credited EDG is necessary to provide adequate core cooling and decay heat removal during performance of the Browns Ferry Nuclear Plant Safe Shutdown Instructions in an Appendix R fire event." The NRC Resident Inspector has been notified. | 100 | 100 | 96 | 100 | 100 | 96 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-03-28
47783 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-03-28 15:00 | 2012-03-28 18:26 | 2012-03-28 | DEGRADED CONDITION IDENTIFIED IN THE B TRAIN CONTAINMENT COOLER UNITS "At 1500 on March 28, 2012, Callaway Plant personnel discovered that the installation of a modification on the two 'B' train containment cooler units had inadvertently introduced a potential failure mechanism to the 'B' train containment coolers. Specifically, with the containment cooling fans initially in fast-speed operation, combined with certain initial plant conditions, thermal overload tripping of the coolers could occur. "In such an event, during some postulated accidents, slow-speed restart of the containment coolers by the Load Shedding and Emergency Load Sequencing system could be prevented. As a result, the 'B' train containment coolers could be rendered unavailable for a portion of a postulated accident. Thus, the safety function of the 'B' train containment cooling fans cannot be assured when this degraded equipment condition is present and the containment cooling fans are run in fast-speed operation. "This condition existed for the 'B' train containment cooling units since they were restored to service from maintenance at 0400 on March 15, 2012. "Upon identification of this condition, the 'B' train containment cooling fans were switched from fast-speed to slow-speed operation and restored to operable status at 1515. This action precludes this degraded equipment condition from adversely affecting containment cooling fan function during an accident. "Concurrent with this condition, the opposite train of containment coolers was removed from service for scheduled maintenance at 0505 on March 27, 2012. As a result, from 0505 on March 27, 2012 until 1515 on March 28, 2012, the safety function of the containment cooling system could not be assured for certain postulated accident conditions. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-03-28
47782 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-03-28 16:48 | 2012-03-28 18:19 | 2012-03-28 | OFFSITE NOTIFICATION OF POTENTIAL RELEASE OF AMERTAP BALLS TO MISSISSIPPI "On 3/28/2012, Xcel Energy Personnel determined that approximately 50% of the Amertap balls recently used were not recovered. A survey of the Mississippi River bank downstream of the plant by site personnel recovered an additional 3 Amertap balls, indicating that the balls were not released to the river. Monticello Nuclear Generating Plant (MNGP) is required to report to the Minnesota Pollution Control Agency (MPCA) when greater than 20% (1 .5 barrels or approximately 7,500) of the Amertap balls are not recovered. This is based on an agreement with the MPCA dated September 12, 2008. The MPCA was notified at 1648 CDT on 3/28/12." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-28
47781 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-03-28 15:03 | 2012-03-28 17:14 | 2012-03-28 | AUTOMATIC REACTOR TRIP DUE TO STEAM GENERATOR HIGH WATER LEVEL CONDITION "At 1503 hours EDT on March 28, 2012, with the unit in Mode 1 at 55% power, an automatic reactor trip occurred. The reactor trip was the result of a turbine trip from a 'B' Steam Generator Hi Level. All Reactor Coolant Pumps (RCP) remained running. "The Auxiliary Feeedwater (AFW) System automatically actuated due to both main feedwater pump breakers opening from a valid feedwater isolation signal. Steam Generator Levels were then controlled by Auxiliary Feedwater pumps. Steam Generator Blowdown was automatically isolated with the AFW actuation. The RCS Code Safety valves, Pressurizer Power Operated Relief Valves (PORVs), Steam Generator PORVs or the Main Steam Safety valves (MSSVs) did not open during the event. All control rods fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently in Mode 3 and stable. "There were no radiological consequences or releases as a result of this event. "The cause of the Steam Generator Hi Level is under investigation. "The Resident NRC Inspector has been informed." | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-03-28
47780 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-28 05:25 | 2012-03-28 12:55 | 2012-03-28 | PLANNED MAINTENANCE ON TSC VENTILATION SYSTEM "Planned maintenance activities are in progress on Catawba Nuclear Station's Technical Support Center (TSC) Emergency Ventilation System. These planned activities include replacement of a relay and relay base that render the ventilation system temporarily inoperable. "The planned maintenance window is not expected to exceed 24 hours. "This report is being made in accordance with 10CFR50.72, criterion (b)(3)(xiii), and in accordance with NUREG-1022, Revision 2, as a condition that may impair the functionality of an Emergency Response Facility." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-28
47779 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-03-26 | 2012-03-28 10:57 | 2012-03-28 | ILLINOIS AGREEMENT STATE REPORT - SHUTTER MECHANISM FAILURE The following information was obtained from the State of Illinois via email: "The Radiation Safety Office for the licensee reported a second device at their facility had a shutter mechanism failure. The shutter was found stuck in the open position on March 26, 2012 during continuation of their routine maintenance check and survey. The gauge is near the top floor of a coker drum away from any routinely occupied work station. The device/area has been posted with appropriate warning notices. Measured radiation levels appear normal for this type of device with the shutter open. There are two other gauges on this vessel which are operating normally. Operators in the area have been informed of the situation and vessel access is prohibited. The area is subject to high humidity and rust build up is the suspected cause of the shutter failure. In the past, the manufacturer has recommended covers for these devices but none are available. The licensee's consultant and the vendor have been called. Both will be on-site again on March 30, 2012 as previously arranged to service a similar other device that failed last week. They will investigate this recent failure at that time." The gauge is an Ohmart Corp. model number SHLG-2, serial number 2605CN and contains a 5 Ci Cs-137 source. The previous failure was reported under NRC EN# 47759. Illinois Item Number: IL12006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-04-02
47778 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-03-28 11:30 | 2012-03-28 10:02 | 2012-03-28 | TONE ALERT RADIOS OUT OF SERVICE FOR PLANNED MAINTENANCE "On March 27, 2012, Cooper Nuclear Station was informed by the National Weather Service that the Shubert NOAA Transmitter will be down for maintenance starting at 1130 on March 28, 2012 with maintenance lasting until approximately 1400 on March 28, 2012. This affects the tone alert radios Cooper Nuclear Station provides to members of the public to notify them of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR50.72(b)(3)(xiii). "State authorities and local county authorities within the 10 mile EPZ have been notified of the condition of the NOAA Transmitter and the effect on the tone alert radios and will utilize Local Route Notification (backup notification method). The licensee has notified the NRC Resident Inspector of the condition." * * * UPDATE FROM ANDREW OHRABLO TO CHARLES TEAL AT 1636 EDT ON 3/28/12 * * * At 1151 CDT the Shubert NOAA transmitter was removed from service. At time 1411 CDT the NOAA transmitter was restored to service. The State and local governments have been notified as well as the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-28
47777 | -1 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2012-03-27 20:20 | 2012-03-27 23:11 | 2012-05-23 | SPENT FUEL HANDLING MACHINE NOT FULLY QUALIFIED FOR A SEISMIC EVENT "The following condition is being reported by Arkansas Nuclear One, Unit 2 (ANO-2) in accordance with 10CFR 50.72(b)(3)(ii)(B), 'Unanalyzed Condition.' Conservative engineering analysis has determined that the Spent Fuel Handling Machine (2H-3) is not qualified in a design basis earthquake event. Current seismic analysis is indicating a lack of margin for several structural parts of the machine. "The Spent Fuel Handling Machine (2H-3) is currently parked and de-energized in a safe position and administratively prohibited from being moved over any irradiated fuel assemblies in the spent fuel pool. Until further engineering evaluation or modifications can occur the Spent Fuel Handling Machine (2H-3) will remain in its current position and de-energized." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM STEVEN COFFMAN TO PETE SNYDER AT 1104 EDT ON 5/23/12 * * * "The purpose of this notification is to retract the previous Event Notification Report #47777 made by Arkansas Nuclear One, Unit 2 on 03/27/2012. The initial report indicated that the Spent Fuel Handling Machine (2H-3) may not have been qualified during a design basis earthquake event due to seismic analysis indicating a lack of margin for several structural parts of the machine. 2H3 was parked and de-energized in a safe position, and the condition was reported in accordance with 10 CFR 50.72(b)(3)(ii)(B), 'Unanalyzed Condition.' "Since the initial report, Engineering has completed a new seismic analysis which demonstrates that the discovered conditions of the Spent Fuel Handling Machine structural parts were adequate to preclude structural failure of the machine in the area of the Spent Fuel Pool. References to the calculations that formulate the basis for this conclusion are documented in the Licensee's corrective action program. "Based on the new seismic analysis, the condition initially reported in EN #47777 did not result in 'an unanalyzed condition that significantly degrades plant safety' and is therefore retracted. "The NRC Resident Inspector has been briefed on the seismic analysis results and informed of this retraction." Notified R4DO (Spitzberg). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-03-27
47776 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2012-03-26 04:30 | 2012-03-27 20:21 | 2012-03-27 | LATE ARRIVAL OF NUCLEAR FUEL SHIPMENT A shipment of nuclear fuel arrived outside of its scheduled delivery window. At no time was the shipment outside the control of the contracted carrier. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2012-03-27
47775 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-03-27 | 2012-03-27 17:54 | 2012-10-30 | HISTORICAL UNAVAILABILITY OF EMERGENCY OPERATIONS FACILITY VENTILATION DUE TO MAINTENANCE "During a review of past maintenance that was performed on the Emergency Operations Facility (EOF) ventilation system, it was identified that there were three periods of time when the maintenance would have impacted the functionality of the facility and the ventilation system would not be able to be restored promptly. Site reporting guidance has been revised to assure accurate reporting. "The periods of time where maintenance impacted the functionality of the EOF are as follows: 1. April 30 to May 1, 2009 for approximately 36 hours due to condenser and air handler replacement. 2. January 14 to 18, 2010 for approximately 96 hours due to damper and ductwork replacement. 3. November 17 to 19, 2010 for approximately 72 hours due to a compressor failure. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since the work activities affected an emergency response facility for the duration of the maintenance. "The Senior Resident Inspector has been informed." * * * UPDATE ON 10/30/2012 AT 0940 FROM JOHN CAVES TO DAN LIVERMORE * * * "On several occasions between August 4, 2009, and November 9, 2011, the Emergency Operations Facility (EOF) ventilation systems were in a degraded state and/or removed from service, for extended periods of time. There were no actual emergencies that occurred during those periods that required activation of the EOF. "A calculation indicated that with the degraded air conditioning system during summer conditions, the temperature in the EOF could reach 87 degrees F. While there is no specific temperature limit for EOF habitability, an elevated temperature is of concern when emergency response organization members are under potential stress, as in emergency response situations. "On January 25, 2010, Harris staff found a damper in the ventilation system stuck in the nearly closed condition. The damper was reopened on the day it was discovered. A calculation indicated that with the ventilation system in the normal mode and the damper stuck, the carbon dioxide concentration in the EOF could have exceeded 0.5%. "The elevated carbon dioxide concentration due to the stuck damper, combined with the stress associated with an actual emergency in a facility and temperatures of 87 degrees, had the potential to impair a key responder's ability to perform an assigned emergency response function." The licensee has informed the NRC Senior Resident Inspector. Notified R2DO (Musser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-27
47774 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-03-27 09:50 | 2012-03-27 14:06 | 2012-03-27 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTUATION "At 1145 CDT on 3/27/12, OPPD [Omaha Public Power District] was notified by Harrison County Emergency Management that the sirens in Harrison County, Iowa were inadvertently activated at 0950 CDT on 3/27/12. This activation occurred during an exercise at Fort Calhoun Station which included FEMA evaluation of local, State, and County participation. The sirens were activated by Iowa Emergency personnel for less than 5 seconds. An OPPD and State of Iowa joint media press release will be conducted following the termination of the Emergency Planning exercise." The licensee notified the State of Iowa EMA and the Harrison County Sherriff's Dispatch. The licensee also notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-27
47773 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-01 21:00 | 2012-03-26 18:19 | 2012-03-26 | 60-DAY OPTIONAL REPORT - INVALID SYSTEM ACTUATION "In accordance with 10CFR50.73(a)(2)(iv)(A), this telephone notification reports an invalid actuation of the Unit 2 train B (2B) Emergency Diesel Generator (DG) on February 1, 2012, at 2100 hours. At the time of the event, Unit 2 was in Mode 5, Cold Shutdown. The 2B DG was being prepared for an operability surveillance following a planned work window. As part of this surveillance, a chart recorder is installed to monitor key DG parameters to include the DG start signal. When the second lead was connected across the starting relay contact test point, a DC ground alarm was received and the 2B DG started. The engine functioned successfully and as expected, the 2B DG did not automatically connect to its safety bus, since no bus under-voltage signal was present. The cause is attributed to a faulty chart recorder in that an inadvertent ground resulted in the actuation of the starting relay. This condition was entered into the corrective action program." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-03-26
47772 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-26 15:30 | 2012-03-26 17:28 | 2012-03-26 | OFFSITE NOTIFICATION DUE TO SEWAGE LIFT STATION OVERFLOW "A discharge was reported to the New Jersey Department of Environmental Protection (NJDEP) at 1712 EDT on 3/26/2012, case number 120326171251. The discharge resulted from a sewage lift station that overflowed into a manhole, #8, which is a permitted outfall to the river. Approximately 1500 to 2000 gallons of sewage overflowed into the manhole." The licensee will notify the Lower Alloways Creek Township. The licensee will also notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-26
47771 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-03-22 | 2012-03-26 14:49 | 2012-03-26 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN INTENDED DOSE The following information was received via facsimile: "On March 23, 2012 the Southeast Regional Office [of the Pennsylvania Department of Environmental Protection - Bureau of Radiation Protection (Department)] received notice from the hospital of a medical event involving yittrium-90 TheraSpheres. "The patient was being treated for disease of the liver and received 76% of the intended dose in the first delivery and 56% of the intended dose in the second delivery. "The cause of the event is currently under investigation. More information will be provided when received. "No harm to the patient is expected. The oncologist was satisfied with the treatment and no additional delivery is anticipated. The Department will conduct a reactive inspection." Pennsylvania Event Report ID No: PA120010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-04-01
47770 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2012-03-25 05:15 | 2012-03-26 10:04 | 2012-03-26 | RESEARCH REACTOR MANUAL SCRAM At 0356 hrs. EDT, while operating at full power, the reactor automatically scrammed on a high signal on period channel 3. At that time, it was believed that the scram was due to noise on the channel. All channels were checked and at 0449 hrs. it was decided that to restart the reactor. During the startup, the rods were pulled to the estimated critical position (ECP) without indication on any of the period channels (3 channels installed). It was decided that the xenon could be precluding the reactor so it was decided to bump the rods out. After bumping out the rods, no increase in period was indicated. During the ensuing discussion, the operator observed power increasing and, at approximately 4 Mw, decided to manually scram the reactor. Investigation into this event is ongoing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MA | NPR | [5 empty] | 0 | 2012-03-26
47769 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-03-25 23:36 | 2012-03-25 23:58 | 2012-03-26 | UNUSUAL EVENT DECLARED DUE TO SEISMIC ACTIVITY On March 25, 2012 at 2336 EDT, an Unusual Event was declared due to an earthquake felt on site. The site entered EAL HU1.1. No plant systems were affected. The National Earthquake Information Center reported a magnitude 3.1 seismic event 6 miles south-south west of Mineral, Virginia. A plant inspection is on-going to determine any plant issues related to the seismic event. Unit 1 is in a refueling outage and containment integrity was maintained. Unit 2 continues in full power operation. The licensee notified the NRC Resident Inspector, State and local agencies. Notified DHS SWO, FEMA, NICC and Nuclear SSA via email. * * * UPDATE FROM TED WEBNER TO VINCE KLCO ON 3/26/2012 AT 0417 EDT * * * On March 26, 2012 at 0410 EDT, the Unusual Event was terminated. The basis for the termination was that all equipment walkdowns are complete with no damage discovered. The licensee will notify the NRC Resident Inspector. Notified the R2DO (Haag), NRR EO (Brown), IRD (Grant), DHS SWO, FEMA, NICC and the Nuclear SSA via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-03-26
47768 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-03-24 16:00 | 2012-03-25 09:20 | 2012-09-12 | AGREEMENT STATE REPORT - OVEREXPOSURE TO RADIOGRAPHER WHEN CAMERA SOURCE BECAME DISCONNECTED The following information was received by facsimile: "On March 24, 2012, the licensee notified the Agency that it one of its radiography teams had experienced a disconnect of a 65 curie iridium-192 on a QSA Delta 880 radiography camera at a temporary work site in Pasadena, Texas. The crank out drive cable had broken and the source had completely disconnected. After an authorized individual performed the source retrieval, the licensee's RSO learned that the radiographer trainer disconnected the source tube from the camera and had carried the source tube around his neck while he climbed down the ladder of the scaffold. The source was in the tube at this time, but it is uncertain at this time the source's location within the tube. When the radiographer trainer reached the platform he removed the source tube from his neck. The licensee's initial dose estimates for the radiographer trainer are a whole body dose of at least 56 rem and an extremity limit that may exceed 100 rem. The radiographer's film badge is being sent for immediate reading. The licensee is conducting an investigation. "NOTE: During the licensee's initial phone call to the Agency, the Agency understood the whole body dose estimate to be 6 rem and considered the event to be a 24-hour report (the Agency did report to the NRC HOO within 24 hours). However, when the Agency received the written initial report this morning, March 26, 2012, it was discovered that the estimate is 56 rem, which requires immediate notification. This report is being submitted to update and upgrade the event. More information will be provided as it is obtained. The State also corrected the source strength to 65 curie Ir-192 source. REAC/TS was notified on 03/26/12 and the licensee has made contact with them. Texas Incident: I-8942 * * * UPDATE FROM KAREN BLANCHARD TO CHARLES TEAL ON 3/29/12 AT 1712 EDT * * * "The radiographer's badge was processed on March 28, 2012. The badge reading was 812 mrem whole body (deep dose equivalent). Dose reconstruction continues as the investigation continues. More information will be provided as it is obtained." Notified R4DO (Farnholtz) and FSME (McKenney). * * * UPDATE AT 1414 EDT ON 09/12/12 FROM KAREN BLANCHARD TO S. SANDIN * * * The following update from the State of Texas was received via email: "Investigation of the event provided the following information. The radiographer stated he had performed a survey of the camera and source guide tube prior to disconnecting it. He stated he observed normal readings, including approximately 20 mr/hr at the camera. He lowered the camera and drive cable assembly down to the radiographer trainee who was working with him. After climbing down the ladder and removing the source guide tube from around his neck, the radiographer walked over to assist the trainee who was having trouble disconnecting the drive cable assembly. The radiographer stated he saw that the camera was not locked and was still in the red position. The radiographer stated he again surveyed the camera and then the source guide tube and got high readings at the end of the source guide tube. Sometime between the time the radiographer began attempting to disconnect the drive cable assembly and the time he surveyed the guide tube, both of their alarming rate meters (ARM) began alarming. They both moved back and notified the licensee's Radiation Safety Officer (RSO) of the apparent disconnect. The radiographer then used a pair of 3-foot long tongs to lift the guide tube from the collimator end. As he lifted the tube, the source fell out onto the floor. He again moved back, re-established a 2 mr/hr boundary, and waited on the RSO. The RSO arrived on-site as did an individual authorized to perform source retrieval. The source was then properly retrieved and secured. The RSO checked ARMs and the survey meter and all were working properly at that time. "The camera, drive cable assembly, and source guide tube were sent to the manufacturer for evaluation. The manufacturer reported that . . . 'the cable was severed directly behind the 550 connector. The male connector passed the no go gauge but is heavily worn . . . The cable is corroded/rusted and stiff at the broken area and was dry of any lubricant grease . . . the control pistol assembly components showed significant signs of rusting and the control housings were taped to allow continued use . . . there are no indications of improper manufacture or defect in the Teleflex drive cable . . . Based on this evaluation, the drive cable failed due to a combination of wear, corrosion and lack of lubrication indicative of improper maintenance.' The radiographer stated he did not check the condition of the crank out drive cable prior to using it (as required) even though he initialed the daily work sheet indicating he had completed his daily equipment check. "The survey meter and ARMs were sent to the manufacturer for evaluation. All were within the calibration date and all were operating properly. The ARMs began alarming at 400 mr/hr when they were checked. "The radiographer was wearing his dosimetry badge on his right chest pocket. It was sent for immediate processing following the incident. The badge reading was 812 mrem. The licensee performed dose assessment calculations for the event and assigned an estimated dose of 29.32 rem for this event. "Key issues identified: 1. Failure to perform proper survey. 2. Failure of licensee to properly inspect and maintain equipment (specifically the drive cable in this instance). 3. Failure of radiographer to perform daily equipment inspections and remove from service components in need of maintenance. 4. Failure to ensure camera is in locked position after cranking source into camera and before proceeding." Notified R4DO (Lantz) and FSME via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-03-28
47767 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2012-03-24 18:55 | 2012-03-25 01:44 | 2012-03-25 | DEGRADATION OF STEAM GENERATOR NOZZLE WELD AREAS "On March 24, 2012, at 1855 [EDT] during the performance of work activities to support Alloy 600 dissimilar metal weld overlay work on the 'B' Reactor Coolant loop hot leg to the 'B' Steam Generator nozzle weld, two through-wall defects were identified. The workers noted a small amount of water seeping from the indications in the nozzle weld area. The indications are in the area of excavation that was being performed for the weld overlay project. Approximately 1 [inch] of weld material had been removed prior to the seepage being identified. "Entered Technical Requirement 3.4 .6, 'ASME Code Class 1, 2 and 3 Components' and immediately initiated actions to isolate the 'B' Reactor Coolant loop. The 'B' Reactor Coolant loop stop valves were closed at 2312 hours on March 24, 2012, which isolated the defects from the reactor coolant system . An engineering evaluation of the defects will be performed and corrective actions implemented. "This event is reportable in accordance to 10CFR50.72(b)(3)(ii)(A) for 'any event or condition that results in the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded'." The licensee notified the NRC Resident Inspector and will notify Louisa County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-03-25
47766 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-23 14:28 | 2012-03-23 17:00 | 2012-03-23 | TURBINE TRIP FOLLOWED BY AUTOMATIC REACTOR TRIP "Salem Unit 2 has experienced an automatic reactor trip at 1428 hours on 3/23/12. "Salem Unit 2 tripped due to a turbine trip above [permissive] P-9. All shutdown and control rods fully inserted on the reactor trip. "At the time of the trip 22 station power transformer [SPT], the 2F and 2G 4KV group buses were not energized causing a loss of 23 and 24 reactor coolant pumps. The auxiliary feedwater (AFW) system auto-started to provide feed to the steam generators. "The crew entered EOP-TRIP-1, then transitioned to the EOP-TRIP-2 and stabilized the plant. Salem Unit 2 is currently in Mode 3 at normal operating temperature and pressure with 21 and 22 reactor coolant pumps in service. "There are no shutdown technical specifications in effect. All ECCS and ESF systems are available. Decay heat removal is being provided by 21 and 22 AFW pumps and the main steam dump system. The plant is aligned with a normal electrical line-up from offsite power sources with the exception of 22 SPT. Restoration of the 22 SPT and 2F and 2G 4KV group buses is in progress. "There were no personnel injuries associated with this event. "This event is reportable per 10 CFR 50.72 (b)(3)(iv)(A) due to the auto-start of the auxiliary feed water pumps." The licensee notified the NRC Resident Inspector. The licensee will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. The licensee anticipates making a press release. * * * UPDATE FROM WILLIAM MUFFLEY TO PETE SNYDER AT 2127 EDT ON 3/23/12 * * * "During the post trip review ... two additional AFW pump start signals were identified. At 1429 hrs. EDT with RCPs 23 and 24 tripped the 21 and 22 steam generators (SG) dipped below the lo-lo level setpoints and caused an AFW actuation to occur. At 1457 hrs. EDT 23 turbine driven AFW pump was stopped in accordance with operating procedures. At 1509 hrs. EDT the 21 SG cleared the low level setpoint and at 1513 hrs. EDT the 22 SG cleared the low level setpoint. At 1523 hrs. EDT the 22 SG dipped below the lo-lo level setpoint and caused an AFW actuation to occur. The two motor drive AFW pumps continued to run throughout this event. "The licensee notified the NRC Resident Inspector and will notify Lower Alloways Creek Township and the States of New Jersey and Delaware." Notified R1DO (Schmidt). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-03-23
47765 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2012-03-22 21:01 | 2012-03-23 14:33 | 2012-03-26 | FITNESS FOR DUTY [FFD] REPORT INVOLVING PROGRAMMATIC VULNERABILITY "On March 9, 2012, Shaw's Vogtle 3&4 Construction Contractor FFD program manager notified SNC [Southern Nuclear Operating Company] FFD program manager of his discovery of anomalies in their random pool while preparing to perform the weekly random pool generation. At that time, approximately 20 people were identified as not being in the pool that had active badges. Corrective actions were implemented to update the pool and provide additional verification of any changes made to the pool. Subsequently discussions with licensing resulted in the conclusion that there was not an indication that there was a programmatic issue and thus was reportable under a 30 day report to the NRC. The NRC was informed of this decision and has been at Vogtle collecting data regarding this event. "Since that time, Shaw has been checking past months to determine the extent of condition. On March 22, at 21:01, Shaw notified SNC that the October - December results of personnel who had active badges but was not in the pool was significantly higher than the January through March results, developed earlier. On the basis of this information, SNC has determined that this now rises to the level of a programmatic vulnerability and is subject to a 24-hour report to the NRC. "SNC is providing this notification under the provisions of 10 CFR 26.719(b)(4) and 26.417(b)(1) as a discovered vulnerability of the FFD program." The licensee informed the NRC Resident Inspectors. * * * UPDATE FROM MAHAN TO HUFFMAN AT 1700 EDT ON 3/26/12 * * * The licensee noted that this event is also being reported under 10 CFR 26.417(b)(1). R2DO (Haag) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | FFD PROGRAMMATIC FAILURE |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 | 26.417(b)(1) |  |  | 0 | 2012-03-23
47764 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-22 21:30 | 2012-03-22 22:53 | 2012-03-22 | POTENTIAL FIRE INDUCED SPURIOUS OPERATION OF STEAM GENERATOR BLOCK VALVES "On February 28, 2005, Duke Energy notified the NRC of McGuire Nuclear Station's (MNS) intent to adopt NFPA 805 in accordance with 10 CFR 50.48(c). On April 18, 2006, Duke Energy notified the NRC that MNS had begun the process of transitioning to NFPA 805. For licensees transitioning to NFPA 805, assuming specific criteria are met, the NRC will exercise enforcement discretion for Appendix R non-compliances identified during the transition process and for existing Appendix R non-compliances that could reasonably be corrected under 10 CFR 50.48(c). As per NRC guidance and policy, enforcement discretion does not relieve the licensee of the requirement to make a required report to the NRC. "As part of the NFPA 805 transition process, MNS has identified Appendix R related noncompliances which are being evaluated for appropriate dispositioning under NFPA 805. The evaluation of the non-compliances has recently identified a condition which could result in fire induced spurious operation of the block valves for the Unit 2 Steam Generator (SG) Power Operated Relief Valves (PORVs). This spurious operation could potentially damage these valves and render them inoperable. Since these valves are unisolable, they could not be repaired to allow the Unit 2 SGs to be used for Unit cool down if needed. "This potential condition could adversely affect the ability of the plant to achieve and maintain a cold shutdown of Unit 2. This represents a condition reportable as per the requirements of 10 CFR 50.72(b)(3)(ii)(B). This potential condition is mitigated by existing compensatory measures (i.e. fire watches) which have been in place as part of the NFPA 805 transition. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-03-22
47763 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-03-20 | 2012-03-22 20:26 | 2012-03-26 | AGREEMENT STATE REPORT - UNDERDOSE DURING LIVER DISEASE TREATMENT "Event type: A medical event (ME) involving the administration of Yittrium-90 SIR-Spheres which is reportable under 10 CFR 35.3045(a)(1)(i). "Notifications: On March 21,2012, the Department's [Pennsylvania Department of Environmental Protection, Bureau of Radiation Protection] Southeast Regional Office received notification via a phone call about this ME. "Event Description: The patient was being treated for disease of the liver and received 77% of the intended dose. "CAUSE OF THE EVENT: Currently under investigation and unknown at this time. "ACTIONS: No harm to the patient is expected. The treating physician notified the patient. "The Department [Pennsylvania Department of Environmental Protection, Bureau of Radiation Protection] plans to do a reactive inspection." PA Event Report ID: PA120009. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM JOSEPH MELNIC TO VINCE KLCO ON 3/26/12 AT 0937 EDT VIA FAX * * * "Notifications: On March 21, 2012, the Department's Southeast Regional Office received notification via a phone call about this ME. After the HOO notification was made the Department was informed that the measurement for actual dose delivered was repeated two times, both indicating the administration was within acceptable limits. "Event Description: The patient was being treated for disease of the liver and was initially thought to have received 77% of the intended dose, however after additional measurements were made the dosage delivered was determined to be 81.2% and 82.2%. "ACTIONS: Medical Event is being retracted." Notified the R1DO (Newport) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-03-28
47762 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-03-22 11:45 | 2012-03-22 17:35 | 2012-03-22 | AGREEMENT STATE REPORT - EQUIPMENT MALFUNCTION DURING TREATMENT The State of Wisconsin provided the following information via e-mail: "On March 22, 2012 at 2:30pm the Wisconsin Radiation Protection Section received a telephone notification that a fire had occurred at the licensee's location while performing a lung perfusion study at 11:45am, utilizing a 60 mCi dose of Tc-99m DTPA. The lung perfusion kit being used was a Biodex Medical Systems model Aerotech 1, lot #: 07811324. Per a discussion with the RSO, a patient was receiving a lung perfusion study when the perfusion kit 'burst into flames.' The Nuclear Medicine Technician (NMT) removed the face mask from the patient and the patient's hair caught on fire and the NMT put the fire out with their hands. The patient was immediately taken to the Emergency Room and the first degree burns on their face and neck have been treated. "The area has been secured and surveys are in progress. The licensee will not be conducting any nuclear medicine procedures until the Radiation Protection Section has completed our investigation." WI Event Report ID: WI120002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-03-27
47761 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-03-14 | 2012-03-22 17:29 | 2012-03-29 | AGREEMENT STATE REPORT - SOURCE LOST DURING TRANSPORT The State of Texas provided the following information via email: "On March 22, 2012, the Agency was notified by a licensee that a 350 millicurie (13 GBq) Americium 241-Beryllium source was lost during shipment. The source was picked up in Fort Worth, Texas by a common carrier for delivery to Houston, TX on March 14, 2012. When the source arrived in Houston, TX it was discovered that the source should have been delivered to the company's Corpus Christi, TX location. The common carrier contacted the licensee in Fort Worth and they agreed to have the source sent to the Corpus Christi location. On March 20, 2012, the licensee in Corpus Christi contacted the licensee in Fort Worth and stated that they had not received the source. The licensee in Fort Worth contacted the common carrier and was informed by them that they could not locate the source, but they were looking for it. On March 22, 2012, at 1420 hours the Fort Worth licensee contacted this Agency to report that they had decided to report the source as lost. "The Agency contacted the carrier and they confirmed that the package was loaded on the truck going from Houston to Corpus Christi. They stated that the truck stopped in San Antonio, TX prior to going to Houston. The common carrier is still looking for the source. They stated that all of their transportation centers have been notified of the lost package. Additional information will be provided as it is received in accordance with SA-300. Texas Incident #: I-8941. * * * UPDATE ON 3/29/12 AT 0918 EDT FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via fax: The report should have stated "that the truck stopped in San Antonio,TX prior to going to Corpus Christi." Notified the R4DO (Farnholtz) and FSME (McIntosh) via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-03-27
47760 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-03-22 10:34 | 2012-03-22 11:56 | 2012-03-22 | NOTICE OF UNUSUAL EVENT - POTENTIALLY HAZARDOUS ATMOSPHERE DUE TO FREON LEAK At 1034 CDT on 3/22/12, Cooper Nuclear Station declared a Notice of Unusual Event due to a freon leak from a glycol compressor in the sub-basement of their Augmented Radwaste Building. This created a potentially unsafe localized atmosphere in that area per Emergency Action Level HU 3.1. The licensee made a public address system announcement to avoid the area and sent personnel to guard the area to prevent entry. The licensee is monitoring the area for any deterioration. Oxygen levels are currently normal. Cooper Nuclear Station personnel plan to isolate the freon leak and ventilate the area to ensure a habitable atmosphere. There are no safety related systems or components in the affected area. Plant operation is unaffected. As of 1045 CDT, the licensee has notified appropriate state and local governmental agencies. The licensee notified the NRC Resident Inspector. Notified DHS SWO, DHS NICC, FEMA and Nuclear SSA via email. * * * UPDATE AT 1320 EDT ON 3/22/12 FROM ROBERT LECHNER TO PETE SNYDER * * * Cooper Nuclear Station personnel monitored the atmosphere in the affected area for safe entry then entered and isolated the freon leak. They did further extensive monitoring for any pockets of trapped freon gas and further ventilated the area to restore the area to a habitable condition. At 1142 CDT Cooper Nuclear Station exited their Unusual Event condition. Offisite notifications were made per 10 CFR 50.72 (b)(2)(xi). A press release is planned to inform the public of this onsite event. Notified DHS SWO, DHS NICC, FEMA and Nuclear SSA via email | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2012-03-22
47759 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-03-21 | 2012-03-22 11:03 | 2012-03-22 | AGREEMENT STATE - PROCESS GAUGE SHUTTER STUCK IN OPEN POSITION The State of Illinois reported the following information via email: "The Wood River Refinery reported that a shutter mechanism on a fixed gauge (Ohmart Model SH-F1B, S.N. 2508CN) was found stuck in the open position during a routine survey and maintenance check. The gauge contained a 3.7 GBq (100 mCi) Cs-137 source. Staff were unable to return it to the shielded position. The gauge is in an unoccupied area. "The device/area has been posted. Surveys indicate normal radiation levels in the vicinity of the device compared to the SSD registry. There is product in the vessel and 2 other gauges are in the vicinity. "Personnel and shift managers have been informed of the situation. A service vendor has been on scene and so far has been unable to close the shutter after lubrication. Additional service measures are being pursed by the vendor." IL Item No. IL12005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-03-27
47758 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-03-21 07:49 | 2012-03-21 13:53 | 2012-03-21 | INADVERTENT OFFSITE NOTIFICATION DURING SIMULATOR TRAINING "At 0749 PDT on March 21, 2012, during a training scenario in the plant simulator, plant personnel inadvertently issued an Alert notification for Diablo Canyon Power Plant (DCPP), Unit 1. This Alert should be disregarded. The Alert was issued as a loss of the Unit 1 fuel cladding barrier with no radioactive release. There is no Alert declaration at DCPP Units 1 or 2, and both units are operating normally. DCPP contacted notified parties to clarify that the Alert notification was inadvertent. "DCPP is making this 4-hr, non-emergency notification under 10 CFR 50.72(b)(2)(xi) as a situation for which an (inadvertent) notification to other government agencies has been made." The licensee is investigating this inadvertent notification but believes that the notification system was still set up from the emergency plan drill which was conducted last week. The licensee notified the NRC Resident Inspector, San Luis Obispo County, and the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-21
47757 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-20 20:17 | 2012-03-20 21:12 | 2012-03-27 | 73.71 REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA The attempted introduction of contraband into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM THOMAS GARRISON TO VINCE KLCO ON 3/27/12 AT 1003 EDT * * * "Catawba security is retracting the one hour call. A follow-up investigation found no malevolent intent." The licensee notified the NRC Resident Inspector and the R2-IAT(True). Notified the R2DO (Haag) and the Part 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-03-20
47756 | -1 | MIDDLESEX CARDIOLOGY ASSOCIATES |  |  |  |  | 2012-03-20 12:30 | 2012-03-20 13:25 | 2012-03-27 | INCORRECT PATIENT ADMINISTERED NUCLEAR STRESS TEST "This will serve as the incident report on a patient who inadvertently received an injection of technetium 99m in the Middletown office of Middlesex Cardiology Associates. [The gentleman] is a 68-year-old patient. He has underlying dementia and, at times, poor understanding of his medical care. He arrived at the office over 30 minutes late for his appointment. He identified himself to the front office staff [by his first name]. Because of HlPPA laws, the front office staff did not announce his full name. It turns out that a separate patient, [with the same first name] was scheduled for a 12:30 PM nuclear stress test. [The patient] was brought to the nuclear cardiology imaging department which is separate from the usual patient waiting room. He was told that he was going to have a pharmacologic stress test performed. Before the medical assistant could ask his date of birth, the patient indicated to the nuclear staff that he had had coffee earlier in the day which raised some confusion as to whether he could undergo pharmacologic stress testing. [The patient] never indicated that he was simply there for an office visit. He was subsequently told that he could only have resting imaging performed and would have to return on a separate day for the pharmacologic stress test. He agreed. He had undergone previous nuclear testing and therefore did not protest having an injection of technetium performed. He subsequently received 32.8 mCi of technetium 99 sestamibi. At that point, the correct nuclear stress test patient, checked in with the front office staff. Immediately, it became evident that there were 2 gentleman [with the same first name] scheduled for separate visits on 3/20/12. License photo identification was then performed. It was then discovered that [the first patient] had inadvertently received the technetium injection inappropriately. Given the fact that this dose of technetium would only produce a total body dose of 0.55 rads or approximately 5.3 mGy, there was not felt to be any concern for long-term medical sequelae. "The patient's physician had a discussion with the patient and subsequently called his daughter to discuss the incident. A detailed letter was also sent to the patient's primary care physician. "Based on NRC regulations, I contacted the [NRC] Operations Center at 1:25 PM on 3/20/12. I spoke to [the Headquarters Operations Officer] to explain the situation. This afternoon, we had a meeting with all front office staff and nuclear staff to review the importance of patient identification so that this type of incident will never occur again. Patients for nuclear testing will be identified by first and last names as well as birthdates to eliminate confusion." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM JOSEPH CORNING TO DONALD NORWOOD AT 1249 EDT ON 3/27/2012 * * * The total body dose received from the injection of techntium 99 was not high enough to warrant reporting this as a medical event. This event is therefore being retracted. Notified R1DO (Newport) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-03-26
47755 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-03-19 16:12 | 2012-03-20 00:20 | 2012-03-21 | POTENTIAL FOR AERIAL LIFT TO IMPACT SERVICE WATER PIPING DURING SEISMIC EVENT "At 1612 on 3/19/12 it was identified that an aerial lift was located in the Auxiliary Building stored in a seismic storage area near Train A and Train B safety related service water piping to Control Room Air Conditioning (CRAC) Alternate Cooling System. This resulted in both trains of Service Water being INOPERABLE per TS 3.7.8 and both trains of CRAC Alternate Cooling system per TS 3.7.11. "At this time, there is no conclusive information that would support the OPERABILITY of the Service Water System during a seismic event therefore this event is being conservatively reported under 50.72(b)(3)(ii)(B), 'The nuclear plant being in an unanalyzed condition that significantly degrades plant safety.' and 50.72(b)(3)(v)(A) and (D) 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structure systems that are needed for: (A) shutdown the reactor and maintain it in a safe shutdown condition, (D) mitigate the consequences of an accident.' "The aerial lift was removed and the plant is no longer in the condition noted above." The NRC Resident Inspector has been informed. * * * RETRACTION FROM JACK GADZALA TO DONALD NORWOOD AT 1130 EDT ON 3/21/2012 * * * "On March 19, 2012, EN #47755 provided notification that both service water trains were potentially inoperable based on the potential for an improperly stored aerial lift to tip onto the adjacent service water piping during a seismic event. The notification was conservatively made due to the lack of conclusive information regarding any potential interaction between the aerial lift and the service water piping during a seismic event. "Subsequent investigation and analysis determined that physical characteristics of the aerial lift are such that it would not have adversely interacted with the service water piping. "Therefore, both service water trains remained operable and this condition did not meet the reportability criteria identified in 10CFR50.72. "As a result, the notification made on 3/19/2012 (EN #47755) is hereby retracted. The NRC Resident Inspector has been notified." Notified R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2012-03-20
47754 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-03-19 13:00 | 2012-03-19 12:41 | 2012-03-20 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "On March 19th 2012 at 1300, Limerick Generating Station will be performing routine preventative maintenance on the Charcoal Adsorber and HEPA Filter associated with the on-site Technical Support Center (TSC) Emergency Ventilation system. While performing this maintenance, the TSC Emergency Ventilation system will not be available to be restored within the time period required to staff and activate the TSC Emergency Response Organization (ERO). "This work is expected to be completed by 3/19/12. If an emergency is declared requiring TSC ERO activation, the TSC will be staffed and activated using emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an Emergency Facility because of the planned unavailability of the TSC Emergency Ventilation system. The NRC Resident Inspector has been informed." The TSC ventilation is expected to be out of service for approximately four hours. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 3/20/12 AT 0019 EDT FROM WEISSINGER TO HUFFMAN * * * The TSC emergency ventilation system has been returned to a normal status. The licensee will notify the NRC Resident Inspector. R1DO (Schmidt) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-19
47753 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2012-03-19 01:19 | 2012-03-19 08:57 | 2012-03-19 | LOSS PUBLIC PROMPT NOTIFICATION CAPABILITY "At approximately 0119 CDT on 3/19/12, Cooper Nuclear Station was informed by the National Weather Service that the Shubert radio transmission tower was not working. This affects the tone alert radios Cooper Nuclear Station provides to members of the public to notify them of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Local county authorities within the 10 mile EPZ have been notified of the condition of the Shubert radio transmission tower and the affect on this tone alert radios and will utilize Local Route Notification (backup notification method.) "At approximately 0635 CDT, the National Weather Service reported that the Shubert radio transmission tower had been restored and tested satisfactorily." The licensee has notified the NRC Resident Inspector and local authorities of the condition. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-19
47752 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2012-03-18 23:36 | 2012-03-19 02:24 | 2012-03-19 | MANUAL REACTOR TRIP DUE TO CONTROL ELEMENT ASSEMBLY ANOMALOUS BEHAVIOR "At 2336 EDT, during performance at Low Power Physics Testing, Unit 1 was manually tripped while the reactor was critical at less than 1% power due to Control Element Assembly (CEA) Regulating Group #3 exhibiting anomalous behavior (continued to insert with no operator action). The trip was uncomplicated and all CEAs fully inserted when the reactor was tripped. No automatic safety system actuations were required and none occurred. The cause for the abnormal CEA performance is under investigation. "The plant is stable in Mode 3 at normal operating temperature and pressure. RCS Heat Removal is being maintained with Auxiliary Feedwater and Atmospheric Dump Valves. The offsite power grid is available and stable. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual RPS actuation with the reactor critical" The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-03-19
47751 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2012-03-18 19:17 | 2012-03-18 21:10 | 2012-03-18 | UNACCOUNTED FOR SAFEGUARDS INFORMATION Some safeguards information is currently unaccounted for. Security personnel are attempting to locate these documents. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-03-18
47750 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2012-03-15 15:30 | 2012-03-16 15:44 | 2012-03-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK SOURCE The following information was provided by the State of Minnesota via email: "Braun Intertec was performing radiography on a valve in a pit at a temporary jobsite. The camera was a model QSA 680 SN: A334 with a 29 Ci Co-60 source model 424-14 SN: 2905. When cranking out the source after about 10-15 revolutions the controls went free; the radiographer could not crank the source back in. The barrier around the worksite was set at <2mR/hr, so the barrier was maintained. The RSO (Radiation Safety Officer) and Corporate RSO were notified and responded to the site. They suspected the drive cable went past the controls. They disconnected the conduit from the controls and were able to use a tool to grab the end of the drive cable and pull back through until the source was back to the shielded position. The exposure level at the crank during the retrieval was <1 mR/hr, and the operation took about 20 min. The RSO and Corporate RSO did not receive a measurable dose during the operation. The two radiographers on site received 4 mR and 2 mR for the shift, not necessarily from the disconnect or retrieval." Minnesota Department of Health Report #MN120004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2012-03-21
47749 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2012-03-11 14:30 | 2012-03-16 14:29 | 2012-03-16 | TECHNICAL SUPPORT CENTER BACKUP DIESEL GENERATOR DECLARED NON-FUNCTIONAL "On March 11, 2012, a maintenance test of the Technical Support Center (TSC) diesel generator was performed. This diesel generator supplies backup A/C power to the TSC in the event of a loss of normal power. During this test, with the diesel generator supplying power to the TSC, two unexpected momentary losses of normal lighting to the TSC were observed. Following this event, the TSC diesel generator was declared non-functional. "High-priority actions to troubleshoot and repair the TSC diesel generator were taken following this event. However, as of 1200 CDT on March 16, 2012, troubleshooting activities are still ongoing, and the cause of the event has not yet been identified. "Normal power to the TSC has been available throughout this event, and the TSC is considered functional. However, due to the duration of the TSC diesel generator non-functionality, Callaway Plant is reporting this condition in accordance with 10 CFR 50.72(b)(3)(xiii) for a loss of emergency assessment capability. "Please note that, in the event of a complete loss of power to the TSC concurrent with a plant emergency, the designated backup facilities will be used in accordance with the Callaway Plant emergency preparedness program procedures. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-16
47748 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-03-16 04:00 | 2012-03-16 10:56 | 2012-03-16 | REFUELING WATER STORAGE TANK CONNECTED TO AN UNQUALIFIED SYSTEM "The Refueling Water Storage Tank (RWST) was placed on purification in accordance with [site procedure] OP-913, Refueling Water Purification Pump Operation, as directed from OP-301-1, Chemical and Volume Control System (Infrequent Operation), at 0400 [EDT] on 3/16/2012 to support make up of level to the RWST. This condition, connection of the purification loop, is not currently allowed based on unresolved seismic concerns with purification piping to the RWST. This was later discovered during a log review at 0545, and operators were immediately directed to remove the RWST from purification. ITS 3.5.4 was applied from 0400 based on when it was determined that this condition had been entered. ITS 3.5.4 was exited at 0622 when the RWST was removed from purification. "This is being reported pursuant to 50.72(b)(3)(v), Event or Condition That Could Have Prevented Fulfillment of a Safety Function." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-03-16
47747 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-03-15 01:00 | 2012-03-16 08:59 | 2012-03-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA DAMAGED DURING BUILDING FIRE A fire at one of the licensee's facilities resulted in damage to a Spec 880 Delta radiography camera (33 Ci of Ir-192; source serial number 76628B and camera serial number D7538). The outer casing was charred and brittle as a result of the fire. The source remained intact and in the shielded position. All radiation levels were normal for a shielded source. QSA global has been contacted and will pick up the camera. There were no personnel exposures as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-03-21
47746 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2012-03-15 08:30 | 2012-03-15 08:32 | 2012-03-15 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "A planned maintenance evolution at the Oyster Creek Nuclear Generating Station will remove the Technical Support Center (TSC) ventilation system from service. Therefore, the TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately six hours from 0800 [EDT] to 1400 today. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72(b)(3)(xiii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC resident has been notified." * * * UPDATE FROM JOHN CLARK TO VINCE KLCO AT 1109 EDT ON 3/15/2012 * * * The TSC was restored to service on March 15, 2012 at 1107 EDT. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Krohn) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-15
47745 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-03-14 20:34 | 2012-03-15 04:12 | 2012-03-15 | HPCI INOPERABLE DUE TO FAILURE OF TURBINE GOVERNOR VALVE "On March 14th, 2012 at 2034 EST the High Pressure Coolant Injection System (HPCI) was declared inoperable due to a failure of the turbine governor valve to respond as expected to demanded position. With the HPCI system flow controller output signal at zero percent demand the governor valve traveled to the mid position and did not remain closed as expected when the oil system auxiliary pump was started. With this unexpected response the speed and flow control system for the turbine is inoperable. The failure was discovered as part of a planned evolution for oil sampling. "All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling (RCIC) system remain operable. "The unit remains at 100% power. "The station has initiated an Event Response Team to identify and correct the cause of the failure. "No personnel injuries resulted from the event. "The NRC Resident Inspector and Lower Alloway Creek Township will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-03-15
47744 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2012-03-14 11:20 | 2012-03-14 18:20 | 2012-03-16 | UNIT 3 STEAM GENERATOR TUBES FAILED IN-SITU PRESSURE TESTING "On January 31, 2012, Unit 3 was shut down due to detection of a tube leak in one Steam Generator (SG). The shutdown was previously reported on Event Notification # 47628. Southern California Edison (SCE) has been performing in-situ pressure testing with non-radioactive water on tubes with significant wear indications. On March 14, 2012, at approximately 1120 PDT, Unit 3 Steam Generator (SG) E088 Tube R106 C78 did not meet the target performance criteria because leakage exceeded 0.5 gallons per minute at the maximum pressure achieved during the test (2,884 psig). This was the leaking tube that resulted in the Unit 3 shutdown. "Subsequently, two additional tubes in Unit 3 SG E088 did not meet the target performance criteria as follows: at 1249 PDT, Tube R102 C78 exceeded 0.5 gallons per minute at 3,268 psig and at 1425 PDT, Tube R104 C78 exceeded 0.5 gallons per minute at 3,180 psig. These occurrences are reportable as an 8-hour notification to the NRC in accordance with 10 CFR 50.72(b)(3)(ii)(A). Testing and inspection of Unit 3 steam generator tubes is ongoing to determine the extent and cause of the observed wear. A follow-up notification will be made for additional in-situ pressure test failures. The extent and cause of the condition will be addressed in the follow-up licensee event report that will be submitted in accordance with 10 CFR 50.73(a)(2)(ii)(A). Defective tubes will be removed from service as required prior to Unit 3 plant startup. "Unit 2 has been shut down since January 9, 2012 for a scheduled refueling outage. SCE previously performed in-situ pressure testing of the tube with the most wear in Unit 2. Results from this test demonstrated that the tube met the target performance criteria. "The NRC Resident Inspector has been notified of this event." * * * UPDATE FROM LEE KELLY TO DONALD NORWOOD AT 2108 EDT ON 3/15/2012 * * * "In-situ pressure testing on Unit 3 steam generator tubes was started on March 14, 2012 and is ongoing. On March 15, 2012, four additional tubes in Unit 3 SG E088 did not meet the target performance criteria of three-times normal pressure conditions as follows: (1) At 1109 PDT, Tube R100 C80 failed at 4,739 psig; (2) at 1437 PDT, Tube R107 C77 failed at 5,160 psig; (3) at 1604 PDT, Tube R101 C81 failed at 4,889 psig; and (4) at 1734 PDT, Tube R98 C80 failed at 4,886 psig. "Testing and inspection of Unit 3 steam generator tubes is ongoing to determine the extent and cause of the observed wear. Follow-up notifications will be made for any additional in-situ pressure test failures." The licensee notified the NRC Resident Inspector. Notified R4DO (Cain). * * * UPDATE FROM LEE KELLY TO JOHN SHOEMAKER AT 2115 EDT ON 3/16/12 * * * "In-situ pressure testing on Unit 3 steam generator tubes was started on March 14, 2012 and is ongoing. On March 16, 2012, one additional tube in Unit 3 SG E088 did not meet the target performance criteria of three-times normal pressure conditions as follows: at 1216 PDT, Tube R99 C81 failed at 5,026 psig. "Testing and inspection of Unit 3 steam generator tubes is ongoing to determine the extent and cause of the observed wear. Follow-up notifications will be made for any additional in-situ pressure test failures." The licensee notified the NRC Resident Inspector. Notified R4DO (Cain). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2012-03-14
47743 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-03-14 13:05 | 2012-03-14 17:32 | 2012-03-16 | LOSS OF THE TONE ALERT RADIO SYSTEM "On Monday, March 12, 2012, at 1435 EDT, Oswego County Warning Point notified Nine Mile Point, and NYS [New York State] Warning Point, via the land line, of a loss of the Tone Alert System for greater than one hour from the National Weather Service as of 1305 hrs. Site Emergency Procedures define a loss of Tone Alert System for greater than one hour, as a significant loss of Emergency Communications (EPIP-EPP-30). "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the NMP [Nine Mile Point] and JAF [James A. Fitzpatrick] Nuclear Power Plants. This failure meets NRC 8-Hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens, which also function as part of the Public Prompt Notification System, remained operable. "The loss of the Tone Alert System constitutes a significant loss of Emergency Off-Site Communications capability. Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper-reach system, which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM NATHAN LILIENTHAL TO VINCE KLCO AT 1050 EDT ON 3/15/2012 * * * "The tone alert system was restored Thursday, March 15, 2012 at 0933 EDT." The licensee notified the NRC Resident Inspector. Notified the R1DO (Krohn). * * * UPDATE FROM JOHN APRIL TO JOHN SHOEMAKER AT 1421 EDT ON 03/16/2012 * * * "Correction to original notification: In the description above, the date of event was incorrectly identified as Monday, March 12, 2012, the date should have been Wednesday, March 14, 2012." Notified the R1DO (Krohn). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-14
47742 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-03-14 13:05 | 2012-03-14 16:22 | 2012-03-15 | TONE ALERT RADIOS OUT OF SERVICE "At 1430 EDT on March 14, 2012, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the Tone Alert Radios had been out of service since 1305 EDT. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "This loss is believed to have been caused by a problem on a Verizon trunk line, which is currently being investigated. "The event has been entered into the corrective action program and the NRC Resident Inspector has been briefed." Licensee also notified the state and local authorities. * * * UPDATE FROM STEVE DEFILLIPPO TO DONALD NORWOOD AT 1207 EDT ON 3/15/12 * * * "On 03/15/2012 at 10:22, JAF was notified by Oswego County Emergency Management that the tone alert radio system had been restored to service 03/15/2012 at 09:33. The NRC Resident Inspector has been provided an update on status of the tone alert radio system." Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-14
47741 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2012-03-14 | 2012-03-14 15:38 | 2012-03-14 | PART 21 - POTENTIAL DEFECT ON ARVAN ELECTRICAL TERMINAL BLOCKS The following information was provided by facsimile: "COMPONENT DESCRIPTION: Arvan electrical terminal blocks, part number MS27212-x-xx, Revision P, sizes -3-xx and -5-xx. any length; Ametek Solidstate Controls part number 03-120608-00. Only lots purchased from 2010 to present are of concern. "PROBLEM YOU COULD SEE: A mottled or marbled appearance, vertical cracks and/or a slim void/flow line on a cut section of the terminal block, "CAUSE: The manufacturer's investigation revealed that an improper application of acetone agent, which ensures proper bonding/blending of materials, was not properly monitored and resulted in intermittent inadequate blending. Not every lot or complete batch run is affected. "EFFECT ON SYSTEM PERFORMANCE: Cracks and/or voids in the material could be exploited should a seismic event occur. "ACTION REQUIRED: We have no known failures of these terminal block products in our systems. We believe the failure rate has been extremely low and the risk is minimal. Each operating facility will need to evaluate the potential risk to their operation. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: If you wish to replace the terminal blocks in your systems, Ametek Solidstate Controls will work with you to arrange replacements. Please contact our Client Services group at 1-800-222-9079 or 614-846-7500 ext. 6260." The nuclear sites identified by the licensee to have these potentially defective parts are: Beaver Valley, Ginna, Harris, Hatch, VC Summer, Watts Bar, Braidwood, Byron, Cook, Davis Besse, Prairie Island, Arkansas Nuclear One, San Onofre Nuclear Generating Station, and South Texas Project. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2012-03-14
47740 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-03-14 08:00 | 2012-03-14 08:00 | 2012-03-15 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "At approximately 0800 EDT on March 14, 2012, preplanned maintenance will be performed on the Technical Support Center (TSC) ventilation system. This maintenance will be performed for door seal replacement, ventilation shaft seal and belt replacement. This maintenance is planned to be performed and completed within 10 hours. If an emergency condition should occur that would require activation of the TSC, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RICHARD VANDENBERG TO JOHN KNOKE AT 1735 EDT ON 03/14/2012 * * * The preplanned maintenance on the Technical Support Center (TSC) ventilation system was completed at 1730 EDT. The TSC is now fully functional. The licensee has notified the NRC Resident Inspector. Notified the R2DO (Guthrie). * * * UPDATE FROM RICHARD VANDENBERG TO CHARLES TEAL AT 0840 EDT ON 03/15/2012 * * * "At approximately 0800 on March 14, 2012 preplanned maintenance will be performed on the TSC ventilation system. This maintenance will be performed for door seal inspections and ventilation fan belt inspections. This maintenance is planned to be performed and completed within 10 hours. If an emergency condition should occur that would require evacuation of the TSC, the Harris Nuclear Plant (HNP) emergency plant has procedural guidance for use of an alternate location. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity reflects an emergency response facility for the duration of the maintenance." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Guthrie). * * * UPDATE FROM RICHARD VANDENBERG TO DONALD NORWOOD AT 1650 EDT ON 03/15/2012 * * * "At approximately 1630 on March 15, 2012, all scheduled maintenance has been completed and the TSC has been restored to a fully functional status." The licensee notified the NRC Resident Inspector. Notified R2DO (Guthrie). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-14
47739 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-13 14:00 | 2012-03-13 17:58 | 2012-03-13 | OFFSITE NOTIFICATION OF A SEWAGE LEAK "A Sewage Lift Station overflow occurred due to equipment failure. The overflow was discovered at 1400 CDT and terminated shortly thereafter. CPNPP Environmental notified TCEQ (Texas Commission on Enviornmental Quality) Region 4 (DFW) at 1441 CDT. This is reportable as a bypass of untreated wastewater as defined in the TPDES [Texas Pollution Discharge Elimination System] Permit. CPNPP Environmental personnel have completed disinfection of the affected area." The licensee estimated the leak to be between 100 and 200 gallons with a small portion reaching the lake. The equipment failure is suspected as being a failed level indicating system. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-13
47738 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-03-13 | 2012-03-13 17:39 | 2012-03-13 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA WAS LOST AND RECOVERED A radiographer working for High Mountain Inspection was conducting radiography on a pipeline near De Beque, CO. The radiographer failed to secure the camera in his pickup truck when he drove off to the next location. Arriving at his destination the radiographer realized his camera was missing and retraced his steps. The radiography camera with a 26 Curie, Ir-192 source was not located. At 1826 EDT the State of Colorado called and said a member of the public had found the missing camera and called the licensee. The licensee is now in possession of the radiography camera and the source has not been tampered with. The camera is a SPEC, s/n 150. The source s/n is SJ0702. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-03-16
47737 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2012-03-12 | 2012-03-13 11:22 | 2012-03-13 | AGREEMENT STATE REPORT - ABORTED FRACTIONAL DOSE TREATMENT The following information was received from the State of New Jersey: "A patient was treated with a Nucletron microSelectron 106.990(v3) HDR unit on March 12, 2012. The prescription dose was 600 cGy per fraction for 5 fractions. The fractional treatment planned was for a total of 14 dwell positions in two different catheters: six dwell positions in the ring to be treated on HDR Channel 1 and eight dwell positions in the tandem to be treated on HDR Channel 3. After all appropriate QA, the patient treatment was started with Channel 1 being the first set of dwell positions treated. At the completion of the Channel 1 treatment, the HDR unit gave an error stating that there was a 'Possible incomplete source retraction in Channel 2.' Even though all radiation indicators did not detect the presence of radiation, and even though the licensee was not using Channel 2, immediate emergency procedures were implemented. The emergency stop was activated and the room was entered with a survey meter to verify that there was no elevated radiation present. All indications were that the source was retracted properly and that there was no danger to the patient or the staff. "The error displayed on the treatment screen indicated that it was possible that dust was on the optocoupler, thus causing the fault. However, the error could not be cleared by using the reset button. Nucletron was immediately contacted. Nucletron support personnel attempted to walk the licensee through some steps that may have cleared the error, but they were unsuccessful. Therefore, the remaining part of the patient's treatment was aborted. Nucletron scheduled one of their service engineers to respond to the licensee's facility to repair the unit. "The authorized user informed the patient that the complete treatment was not delivered due to the machine malfunction and that the authorized user would determine what action to take on the future fractions. The patient and the treatment room were surveyed prior to release. No elevated readings were observed. The patient received 120 cGy (versus the prescribed dose of 600 cGy). The deviation from the written directive was documented in the patient's chart." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-03-19
47736 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-03-13 08:00 | 2012-03-13 08:10 | 2012-03-13 | EMERGENCY OPERATIONS FACILITY PLANNED MAINTENANCE "At approximately 0800 EDT on March 13, 2012, preplanned maintenance will be performed on the Emergency Operations Facility (EOF) ventilation system. This maintenance will be performed for charcoal sampling and filter testing. This maintenance is planned to be performed and completed within 10 hours. If an emergency condition should occur that would require activation of the EOF, the Harris Nuclear Plant (HNP) emergency plan has procedural guidance for use of an alternate location. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1707 EDT ON 3/13/2012 FROM RICHARD VANDENBERG TO MARK ABRAMOVITZ * * * Maintenance was completed and the system tested operable at 1645 EDT. The licensee notified the NRC Resident Inspector. Notified the R2DO (Guthrie). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-13
47735 | -1 | ENERSYS |  |  |  |  | 2012-03-12 | 2012-03-12 15:33 | 2012-05-11 | INTERIM REPORT CONCERNING BATTERY CELLS WITH POTENTIALLY REDUCED DISCHARGE CAPACITY "This letter will serve as the interim report to the Commission as pursuant to 10CFR21.21 (a) (2). The notification is in regards to a 2GN-23 battery manufactured by EnerSys and installed as part of Station Battery 2-2 at the Dominion Virginia Power, North Anna Station. Battery verification testing performed at North Anna indicated that although the battery was able to meet North Anna's 2 hour discharge requirements, cell #59 appeared to show reduced capacity. As a result, Dominion returned cells #59 and #60 to EnerSys. The cells were received at the EnerSys Corporate Laboratory under Return for Analysis (RFA) ENS-11204. "During our analysis, which consisted of float charging, discharge testing at the 3 hour rate and an internal inspection it was determined that the cell was unable to meet the defined technical requirements for discharge capacity. Following the determination a series of analytical tests were ordered to perform more in depth analyses of the internal components. Testing on the component samples is currently underway. At this time we have not yet been able to determine if a "defect" as defined in Part 21 exists and therefore this interim report has been prepared. It is expected that the current tests will be completed by May 11, 2012. However, it should be noted that further analysis including the return of additional cells may be required to determine the cause and the reportability under Part 21 reporting." "Throughout the return and analysis processes EnerSys has been in contact with representatives of the North Anna Station. They have been made aware of the electrical test results and recently of the internal inspection results. They are also aware that there has been no cause determination at this time. Station personnel have also been notified that this interim report has been issued." * * * RETRACTION FROM WILLIAM ROSS TO HOWIE CROUCH AT 0953 EDT ON 5/11/12 * * * The following information was received from EnerSys via fax: "Subsequent to the March 12th letter, analytical testing on the components of the returned cells was completed. The results indicated there were no material composition discrepancies or assembly process anomalies. The only issue seen in cell #59 was that a portion of the positive active material physically separated from the positive grid structure. Additionally, data recorded during the manufacturing process was reviewed with no issues or nonconformities noted. "A visit to the North Anna site was undertaken by EnerSys Engineering to review information from both Station 1 and Station 2. Battery verification testing at both stations showed all station batteries to have acceptable performance. A comparison of the testing performed by North Anna and the testing performed by EnerSys indicated that there was no further capacity degradation in cell #59. It is expected that the cells in the two station batteries will perform similarly. "Based upon our further investigation we have concluded that no deviation per 10CFR21.21 exists. The positive active material separation was determined to be to a unique inconsistency in that plate curing lot." Notified R2DO (Freeman) and NRR Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-03-13
47734 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-03-10 | 2012-03-12 20:18 | 2012-03-12 | AGREEMENT STATE REPORT - TWO MISSING MOISTURE DENSITY NUCLEAR GAUGES The following information was provided by the State of California via email: "On March 12, 2012, the RSO at Consolidated Engineering called the RHB [State of California - Radiological Health Branch] to report two missing moisture density nuclear gauges from their Oakland, CA storage facility, followed by an email (see below) detailing the events: "On January 4 and January 5, 2012, as part of our bi-annual inventory, personnel performed an audit on a number of our nuclear gauges as required by our license. The inventory report was submitted to the RSO for review. Additional information was requested by the RSO on some of the gauges as is normal and customary. All of the gauges at that time were present and accounted for and were found to be satisfactory. "On January 26, gauge # 0840 was signed in and out of our Oakland laboratory by one of our senior technicians. He subsequently used a different gauge in the days that followed. As part of my continuing duty to monitor locations and conditions of gauges, it became apparent to me last week that one of our gauges, #0840 was not in its designated storage location. In the course of calling all of our technicians and evaluating all of our storage locations, we called all gauges to be brought into our San Ramon office on Saturday March 10th. A second inventory was performed at that time on all of the gauges on our license. It was noted that gauge #0840 was missing as was gauge #5027, which was also stored in the Oakland location. "We continued to exhaust all records, including sign-in and sign-out logs, report forms and checking with our license repair personnel and have concluded today that these gauges were more than likely stolen out of our Oakland office in January. Manufacturer Model # Serial No Last documented use of gauge Troxler 3411B T341 5027 06 January 2012 CPN MC3 M320400840 26 January 2012 "The [source] quantities are as follows: CPN, 10 millicuries of Cesium 137 and 50 millicuries of Americium 241 Troxler, 09 millicuries of Cesium 137 and 44 millicuries of Americium 241." California Incident #5010-031212 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-03-15
47733 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-12 07:42 | 2012-03-12 11:51 | 2012-03-12 | OFFSITE NOTIFICATION - NON-WORK RELATED ON-SITE FATALITY "At 0742 PDT on March 12, 2012, a non-work related on-site fatality occurred at the Diablo Canyon Power Plant. The fatality was not related to the health and safety of the public or on-site personnel. Specifically, a contractor for Pacific Gas and Electric (PG&E) was found in the Engineering Offices before work hours with no pulse or life signs. The individual was promptly attended to by Diablo Canyon Industrial Fire Officers and a transfer to a local hospital by ambulance was completed. The individual was pronounced dead at the hospital. "The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved . The work location was outside of the Protected Area. "PG&E has not observed any heightened public, media, or government concern as a result of the fatality. Because the fatality is unrelated to Diablo Canyon Power Plant industrial or radiological health and safety, no news release is planned. "Because the fatality was not work-related, nor the result of an accident, no notification to other government agencies was made at the time. However, PG&E may make a notification to the California Occupational Safety and Health Administration due to a cardiac arrest on-site. Thus this ENS notification is in response to a notification to another government agency in accordance with 10CFR50.72(b)(2)(xi). "The deceased person worked for Enercon Services. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-12
47732 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2012-03-11 09:00 | 2012-03-12 10:44 | 2012-03-12 | OFFSITE NOTIFICATION TO STATE REQUIRED BY NPDES PERMIT FOR A BYPASS DISCHARGE "Facility: Westinghouse Electric Company LLC (WEC), Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: March 11, 2012 approximately 0900 "Reason For Notification: "On March 12, 2012, the Westinghouse Environmental Engineer was notified that the level readings of the South Lagoon indicated that a leak has developed in the South Lagoon liner. This liner was recently replaced. The South Lagoon is one of the lagoons used for settling solids from treated process wastewater prior to discharge. As the lagoons are located downstream of the Columbia plant wastewater radiological treatment systems, the wastewater in the lagoons is below the 10 CFR Part 20 radioactive materials discharge limits. However, the final discharge monitoring station required by the permit for chemicals are located downstream of the settling lagoons and such a leak is therefore an unanticipated bypass. The current sample analysis of the South Lagoon wastewater reflect the activity is < 4.6 x10 (-7) ÁCi / ml and chemical results are within permit limits. "Liquid discharges from the Columbia Plant are regulated with regard to chemical pollutants through the SC-DHEC/EPA administered NPDES (National Pollutant Discharge Elimination System) permit SC#0001848. Westinghouse is required to notify SC-DHEC of unanticipated bypass conditions in accordance with Permit. "Notification to NRC is being made based on 10 CFR70 Appendix A, Section (c) Concurrent Reports: "' Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made shall be reported to the NRC Operations Center concurrent to the news release or other notification.' "As Found Condition: See reason for notification. "Summary of Activity: - Liquid inflows to the South Lagoon have been rerouted to other authorized locations - Westinghouse is emptying the South Lagoon through the normal monitored effluent discharge point. - The liner vendor has been contacted and arrangements are in progress for the vendor to conduct necessary inspections and repairs as soon as practicable. - Westinghouse has initiated additional monitoring of the wells in close proximity of the South Lagoon to better assess any potential environmental impact. - The event has been entered into the plant's Corrective Action Process and a thorough review will be performed to identify the cause of the event. "Conclusions - The problem was identified by Westinghouse personnel. - At no time was the health or safety to any employee or member of the public in jeopardy. - SC-DHEC has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2012-03-12
47731 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2012-03-12 | 2012-03-12 08:06 | 2012-03-12 | AGREEMENT STATE REPORT - SURFACE CONTAMINATION IDENTIFIED ON LAB FLOOR The following information was received from the State of Tennessee via e-mail: "During the routine lab cleanup/surveys, the RSO found 50-70 spots of contamination throughout the lab on the floor. It was determined that the contamination had occurred when a pharmacist working with I-131 capsules under the hood, had removed his glove within the hood. Subsequently, the glove had fallen to the floor depositing an unknown quantity of I-131. The pharmacist then walked through the lab and spread the contamination throughout. The pharmacist failed to survey the area or himself upon exiting the lab. The RSO found no contamination outside the restricted area. The RSO proceeded to cover the floor with cardboard, covering all areas of contamination. Areas were surveyed and the dose rates were very low even at 1 ft. from the I-131 contamination. There were no dose readings at 1 meter. All staff bioassays were below detectable limits." TN Report ID: TN-10-082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-03-15
47730 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-03-12 08:27 | 2012-03-12 08:55 | 2012-03-13 | PLANNED MAINTENANCE WINDOW ON TECHNICAL SUPPORT CENTER VENTILATION "Planned preventive maintenance activities are being performed on the Hatch Nuclear Plant's Technical Support Center (TSC) Emergency Ventilation System on Monday, March 12, 2012. These maintenance activities include the performance of absorber charcoal replacement and DOP testing per 42SV-X75-001-1, 'Testing of TSC Filter Train.' These work activities are planned to be completed within the (12) hour day shift on 03/12/2012. "During the time these activities are being performed, the TSC Emergency Ventilation System will be inoperable. As such, the TSC HVAC will be rendered non-functional during the performance of these work orders. If an emergency is declared requiring activation of the TSC during the time these work activities are being performed, then the contingency plans call for utilization of the TSC as long as habitability and radiological conditions allow. Procedure 73EP-EIP-063-0, 'Technical Support Center Activation,' provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM CHRIS BURKE TO JOHN KNOKE AT 1644 EDT ON 3/13/12 * * * "During post Preventive Maintenance [PM] activity testing, the TSC emergency filter train bypass valve 1X75F005 damper failed to meet leakage criteria (CR 422749). PM activities were halted and a corrective maintenance Work Order SNC377526 initiated at approximately 2030 EDT to investigate, repair and retest the bypass valve damper. Repair work to the TSC emergency filter train bypass valve was completed. The retest and verification was performed and the TSC HVAC system returned to service at 1550 EDT on 3/13/12." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Eugene Guthrie) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-12
47729 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-03-09 14:00 | 2012-03-09 19:48 | 2012-03-09 | FAILURE OF A TECHNICAL SUPPORT CENTER AIR HANDLING UNIT "At approximately 14:00 on March 9, 2012, with the Harris Nuclear Plant operating at 100% power in mode 1, Air Handler 17 was discovered not operating. Air Handler 17 provides ventilation supporting environmental habitability to the Technical Support Center (TSC) to keep ambient temperatures comfortable for personnel and to ensure communications and assessment equipment remain functional. This degrades the heating and cooling capacity of the TSC by approximately a third. Due to the cool weather in the forecast, the remaining cooling systems will be operating more efficiently than they would in the hot summer months, which mitigates the impact of the degraded ventilation system. The system will be repaired expeditiously. The cause of the equipment failure is not yet known but will be investigated in the site corrective action program. This report is being made in accordance with 10 CFR 50.72, criterion (b)(3)(xiii) as a condition that may impair the functionality of an Emergency Response Facility. The plant continues to operate at 100%. Other equipment functioned as expected. The on call Emergency Response Manager and Site Emergency Coordinator (TSC) have been notified and the alternate TSC is available." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-09
47728 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-08 18:50 | 2012-03-09 19:17 | 2012-03-09 | INOPERABLE STEAM GENERATOR NARROW RANGE LEVEL TRANSMITTERS DUE TO PART 21 CONCERN "Pacific Gas and Electric (PG&E) is supplying this information as a voluntary report. On March 8, 2012, at 1850 PST, Diablo Canyon Power Plant (DCPP), Unit 1, declared the steam generator (SG) 1-1 narrow-range, low-low, water level channels for level transmitters LT-517 and LT-519 inoperable. This resulted from DCPP determining that the low-low setpoints were non-conservative as a result of its evaluation of the Rosemount Nuclear's 10 CFR Part 21 notification titled 'Notification Under 10 CFR Part 21 on Certain Rosemount Model 1154 Series H Pressure Transmitters,' dated March 2, 2012. "PG&E determined that the following SG narrow-range level transmitters having reactor protection and emergency safeguards actuation functions are affected: Unit 1: - two channels on SG 1-1 - one channel each on SGs 1-2 and 1-4 Unit 2: - one channel each on SGs 2-1, 2-2, 2-3 and 2-4 "The Part 21 notification identified that the high temperature/pressure accuracy specification changed for certain transmitters which have higher impedance resistors installed in their temperature compensation circuitry. PG&E's evaluation concluded that narrow range SG low-low level setpoint uncertainty increased by as much as 2 percent of span due to the revised specification. Under the most limiting conditions, this deficiency could result in a short delay in relay actuation. "At 1953 PST, DCPP personnel declared the LT-517 and LT-519 water level low-low channels for SG 1-1 to be operable after adjusting the low-low setpoints from 15 percent to 17 percent on SG 1-1. DCPP also changed the low-low setpoints on SG 1-2 and SG 1-4 on March 8, 2012, and is changing this setpoint on all four of the Unit 2 SGs. "PG&E plans to submit a Licensee Event Report on this issue. "Plant personnel notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2012-03-09
47727 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-03-08 | 2012-03-09 15:57 | 2012-03-09 | AGREEMENT STATE REPORT - UNDERDOSE DURING HEPATIC TREATMENT USING YTTRIUM-90 THERASPHERES The following information was received via e-mail from the State of North Carolina Radiation Protection Section: "The agency [NC Radiation Protection Section] was notified of a medical event at UNC - Chapel Hill by the RSO. The event occurred yesterday. The patient was administered a Y-90 therasphere dose. Three flushes were done and proper surveys were made to ensure none of the dose was left in the IV lines. As per protocol, dose delivered is calculated via measurement of the administration vial and the waste collection vial. At this point it was noted that the patient only received 78% of the prescribed dose. The surveys indicate that the dose was left in the administration vial. "Exact prescription dose was not provided at this time. No cause has been determined yet. There was no spilling, but the physician did note that it was harder to push the plunger for the flush to go through than he usually experiences. A second dose was delivered to a different patient using the same lot today, and the administration was successful (95% delivered). "The patient who received the underdose has not yet been notified due to other health complications not caused by the underdosage. The patient's physician is aware and waiting for an appropriate opportunity to inform the patient. It has been determined that a second dose will not be administered since the physician has deemed the dose received adequate." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-03-15
47726 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-03-08 22:18 | 2012-03-08 23:26 | 2012-03-08 | REPORT OF A SINGLE EMERGENCY SIREN ACTUATION "Limerick Generating Station was informed by Montgomery County 911 dispatch center that Limerick Emergency Preparedness Zone (EPZ) siren # 128, at the corner of Vaughn and Springer town roads in Montgomery County was sounding. "Notification time was 2218 EST. The siren was silenced at 2227 EST. "The siren maintenance contractor was contacted for repairs. "No actual plant emergency exists. The siren activation was caused by an equipment malfunction. "The remaining 164 of 165 Limerick EPZ sirens remain functional. No other reportability thresholds have been met or exceeded. "An 'Event of Potential Public Interest' will be issued to the state and local agencies." The licensee has notified the NRC Resident Inspector. The licensee will also notify state and local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-08
47725 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-03-08 09:54 | 2012-03-08 13:40 | 2012-03-08 | NOTIFICATION OF THE MINNESOTA POLLUTION CONTROL AGENCY FOR RELEASE OF AMERTAP BALLS "At 0954 on 3/8/12 Xcel Energy notified the Minnesota Pollution Control Agency of an Amertap ball release exceeding 1.5 barrels per agreement. Three barrels of Amertap balls are unaccounted for. Plant operational personnel are inspecting the site water system for unaccounted Amertap balls. A survey of the river performed by personnel only produced 4 of the missing balls." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-08
47724 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-03-07 13:15 | 2012-03-08 11:02 | 2012-03-08 | LOCAL ALARM HORN WAS FOUND TO BE INAUDIBLE DURING ROUTINE TESTING "At approximately 1315 EST on 3/7/12, it was discovered during routine testing on an outdoor Criticality Accident Alarm System (CAAS) Data Acquisition Module (DAM #21), that the local alarm horn in the Wilmington Field Services Center (WFSC) building #1 in-vessel tooling refurbishment area was inaudible. The cause of the condition is under investigation. "Personnel were removed from the in-vessel tooling refurbishment area until compensatory measures were established. There are not active fissile material operations impacted by this discovery, thus no unsafe condition existed. The licensee notified the NC Division of Radiation Protection and New Hanover County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2012-03-08
47723 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2012-03-01 19:06 | 2012-03-07 16:00 | 2012-03-07 | FAILURE TO FOLLOW SITE FITNESS FOR DUTY PROCEDURES "On March 01, 2012, it was discovered that a [Contractor] program manager intentionally failed to implement a procedure change as instructed by management. An initial investigation has determined that interim compensatory actions were in place prior to this pending procedural change. The involved manager's access authorization has been revoked. Southern Nuclear Operating Company, Inc. (SNC) was notified by [the Contractor] of this discovery on March 06, 2012 at 19:00 EST. "SNC is providing this notification under the provisions of 10 CFR 26.719(b)(3) as an intentional act that casts doubt on the integrity of the FFD program. "At the time of this report, no regulatory barriers for individuals assigned to perform duties that require them to be subject to the FFD program have been breached regarding this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2012-03-07
47722 | -1 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2011-07-05 | 2012-03-07 14:45 | 2012-04-19 | MEDICAL EVENT - DOSAGE DELIVERED TO PATIENT DIFFERED BY 20% FROM PRESCRIBED DOSAGE On 7/5/11 a male patient receiving treatment for prostate cancer was supposed to receive 52 Iodine-125 seeds to the prostate. The physician conducting the surgery injected 21 of the 52 seeds to an area outside the target volume. Only 31 of the 52 seeds were injected into the targeted area. The physician and patient will be advised of the disparity in dosage. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 1100 EST ON 4/19/12 FROM RICHARD TO SIMPSON * * * The licensee is retracting this event report after a review and evaluation of the doses administered. The licensee has determined that this event is not reportable based on the delivered dose not differing by 20% from the prescribed dosage and is therefore not reportable under 10 CFR 35.3045. The licensee has discussed this conclusion with NRC Region 3 (Warren). R3DO (Peterson) and FSME (McIntosh) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-03-13
47721 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-03-06 16:13 | 2012-03-06 19:33 | 2012-03-06 | LOSS OF EMERGENCY SIRENS DUE TO ROUTER POWER SUPPLY FAILURE "At 1613 [CST], FCS [Fort Calhoun Station] Control Room was notified by corporate communications that 2 non-adjacent sirens out of 101 total sirens lost communication. These were Siren #1 at 1602 [CST] and Siren #50 at 1609 [CST] due to potential router issues. Required compensatory actions were established at 1630 [CST] for loss of the 2 sirens. Initial troubleshooting revealed radio communication failed at 1543 [CST] and manual testing of the remaining sirens was instituted. "At 1643 [CST], corporate communications notified the Control Room initial testing on Siren #2 was not responding and indicative that all sirens were lost. Based on that report, all sirens for the Alert Notification System within the Emergency Planning Zone (EPZ) were declared nonfunctional and notifications were completed. Local Law Enforcement has been notified in the required surrounding counties to perform required actions in case of an emergency with the sirens unavailable. Compensatory measures are in place to ensure notification of the public by local law enforcement in case of an actual emergency. "Troubleshooting of the siren's communication system revealed that a peripheral router dual power supply had failed at 1539 [CST] and has been replaced. All repairs completed and retested satisfactorily with proper communications confirmed with each siren. As of 1750 [CST], all sirens [were] restored to functional status. The power supply failure resulted in 2.2 hours with the sirens being unavailable. Notifications have been completed with compensatory actions by local law enforcement secured. "This is being reported per 10CFR50.72(b)(3)(xiii) for, 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability'." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-06
47720 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-03-06 06:24 | 2012-03-06 08:16 | 2012-03-06 | NOTIFICATION OF UNUSUAL EVENT DUE TO UNIDENTIFIED RCS LEAKAGE GREATER THAN 10 GPM "Unidentified or pressure boundary leakage greater than 10 gpm [was indicated] due to changing Reactor Coolant System (RCS) level. Investigation of the event indicates that the reactor vessel head vent spool piece was removed at the time the RCS level started decreasing. A vacuum existed in the RCS at the time of removal of the spool piece which caused air to enter the reactor vessel head. The RCS level decrease was due to this. The charging system was placed in service at 80 gpm to regain the RCS level back to the original level. A walk down of all plant areas where leakage could have occurred has been completed with no leakage found. The charging system has been secured and RCS level is stable at this time." The licensee notified the NRC Resident Inspector, the State of Minnesota, the State of Wisconsin, and local authorities in both states. The licensee will be issuing a press release. * * * UPDATE FROM STEVE SCHMIDT TO VINCE KLCO AT 1523 EST ON 3/6/2012 * * * "NUE [Notification of Unusual Event] CU1.1, unidentified or pressure boundary leakage greater than 10 gpm that was entered at 0624 [CST] on 3/6/2012 at the Prairie Island Nuclear Plant has been terminated at 1136 on 3/6/2012. The entry criteria for CU 1.1 is no longer met as validated by a stable reactor coolant system level and no leakage found by plant walk downs." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Ring), NRR-EO (Chernoff), IRD (Kozal) and the following federal agencies: DHS-SWO, FEMA, USDA, HHS, DOE, EPA, NuclearSSA and DHS-NICC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-03-06
47719 | 0 | CAMDEN CLARK MEMORIAL HOSPITAL |  |  |  |  | 2011-02-25 12:00 | 2012-03-05 16:17 | 2012-12-03 | DOSE RECEIVED BY PROSTATE LESS THAN PRESCRIBED At the request of NRC Region I, Camden-Clark Memorial Hospital reassessed records from a prostate radioactive seed implantation procedure that had been performed on February 25, 2011. The record review indicated that the patient had received roughly 80 percent of the prescribed dose. "The effect on the patient has been minimal as the desired response was achieved. The long term effect will be under constant follow-up. "The entire implant process will be reviewed with special attention to real time seed placement and subsequent thirty day image evaluation with respect to NRC regulatory guidelines. "The attending physician, based on medical judgment, felt that notifying the patient would be harmful. The patient is under the care of oncologic physicians and will be followed appropriately as per his disease type." * * * UPDATE AT 1636 EST ON 12/03/12 FROM DAN BERKLEY TO S. SANDIN * * * The licensee is updating the report with the following information: "That (1) the dose received by the target was less than 80% of the prescribed dose and (2) a small volume of tissue outside of, and adjacent to, the treatment site received a dose that was greater than 10 Gy and more than 50% greater than the prescribed dose to that location." The licensee discussed this update with R1 (Weidner). Notified R1DO (Jackson) and FSME Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-03-11
47718 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-03-05 12:36 | 2012-03-05 15:39 | 2012-03-05 | LOSS OF TONE ALERT RADIO SYSTEM "On Monday, March 5, 2012, at 1305 EST, Oswego County Warning Point notified Nine Mile Point [NMP] and NYS [New York State] Warning Point, via the RECS Line, of a loss of the Tone Alert System for greater than one hour as of 1236 EST from the National Weather Service. Site Emergency Procedures define a loss of Tone Alert System for greater than one hour as a significant loss of Emergency Communications (EPlP-EPP-30). "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the NMP and JAF [James A. FitzPatrick] Nuclear Power Plants. This failure meets NRC 8-hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens, which also function as part of the Public Prompt Notification System, remained operable. "The loss of the Tone Alert System constitutes a significant loss of emergency off-site communications capability. Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper-reach system, which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "As of 1327 EST on March 5, 2012, Nine Mile Point was notified by the Oswego County Warning Point that the Tone Alert System has been returned to service." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-05
47717 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-03-05 11:36 | 2012-03-05 14:46 | 2012-03-05 | LOSS OF TONE ALERT RADIO SYSTEM "At 1303 EST on March 5, 2012, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 1136 EST on March 5, 2012. The Tone Alert Radio System was restored at 1327 EST on March 5, 2012. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures were verified to have been available. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel were also available for 'Route Alerting' of the affected areas of the EPZ." The portion of the EPZ population affected is approximately 10%. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-03-05
47716 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2012-02-16 | 2012-03-02 16:51 | 2012-04-03 | PART 21 REPORT - ROSEMONT PRESSURE TRANSMITTERS OUT OF TOLERANCE CONDITION The following information was received by facsimile: "During the course of qualification testing to replace certain diodes identified for obsolescence, an out of tolerance condition during steam pressure/temperature testing was observed on a test pressure transmitter in the qualification program. Through investigation into the out of tolerance condition, it was determined that the condition was not related to the replacement diode, but rather the result of the magnitude of a resistance change made to the transmitter temperature compensation circuitry during a final factory acceptance test. A brief description of the final acceptance test follows. "During pressure transmitter final processing, a test is conducted on Model 1154 Series H pressure transmitters to assess the effects of ambient temperature changes on the 4mA to 20mA analog output. The temperature test is performed on each transmitter to verify the transmitter accuracy performance over normal operating temperatures from 40 F to 200 F. If the transmitter does not meet the acceptance criteria for the test, changes can be made to the compensating resistor values to optimize performance in the normal operating temperature range. If the resistance adjustment is too large, it has been determined that the accuracy of the pressure transmitter relative to the published steam pressure/temperature profile and accuracy specification may be exceeded during a steam pressure/temperature event. "The magnitude of output shift during steam pressure/temperature conditions, that is attributable to the resistance changes made in final processing, is predictable based on the specific amount of resistance added or subtracted during the compensation process for each transmitter. Accordingly, RNII [Rosemount Nuclear Instruments, Inc] has reviewed the production records for the potentially affected transmitters and a revised steam pressure/temperature accuracy specification has been established for each shipped pressure transmitter. The revised steam pressure/temperature accuracy specification has been listed by serial number. "This revised specification supersedes the published steam pressure/temperature accuracy specification for all Model 1154 Series H pressure transmitters affected by this notification. Also note that for certain calibrations with large zero elevation and suppressions as defined in RNII's Part 21 Notification, dated February 23, 2012, an alternate steam pressure/temperature accuracy specification is also provided for pressure transmitters that are affected by both notifications. All other 1154 Series H published specifications remain unchanged. "On February 23, 2012, it was concluded that a substantial safety hazard may exist. RNII does not have sufficient information to determine the potential safety impact in plant applications. As a result, a notification about the potential substantial safety hazard is being made in accordance with 10 CFR Part 21 to customers who purchased affected 1154 Series H pressure transmitters. "The manufacturing rework procedure 01153-3000 has been updated to limit the amount of acceptable resistance that may be added or subtracted during final testing. A revised steam pressure/temperature accuracy specification for each pressure transmitter impacted by this notification has been determined. "RNII recommends that users review the application where 1154 Series H pressure transmitters are used to determine if there are safety considerations related to the revised steam pressure/temperature accuracy specification." The United States nuclear sites associated with this Part 21 are: Farley, D.C. Cook, Palo Verde, ANO-1, Calvert Cliffs, Point Beach, Oconee, Catawba, Waterford 3, Braidwood, La Salle, Davis Besse, Crystal River 3, Vogtle, Millstone, Diablo Canyon, Salem, Hope Creek, San Onofre, South Texas, Watts Bar, Comanche Peak, Wolf Creek, St. Lucie, Dominion Energy - Unspecified, and Northeast Nuclear Energy - Unspecified. * * * UPDATE FROM DUYEN PHAM TO PETE SNYDER ON 4/3/12 AT 1531 EDT * * * The following information was received by facsimile: This revision potentially affects the following commercial nuclear power plant sites in the United States: 1. Calvert Cliffs, 2. Millstone, 3. Hope Creek, 4. Salem, 5. Catawba, 6. Crystal River, 7. Farley, 8. Oconee, 9. St. Lucie, 10. Vogtle, 11. Watts bar, 12. Braidwood, 13. Davis Besse, 14. D.C. Cook, 15. LaSalle, 16. Point Beach, 17. Arkansas Nuclear One, 18. Comanche Peak, 19. Diablo Canyon, 20. Palo Verde, 21. San Onofre, 22. South Texas Project, 23. Waterford 3, and 24. Wolf Creek. "Note: Notification #1 [EN #47693], dated 23 February 2012 (and revised on 2 April 2012) impacts ALL 1154 Series H pressure transmitters range codes 4 to 8 shipped since 1988. This does NOT impact the 1154SH9 since the 1154SH9 has a wider steam pressure/temperature specification. The revised specification is the same for all affected transmitters. "Note: Notification #2 [this report - EN #47716], dated 2 March 2012 (and revised as of today [3 April 2012]) impacts only a subset of 1154 Series H pressure transmitters range codes 4 to 9 shipped from March 1994 to February 2012. This is a smaller affected population and does include the range 9 in the scope. The revised specification for this second issue is serial number dependent and only affects the transmitters listed in Appendix A [of the full part 21 report]." Notified R1DO(Caruso), R2DO(McCoy), R3DO(Bloomer), R4DO(Haire), and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2012-03-05
47715 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2012-03-03 09:58 | 2012-03-03 13:45 | 2012-03-03 | OFFSITE NOTIFICATION DUE TO OIL SHEEN IN HUDSON RIVER "Indian Point Unit 3 is at 100% power. At approximately 0958 EST on 3/3/2012, an oil sheen was observed in the discharge canal and Hudson River. The size of sheen in river was about 10 square feet and the source of the sheen is not known at this time. Oil is suspected, but not yet confirmed. There is no adverse impact on the plant. All required notifications have been made, including the New York State Department of Environmental Conservation, Westchester County Department of Health, and the U.S. Coast Guard National Response Center." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-03-03
47714 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-20 | 2012-03-02 11:41 | 2012-06-08 | RADIOGRAPHY CAMERA SOURCE ASSEMBLY SLIDE CONNECTOR INOPERABLE The following information was provided by the State of Arkansas via E-mail. "During a telephone call on February 29, 2012 with International Testing and Inspection Services, Inc., the company president stated that they had returned a sealed source (QSA Global, Inc., Model Number 87703, Serial Number 70162B) contained in a radiography camera (Industrial Nuclear Company, Inc., Model Number IR-100, Serial Number 4311) after the slide connector on the source assembly would not move. "On March 1, 2012, two health physicists from the Arkansas Department of Health, Radiation Control Program went to the licensee's facility to determine if this met the reporting requirements of 10CFR 30.50(b)(2). The Arkansas equivalent regulation is RH-1502.f.2. "The Radiation Safety Officer was not available at the time; however, the health physicists were able to interview the radiography crew using the camera during the failure. The radiography crew indicated that upon arrival at a job site on February 20, 2012, while attempting to connect the control assembly cable, they were unable to move the slide connector on the source assembly. They contacted the company president and returned to the office. The company president informed the Radiation Safety Officer. "After returning to the office the camera and source were removed from service and returned to Industrial Nuclear Company, Inc. (manufacturer of the camera) on February 24, 2012. Leak tests performed on the camera and sealed source upon arrival at INC, Inc. indicated no contamination. "Since the source assembly was manufactured by QSA Global, Inc.; Industrial Nuclear Company, Inc. indicated to the licensee that a cause was not identified but that the source assembly needs to be replaced. "The Arkansas Radiation Control Program has determined that this is reportable under 10CFR 30.50(b)(2) and is making this report to the [NRC] Operations Center. The Program [Arkansas Department of Health, Radiation Control Program] continues to investigate to identify the problem with the source assembly. "No overexposures to the public or to the radiography crew resulted from this event." * * * UPDATE FROM STEVE MACK TO DONALD NORWOOD AT 1556 EDT ON 6/8/2012 VIA E-MAIL * * * "A written report was received from the licensee dated March 23, 2012 describing the discovery of the damaged slide connector on the source assembly. "A routine compliance inspection was performed on May 22, 2012. "The cause of the damage to the slide connector on the source assembly was not determined. "The Arkansas Department of Health considers this event closed." Notified R4DO (Gepford) and FSME Events Resource by E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2012-03-07
47713 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-03-01 17:05 | 2012-03-01 18:41 | 2012-03-01 | BATTERY ROOM VENTILATION SYSTEM DEGRADED "While Units 1 and 2 were in Mode 1, operating at 100% power, an issue was identified with the doors for the safety related battery rooms and their normal position. Several doors to the battery rooms were found to be held open via electromagnetic door devices. These doors are an integral part of their battery room exhaust system. As designed, there is no uninterruptible power to the door mechanisms, all the doors are expected to close in the event of a Loss of Offsite Power. "The closure of the doors to the battery rooms, being an integral part of the exhaust system, would disrupt ventilation in the battery rooms and could allow hydrogen to increase to unacceptable levels during Loss of Offsite Power events. "Compensatory measures have been taken to secure the doors open to maintain the hydrogen purging function before required limits are reached. The battery room ventilation system remains functional supporting operability of the batteries. "Luminant Power determined this issue to be reportable as an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B)." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-03-01
47712 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-03-01 09:15 | 2012-03-01 12:12 | 2012-03-01 | EXTERNAL RADIATION LEVELS EXCEEDED PART 20 LIMITS DURING SHIPMENT "Evaluation of LTC [Lynchburg Technology Center] AmBe Shipment issues for 03/01/12 receipt. "The conditions for reporting under the requirements of 10 CFR 20 1906(d) have been met. QWI 14.1.10 Classification & Notification Criteria for Unusual Incidents Radiation Protection section - for shipments, bases reporting requirements on receipt of a shipment with radiation or contamination levels in excess of 10 CFR 20.1906(d). This requirement was exceeded and an NRC report is required. The truck cab sleeping area (normally occupied space) dose rate of 3.4 mRem/hr is greater than the allowable limit of 2.0 mRem/hr. The private carrier personnel state that they do not have dosimetry. "Immediate Actions Taken: Digital photographs have been taken, confirmatory surveys (with other instruments) were taken, additional spot surveys were taken, the shipper has been notified, and an evaluation of the regulations has been made." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2012-03-02
47711 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-01-31 | 2012-03-01 09:26 | 2012-03-01 | AGREEMENT STATE REPORT - POSSIBLE EXCEEDANCE OF ANNUAL DOSE LIMIT The following information was received from the State of Louisiana via facsimile: "[An individual's] badge received 2709 mRem for December 2011, which gave him a yearly exposure of 5609 mRem for 2011. [The individual had] performed radiography for the first fifteen days of December. [During] the second half of December he worked on paperwork before leaving the company. He had left his personal radiation monitoring equipment in the front compartment of the x-ray rig truck during the second half of December." The State of Louisiana will investigate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-03-06
47710 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-03-01 | 2012-03-01 05:51 | 2012-03-01 | MANUAL REACTOR PROTECTION SYSTEM ACTUATION DUE TO AUTOMATIC TURBINE RUNBACK "On March 1,2012, at approximately 0224 [EST], a manual Reactor Protection System (RPS) actuation was initiated due to 3 turbine bypass valves going open as a result of an automatic turbine runback signal. At the time of the event, the plant was in Mode 1 at 100% power. All control rods are inserted into the core and the plant is currently stable in Mode 3 (Hot Shutdown) with reactor pressure at approximately 930 psig. "No Emergency Core Cooling Systems were required or utilized to respond to the event and there were no other reportable actuations. Reactor coolant level is being maintained in its normal band by the feedwater system and decay heat is being removed by the condenser. The plant is in a normal electrical line-up with all three Emergency Diesel Generators operable and available if needed. The cause of the automatic turbine runback has not been determined and is being investigated. "During the transient, Reactor Water Cleanup System (RWCU) tripped. No automatic isolation signal was received. "At the time of the event, restoration of a Stator Water Cooling pressure gauge was being performed [following maintenance]. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-03-01
47709 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2012-02-29 12:22 | 2012-02-29 18:07 | 2012-02-29 | SECONDARY CONTAINMENT ISOLATION DAMPERS FAIL TO CLOSE DURING QUARTERLY SURVEILLANCE "On 2/29/2012 at 0905 [CST] during scheduled surveillance testing it was discovered that Secondary Containment isolation damper 1VAD017B3 would not fully isolate. 1VAD017B3 was declared inoperable per Technical Specification 3.6.4.2 Condition A and an 8 hour action statement to isolate the affected flowpath via a closed and deactivated damper was entered. While performing subsequent actions to isolate the companion isolation damper, 1VAD017A3, it was found on 2/29/2012 at 1222 [CST] that this damper also failed to fully isolate. This left both Secondary Containment isolation dampers in the same flowpath unable to isolate, and Technical Specification 3.6.4.2 Condition B was entered with a 4 hours action statement to isolate the affected flowpath. This condition is reported under 50.72(b)(3)(v)(C), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of the structures or systems that are needed to control the release of radioactive material. "Further actions to isolate the flowpath were successful and both 4 hour and 8 hour Technical Specification action statements were completed within the required time." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2012-02-29
47708 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-02-28 17:31 | 2012-02-28 19:03 | 2012-02-29 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER Byron Unit 1 declared an Unusual Event due to a loss of offsite power for greater than 15 minutes (EAL MU-1). The 1A and 1B emergency diesel generators auto-started and automatically restored power to ESF (Engineered Safety Feature) Busses 141 and 142. The 1A Auxiliary Feedwater pump auto-started due to an undervoltage signal to ESF bus 141. The 6.9 KV Busses (Non-ESF) and 4.16 KV Busses (Non-ESF) auto transferred to the Unit Auxiliary Transformers and Unit 1 remained online. The ESF reserve feed breakers are available and in the process of transferring ESF loads over to Unit 2 via the ESF cross-ties. This will allow shutdown of the 1A and 1B diesel-generators and allow alignment to standby status. Switchyard repairs are being initiated. The licensee notified the State of Illinois, Ogle County, Oregon and Byron municipalities and the NRC Resident Inspector. The licensee plans on issuing a news release. Unit 2 remained online and was unaffected throughout the event. Notified Nuclear SSA and NICC vie email. * * * UPDATE FROM CHRISTOPHER COTE TO CHARLES TEAL ON 2/29/12 AT 2222 EST * * * "Termination of Unusual Event. Repairs to switchyard components are complete. Offsite power has been restored to Unit One System Auxiliary Transformers. Unit One 4 KV ESF busses have been re-energized from Unit One System Auxiliary Transformers and are no longer cross tied to Unit Two System Auxiliary Transformers. This restores the normal electrical lineup to the ESF busses. The entry conditions for MU-1 are no longer met." The licensee has notified the NRC Resident Inspector, the State of Illinois, Ogle County, Oregon and Byron municipalities. Notified R3DO (Stone), NRR EO (Lee), IRD (Morris), and other FEDS (DHS SWO, DHS NICC, FEMA, and NuclearSSA via email). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2012-02-28
47707 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-02-28 15:44 | 2012-02-28 17:59 | 2012-02-28 | UNANALYZED CONDITION RELATED TO CERTAIN POSTULATED FIRE CONDITIONS "At 1544 CST on February 28. 2012, it was identified that under certain fire conditions, the ability to meet the performance criteria of the approved Fire Protection Program may be challenged. Specifically the cabling within the Dedicated Fire Zone may be affected under certain fire conditions resulting in fire induced spurious operation of valves RC-46 (pressurizer/reactor head vent), PR-33A (pressurizer head vent) and RC-45A (reactor head vent). The ability to maintain pressurizer level within the indicated range may be challenged due to these spurious valve openings during these postulated conditions. "Contingency actions per the Fire Protection Program to address the fire in the area of concern have been established (hourly fire watch). This condition is reported pursuant to 10CFR50.72 (b)(3)(ii)(B). "Similar conditions have been previously reported by the licensee in EN #44482 and EN #47686. The compensatory measures that had been put in place for those earlier conditions remain applicable to this current condition." The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-02-28
47706 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2012-02-24 | 2012-02-28 15:21 | 2012-02-28 | PART 21 REPORT - POTENTIAL MINIMUM WALL VIOLATION ON SEISMIC PLATE VALVE BODIES "While reviewing Valve Body drawing 16B2201, it was discovered that an area in the packing bore has the possibility to not meet the minimum wall requirements of ASME B16.34 for a Class 150 valve at the minimum material condition due to a potential stack up of tolerances. "Upon discovery of this possible failure to comply, an investigation was performed on all NPS 3-12 Type A11 Class 150 Seismic Plate Valve Bodies and it was determined that this issue was isolated to the NPS 8 Type A11 Class 150 Seismic Plate Valve Body per drawing 16B2201. "It is the opinion of Fisher that there is no inherent safety risk associated with this situation. Fisher will be working with the individual plants [Clinton Power Station and Watts Bar] in question to measure the actual dimensions of the bodies to determine if a problem exists and will take appropriate corrective action." Fisher Information Notice: FIN 2012-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2012-02-28
47705 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2012-02-27 14:30 | 2012-02-28 14:19 | 2012-02-28 | UNANALYZED PIPING CONFIGURATION DISCOVERED "During a GNF-A ongoing review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), facility walk-downs of the process gas piping were performed that identified a configuration that was different than previously analyzed. Based on a review of this as-found condition, it was discovered at 1430 EST February 27, 2012 that the system was different than analyzed in the ISA. "Production operations in the affected area have been suspended pending an administrative update of the ISA to reflect current conditions. Additional corrective actions and extent of condition are being evaluated. At no time did an unsafe condition exist. "While this discovery did not result in an unsafe condition, it is being reported pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours." The licensee notified the NC Division of Radiation Protection and New Hanover County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2012-02-28
47704 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2010-01-19 | 2012-02-28 13:09 | 2012-02-28 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK IN OPEN POSITION The following was received from the State of Tennessee via facsimile: "On January 19, 2010, during performance of routine shutter check, it was discovered that the shutter on an Ohmart Model SH-F2 source was stuck in the open position. In an attempt to open the shutter by hand, the shutter handle separated from the top of the housing. Two bolts attaching the handle were sheared off. The gauge was manufactured in 12/04 and is located on a column which is part of a polymer manufacturing process. The gauge contains 150 milliCuries of Cesium-137. Ohmart technicians were called to repair the shutter. No individuals were exposed to the excessive levels of radiation." Event Report ID No.: TN-10-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-03-02
47703 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2009-08-10 | 2012-02-28 13:09 | 2012-02-28 | AGREEMENT STATE REPORT - EFFLUENT CONCENTRATIONS EXCEEDED REGULATORY LIMITS The following was received from the State of Tennessee via facsimile: "A pharmacy technician noted that the exhaust fan connected to the I-131 glove box was not working. Maintenance was contacted and found a broken fan belt which was repaired the same day. Up to 35% of the air exhaust of the I-131 vapor was not available for dilution. On 8/28/09, it was noted the effluent concentration of I-131 was over the limit of state regulations. It was immediately reported to the Radiation Safety Officer. An investigation revealed a bolus of I-131 was released through the ventilation system. Minor release in the room but the continuous air concentration in the pharmacist's breathing zone remained under regulatory limits. Surveys of the room revealed three locations of fixed contamination which were covered with cardboard and allowed to decay to background. All staff bioassays were below detectable limits." Event Report ID No.: TN-09-110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-03-02
47702 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2010-10-19 16:30 | 2012-02-28 13:09 | 2012-02-28 | AGREEMENT STATE REPORT - SOURCE CARRIER ON OHMART GAUGE FAILED TO RETRACT The following was received from the State of Tennessee via facsimile: "On 10/19/10, it was discovered that the source carrier on Ohmart gauge, Model SHLM-C, could not retract from the well pipe back into the source holder. An Ohmart technician attempted to repair the gauge without success. A visual inspection confirmed that the process materials had leaked into the well pipe around the source carrier preventing retraction of the source. A remediation team was called to retrieve the source carrier. The gauge contained Cesium-137, two sealed sources of 63 milliCuries each." Event Report ID No.: TN-10-143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2012-03-02
47701 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2012-02-24 11:26 | 2012-02-27 15:38 | 2012-02-27 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following was received from the State of Kentucky via facsimile: " KY RHB [Kentucky Radiation Health Branch] was notified by telephone and email on 2/24/12 at 2:32 p.m. EST by the Radiation Safety Officer at East Kentucky Power Cooperative of a shutter on a Kay-Ray Model 7700D (S/N 17902) containing 10 mCi of Cs-137 being stuck in the closed position. The event occurred on 2/24/12 at 12:26 p.m. EST. The RSO is stationed in Winchester, KY and the incident occurred at the licensee's facility in Maysville, KY. The State has received an initial telephone notification and an initial written report from the licensee and will continue to keep NRC informed of the status of our investigation." KY Event Report ID No: KY 120001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2012-03-01
47700 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-02-27 10:30 | 2012-02-27 11:17 | 2012-02-27 | AGREEMENT STATE REPORT - LOST PO-210 SOURCE The following was received from the state of North Carolina Division of Radiation Control by facsimile: "On February 16, 2012, the Section [North Carolina Division of Radiation Control] received a letter from the RSO for Carolina Custom Finishing LLC, License Number: 076-1820-0G, [stating] that on February 13, 2012, [the licensee] could not find a Po-210 source, 10 mCi, Model P-2021, S/N A2HL674. [This source is contained in] a static eliminator used for painting customer parts. [The RSO] performed an inspection and area survey of the facility on February 22, 2012 and could not locate the above source." NC Incident Number: 12-25 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-03-01
47699 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-02-26 15:46 | 2012-02-26 20:15 | 2012-03-01 | LOSS OF PLANT ASSESSMENT CAPABILITIES DUE TO AN OUT OF SERVICE PLANT PROCESS COMPUTER "Calvert Cliffs will be performing planned maintenance to the U-1 Plant Process Computer to install isolation transformers. This maintenance window was expected to start at 2100 [EST] today, 2/26/2012, but the U-1 Plant Process Computer failed at 1546 this afternoon and it was decided to commence the planned maintenance window at that time versus spending resources to attempt recovery of the computer for just a short time period. The planned maintenance window is expected to be 54 hours long and end February 28, around 2300. This will impact the Unit 1 data dissemination to the Safety Parameter Display System (SPDS), TSC Computer. PI [Plant Trending Software] and ERDS will also be out of service for both Unit-1 and Unit-2. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. Control Room Emergency Response Organization personnel will use backup methods already captured in emergency response procedures to disseminate plant parameter data to the effected Emergency Response Facilities and NRC during the plant data network outage. MIDAS (Meteorological Data) will continue to be operational at the site. "Applicable Reporting Requirement: 10 CFR 50.72 (b) (3) (xiii); 8 Hour report." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1209 EST ON 03/01/12 FROM JAY GAINES TO S. SANDIN * * * "At 1000 [EST] this morning planned maintenance was completed to the Unit 1 plant process computer. All plant assessment capabilities have been restored." The licensee informed the NRC Resident Inspector. Notified R1DO (Ferdas). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-26
47698 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-16 | 2012-02-24 16:54 | 2012-02-24 | AGREEMENT STATE REPORT - MISADMINISTRATION OF A RADIOPHARMACEUTICAL The following information was received from the State of Texas via email: "On 2/22/12 the licensee notified the Agency [Texas Department of State Health Services] of a medical event that occurred on 2/16/12. The licensee reported that the wrong radiopharmaceutical had been administered to a patient. Tc-99m MAA was administered rather than the prescribed Tc-99m Pertechnitate. During the administration of the wrong drug, an estimated 1/3-1/2 of the dose infiltrated the skin causing an estimated 400 rad exposure subcutaneously. The referring physician and patient have been notified. No signs or symptoms have been observed in the patient as a result of the incident. The estimated exposure is being reevaluated by the licensee." Texas Incident: I-8937 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-03-01
47697 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-02-24 00:37 | 2012-02-24 07:42 | 2012-03-01 | VALID REACTOR PROTECTION SYSTEM ACTUATION DURING NEUTRON INSTRUMENT TESTING "On 2/24/2012 at 0037 EST, Unit 1 was in Mode 4 when an unplanned Reactor Protection System (RPS) actuation occurred. The trip occurred while operators were returning the Mode Switch to the 'Shutdown' position during restoration from Neutron Instrumentation testing. Jumpers had not been installed to bypass this actuation signal at the time the Mode Switch was operated, resulting in a valid signal of the RPS. "The RPS actuation is reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A). "The safety significance of this event was minimal. Plant equipment performed as expected. All control rods were inserted prior to the RPS actuation and remain inserted. "The RPS actuation was reset and the plant remains in Mode 4." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MARK TURKAL TO JOHN KNOKE AT 1316 EST ON 3/1/12 * * * "Based on a detailed review of NUREG-1022, Revision 2, 'Event Reporting Guidelines 10 CFR 50.72 and 50.73,' this event has been determined not to be reportable under 10 CFR 50.72(b)(3)(iv)(A). The RPS actuation was inadvertent and was caused by a human error (i.e., failure to install appropriate jumpers) that occurred during a surveillance test. This RPS actuation was not in response to actual plant conditions satisfying the requirements for initiation of the RPS. There was no plant condition present that either warranted a scram or would prompt manual operator action in anticipation of scram condition. Therefore, this RPS actuation is considered invalid and is not reportable per 10 CFR 50.72(b)(3)(iv)(A). "Investigation of this condition is documented in the corrective action program in Condition Report (CR) 519432. "The NRC Resident Inspector was notified of this retraction." Notified the R2DO (Mark Franke). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-02-24
47696 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-02-23 22:00 | 2012-02-24 04:24 | 2012-04-05 | LOSS OF 21 OUT OF 101 EMERGENCY SIRENS "Communications has been lost to 21 sirens out of 101. The loss of communications does not allow the activation of the sirens. Almost all of Harrison County and Pottawattamie County in Iowa are without communications to the sirens. There are compensatory measures in place to ensure notification by local law enforcement in case of an actual emergency to inform the public in these areas. "This is being reported per 10CFR50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, off site response capability, or communications capability'. "An attempt is being made to reboot the siren's communication system in order to restore the sirens. During the reboot, sirens in Washington County, Nebraska, will also lose communications and therefore will not be functional. Local Law Enforcement has been notified in Washington County to perform compensatory measures in case of an emergency." The NRC Resident Inspector has been informed. * * * UPDATE FROM DAVID SPARGO TO DONALD NORWOOD AT 0621 EST ON 2/24/2012 * * * "As of 0518 CST, communications has been reestablished and all sirens were returned to service." The licensee notified the NRC Resident inspector. Notified R4DO (Deese). * * * UPDATE FROM ERICK MATZKE TO HOWIE CROUCH AT 1602 EDT ON 04/05/12 * * * "Following an investigation of the siren failure, it was determined that all sirens were lost for a period of time from approximately 1809 CST February 23, 2012 until 0518 CST February 24, 2012. The control room was notified at 0215 CST February 24, 2012 and compensatory measures were established for all affected counties in Iowa and Nebraska. No new compensatory measures or actions are or were required." The licensee has notified the NRC Resident Inspector. Notified R4DO (Haire). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-24
47695 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-24 05:00 | 2012-02-23 14:28 | 2012-02-23 | PLANNED MAINTENANCE WILL RESULT IN THE TECHNICAL SUPPORT CENTER BEING UNAVAILABLE "The Technical Support Center will be unavailable for approximately 10 hours due to planned maintenance on motor control center SMXE." Maintenance is expected to begin at 0500 on February 24, 2012. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-23
47694 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-02-23 09:00 | 2012-02-23 12:52 | 2012-02-23 | OFFSITE NOTIFICATION DUE TO AN INTAKE STRUCTURE OIL SPILL "On February 23, 2012, at 0900 CST, an oil leak was identified from a gear box in the intake structure that had leaked into the circulating water cell. Prompt action was taken to stop the leak. Less than or equal to 1 pint of oil was spilled into the circulating water cell and, subsequently, to the Missouri River. The spill has been stopped and clean up of the oil sheen in the intake cell is proceeding. A visible oil sheen was noted on the Missouri River downstream of the station's intake structure near the station's outfall. The gear box has been drained to prevent any further leakage. Notifications will be made per Fort Calhoun Nuclear Station's National Pollutant Discharge Elimination System (NPDES) permit. Samples will be taken for off site analysis to determine the quantity of oil discharged. The State of Nebraska, Department of Environmental Quality and National Response Center will be notified. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi), 4 hour non-emergency notification due to a notification being made to a Government Agency (State of Nebraska, Department of Environmental Quality and National Response Center)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-23
47693 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2012-02-16 | 2012-02-23 11:08 | 2012-04-02 | PART 21 REPORT - ROSEMOUNT PRESSURE TRANSMITTERS WITH NONZERO BASED CALIBRATIONS The following information was received by facsimile: "During the course of qualification testing to replace certain diodes identified for obsolescence, RNII [Rosemount Nuclear Instruments, Inc.] has determined that Model 1154 Series H range code 4-8 pressure transmitters with a significantly elevated or suppressed 4 mA point may not meet the published steam pressure/temperature accuracy specification. "The out of tolerance condition observed during steam pressure/temperature qualification testing is not related to the replacement diode changes. It is an inherent performance characteristic related to large zero elevation or suppression. The steam pressure/temperature accuracy specification will be revised to account for nonzero based calibrations with a significantly elevated or suppressed 4 mA point. "This revised specification supersedes the published steam pressure/temperature accuracy specification for all Model 1154 Series H pressure transmitters affected by this notification. "RNII recommends that users review the application where 1154 Series H range code 4-8 pressure transmitters are used to determine if there are safety considerations related to the revised steam pressure/temperature specification." Rosemount Nuclear has provided instruments to the following list of domestic U.S. customers: Alabama Power; American Electric Power; Arizona Public Service/Pinnacle West; Bechtel Power; Constellation Energy; Dominion Nuclear Connecticut/Dominion Generation; Duke Energy; ECFS MCS; Edison Material Supply; Electro Mechanics; Entergy; Exelon Generation; Florida Power and Light; FPL Energy; Georgia Power; Northern States Power-Minnesota DBA XCEL Energy; Pacific Gas and Electric; Progress Energy Florida; Progress Energy Carolinas; PSEG Nuclear; South Carolina Electric and Gas; Southern California Edison; Southern Nuclear Operating Company; STP Nuclear Operating; Tennessee Valley Authority; TXU/Luminant; Westinghouse Electric. * * * UPDATE FROM DUYEN PHAM TO PETE SNYDER ON 4/2/12 AT 1224 EDT * * * The following information was received by facsimile: "This revision only affects Section 4.0 of the 23 February 2012 notification letter. The pressure values listed in Section 4.0 at 8 hours and 56 hours have been corrected. No other changes have been made." Notified R1DO(Caruso), R2DO(Lesser), R3DO(Dickson), R4DO(Haire) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2012-03-05
47692 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-01-31 | 2012-02-23 08:28 | 2012-02-23 | AGREEMENT STATE REPORT - CONTAMINATION LEVELS EXCEED ACTION LEVELS The following was received from the Commonwealth of Massachusetts via facsimile: "On Tuesday, 1/31/12, routine contamination surveys discovered approximately 0.5 nCi of Ir-192 outside of the restricted area on the first floor. The calculated dose for an 8-hour exposure to this RAM is 0.7 mrem. The contamination survey results prompted QSA to perform additional surveys to determine the source of contamination. Survey wipes yielded 10,000 to 30,000 dpm over large areas (approximately 2 feet x 2 feet) at different locations. "Upon investigation, QSA discovered that the exhaust fan on the Ir-192 source production hot cell had been turned 'off.' The exhaust fan was immediately turned back 'on.' About one week earlier, Ir-192 from a supplier was transferred into the hot cell. This operation requires the hot cell exhaust fan to be turned 'off' temporarily. QSA realized that the exhaust fan had not been turned back 'on.' "Radiation workers who performed hot cell production operations during the time the exhaust fan was 'off' were subjected to whole body counts performed at MIT. The whole body counts indicated workers ingested 12 to 20 nCi of Ir-192 and based on the MIT results, the RSO calculated the committed dose to be less than 2 mrem. "Since the contamination discovery, QSA has performed cleaning operations on the first and second floors, daily survey monitoring of the first and second floors, and radiation workers performing production operations using the Ir-192 hot cell have worn full protective clothing suits. QSA reports daily surveys results indicate contamination levels have steadily decreased." Docket No: 14-0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-02-28
47691 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-22 | 2012-02-23 08:21 | 2012-02-23 | AGREEMENT STATE REPORT - STUCK GAUGE SHUTTER The following information was received via facsimile: "On February 22, 2012, the State of Texas was notified by the licensee that the shutter on an Ohmart SH-F1A nuclear gauge containing 50 millicuries of cesium 137 was found stuck in the open position. The gauge shutter was being closed to reduce dose rates in an area where calibration of equipment was to be done. Open is the normal position for the gauge and the gauge does not create any additional exposure risk to any individual. The licensee is making arrangements with the manufacturer for repairs to the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-02-28
47690 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-02-22 23:19 | 2012-02-23 02:55 | 2012-02-23 | MANUAL REACTOR SCRAM DUE TO HIGH DELTA-P ACROSS CIRCULATING WATER PUMP TRAVELING SCREENS "At 2319 hours EST, a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 in anticipation of a loss of condenser vacuum. Shortly before the manual RPS actuation, Circulating Water Intake Pump (CWIP) 1B tripped due to high delta-pressure across the intake traveling screen. This caused the trip of the remaining pumps. Previously, at 1859 hours, balance of plant (BOP) bus Common C unexpectedly de-energized. This caused loss of power to the CWIP traveling screen motors which, in turn, lead to the high delta-pressure across the traveling screen(s). "All control rods inserted properly. As a result of the scram, reactor water level reached the Low Level 1 actuation set point and Primary Containment (i.e., Group 6) isolation occurred. All systems functioned as designed. The High Pressure Coolant Injection (HPCI) system is being used, as needed, for pressure control. The Reactor Core Isolation Cooling (RCIC) system is being used, as needed, for level control. No Safety/Relief Valves (SRVs) actuated as a result of the manual RPS actuation. "The manual RPS actuation is reportable in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). The actuation of the HPCI and RCIC systems and the Group 6 isolation are reportable in accordance with 10CFR50.72(b)(3)(iv)(A)." The unit is currently in Mode 3 with a cooldown in progress. The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes). * * * UPDATE FROM STEWART BYRD TO CHARLES TEAL AT 0741 EST ON 2/23/12 * * * "At 2319 hours EST, a loss of all Circulating Water Intake Pumps caused a lowering vacuum on Unit 1. As previously reported (i.e. Event Notification 47690), a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 at this time. In addition, a valid actuation of the RPS, High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC), and a Group 6 isolation was reported in accordance with 10CFR50.72(b)(3)(iv)(A). At 2342, Main Condenser vacuum was 15 in. Hg and lowering. All Main Steam Isolation Valves were slow closed in anticipation of Group 1 isolation at this time. This follow-up notification is being made to report the manual actuation of the Group 1 isolation valves in accordance with 10 CFR 50.72(b)(3)(iv)(A). The Group 1 isolation was discussed with the NRC during initial notification of EN 47690, and this follow-up is providing written notification of the MSIV closure." The NRC Resident Inspector has been notified. Notified R2DO (Ernstes). | 0 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-02-23
47689 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-23 01:22 | 2012-02-23 01:29 | 2012-02-23 | OFFSITE NOTIFICATION TO LAW ENFORCEMENT Offsite notification to law enforcement agencies was made by the licensee due to an individual making threats against personnel and security at the site. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-23
47688 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2012-02-22 18:45 | 2012-02-23 00:45 | 2012-02-24 | SUSPICIOUS PACKAGE DISCOVERED ON SITE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73 "At 1852 hours, Palo Verde Unit 1 was notified of a suspicious package located in the Owner Controlled Area outside the Protected Area. Maricopa County Sheriff's Office was contacted for assistance with a bomb disposal unit. Local media has become aware of this event and expressed interest by dispatching helicopters and television crews. "There are no safety systems impacted by the package and operations personnel are not hampered in their ability to operate safety related equipment. There is no release of radioactivity to the environment as a result of this package and it has not adversely affected the safe operation of the plant or health and safety of the public. All three Palo Verde units are being maintained stable at approximately 100% power. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DELBERT ELKINTON TO VINCE KLCO ON 2/24/12 AT 1619 EST * * * "The Maricopa County Sherriff's Office bomb disposal unit responded and inspected the package. The suspicious package contained a granular absorbent material, similar to that used to clean liquid spills. The event was terminated at 23:02 AZ MST [on 2/22/12]. The NRC Resident Inspector has been updated." Notified the R4DO (Deese). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-23
47687 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2012-02-22 20:14 | 2012-02-22 23:36 | 2012-02-23 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABILITY OF EMERGENCY CORE COOLING SYSTEMS "At 1859 hours EST, the Brunswick site experienced a loss of balance of plant (BOP) bus Common C. As a result, makeup pumps to the ECCS discharge line keepfill systems lost power. At 1905 on Unit 1, 'A' loop of the Core Spray (CS) system received a low discharge pressure alarm and was declared inoperable. At 1916 hours, 'B' loop of the Residual Heat Removal (RHR) system received a low discharge pressure alarm and was declared inoperable. With the loss of the second low pressure ECCS system, Condition J of Technical Specification 3.5.1, 'ECCS Operating,' was entered, which requires the Unit 1 to enter LCO 3.0.3 immediately. At 1931 hours, 'A' loop of RHR was declared inoperable due to low discharge pressure. Power reduction of Unit 1 was initiated at 2014 hours. "At 2055 hours on Unit 2, 'A' loop of the Residual Heat Removal (RHR) system received a low discharge pressure alarm and was declared inoperable. At 2128 hours, 'B' loop of the Core Spray (CS) system received a low discharge pressure alarm and was declared inoperable. With the loss of the second low pressure ECCS system, Condition J of Technical Specification 3.5.1, 'ECCS Operating,' was entered, which requires the Unit 2 to enter LCO 3.0.3 immediately. Power reduction of Unit 2 was initiated at 2219 hours. "This event reportability is in accordance with 10CRF50.72(b)(2)(i), Technical Specification Required Shutdown, due to inoperability of ECCS systems. "The initial safety significance of this event is minimal. Offsite power and the Emergency Diesel Generators are operable. The High Pressure Coolant Injection (HPCI) system remains operable on both Unit 1 and Unit 2. The Reactor Core Isolation Cooling (RCIC) system remains operable on Unit 1 and is being restored following maintenance on Unit 2. "Troubleshooting activities to determine the loss of the BOP Common C bus are in progress. Efforts are in progress to install temporary power to the keepfill makeup pumps." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM CURTIS DUNSMORE TO DONALD NORWOOD AT 0223 EST ON 2/23/2012 * * * "Unit 1 - At 2315 hours, temporary power was provided to the ECCS keepfill makeup pump and the ECCS systems were restored. LCO 3.0.3 was exited on Unit 1 at 0041 hours with restoration of the 'A' and 'B' loops of the RHR systems. The 'A' loop of the Core Spray system was restored at 0058 hours on 2/23/2012." During the shutdown, Unit 1 was manually scrammed due to high delta-pressure across the Circulating Water Pump traveling screens. See EN #47690 for details. "Unit 2 - At 2315 hours, temporary power was provided to the ECCS keepfill makeup pump and the ECCS systems were restored. LCO 3.0.3 was exited on Unit 2 at 2354 hours with restoration of 'B' loop of the RHR system. The 'A' loop of the Core Spray system was restored at 0039 hours. Unit 2 was at 96% of Rated Thermal Power when the shutdown was terminated." The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes). | 73 | 96 | 0 | 88 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-02-22
47686 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2012-02-22 13:07 | 2012-02-22 18:10 | 2012-02-22 | UNANALYZED CONDITION RELATED TO CERTAIN POSTULATED FIRE CONDITIONS "At 1307 CST on February 22, 2012, it was identified that under certain fire conditions, the ability to meet the performance criteria of the approved fire protection program may be challenged. Specifically the cabling for Train A Pressurizer Power Operated Relief valve and Train B Pressurizer Power Operated Relief valve alternate circuits may be affected under certain fire conditions affecting the relay room. The ability to maintain pressurizer level within the indicated range may be challenged due to a spurious opening of a pressurizer power operated relief valve during these postulated conditions. "Compensatory actions to address the fire in the area of concern are in place. This condition is reported pursuant to 10CFR50.72(b)(3)(ii)(B). "A similar condition was previously reported [by the licensee] in EN #44482. The compensatory measures that had been put in place for that earlier condition remain applicable to this current condition." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-02-22
47685 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2012-02-17 | 2012-02-22 17:21 | 2012-02-22 | MISSING UPPER MOUNTING PADS ON SUBCOVER ASSEMBLIES "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 12/20/11 upon notification of an issue with four subcover assemblies at Perry Nuclear Power Plant. It was reported that Perry was performing a maintenance activity whereby they were replacing four cylinder head subcover assemblies on their Enterprise diesel engine. During installation, it was noted that qty. 2 of 11 bolt holes were missing an upper mounting pad. This was visually apparent once the customer attempted to install the bolts, which have a 6" length. The two areas missing the upper landing pad did not have an area for the underside of the bolt head to rest upon. "The evaluation was concluded on 2/17/12 and it determined that this issue is a reportable defect as defined by 10CFR21. "DISCUSSION: "Lack of the mounting pads alone will not result in a failure, however if a customer attempts to install the subcover without recognizing the missing material, there is the possibility that two of the eleven hold down bolts will provide no clamping function. This may result in loosening of the subcover mounting which could allow the cover to separate from the cylinder head. "The subcover is a device that is fastened to the top of the cylinder head and provides support for the rocker arms and rocker shafts and encloses the valve stem area. There is one subcover per cylinder head and thus for a model DSRV-16-4 Enterprise engine there are 16 subcovers. Failure of a subcover would impact the ability of either of the corresponding rocker arms to provide the mechanical force to actuate the intake and exhaust valves. Without valve actuation, that particular power assembly would be unable to generate power which would reduce the output of the emergency diesel generator (EDG). Failure of the EDG to produce its nameplate rated power could prevent the safe shutdown of the nuclear power plant during an emergency situation. "AFFECTED USERS AND SHIPMENTS: "ESI has supplied subcovers with the incorrect mounting pad to the following customers [in USA]: "Perry; Qty: 4; Date: October 2011. "Note: The subcovers returned by Perry are the subject of this evaluation. "CORRECTIVE ACTIONS: "Customers may elect to justify use of a shorter bolt to facilitate installation of in-stock covers. Otherwise it is ESI's recommendation that customers return the subcovers for replacement. "The root cause analysis determined that the cause of this issue was that the pattern for the casting is missing the portions that would ultimately form this upper mounting pad. In addition, the machining drawing was unclear in showing these locations. As a result, ESI's inspections did not specifically check for these locations and the non-conforming subcovers were shipped to the customer. "The pattern is now being corrected to ensure the presence of the upper mounting pads. Also, ESI's dedication report is being revised to add specific checks to inspect for the presence of these pads. This will be completed prior to any future shipments of this item." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2012-02-22
47684 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-02-22 13:45 | 2012-02-22 13:58 | 2012-02-22 | ELECTRICAL DISTRIBUTION SYSTEM MAINTENANCE TO IMPACT EMERGENCY RESPONSE FACILITIES "Calvert Cliffs will be performing planned U-1 Refueling Outage maintenance to a portion of the sites 1E Electrical Distribution System. This maintenance window is expected to be 36 hours long and will start at 1400 today. This will impact the dissemination of plant data to the TSC, EOF, and OSC. ERDS will also be out of service for both Unit-1 and Unit-2. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. "Control Room Emergency Response Organization personnel will use backup methods already captured in emergency response procedures to disseminate plant parameter data to the effected Emergency Response Facilities and NRC during the plant data network outage. MIDAS (Meteorological Data) will continue to be operational at the site." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-22
47683 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-02-21 23:42 | 2012-02-22 01:55 | 2012-02-22 | MANUAL REACTOR TRIP DUE TO FEEDWATER HEATER HI HI ALARM "During a normal shutdown in preparation for refueling outage 2R27, with Unit 2 at approximately 11.42% power, Unit 2 was manually tripped on 2/21/2012 at 2342 CST. The manual reactor trip was in response to a 21/22/23 Feedwater Heater Hi Hi alarm and was directed by the alarm response. Procedure 2E-0, 'Reactor Trip or Safety Injection,' was completed at 2345 CST. No Safety Injection was required. 2ES-0.1, 'Reactor Trip Recovery,' is in progress. Offsite power remains on all safeguards buses for both units. Unit 2 decay heat is via forced circulation and condenser steam dump with main feedwater providing flow to 21/22 steam generators. Auxiliary Feedwater start was not required and Unit 2 AFW remains in its safeguards alignment. No emergency event was declared as a result of this trip. Unit 1 remains at 100% power in Mode 1. Reportable actuations are: Unit 2 reactor protection (scram). The NRC Resident Inspector was notified. State [State of Minnesota] / local [Goodhue county] / Press release will be made. Other government agencies will not be notified. Nothing unusual / not understood. Unit 2 will continue to mode 5." | 0 | 0 | 0 | 0 | 11 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-02-22
47682 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-02-21 13:45 | 2012-02-21 13:57 | 2012-02-21 | TRITIUM IDENTIFIED ONSITE ABOVE THE VOLUNTARY REPORTING THRESHOLD "On February 17, 2012, North Anna Power Station (NAPS) was notified by its vendor laboratory that a water sample, taken from an onsite ground water sample point, was confirmed to contain tritium above the voluntary reporting threshold of 20,000 picocuries per liter(pCi/L). The water sample, measuring 53,300 pCi/L, was obtained as a part of ongoing activities to determine the source of tritium previously reported to the state and NRC on October 29, 2010 (Event Notification - 46377). Current hydrological studies have determined the ground water in the area migrates to the station power block which is in the opposite direction from the lake. The ground water at the power block is collected in building subsurface drains and transported to a clarifier for processing. Clarifier discharge is accounted for as a monitored liquid effluent release pathway under the radiological effluent control program in accordance with the station's Offsite Dose Calculation Manual. As such, there is no increase to the projected annual dose to a member of the public. There are also no sources of drinking water in this area. Sampling of eight (8) ground water sample points outside the station protected area show no detectable levels of tritium confirming there is no migration offsite. "The NRC Resident Inspector has been notified. A 30 day written report will be submitted to the NRC in accordance with NEI 07-07, Industry Ground Water Protection Initiative - Final Guidance Document." The licensee will inform both state and local agencies. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-21
47681 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2012-02-21 00:55 | 2012-02-21 11:38 | 2012-05-03 | DATA PROCESSING NETWORK FAILURE IMPACTED EMERGENCY RESPONSE DATA SYSTEM "At 0055 PST on 2/21/12, it was discovered that portions of the data processing network (eDNA) had failed. This failure resulted in the Emergency Response Data System (ERDS) entering a mode of operation that caused an interruption of the ability of the ERDS transmission capabilities. At approximately 0213 PST on 2/21/12, actions were taken and all transmission capabilities were restored. The total outage time was determined to be 78 minutes. During the period that ERDS was not available, backup communications were available, "This is determined to be a partial, but major loss of emergency assessment capability, and is reportable under 10 CFR 50,72(b)(3)(xiii) as 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portions of control room indication, Emergency Notification System, or offsite notification system)'." "The cause of the data processing network (eDNA) and ERDS failure is under investigation." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM RICHARD GARCIA TO PETE SNYDER AT 1950 EDT ON 5/3/12 * * * "This event was revisited for a formal reportability assessment and concluded to be not reportable since the capability to transmit data of interest to the NRC was available via the ENS at all times during the ERDS outage. In addition the ERDS system is noted as a supplement to the ENS in 10 CFR 50, Appendix B. Given the limited duration of the event and availability of ENS for data transmission, no major loss of emergency assessment capability occurred." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-21
47680 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-11-30 | 2012-02-21 09:13 | 2012-02-21 | AGREEMENT STATE REPORT - LOSS OF ONE STATIC ELIMINATOR The following information was received from the State of Iowa via email: "Agri-Industrial Plastics Company, a general license registrant, reported the loss of one static eliminator, NRD model P-2021-8201, serial number A2HL930, containing 10 millicuries of Polonium-210. The device was used to eliminate static on plastic particles from the trimming of plastic parts. The device was last used on November 30, 2011. The registrant has spent several hours looking for the device. The registrant will be eliminating all remaining static eliminators and returning them to the manufacturer. "Source/Radioactive Material: Sealed source ionizing Manufacturer: NRD, INC. Model Number: P-2021-8201 Serial Number: A2HL930 Radionuclide: PO-210, .010 Ci, 0.37 GBq "Device Name: Static elimination device Manufacturer: NRD, INC. Model Number: P-2021-8201 Serial Number: A2HL930" The state indicated the cause of the loss was due to inattention to detail. Iowa Event Number IA120002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2012-02-24
47679 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2012-02-19 19:04 | 2012-02-19 22:00 | 2012-02-19 | MANUAL REACTOR SCRAM DURING SHUTDOWN DUE TO LOWERING REACTOR VESSEL WATER LEVEL (RVWL) "On 2/19/2012 at 1904 hrs [CST] the reactor was manually scrammed from approximately 23% core thermal power due to lowering reactor water level. All control rods fully inserted and all systems actuated and operated as designed. The Reactor Core Isolation Cooling System was manually initiated to assist in level control. No safety relief valves actuated. Reactor level and pressure are currently being controlled within normal bands. Group 2 and 3 RHR Isolation signals were received, however no valve movement occurred since the affected valves are normally closed. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(iv)(A) for the manual start of the core isolation cooling system." The lowest Reactor Vessel Water Level [RVWL] observed was -38 inches WR [Wide Range]. RVWL was restored by placing the "A" Reactor Feed Pump [RFP] in service. The "B" RFP which had been operating was secured for troubleshooting. The Unit was in the process of shutting down for its scheduled Refueling Outage #18. The NRC Resident Inspector was in the control room at the time of the transient. | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-02-19
47678 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-02-19 01:01 | 2012-02-19 03:36 | 2012-02-19 | TRANSPORTING OFF-SITE OF AN INJURED AND POTENTIALLY CONTAMINATED INDIVIDUAL At 0025 EST, on 02/19/12, a Williams contractor (carpenter) slipped in a puddle of water and fell backwards striking his head and back on the floor of the Turbine building. At 0030 EST, the Shift Manager requested on-site First Responders to report to the scene of the accident. The individual was assessed by Williams safety personnel and SNC First Responders and then packaged for long spine immobilization. At 0101 EST the Shift manager requested Appling County 911 to transport the injured and potentially contaminated individual to Appling County Hospital for evaluation. At 0307 EST, the injured individual was surveyed and found not to be contaminated. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE AT 1704 EST ON 02/19/12 FROM DANIEL KOMM TO S. SANDIN * * * The licensee is retracting this report based on the following: "This notification of retraction is being made based on additional information provided by the Health Physics personnel that accompanied the individual to the hospital. Surveys were taken of the individual and clothing and there was no contamination present. Based on the unknown status of individual and clothing upon leaving the site, a notification was initially made as potentially contaminated. Based on the final information obtained at the hospital of no contamination present, the transport of this injured individual to the local hospital does not meet the reporting requirements of 10CFR50.72(b)(3)(xii) and is being retracted. The injured individual was assessed by medical staff and was released back to work without restrictions." The licensee informed the NRC Resident Inspector. Notified R2DO (Desai). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2012-02-19
47677 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2012-02-18 08:36 | 2012-02-18 16:25 | 2012-02-19 | LOSS OF SPDS AND ERDS DUE TO HARD DRIVE FAILURE "At approximately 0836 hours [EST] on Feb. 18, 2012, the Unit 1 Safety Parameter Display System (SPDS) became non-functional, and therefore was not available in the Control Room or in the emergency response facilities. Efforts are underway to restore the system. The loss of SPDS and ERDS is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). Troubleshooting efforts continue to restore the SPDS. The station remains capable of performing dose assessment using manual inputs per site procedures. The Control Room also continues to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessments. "The NRC Senior Resident Inspector has been notified." * * * UPDATE FROM DANIEL KOMM TO JOE O'HARA AT 0751 ON 2/19/12 * * * "As of 0715 EST on 2/19/12, the Hatch Unit 1 SPDS and ERDS systems have been returned to functional status and are providing plant information. The ERDS system is capable of transmitting data to the NRC if required during an event." The NRC Resident Inspector has been notified. Notified R2DO(Desai) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-18
47676 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-17 | 2012-02-17 16:21 | 2012-02-24 | AGREEMENT STATE REPORT INVOLVING POTENTIAL RADIOGRAPHER OVEREXPOSURE The following information was received from the State of Texas via email: "On February 17, 2011, the Agency [State of Texas] was notified by the licensee of an overexposure event involving one of their radiographers. The radiographer was working in a shooting bay at the licensee's facility using a QSA D880 radiography camera serial number D7293 containing a 37 curie iridium 192 source. The radiographer entered the shooting bay to setup for their next shoot. They stated that they carried their dose rate meter with them but did not pay attention to the reading. The radiographer completed the setup and left the shooting bay. The radiographer attempted to crank the source out, but discovered that the source was already cranked fully out. The radiographer cranked the source back to the fully shielded position and notified their Radiation Safety Officer (RSO) of the event. The RSO questioned the radiographer and found that the radiographer had spent approximately 3 minutes within 10 inches of the source, and about 3 minutes at 3 feet from the source during the setup. Initial calculations by the licensee indicated that the radiographer may have received as much as 20 rem TEDE from the event. The RSO stated that the radiographer did not have to relocate the source to perform the shot so they do not believe there is any extremity dose involved. The RSO also stated that the electrical breaker that supplied power to the shooting bay had been opened therefore the alarm did not function. The RSO stated that they were going to review security video to determine who opened the breaker. The radiographer has been removed from all work involving exposure to radiation and their personal monitoring device will be sent to the licensee's processor. The Agency provided contact information for the Radiation Emergency Assistance Center/Training Site to the RSO. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-8934 * * * UPDATE FROM ART TUCKER (VIA EMAIL) TO HOWIE CROUCH @ 1727 EST ON 2/24/12 * * * "On February 24, 2012, the licensee reported that after two reenactments of the event, the licensee now believes that the total exposure time to the radiographer to be 2 minutes and 30 seconds. The licensee was also able to use the radiographer's cell phone records as the radiographer was talking on their phone while setting up the shot. The distance for the radiographers TEDE dose was determined to be 12 inches. The licensee now estimates that the TEDE dose for the radiographer was 8.1 rem. "The radiographer has provided three blood samples for evaluation. All three samples were determined to be normal. The radiographer's doctor is consulting with [name redacted] REAC/TS. Additional blood samples are scheduled in the future. "The licensee determined that the power breaker to the alarming area radiation monitor was opened by a coworker who believed the breaker only supplied power to a ventilation fan. The operation of the alarm had been verified at the beginning of the start of that shift." Notified R4DO (Deese) and FSME EO (O'Sullivan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-02-22
47675 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-18 | 2012-02-17 14:11 | 2012-02-17 | AGREEMENT STATE REPORT INVOLVING SHUTTER TEST FAILURES ON FIXED GAUGES The following information was received from the State of Pennsylvania via fax: "Notifications: On Wednesday February 15, 2012, the licensee left a voice message to the Central Office and followed with a phone conversation on February 16th regarding an event that took place on January 18, 2012. Additional information was then sent to Central Office via email on Friday, February 17, 2012. This event is reportable within 24-hours under 10CFR30.50(b)(2). "Event Description: Shutter test failures occurred on 3 fixed gauge devices at the Sunoco Philadelphia Refinery. Air actuators are used as the primary testing means to close the shutters. All three actuators failed to close the shutters on the devices and the instrument technicians were unable to manually close the shutters. The instrument technician foreman was unaware of any reporting requirements to the State and did not communicate this event to the Radiation Safety Officer (RSO) until February 14, 2012. "The 3 devices are identified as: Manufacturer: Ohmart Vega Model: SH-F1 Serial #: OVO125; OVO129; OVO131 Isotope: Cs-137 Activity: 10 mCi (each) "CAUSE OF THE EVENT: Air actuator malfunction "ACTIONS: The manufacturer has been contacted and the parts have been ordered to repair the shutter mechanisms. The RSO reported that the failures of the shutter mechanism do not pose any additional threat to employee safety, and surveys in the area indicate readings of <0.5 mR/hr at 1 foot from the source. The Department plans to do a reactive inspection. "Media attention: None at this time "Event Report ID No.: PA120008" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-02-22
47674 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2012-02-16 | 2012-02-17 14:08 | 2012-02-17 | AGREEMENT STATE REPORT INVOLVING A FAILED LEAK TEST OF AN ECD SOURCE The following information was received from the State of Colorado via fax: "On February 16, 2012 Test America at 4955 Yarrow Street in Arvada, Colorado (CO License # 486-03), notified the Colorado Department of Public Health and Environment that one of their Ni-63 electron capture detectors [ECD] failed a leak test. The leak test results for Device HPU0946 exceeded the 0.005 microCurie level. The test wipe measured at 0.0062 microCurie. "The ECD detector was immediately withdrawn from service and the instrument in which the ECD was located was decontaminated by cleaning with Radiac Wash solution. A direct beta survey was then performed which showed no residual contamination present on the instrument or ECD. ECD No. HPU0946 was sent to the manufacturer for repair." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-02-22
47673 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-17 13:05 | 2012-02-17 14:04 | 2012-02-17 | OFFSITE NOTIFICATION OF WASTE WATER POND TOXICITY LEVELS EXCEEDING LIMITS "On 02/17/12, McGuire Environmental Management notified the North Carolina Department of Environment and Natural Resources located in Mooresville, NC of a failed toxicity test on our waste water discharge point 002 (WC Pond). This test is required quarterly by our NPDES (wastewater) Permit. "Discharge was stopped yesterday (02/16/12) afternoon and we are currently pulling toxicity tests on the WC Pond and Initial Holdup Pond to determine if we still have toxicity. No WC Pond release will occur until toxicity results are known to be within acceptable limits." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-17
47672 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-02-16 11:00 | 2012-02-17 10:20 | 2012-02-17 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON A METAL THICKNESS GAUGE The following report was received via e-mail: "On February 16, 2012, during leak testing by a consultant vendor a radioactive materials gauge shutter was discovered to be stuck open. No radiation exposure to personnel occurred. "The device is identified as: Manufacturer: LFE Model: SS-3A Serial #: 02311 Isotope: Am-241 Activity: 37 GBq (1 Ci) "The gauge manufacturer was notified and repairs are scheduled to be conducted today. "Event Report ID No.: PA120007" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-02-22
47671 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-02-15 | 2012-02-16 18:03 | 2012-02-16 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISURE DENSITY GAUGE The following information was received from the State of California via email: "On 02/16/12, the RSO at Testing Engineers (TE) contacted the RHB [Radiological Health Branch] reception desk to report a stolen gauge. She reported that an employee had his truck stolen which also contained his nuclear gauge. The gauge a CPN MC1, S/N MD 20206438 containing 10 mCi of Cs-137 and 50 mCi of Am-241 was stolen yesterday (02/15/12) between 1:00 to 4:15 pm [PST] in a parking lot near the employee's residence . . . [in] Fremont, CA. The gauge was stored inside of its transportation case and placed in the back of the truck with the bed cover locked in place. The transport case was secured with a cable attached to the bed of the truck. The gauge user found the truck stolen around 4:15 pm [PST]. The incident was reported to the Fremont police at that time. The gauge user failed to notify the RSO of the stolen gauge until the following day (02/16/12) [in the] morning. "On 02/16/12, The TE [Testing Engineers, Inc.] RSO also notified this incident to Operations Emergency Center (report # 120902) and the NRC. "5010 Number (Date Notified): 021612" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-02-21
47670 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2012-02-16 13:42 | 2012-02-16 15:03 | 2012-02-16 | LOSS OF SPDS GREATER THAN EIGHT (8) HOURS DUE TO HARD DRIVE FAILURE "At approximately 0542 hours [EST], the Safety Parameter Display System (SPDS) became non-functional, and therefore was not available in the Control Room or in the emergency response facilities. Efforts are underway to restore the system, but as of 1342 hours [EST] these efforts have not been successful. The loss of SPDS for more than 8 hours is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). Troubleshooting efforts continue to restore the SPDS. The Emergency Response Data System (ERDS) remains functional, and the station remains capable of performing dose assessment using manual inputs per site procedures. The Control Room also continues to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessments." "The NRC Senior Resident Inspector has been notified, and the State of Ohio Emergency Management Agency will be notified." * * * UPDATE AT 2315 EST ON 02/16/12 FROM TOM COBBLEDICK TO S. SANDIN * * * As of 2100 EST on 02/16/12 the SPDS has been restored to service and is functioning properly. The licensee will inform the NRC Resident Inspector. Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-16
47669 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-02-16 | 2012-02-16 11:55 | 2012-02-16 | AGREEMENT STATE REPORT - GAS EXPLOSION OF X-RAY INSPECTION TRAILER - STORED SOURCE UNAFFECTED The following report is an edited version of information was provided by the North Carolina Radiation Protection Section via e-mail: "On February 16, 2012 the agency [NC Radiation Protection Section] was notified of a propane tank explosion near Gastonia, NC by the corporate RSO of JANX [NDT/NDE]. This morning when workers at the job site started a generator, an explosion [occurred and] damaged an x-ray trailer at the site. The source of the explosion seems to be a leaking valve on a propane tank. The explosion 'blew off' a wall [of the trailer] and resulted in some burning. On board this trailer was a 1 Ci Ir-192 stopping source contained in a SPEC check model housing. The corporate RSO indicated that the trailer had three compartments and, from what he understood, the back-up x-ray unit onboard the trailer was damaged (Panasonic XIT) [but] the compartment in which the [Ir-192] source was stored was not damaged during the explosion. The housing of the source itself did not show any damage and all radiation levels were normal. The 1 Ci source was moved to a secured Industrial Radiography truck containing a SPEC 150 camera with 110 Ci of Ir-192 that was also on site but not damaged during the explosion. This truck has increased controls on it and was not damaged. "Two employees have been taken to the emergency room for injuries and the local RSO is on his way to the incident (~10:30am). A NC Rad Mat Inspector was in the area and he will go and verify the report of the corporate RSO. "The corporate RSO that will be expected [to provide] a written report within 30 days and to leak test the source to ensure that there was no damage. [The NC State x-ray staff] has been notified about the industrial radiography unit [and] they have since contacted the licensee. Since they were working under reciprocity of an NRC license, [NC will also] notify NRC Region I agreement state officer, Monica Oreindi. "There are no radiation concerns to public health and safety at this time. The inspector was sent just for verification of the report. "The North Carolina License Number of JANX is 085-1117-2 and physical location address is 1073 Kentland Drive in King, NC 27021. The licensee had issued a reciprocity notification using their NRC license NRC: 21-16560-01 (Reciprocal License NO. 122-0361-R) for their work at the location of the explosion. The notification listed 1441 Delta Drive, Gastonia, NC as the location for work. "Local media is on site." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-02-21
47668 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-02-16 07:08 | 2012-02-16 09:00 | 2012-02-16 | INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2012-02-24
47667 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-02-14 | 2012-02-16 08:01 | 2012-02-16 | AGREEMENT STATE REPORT - X-RAY FLUORESCENCE ANALYZER STUCK OPEN SHUTTER The following report was received via e-mail: "On February 14, 2012, the operator of the handheld unit notified the Radiation Safety Officer (RSO) that he just got a 'shutter not available' message on the unit. The RSO was at a different plant and he instructed the operator to turn off the unit, remove the battery pack, place the unit in the case, and secure the unit. Upon examination on February 15, 2012, the same message was displayed when the battery was installed. The RSO performed a survey indicating 40 microR/hr at a distance of 1ft. The employee was wearing extremity dosimetry at the time of the event which has been sent for evaluation. More details will follow when available. "The device is identified as: Manufacturer: Thermo Niton Model: XLp 818 [The XLp is an x-ray fluorescence (XRF) analyzer.] Serial #: 5917 Isotope: Am-241 Activity: 30 mCi "A local service provider has been contacted to try to close the shutter and package the device so it can be returned to the manufacturer. The RSO sent out the employee's dosimetry to be analyzed. Licensee has been made aware of the 30-day follow-up report requirement." PA Event Report No.: PA120006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-02-21
47666 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-11-02 | 2012-02-15 15:39 | 2012-02-15 | AGREEMENT STATE REPORT - LOSS OF 13 Ni-63 SOURCES Groundwater Analytical Company, Massachusetts radioactive materials licensee G0046, underwent bankruptcy proceedings. Their assets were subsequently seized in a bank action and auctioned off by The Branford Group. Among the items auctioned were 13 Ni-63 sources associated with gas chromatograph devices. This auction took place on 11/2/2011. The Massachusetts Radiation Control Program (Agency) discovered this event on 2/15/2012 and has opened an investigation to find the missing radioactive sources. The auction house which handled the transfer of the gas chromatographs has indicated that they have records of the individuals who purchased the items and will be providing that information to the Agency by the end of the week. The Agency continues the investigation into this matter and this item remains open. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-02-20
47665 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-02-15 12:44 | 2012-02-15 15:33 | 2012-02-15 | OFFSITE NOTIFICATION OF SEWAGE SYSTEM RELEASE "At 12:44 on 2/15/2012, the Virginia Department of Environmental Quality was notified of a sewage system release that had the potential to reach state waters. On 2/14/2012, it was identified that water was flowing from a manhole cover near the North Anna training building. Further review identified the training building sewage lift station had lost power and that the water line in the manhole discharges to the lift station. It was estimated that approximately 120-200 gallons of untreated water reached the ground around the manhole before power was restored to the lift station. Upon further investigation, the station could not confirm whether untreated water reached Lake Anna." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-15
47664 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2012-02-15 08:25 | 2012-02-15 12:25 | 2012-02-15 | OFFSITE NOTIFICATION DUE TO INADVERTENT MANUAL SIREN ACTIVATION "At 0825 CDT on 2/15/2012, the Monticello Nuclear Power Generating Plant (MNGP) received a report from the Sherburne County Sheriff Dispatcher that there had been an inadvertent manual initiation of Emergency Preparedness sirens in the county while performing siren testing. All plant conditions/parameters are normal. A total of 48 emergency sirens were on for approximately one minute before being secured. All sirens are currently functional. "Sherburne County and the site NRC Resident Inspector have been notified." The licensee also notified the Wright County offices. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-15
47663 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-02-14 12:40 | 2012-02-14 12:55 | 2012-02-14 | LOSS OF EMERGENCY RESPONSE FACILITY INFORMATION SYSTEM DUE TO PLANNED MODIFICATION "At 1240 EST, on February 14, 2012, power was removed to a major portion of the Emergency Response Facility Information System (ERFIS) to perform a planned modification on Power Panel - 8. This work will install a new breaker in PP-8 requiring that the panel be de-energized for the maintenance. The expected duration of ERFIS inoperability is approximately 6 hours. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above-described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An additional message will be provided when the ERFIS is restored. It should also be noted that during the period of ERFIS inoperability, it is likely that the system could be restored within one hour to support Emergency Response Facility activation. This report is provided to conservatively cover the possibility that restoration within one hour may not be able to be accomplished if facility activation were to occur. The NRC Resident Inspector has been notified." * * * UPDATE FROM KEN BOYD TO DONALD NORWOOD AT 1516 EST ON 12/14/2012 * * * "At 1240 EST, on February 14, 2012, the Emergency Response Facility Information System (ERFIS) computer system became inoperable. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). Actions were completed to restore the ERFIS computer system to an operable status at 1458 EST on February 14, 2012. Alternate methods, as described in plant procedures, were available for the above-described functions during the time that the ERFIS computer system was inoperable. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still have been made, if required, during the time that the ERFIS Computer system was inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability." The licensee notified the NRC Resident Inspector. Notified R2DO(Desai). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-14
47662 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2012-02-14 11:15 | 2012-02-14 11:55 | 2012-02-14 | STOLEN TROXLER MOISTURE DENSITY GAUGE "The S.C. Department of Health and Environmental Control [SCDHEC] was notified on Tuesday, February 14, 2012, at 1115 [EST], that a Troxler Model 3411B gauge, s/n 9247, containing 8 mCi of Cs-137 and 40 mCi of Am-241:Be, was stolen from the truck bed of the vehicle driven by [an employee] while parked at his home overnight. [The employee] noticed that the gauge was missing at approximately 0700 [EST]. [The employee] called [the SCDHEC] to report the theft of the material. He stated that the Charleston County Sheriff's Department had been notified and was handling the incident. [The SCDHEC notified] the S.C. Fusion Center of the incident." "The event is open pending the licensee's investigation and report to [the SCDHEC]. Updates will be made through the NMED system." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2012-02-17
47661 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2012-02-13 | 2012-02-13 16:44 | 2012-02-13 | AGREEMENT STATE REPORT - CRUSHED TROXLER GAUGE The following information was received via facsimile: A dump truck ran over a Model 3440 Troxler portable gauge on the shoulder of the NJ Garden State Parkway at mile marker 54. The Troxler portable gauge was a model 3440 containing 8 mCi Cs-137 and 40 mCi Am-241. * * * UPDATE ON 2/15/12 AT 11:45 FROM JAMES McCULLOUGH TO KARL DIEDERICH VIA E-MAIL * * * "NJDEP RMP [New Jersey Department of Environmental Protection Radioactive Materials Program] staff responded to investigate the incident and observe the licensee's actions to recover the damaged device. Staff performed radiation area surveys and wipe tests to assess the situation. The licensee hired a consulting physicist who was observed (at about 9PM) while the device was recovered, shielded, and prepared for transport back to the licensee's office storage location." Notified R1DO (Powell) and FSME EO (Giantelli). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-02-16
47660 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-12 08:34 | 2012-02-12 09:26 | 2012-02-12 | UNUSUAL EVENT DUE TO ELECTRICAL FAULT IN 161 KV SWITCHYARD "At 0756 [EST] on 2/12/12, an electrical event occurred in the 161 kV switchyard that resulted in bus differential relay operating, and opening all PCBs [Protective Circuit Breakers] within 161 kV bus 2-2. Shortly after, a call was received from site security regarding an explosion in the switchyard. "At 0820, a report was received that visible damage was present on an insulator between a PCB and a Motor Operated Disconnect (MOD) in the 161 kV switchyard, which is where the fault occurred. Follow up reports indicated an oil leak from a current transformer. Two other PCBs were identified to have visible damage. After the event, while opening MODS for PCBs that tripped open, the 'A' phase for one MOD did not open. "No safety related equipment required to establish or maintain safe shutdown was affected. All the Diesel Generators remain in operable standby conditions. "Unit 1 remained steady at 100% with no transients. "Unit 2 had a 2B Condenser Circ Water pump trip off. Crew responded to the pump trip and Unit 2 remains at 100%. "One offsite power source is inoperable and second offsite power source has been verified operable. Grid status is Yellow." There were no personnel injuries reported due to the fault and resulting explosion. The loss of the offsite power source resulted in the licensee entering a 72-hr. LCO. The licensee is investigating both the cause of loss of offsite power and the circulating water pump trip. The licensee has notified the State of Tennessee and the NRC Resident Inspector. * * * UPDATE FROM KEVIN WILKES TO HOWIE CROUCH AT 1056 EST ON 2/12/12 * * * At 1019 EST, the licensee terminated their Notification of Unusual Event. The basis for termination was that the fault was cleared and the conditions for EAL entry no longer exists. The licensee has made state and local notifications and has notified the NRC Resident Inspector. Notified R2DO (Calle), IRD (Kozal), NRR (Evans), DHS (Beach), FEMA (Fuller), and NICC (Berger) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-02-12
47659 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-09 18:00 | 2012-02-11 10:32 | 2012-02-15 | AGREEMENT STATE REPORT - INDUSTRIAL GAUGE STUCK SHUTTER The following information was received by email: "On February 10, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee that the shutter on an Ohmart model SH-LG 2 nuclear gauge containing 8.5 curies of Cesium-137 was found to be stuck in the open position. Open is the normal position for the shutter and the failure does not pose any additional exposure risk. The licensee is trying to lubricate the operating arm in an effort to free the shutter. The licensee has contacted the manufacturer for assistance. Additional information will be provided in accordance with SA-300." Texas Incident: I-8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-02-15
47658 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2012-02-10 | 2012-02-10 18:54 | 2012-02-10 | UNANALYZED CONDITION - GUIDANCE NOT ADEQUATE TO MITIGATE A DESIGN BASIS FLOOD "During a review of the station's procedures for responding to external flooding conditions, it was determined that the guidance is not adequate to mitigate a design basis flood event (1014 feet mean sea level [msl]). "Compensatory actions have been identified and are being implemented. Additional corrective actions are being evaluated. "The plant is currently in Mode 5, Cold Shutdown, with a river level of 986 feet 2 inches msl with no predictions for river level to pose a threat to safety related components." NRC inspectors identified procedural inadequacies relating to the mitigation of flooding. The licensee is addressing the procedural inadequacies. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-02-10
47657 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2012-02-10 01:34 | 2012-02-10 07:31 | 2012-02-10 | MAINTENANCE ACTIVITIES CAUSE AN INADVERTENT EMERGENCY DIESEL GENERATOR START "On February 10, 2012, with Unit 1 in Mode 5, while performing scheduled maintenance, a technician inadvertently made contact with a component that caused an undervoltage condition on an essential bus, resulting in the automatic start and loading of the 1B Emergency Diesel Generator (EDG). Prior to the event the 1B EDG was inoperable and not required by Technical Specifications; however, the 1B EDG was available. All equipment responded as expected. Currently maintaining the plant in Mode 5. Decay heat removal is being supplied by the 1A Shutdown Cooling train and was never interrupted. There was no impact on the Shutdown Safety Assessment. "Unit 2 was unaffected and remains in Mode 1 at 100% power. "This event is reportable pursuant to 10CFR 50.72(b)(3)(iv(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2012-02-10
47656 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2012-02-09 17:55 | 2012-02-09 22:21 | 2012-02-09 | MAIN STEAM LINE PRESSURE TRANSMITTERS FOUND INOPERABLE "A condition was discovered on February 9, 2012 that could have prevented fulfillment of the safety function to shutdown the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. "During maintenance performed on the main steam line pressure transmitters on both trains, the one-time use only EEQ seals were not replaced rendering the transmitters inoperable. These transmitters initiate safety injection and main steam isolation functions in the event of a main steam line break. Since all transmitters were inoperable this condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(A) and (D)." The condition existed for about a week. "Subsequently the required number of transmitters have been repaired and are operable. "The NRC Senior Resident Inspector was notified and was present in the control room during the repair activity." The licensee also notified the State of Connecticut. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2012-02-09
47655 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2012-02-09 17:00 | 2012-02-09 20:37 | 2012-02-09 | POTENTIAL DEGRADATION OF TECHNICAL SUPPORT CENTER HABITABILITY "The dose calculation of record documents is that the assumed inleakage to the technical support center (TSC) is 60 cubic feet per minute (CFM), The calculation does not provide a documented validation of why the 60 CFM value is conservative and acceptable. Engineering judgment supports the likely validity of the 60 CFM value. However, if the inleakage value is not valid by a sufficient margin, the TSC would not meet the habitability design basis requirements. This report is submitted based upon a potential loss of emergency assessment capability, offsite response capability, or off site communications capability in accordance º 50.72(b)(3)(xiii). "Existing procedures require monitoring habitability of the TSC and taking action in the event radiological conditions preclude occupancy. The on-duty TSC Site Emergency Coordinator, TSC Radiological Control Director, and Emergency Operations Facility Emergency Response Manager have been informed of the condition and the protocol for utilization of alternate facilities. A walkthrough of the process will be held for others holding those positions in a timely manner. "The Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-09
47654 | -1 | WATERFORD | 3 |  |  | [3] CE | 2012-02-09 | 2012-02-09 17:07 | 2012-02-17 | ENTRY OF UNAUTHORIZED INDIVIDUAL A person entered an area of the plant he was not allowed access to. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 2/17/12 AT 1302 FROM HARDIN TO HUFFMAN * * * The licensee is retracting this event based on the results of its investigation. The unauthorized access was determined to be inadvertent and without malevolent intent. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. R4DO(Miller) notified. 73.71 Group was e-mailed a copy of this retraction. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-02-09
47653 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2012-02-08 16:30 | 2012-02-09 14:01 | 2012-02-09 | CONTAMINATED INDIVIDUAL RECEIVES MEDICAL ATTENTION ONSITE "On February 8, 2012, at 1630 [CDT] Honeywell employee was admitted to the plant's Dispensary for treatment of a thermal burn to the neck from a steam line. The plant's nurse treated this individual at the Dispensary. Health Physics staff performed whole body survey after treatment and discovered that employee's boots contamination exceeded 8000 dpm/100cm2. The employee was not transported off site." The source of the contamination was uranium and uranium ore concentrate. Contaminated areas of the plant were surveyed for remediation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2012-02-09
47652 | 0 | WATERFORD | 3 |  |  | [3] CE | 2012-02-08 10:47 | 2012-02-09 09:37 | 2012-02-09 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during random testing. The employee's access to the plant has been terminated and his badge deactivated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2012-02-09
47651 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2012-02-08 13:35 | 2012-02-08 19:31 | 2012-02-08 | SCRAM FUNCTIONALITY MAY BE DEGRADED IN A APPENDIX R FIRE "During BFNP NFPA 805 transition review, it was determined in the vent of an Appendix-R fire, the Reactor Protection System (RPS) function could be rendered not functional. The current Appendix R Safe Shutdown Analysis states: "The safe shutdown function of the Reactor Protection System (RPS) is to initiate reactor scram through actuation of the control rod drives. The RPS includes the RPS motor-generator power supplies and associated control and indicating devices, sensors, relays, bypass circuitry, and switches that initiate rapid insertion of control rods (scram) to shutdown the reactor. The RPS utilizes a fail-safe design so that device failures or a loss of power will result in control rod insertion. The scram function will remain available despite any fire-induced spurious signals that may be generated due to the effects of a postulated fire in any fire area. This system is expected to perform its function automatically, however credit is taken only for manual scram. No additional analysis is needed to ensure the availability of reactor scram in the even of a fire. "Due to lack of physical separation with 120 volt AC lighting circuitry, the RPS system potentially could remain energized due to a postulated hot short circuit during a fire which could potentially prevent the control rods from inserting. Therefore, the fail-safe design of the RPS system would not be maintained. Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the BFNP Fire Protection Report. "This event is reportable as an 8-hour notification to the NRC in accordance with 10CFR50.73(a)(2)(ii)(B). "The NRC Resident Inspector has been notified of this event. "This event was entered into the licensee's Corrective Action Program as PER 503304." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-02-08
47650 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2012-01-31 | 2012-02-08 15:51 | 2012-02-08 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The following was received from the State of Oklahoma via email: "On January 31, 2012, Oklahoma Department of Environmental Quality (ODEQ) received email notification from America Multi-Cinema, Inc. (AMC) that they had lost one (1) tritium (H-3) radioluminescent exit sign. The amount of H-3 is unknown. AMC has filed a report for the Oklahoma City Police Department. The case number is 12-001181. According to AMC, the missing exit sign was discovered before a site survey had been performed, so AMC could not provide the manufacturer or serial number of the stolen unit. At this time, no further information is available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2012-02-14
47649 | 0 | AMERICAN ELECTRIC POWER |  |  |  |  | 2012-02-07 | 2012-02-08 15:55 | 2012-02-08 | BROKEN SHUTTER CABLE ON FIXED PROCESS GAUGE While closing a the shutter on a Thermo Fisher Model 5197 gauge containing 100 milliCuries of Cs-137, the operating cable broke. There were no personnel exposures. The gauge shutter is currently shut. The licensee is contacting the manufacturer to arrange for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-02-08
47648 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2012-02-02 | 2012-02-08 16:00 | 2012-06-08 | AGREEMENT STATE REPORT - Y-90 DOSAGE TO UNINTENDED AREAS The following was received from the State of Minnesota via email: "On February 3, 2012, Minnesota Department of Health Radioactive Materials unit received notice that a licensee had a medical event during a Y-90 SIRS spheres procedure. After infusion of radioactive Y-90, in the form of SIRS spheres for treatment of the liver, it was discovered, by follow-up radionuclide scanning, that some of the material was not in the liver as intended. Material appeared in vessels involving the spleen and digestive track instead. The amount has not been determined at this time, but it is possible that this may cause unintended, permanent, functional damage. The interventional radiologist involved with the treatment has ensured us that the patient will be notified along with the referring physician today. It is likely that some form of medical intervention will be taken. "On February 6, 2012, the Radioactive Material supervisor and inspector met with the licensee to discuss the medical event. The Y-90 SIRS spheres procedure went accordingly to plan; it was discovered on the follow-up SPECT imaging that an estimated 10%-15% of the material was in the spleen, gastric fundus, and duodenum. The patient and ordering physician had been notified. The intended area for the material was the liver with an activity of 50 GBq. The three unattended areas that were discovered with material were estimated to receive a dose of 0. The Medical Physicist gave us the best preliminary dose estimates based on CT images obtained the day after the procedure at which the stomach and duodenum were different in shape. Early dose estimates for each region (spleen, gastric fundus, and duodenum) estimates approximately 30 Gy for each area. "The Minnesota Department of Health Radioactive Materials unit will continue communication and obtain the final estimation for dose estimates." * * * UPDATE FROM TERESA PURRINGTON TO VINCE KLCO AT 1055 EST ON 2/14/2012 * * * The following information was received by email: "Abbott Northwestern has submitted final best estimates pertaining to the medical event of Y-90 SIRS Spheres that occurred on Thursday, February 2, 2012. The final administered activity after accounting for loss in the delivery system was 1.53 GBq, original activity was 1.55 GBq. Estimates of radioactivity, organ volumes and radiation dose were derived by evaluation of SPECT CT images. The final best estimates are determined as follows: "Organ / tissue Fraction of activity Volume (cc) Average dose (Gy) Liver 0.839 1209 53 Fundus of stomach 0.058 101 44 Spleen 0.093 200 35 Portion of duodenum 0.010 41 35 "These estimates have a relatively high uncertainty (at least 20%) and local concentrations and doses may be significantly higher. Maximum concentrations per pixel in the SPECT images were as much as 50% higher than the average concentration." Notified the R3DO (Passehl) and FSME EO (McIntosh). * * * UPDATE FROM TERESA PURRINGTON TO DONALD NORWOOD at 1141 EDT on 6/8/2012 * * * Event title edited to better characterize the event. Notified R3DO (Passehl) and FSME_Events Resource both via E-mail. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2012-02-14
47647 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-01-24 | 2012-02-08 13:45 | 2012-02-08 | AGREEMENT STATE REPORT - CONTAMINATED VARIAN DETECTOR The following was received from the State of California via email: "On January 24, 2012, RHB was informed by the owner of National Analytical Instruments [...] that he had purchased a Varian UV-VIS detector from Golndustry Dovebid back in 06/11/2008 and he subsequently learned this device was contaminated with C-14. "The purchase invoice ID is # 2169450, and the following equipment was indicated on the invoice: Varian ProStar 320, s/n 1550, Lot # 143568. The equipment has a Pfizer's asset number 16468. According to [the owner], the equipment came from Pfizer in Ann Arbor, Michigan, and that this laboratory has been owned by the University of Michigan since 2007. "On January 24, 2012, the RHB inspector confirmed contamination of the Varian UV-VIS detector. A Thermo Scientific, RadEye B20-ER, s/n 0242 GM, survey meter was used to check for contamination, and contamination was observed with the maximum reading of 25 CPS. On January 26, 2012, in the presence of RHB inspector, the Pfizer San Francisco RSO took surveys, and also confirmed contamination of the Varian UV-VIS detector. The Pfizer RSO also took possession of the contaminated equipment." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-02-13
47646 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2012-02-07 19:00 | 2012-02-08 12:18 | 2012-02-08 | AGREEMENT STATE REPORT - PATIENT RECEIVED DOSE LESS THAN INTENDED The following was received from the state of New Jersey via email: "A patient was treated with a Varian VariSourceTM HDR unit on February 7, 2012. The prescription dose was 200 cGy per fraction for 8 fractions. The first two fractions were delivered to the patient with a fractional dose of 25 cGy instead of the prescribed fractional dose of 200 cGy before the discovery of the event around 7 p.m. on February 7, 2012. The initial treatment plan was designed for a single fractional dose of 200 cGy and was approved on screen by the physician. The plan was later modified to 8 fractions with a fractional dose of 200 cGy before the delivery of the first fraction. This modification was however done incorrectly and the isodose line of 200 cGy, instead of 1600 cGy, was planned to cover the target volume. [Isodose means a radiation dose of equal intensity to more than one body area.] Two fractions of treatment (out of a planned 8) were delivered on 2/7/2012 before discovery of the event, resulting in a dose of 25 cGy per fraction (instead of 200 cGy) prescribed to the target volume." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-02-14
47645 | 0 | CHASE ENVIRONMENTAL GROUP |  |  |  |  | 2012-02-08 08:30 | 2012-02-08 10:13 | 2012-02-09 | SHUTTER ON THICKNESS GAUGE STUCK OPEN "Chase Environmental Group employees discovered an abnormally high radiation reading on contact with a sealed source gauge at approximately 8:30 a.m. EST. Contact readings were 150 mR/hr with the window of the gauge. The shutter indicator light on the C-Frame indicated that the shutter was closed. Cycling the shutter controls did not change the radiation measurements on contact with the window, however the indicator lights cycled from closed to open to closed again. "The manufacturer was notified and the manufacturer advised that air pressure should be disconnected to cause the shutter to close. After removing air, no changes to radiation levels were found. Nucor employees are arranging for the manufacturer to come on site to repair the gauge as soon as possible. "Because the shutter will not close, Nucor has locked out air and electrical power to the device to prevent inadvertent operation, and cordoned off the area to prevent anyone from accessing the gauge. Measurements at one foot from the window of the gauge were less than 2 mR/hr. The area is posted as a Radiation Area. Chase Environmental Group employees made all radiation measurements and were wearing dosimetry. No overexposures are expected. "The gauge involved is at the Nucor Steel company in Crawfordsville, IN. The Nucor NRC License number is 13-25975-01 and the RSO is Dave Sulc. The gauge is a DMC Am-5A, serial# BS21645. The source is Am-241, activity of 1 Ci, and serial# 1979LQ. This is a C-frame thickness gauge to measure steel in a pickling process in the Cold Mill facility of Nucor Steel. The previous leak test of the gauge was August of 2011. "Chase Environmental Group (licensed in the state of TN, R-01108-E19) is a contractor to Nucor for consulting, training, and leak testing." * * * UPDATE FROM CHRIS ECHTERLING TO JOE O'HARA AT 1608 EST ON 02/09/12 * * * The following was received via e-mail. "On February 8th, 2012, a sealed source gauge abnormal event was reported, event# 47645. Today, a representative from Advanced Gauging Technologies, LLC arrived at Nucor Steel Crawfordsville and was able to repair the gauge successfully. The shutter and indicator lights are now operating appropriately." Notified R3DO(Giessner) and FSME EO(Michalak). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2012-02-08
47644 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-06 17:19 | 2012-02-06 20:40 | 2012-02-06 | MANUAL RPS ACTUATION DUE TO TURBINE TRIP "Unit 2 had been connected to the grid at 1431 CST today following a recent forced outage and was in the process of power ascension in accordance with plant procedures. At approximately 25% reactor power (approximately 240 MWe), the operators were transferring main feed flow to the steam generator lower nozzle through the feedwater isolation valves, (i.e. 2FW009A, B, C, D). "2FW009C was the first valve to be opened due to previously experienced problems with this valve being stuck in the seat. No issues were experienced during the opening of 2FW009C. Upon opening of 2FW009C, the 2C steam generator level began to rise as expected. The operators throttled back feedwater flow to control steam generator level. However, the 2C steam generator level increased to the High-High level setpoint of 80.8% (p-14). Since the reactor was below 30% (P-8), no automatic reactor trip signal was generated. However, the turbine automatically tripped, a feedwater isolation signal was initiated, and 2C Main Feedwater pump trip occurred as designed. With no main feedwater flow available, the operators manually tripped the reactor and entry into procedure 2BEP 0, Reactor Trip or Safety Injection Unit 2 was entered. The operators then manually started the 2A and 2B Auxiliary Feedwater pumps to supply water to the steam generators prior to reaching the Low-Low steam generator level setpoint of 36.3%. "Transition from 2BEP 0 to 2BEP ES-0.1, Reactor Trip Response, was completed and the emergency procedures were exited. Unit 2 is being maintained in a stable condition in Mode 3." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2012-02-06
47643 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2012-02-06 | 2012-02-06 17:56 | 2013-02-03 | PART 21 - DEFECTIVE PLUG INSULATORS The following report was received via fax: "This letter is issued to provide initial notification of a potential defect in Plug Insulators (P/N: GB-1A-1) supplied as part of GRAYBOOT 'A' (GB-1A) Connector Kits. There are two affected lots of Plug Insulators (Lot #: BA59961 and BA67711). The potential defect is an out of tolerance dimension that will possibly affect the sealing ability of the Plug Insulator to wire interface. "The affected Customers and their associated Purchase Orders are listed below. All Customers will be notified today. Ralph a. Hiller; PO: NUC7505, Item 1, 15 Kits (P/N: GB-1A [16-18], Lot BA59961) supplied 19JAN2012. Bruce Power, PO: 00168187, Item 1, 20 Kits (P/N: GB-1A [12-14], Lot BA59961) supplied 13DEC2011. Dominion - Surry, PO: 45886290, Item 1, 22 Kits (P/N: GB-S-1A, Lot BA59961) supplied 19DEC2011. Dominion - Surry, PO: 45897749, Item 2, 30 Kits (P/N: GB-S-1A, Lot BA67711) supplied 01FEB2012. Ringhals AB, PO: 621728-053, Item 10, 30 Kits (P/N: GB-1A [16-18], Lot BA59961) supplied 19DEC2011. Ringhals, PO: 620625-066, Item 10, 300 parts (P/N: GB-1A-1, Lots BA59961/BA67711) supplied 30JAN2012. Ringhals, PO: 620996-066, Item 50, 1 Kit (P/N: GB-1A [16-18], Lot BA59961) supplied 29NOV2011. OKG, PO: 4113847, Item 4, 86 parts (P/N: GB-1A-1, Lot BA59961) supplied 30NOV2011. "It is requested that all affected parts be returned for replacement to QualTech NP; 330 West Park Loop; Huntsville, AL 35806. Customers can contact Cindy Tidwell at (256) 895-7250 ext. 229 for freight collect shipping instructions. "Additional details, corrective actions and root causes will be provided once complete. If you require additional information or would like to discuss this further please do not hesitate in contacting:" Tony Gill Quality Assurance Supervisor QualTech NP, Huntsville A business unit of Curtiss-Wright Flow Control Company Office 256-722-8500 ext. 1 Cell 256-426-4558 tgill@curtisswright.com * * * UPDATE FROM TONY GILL TO JOHN SHOEMAKER ON 02/03/2013 AT 17:55 EST* * * "This letter provides for the formal closeout of notification 10CFR21-2012-01. The initial notification was made on February 06, 2012. All corrective actions and corrective actions to prevent recurrence have been completed and all affected parts listed on the initial notification have been returned by our customers and replacement items supplied. All affected parts in inventory at our facility were removed and discarded. "The initial corrective action was to retrieve all affected parts both in our inventory and those provided to our customers as safety-related. As stated above, all affected parts have been returned and/or retrieved from inventory and discarded. "There were four primary root causes identified that allowed the defective items to be manufactured and accepted. The causes are listed below: 1. Mold sections/mold inserts for the two different size plug insulators (regular and oversized) are used in the same mold assembly. Not all required mold parts were removed when changing from the manufacture of oversized to regular boots causing the defective parts to be manufactured. 2. Vendor did not verify the affected dimension prior to shipment of the parts to QualTech. 3. The inspection drawing in the QualTech dedication guidelines was not clear as to the required dimension to be verified. 4. The QualTech Inspector incorrectly interpreted the inspection drawing and verified the wrong dimension thus accepting the defective parts. "The corrective actions to prevent recurrence have been completed and include the following: 1. An additional mold was purchased from our supplier to prevent mixing of inserts. Now there are no mold parts utilized in the manufacture of different sized plug insulators (regular vs. oversized). This issue was one of the primary causes of the defect. 2. Notification was made to our supplier and corrective actions implemented at their facility. 3. The QualTech inspection drawing in the affected dedication guidelines was revised to better define the required dimension. 4. The error was discussed with the QualTech Inspector to ensure understanding of the critical dimension. "Based on the above information and corrective actions this part 21 file is considered closed. If you would like to discuss this information further please contact the undersigned at 256-722-8500 ext. 131 (office), 256-426-4558 (cell), or tgill@curtisswright.com. Tony Gill Quality Assurance Manager QualTech NP, Huntsville Operations a business unit of Curtiss-Wright Flow Control Company Notified R2DO (Haig) and the Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21 |  |  |  | 0 | 2012-02-06
47642 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-01-11 | 2012-02-06 14:54 | 2012-02-08 | AGREEMENT STATE REPORT - PACKAGE RECEIVED CONTAINING LEAKING SOURCES The following was received from the State of California via email: "On Jan. 26, 2012, [the] NRC sent an e-mail to RHB [Radiation Health Branch] management stating that General Nucleonics, Inc. had 22 boxes containing Inflight Blade Inspection (IBIS) devices containing Sr-90 sources (500 microcuries each, Generally Licensed devices) returned to them from the Dept. of the Navy. When the packages were opened, it was discovered that 11 devices were damaged and 5 had removable contamination above 0.005 microcuries. The source manufacturer is QSA Global (formerly AEA Tech), model was Amersham/ now GNI PN # 12205-5 and were installed into GNI PN 12210-1 IBIS Pressure Indicators. Leak testing was performed on 1/11/2012. Source # 3482 / IBIS # 1798, leak test results: 0.13 microcuries of contamination; Source # 1673/ IBIS # 095, leak test results: 0.38 microcuries of contamination; Source # 235 / IBIS # 288, leak test results: 0.30 microcuries of contamination; Source # 2926/ IBIS # 371, leak test results: 0.15 microcuries of contamination; Source # 2843/ IBIS # 378, leak test results: 0.22 microcuries of contamination. "All indicators were placed into sealed bags and placed into a glove box. The source receiving and testing areas were checked for contamination and none was found. Each IBIS was installed on a U.S.N. CH-53 Sikorsky helicopter for 'warning' of incipient blade failure. Damage had occurred to the top of the indicators, source capsules had been damaged and the source retaining rods were bent from their normal vertical positions. General Nucleonics will be eventually disposing of these devices through a radioactive waste broker." CA 5010 #: 012612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-02-09
47641 | 0 | DEPARTMENT OF VETERAN AFFAIRS |  |  |  |  | 2012-02-06 12:15 | 2012-02-06 15:13 | 2012-02-06 | PACKAGE SURFACE CONTAMINATION IN EXCESS OF REPORTING LIMITS "Per 10 CFR 20.1906(d), [The Department of Veterans Affairs is] reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received today (February 6, 2012) at around 12:15 PM ET by VA Medical Center, West Palm Beach, Florida. The VA Medical Center, West Palm Beach, Florida, holds permit number 09-25328-01 under the master materials license. A wipe test performed on the external surface of the package indicated a removable contamination level of 962 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2. "The package contained Technetium-99m labeled radiopharmaceuticals and was shipped from Cardinal Health in Jupiter, Florida. "The vendor/shipper serves as the final delivery carrier. "The VA facility Radiation Safety Officer immediately notified the vendor about the contaminated package at about 12:30 PM ET. As corrective action, the package was set aside in a restricted area at the VA Medical Center to provide time for decay. The permittee does not plan to use the dosage." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2012-02-06
47640 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-02-06 13:00 | 2012-02-06 14:32 | 2012-02-06 | OFFSITE NOTIFICATION DUE TO UNPERMITTED RELEASE "The Minnesota Pollution Control Agency (MPCA) was notified of a release of 27 gallons from the condensate system. The release contained the following chemicals: 1) 11.2 ppm of methoxy propylamine (MPA); 2) 8.1ppm of ammonia; 3) 11.2 ppb of hydrazine; 4) 1.50 E-5 microCi/mL (15,000 pCi/L) of tritium. "The condensate was released from parts Warehouse #1 heating steam system overflow vent. Condensate return pumps failed to operate causing 27 gallons of condensate to backup and overflow onto the ground. A catch basin has been installed and the steam inlet valve has been closed preventing the addition of steam into the system. "The NRC Resident Inspector has been informed. " The licensee also notified the Prairie Island Dakota Indian Community. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-06
47639 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-02-05 17:15 | 2012-02-05 20:59 | 2012-02-05 | OFFSITE NOTIFICATION TO NY PUBLIC SERVICE COMMISSION "This report is being made pursuant to 10CFR50.72(b)(2)(xi). At 1715 [EST], a site security officer was discovered unresponsive on the north end of the Unit 2 turbine hall by a fellow officer. The cause of the individual's unresponsiveness is unknown but appears to be personal health related. The individual was unresponsive to revival attempts and transported by ambulance to the local Hudson Valley Hospital. The individual was pronounced dead at the hospital. "The individual's security contingent equipment was immediately secured on discovery. This event had no impact on the status of IPEC plant operation and all applicable security procedures / requirements were followed upon discovery." The licensee notified New York State Public Service Commission and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-05
47638 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-05-11 | 2012-02-05 18:06 | 2012-02-05 | UNANALYZED CONDITIONS DISCOVERED DURING NFPA 805 TRANSITION REVIEW During the licensee's NFPA 805 transition review process, several unanalyzed conditions were discovered but determined to be not reportable at that time. During subsequent review, the licensee determined these conditions did meet reporting requirements. The following unanalyzed conditions affect all three Browns Ferry units: "On 5/11/2010, it was determined that in the event of an Appendix-R fire, multiple hot shorts affecting reactor pressure instrument loops, Safety Relief Valves (SRV) overpressure logic or ADS [Automatic Depressurization System] logic could cause 2 to 13 SRVs to spuriously open, for certain fire areas. The current Appendix R safe shutdown analysis only assumes 2 SRVs spuriously open. The issue has significant safety impact due to the potential for one fire scenario to result in spurious opening of multiple SRVs, loss of low pressure inventory makeup, and loss of the condensate system for inventory makeup, which would challenge adequate core cooling during performance of Safe Shutdown Instructions. "On 8/18/2010, it was determined that in the event of an Appendix-R fire, fire induced circuit damage can potentially result in the inability to manually close the following Motor Operated Valves: Residual Heat Removal Heat Exchanger outlet valves and Emergency Equipment Cooling Water pump cross-tie valves. The failure to be able to manually close these valves could result in the loss of decay heat removal function and loss of credited diesel generators to power required safe shutdown equipment. These issues have significant safety impact since the capability to manually close these valves is necessary to ensure adequate core cooling during performance of BFN Safe Shutdown Instructions. "On 9/30/2010, it was determined that in the event of an Appendix-R fire, fire induced multiple hot shorts could cause both Inboard and Outboard RHR test return valves, and Drywell Spray and Suppression Pool Spray valves to spuriously open due to damage to the valve control circuit cables. This could result in draining of the Pressure Suppression Chamber Head Tank and the affected low pressure Emergency Core Cooling System loop piping (RHR or CS). Consequently, the discharge pipe in the credited Residual Heat Removal (RHR) loop may not be filled and vented when the Safe Shutdown Instructions (SSIs) call for the RHR pump to be started. The resulting water hammer could result in piping system damage resulting in loss of core cooling and decay heat removal functions and loss of suppression pool inventory. Additionally, single spurious actuation of Core Spray (CS) test return valves due to fire damage to their control circuits could have the same results. These issues have significant safety impact since they would challenge the ability to provide adequate core cooling during performance of Safe Shutdown Instructions. On 8/22/2011, two unanalyzed conditions were discovered: First, "it was determined that, in the event of an Appendix-R fire in certain areas, fault propagation due to loss of the breaker control circuit in conjunction with power cable damage could result in de-energization of the associated 4kV Shutdown Board. This potential exists since some 4kV Shutdown Board load breakers are not equipped with separate fuses for trip circuits extending beyond the board. This condition could result in a loss power to credited safe shutdown equipment that would challenge the ability to provide adequate core cooling during performance of BFN Safe Shut down Instructions. Second, "it was determined that in the event of an Appendix-R fire in certain areas, Multiple Spurious Operations (MSO) could result in the Main Steam Isolation Valves failing to close, or to re-open. This potentially results in a challenge to control inventory loss during performance of Safe Shut down Instructions. The following unanalyzed condition only affects Unit 2: "On 8/18/2010, it was determined that in the event of an Appendix-R fire, fire induced circuit damage can potentially result in the inability to manually close certain Main Steam Drain Line Motor Operated Valves. The current Appendix R safe shutdown analysis credits manual closure of these valves. Failure to close these valves results in loss of suppression pool inventory which could challenge adequate core cooling during performance of BFN Safe Shutdown Instructions." Compensatory actions in the form of fire watches to mitigate all these conditions are in place in accordance with the BFNP Fire Protection Report. The licensee will make the required 60-day written reports in accordance with 10CFR50.73(a)(2)(ii)(B). These events were entered into the licensee's Corrective Action Program. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-02-05
47637 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-03 | 2012-02-03 22:10 | 2012-02-03 | VOLUNTARY REPORT - DESIGN VULNERABILITY IN 4.16kV BUS UNDER-VOLTAGE SCHEME "On January 30, 2012, a design vulnerability was discovered at Byron and Braidwood stations in the Engineered Safety Feature 4.16kV bus under-voltage protection scheme for Braidwood Station Units 1 and 2. Specifically a voltage unbalance created by an open circuit of either the A or C phase from the offsite grid to the System Auxiliary Transformers (SAT) is not designed to actuate the protective relays on the 4.16kV safety bus that provides isolation from the offsite grid and the automatic start and loading of the emergency onsite diesel generators. "Two under-voltage relays are provided on each 4.16kV safety bus, which are combined in a two out of two logic to generate a loss of power signal. The relays are sensing voltage between two phases (i.e., A&B and B&C). An open circuit condition on the C phase or the A phase would not satisfy the two out of two logic. This condition results in both 4.16kV safety buses remaining energized with a bus undervoltage situation and results in equipment protective devices actuating from over-current conditions. "This configuration is a non-conforming condition in that the design of the under-voltage relays and logic was intended to identify degraded grid conditions, not loss of a single phase. With an open circuit on the A or C phase from the grid to the SATs, during normal operations, operators have to diagnose the condition and manually isolate safety buses from offsite power which would automatically start and load the emergency diesel generators. During a design basis event concurrent with an open circuit on A or C phase from the grid to the SATs, analysis performed to date indicates that starting of the ECCS loads would have caused the bus voltage to decrease sufficiently to actuate the under-voltage protective relays and restore cooling with emergency onsite power without challenging fuel design limits. "The 4.16kV safety bus under-voltage protection scheme at Byron and Braidwood is believed to be a typical industry design. This design issue is being evaluated at the other Exelon stations. The results of this evaluation will be shared with the NRC. Therefore, this condition is being reported as a voluntary notification due to its potential generic industry applicability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2012-02-03
47636 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-02-03 | 2012-02-03 22:10 | 2012-02-03 | VOLUNTARY REPORT - DESIGN VULNERABILITY IN 4.16kV BUS UNDER-VOLTAGE SCHEME "On January 30, 2012, a design vulnerability was discovered at Byron and Braidwood stations in the Engineered Safety Feature 4.16kV bus under-voltage protection scheme for Byron Station Units 1 and 2. Specifically a voltage unbalance created by an open circuit of either the A or C phase from the offsite grid to the System Auxiliary Transformers (SAT) is not designed to actuate the protective relays on the 4.16kV safety bus that provides isolation from the offsite grid and the automatic start and loading of the emergency onsite diesel generators. "Two under-voltage relays are provided on each 4.16kV safety bus, which are combined in a two out of two logic to generate a loss of power signal. The relays are sensing voltage between two phases (i.e., A&B and B&C). An open circuit condition on the C phase or the A phase would not satisfy the two out of two logic. This condition results in both 4.16kV safety buses remaining energized with a bus undervoltage situation and results in equipment protective devices actuating from over-current conditions. "This configuration is a non-conforming condition in that the design of the under-voltage relays and logic was intended to identify degraded grid conditions, not loss of a single phase. With an open circuit on the A or C phase from the grid to the SATs, during normal operations, operators have to diagnose the condition and manually isolate safety buses from offsite power which would automatically start and load the emergency diesel generators. During a design basis event concurrent with an open circuit on A or C phase from the grid to the SATs, analysis performed to date indicates that starting of the ECCS loads would have caused the bus voltage to decrease sufficiently to actuate the under-voltage protective relays and restore cooling with emergency onsite power without challenging fuel design limits. "The 4.16kV safety bus under-voltage protection scheme at Byron and Braidwood is believed to be a typical industry design. This design issue is being evaluated at the other Exelon stations. The results of this evaluation will be shared with the NRC. Therefore, this condition is being reported as a voluntary notification due to its potential generic industry applicability." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2012-02-03
47635 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2011-12-01 | 2012-02-03 15:35 | 2012-02-03 | PART 21 REPORT - FOREIGN MATERIAL FOUND IN EMERGENCY DIESEL GENERATOR HIGH PRESSURE FUEL HOSE Cooper Nuclear Station (CNS) returned one high pressure fuel hose to Engine Systems, Inc. (ESI) because CNS had found foreign material within the hose during receipt inspection. This fuel hose was one of four fuel hoses that had been supplied to CNS by ESI in October 2011. ESI performed an evaluation and found very small pieces of the elastomer tube internal to the hose. Apparently these pieces were introduced during assembly of the end fittings onto the hose during fabrication of the hose assembly. When installed, this fuel hose would be located after the engine fuel filter and before the fuel injection pumps. Foreign material within this hose could migrate to the fuel injection pumps. The entrance of foreign material could impact operability of one or more fuel injection pumps and therefore affect fuel delivery to one or more engine cylinders. This could impact the load carrying capability of the diesel engine or possibly cause complete engine shutdown. Either scenario has the potential to prevent the emergency diesel generator from performing its safety related function. These hoses were supplied only to CNS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2012-02-03
47634 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2012-02-03 10:35 | 2012-02-03 13:09 | 2012-02-03 | CONTROL ROOM EMERGENCY VENTILATION AIR CONDITIONING SYSTEM INOPERABLE "On February 3, 2012, at 1035 hours [CST], the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable when the electrical feed breaker to the Refrigeration Compressor Unit (RCU) was found in a tripped condition. As a result, Technical Specification 3.7.5, Condition A, was entered. Troubleshooting is in progress at this time. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident." The LCO places the plant in a 30-day action statement. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-02-03
47633 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2012-02-02 | 2012-02-03 11:10 | 2012-02-03 | AGREEMENT STATE REPORT - DOSE DELIVERED TO WRONG PATIENT The following report was received from the State of Utah via email: "Two patients were scheduled to receive TheraSphere infusions containing microspheres of Yttrium-90 on the same day [02/02/12]. Patient #1 was to receive 5.32 GBq for a treatment dose of 120 Gy. Patient #2 was to receive 1.77 GBq for a treatment dose of 120 Gy. Patient #1 received the dosage for Patient #2 (i.e., 1.77 GBq). The error was detected prior to Patient #2 receiving a dosage. The licensee determined that Patient #1 received a dose that was 33% lower than the prescribed dose in the written directive. The licensee determined this to be a medical event. However, the licensee did not provide enough information to determine if this event is or is not an Abnormal Occurrence. An on-site investigation is planned by the Utah Division of Radiation Control to occur within the next several days." Utah Event Report ID Number: UT120001. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2012-02-09
47632 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-02-03 08:22 | 2012-02-03 08:22 | 2012-02-03 | LOSS OF PLANT COMMUNICATIONS DUE TO SCHEDULED MAINTENANCE "Calvert Cliffs will be implementing scheduled maintenance to the plant data network to install a data diode to meet the new cyber security requirements listed in 10 CFR 5.71. This work will require the TSC, OSC and subsequently the EOF to lose normal data flow from the plant data network for a period of approximately 6 to 8 hours. ERDS will also be unavailable during this maintenance. Should an emergency be declared during this period, the Control Room will continue to have the capability to retrieve plant data inputs to assess plant conditions and perform core damage assessment. Control Room Emergency Response Organization personnel will use backup methods already captured in emergency response procedures to disseminate plant parameter data to the effected Emergency response Facilities and NRC during the plant data network outage. MIDAS (Meteorological Data) will continue to be operational at the site." The licensee notified the NRC Resident Inspector. | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-02-03
47631 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2012-02-01 | 2012-02-02 14:40 | 2012-02-02 | AGREEMENT STATE REPORT - STUCK SHUTTER ON INDUSTRIAL GAUGE The following information was obtained from the State of Wisconsin via fax: "On February 1, 2012, the Wisconsin Radiation Protection Section received notice that the licensee had a gauge with a stuck shutter. The device is an Ohmart SHD-0 fixed gauge (serial number 64781) originally containing 250 mCi of Cs-137. A licensed service provider unmounted the gauge and attempted to fix the shutter but was unsuccessful. The RSO placed the device in a secured, remote storage location with the radiation beam pointing into the ground. Exposure rates at 1 foot are less than 2 mR/hr. "The Radiation Protection Section will continue to monitor the situation, pending replacement or disposal of the device, and will perform an inspection within the next two weeks." WI Event Report No.: WI120001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2012-02-07
47630 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2012-02-01 | 2012-02-01 15:33 | 2012-06-06 | PART 21 REPORT - FAILURE OF CRD COLLET RETAINER TUBE/OUTER TUBE WELD The following information was received via facsimile: "During a recent refurbishment of a Control Rod Drive (CRD) performed by GE Hitachi Nuclear Energy (GEH) for a domestic customer a 360 degree failure of the collet retainer tube fillet weld was identified. This weld is part of the CRD 919D258G003 Cylinder, Tube and Flange (CTF) assembly. The collet retainer tube fillet weld was performed in 1983 and subsequently assembled into a Group 003 part number 919D258G003 CTF. This G003 CTF assembly was assembled into a CRD in 1995 and placed into service in 1996. GEH continues to investigate the cause(s) of the failed fillet weld. Once the cause of the fillet weld failure is determined, GEH will review the extent of condition of this failure as well as the consequences to determine if a reportable condition exists. "There were no adverse effects on the CRD's operation observed due to this failure. "This 60-day interim notification, in accordance with 10CFR Part 21.21(a)(2), will be sent to all BWR/2-6 plants that utilize CRDs equipped with either 919D258G002 or 919D258G003 CTF assemblies." The affected plants are: Nine Mile Point 1-2, Fermi 2, Columbia, Grand Gulf, River Bend, Fitzpatrick, Pilgrim, Vermont Yankee, Clinton, Dresden 2-3, LaSalle 1-2, Limerick 1-2, Oyster Creek, Peach Bottom 2-3, Quad Cities 1-2, Perry 1, Duane Arnold, Cooper, Susquehanna 1-2, Brunswick 1-2, Hope Creek, Hatch 1 - 2, Browns Ferry 1-3, Monticello, and Millstone. * * * UPDATE FROM GE HITACHI VIA FAX AT 1259 EDT ON 6/6/12 * * * "GEH has completed the evaluation of this condition and has determined that the failure of Control Rod Drive collet retainer tube fillet weld is not a Reportable Condition as defined by 10CFR Part 21." Notified R1DO (Cahill), R2DO (Widmann), R3DO (Passehl), R4DO (Gepford) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2012-02-01
47629 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-11-30 07:58 | 2012-02-01 12:49 | 2012-02-01 | OFFSITE NOTIFICATION DUE TO UNMONITORED RELEASE OF TRITIUM (HEATING STEAM CONDENSATE) "Heating Steam condensate containing 9,430 picocuries per liter [pCi/L] of tritium overflowed from the Main Warehouse between November 22, 2011 and November 29, 2011. The US EPA drinking water limit for tritium is 20,000 pCi/L. "The Warehouse Condensate Return system failed to operate which resulted in the overflow of the Heating Steam condensate. There was a potential for the condensate to enter the environment where it could reach groundwater. The released volume for this event was conservatively calculated to be up to 3,900 gallons. The 122 Condensate Return Pump was replaced and the system was restored to service. "This voluntary report is in accordance with the Nuclear Energy Institute's Industry Ground Water Protection Initiative." The licensee has notified the NRC Resident Inspector and will inform state and local agencies of this event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-02-01
47628 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2012-01-31 17:30 | 2012-01-31 22:58 | 2012-01-31 | MANUAL TRIP DUE TO A PRIMARY TO SECONDARY LEAK GREATER THAN 30 GAL/HR "At 1505 PST, Unit 3 entered Abnormal Operation Instruction S023-13-14 'Reactor Coolant Leak' for a steam generator leak exceeding 5 gallons per day. "At 1549 PST, the leak rate was determined to be 82 gallons per day. At 1610 PST, a leak rate greater than 75 gallons per day with an increasing rate of leakage exceeding 30 gallons per hour was established and entry into S023-13-28 'Rapid Power Reduction' was performed. "At 1630 PST, commenced rapid power reduction per S023-13-28 'Rapid Power Reduction'. At 1731 PST, with reactor power at 35% the Unit was manually tripped. At 1738 PST, Unit 3 entered Emergency Operation Instruction S023-12-4 'Steam Generator Tube Rupture'. "At 1800 PST the affected steam generator was isolated." All control rods fully inserted on the trip. Decay heat is being removed thru the main steam bypass valves into the main condenser. Main feedwater is maintaining steam generator level. No relief valves lifted during the manual trip. The plant is in normal shutdown electrical lineup. Unit 2 is presently in a refueling outage and was not affected by this event. The licensee has notified the NRC Resident Inspector. The licensee has issued a press release. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-01-31
47627 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-01-31 | 2012-01-31 14:36 | 2012-01-31 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE This information was provided by the State of California by e-mail: "The Alternate RSO for Construction Testing & Engineering reported a Troxler 3440, serial number 22426, containing 9 mCi of Cs-137 and 44 mCi of Am-241, was stolen out of the cab of his pickup, which was parked in his driveway. . . sometime last night. "The Licensee notified the Manteca Police Department and is working on posting a reward for the safe return of the gauge." CA Report Number: 013112 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-02-03
47626 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2012-01-30 18:56 | 2012-01-30 19:15 | 2012-01-30 | UNUSUAL EVENT DECLARED DUE TO AN EARTHQUAKE OF MAGNITUDE 3.2 At 1856 EST, North Anna, Units 1 and 2, experienced an onsite seismic event. This was confirmed by the National Earthquake Information Center to be a magnitude 3.2. Based on these 2 indications the licensee declared an Unusual Event per EAL HU 1.1. The earthquake did not impact operations or equipment, and both units remain at 100% power. To exit the Unusual Event the licensee will need to verify that no damage was sustained to any systems or equipment. Presently the licensee is conducting a walkdown to verify no damage was incurred. The licensee has notified the NRC Resident Inspector. The licensee also notified the state and other government agencies. * * * UPDATE AT 0048 EST ON 1/31/12 FROM ROGER SMUTHERS TO PETE SNYDER * * * "The NOUE declared at 1856 EST on 1/30/12 has been terminated [at 0035 EST]. The event has been terminated after completion of AP-36, which is the procedure used when seismic activity is experienced. The abnormal procedure included engineering and operations inspections of various systems throughout the station, all of which were completed satisfactorily with no damage found relating to the seismic event." "None of the stations seismic instrumentation actuated during the event due to low seismic activity felt at the station. The newly installed Free Field Seismic Instrumentation did not actuate which has a trigger point of 0.01 g's further demonstrating the low level of the seismic activity experienced at the station." The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser), NRR (Lund), IRD (Grant), DHS (Gates), and FEMA (Biscoe). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-01-30
47625 | 0 | UNIV OF TEXAS |  |  |  | 1100 KW TRIGA MARK II | 2012-01-27 11:16 | 2012-01-30 16:02 | 2012-01-30 | TECHNICAL SPECIFICATION VIOLATION DISCOVERED The licensee has determined that technical specification 6.5.2 was violated. "The annual maintenance outage was conducted during the first two weeks in January 2012, with the biennial fuel inspection occupying most of the effort during the outage. On January 11th, the instrumented fuel elements were disconnected from the safety system for routine biennial surveillance which tests for unacceptable changes in fuel element length and bend. The surveillance was completed and the safety system restored on the same day. Maintenance was completed and normal operations resumed on January 23rd. Two non-routine maintenance items remain to be completed, installation of a 3rd safety channel calibrated to provide indication in the range where the safety limit is challenged, and replacement of an instrument rack in the control room to accommodate additional equipment supporting a facility security upgrade. "On Monday January 23rd, the reactor was operated to support experiment operations coincident with reactor operator training. The preoperational checkout indicated satisfactory operation of the safety system, including the fuel temperature channels. Shutdown fuel temperatures were within tolerance for ambient conditions. Preoperational checks were completed at 9:32, with startup to 50 watts initiated at 09:33. Critical checks at 50 watts were accomplished at 9:33, followed by ascension to 100 kW at 10:00. Records of 100 kW operating data (status window print files) indicated 18?C on fuel temperature channel 1 and 83?C on fuel temperature channel 2; the senior reactor operator who performed the operation did not recognize the difference in temperature. The reactor was shutdown on completion of the experiment at 10:40. "The next operation occurred on January 27th. Shutdown fuel temperatures were within tolerance for ambient conditions. Preoperational checks were completed at 9:09 with 50 watt critical data obtained at 9:13. Reactor power of 100 kW was achieved at 9:21, and 500 kW at 9:54. Records (status window print files) show fuel temperature channel 1 did not change from approximately 18?C at 100 kW and 500 kW. The senior reactor operator who performed the operation did not recognize the difference in temperature between fuel channel 1 and fuel channel 2. The reactor was shutdown at 11:16. Prior to a planned startup, the minor deviation between fuel temperatures at shutdown was noted to be unusual which prompted recognition of the previous 500 kW operating temperature. A preoperational check was performed, with no indication of abnormalities. Operations were terminated for investigation. "INVESTIGATION "The output of the thermocouple at fuel temperature channel 1, and was noted to be erratic when the wires at the pool side terminal were moved. It was noted that the nylon braid insulation was frayed and the black electricians tape around the lead wire was degraded. Resistance readings confirmed that perturbing the thermocouple lead wire causes the resistance of the detector loop to vary erratically, and that an alternate thermocouple loop is stable when the wires are moved. "A functional response test was performed using the chill water system to cool the pool below ambient, and fuel temperature 2 was observed to fall significantly below ambient (about 13?C ) while fuel temperature channel 1 dropped slightly, to about 17?C. There are three thermocouples in each instrumented fuel element, although the fuel temperature monitoring channel uses only one of the three. Fuel channel 1 temperature monitoring channel was connected to an alternate thermocouple and the indication came into agreement with fuel temperature channel 2 and the pool water temperature channel. "The plug and socket connector for fuel channel 1 was inspected, and it was noted that the wires entering the plug were frayed, facilitating a short circuit and an alternate thermocouple junction. It is not possible to unambiguously identify the short circuit path, but there is a metal identification tag, and a metal strain relief device that are in contact with the thermocouple lead wire assembly. Therefore the thermocouple junction being sensed by fuel temperature channel 1 was an inadvertent connection at the plug, sensing ambient air temperature. The wires at the fuel temperature channel 2 plugs were fabricated with sleeves over the wires, preserving the insulation, providing additional electrical isolation between the wires, and preventing sharp bends in the wires. "At this point, an alternate thermocouple has been connected to fuel temperature channel 1, resistance readings indicate no short circuits, and the laboratory Director is preparing a restart letter with compensatory measures to be implemented pending development of permanent corrective action." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | TX | NPR | [5 empty] | 0 | 2012-01-30
47624 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-01-30 10:01 | 2012-01-30 11:39 | 2012-01-31 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES At 1101 EST, Byron Unit-2 experienced a reactor trip due to RCP undervoltage. All rods fully inserted, MSIV's were manually closed and decay heat is being removed by Auxiliary Feedwater pumps running and steam leaving via atmospheric relief valves. The unit is currently in a natural circulation cooldown with the diesels supplying station emergency loads. Licensee will be cooling the plant down to Mode 5. At 1118 EST, Byron declared an Unusual Event due to a loss of offsite power on Unit 2 from a faulted Station Auxiliary Transformer (SAT). The faulted SAT caused both 6.9 kV and 4.1 kV bus voltage to drop. Smoke was observed coming from the SAT with no visible flames being apparent. This caused bus loads to trip without a complete loss of ESF busses 241 and 242. These buses were manually disconnected from the SAT, which transferred the load to the emergency diesel generators 2A and 2B. Both diesel generators started and loaded without incident. Offsite assistance was requested from the local fire department as a precaution. The licensee is also declaring notification for 10 CFR 50.72(b)(3)(v)(D) Unit 1 is not being affected by this event and remains at 100% power. The licensee has notified the NRC Resident Inspector. * * UPDATE FROM GREG BALESTRIERI TO JOHN KNOKE AT 2119 EST ON 01/31/12 * * "At 2000 CST on 1/31/12, Byron terminated their Unusual Event due to the Loss of Offsite Power to Unit 2. Switchyard repairs were completed and offsite power has been restored to essential busses 241 and 242 thru System Auxiliary Transformers 242-1 and 242-2. Unit 2 Emergency Diesel Generators have been shutdown." The licensee is citing classification 10 CFR 50.72(c)(1)(iii) The licensee has notified the NRC Resident Inspector. Notified R3DO (James Cameron), NRR EO (Louise Lund), IRD MOC (Scott Morris), DHS (Konopka) and FEMA (Hollis). Licensee may issue a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) | 0 | 2012-01-30
47623 | -1 | BAYHEALTH MEDICAL CENTER |  |  |  |  | 2012-01-25 09:30 | 2012-01-26 15:22 | 2012-01-27 | MISADMINISTRATION OF THALLIUM DURING CARDIO STRESS TEST A patient received 100% more than the prescribed dose of thallium. The patient was to receive 3.5 milliCuries of thallium followed by 30 milliCuries of Cardiolite, a Tc-99M radiopharmaceutical. Instead, the patient received 3.5 milliCuries of thallium then received an additional 3.6 milliCuries of Thallium. The technician stated that he got confused where the patient was in the treatment process. The patient and physician have been informed. The licensee is awaiting dosimetry results to determine the organ dosage but does not believe there will be any recurring medical effects from this event. * * * RETRACTION AT 1227 EST ON 1/27/12 FROM MUNDORF TO HUFFMAN * * * The licensee is retracting this event report after a review and evaluation of the doses administered. The licensee has determined that this event is not reportable based on the unintended dose being less than 5 Rem effective dose equivalent and therefore not reportable under 10 CFR 35.3045. The licensee has discussed this conclusion with NRC Region 1 (Lanzisera). R1DO (Dental) and FSME (McIntosh) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-02-01
47622 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-01-25 21:00 | 2012-01-25 21:39 | 2012-01-26 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "Planned preventive maintenance activities are being performed on the Braidwood Nuclear Station Technical Support Center (TSC) Ventilation System. These work activities are planned to be performed and completed expeditiously within 8 hours. This maintenance activity includes the performance of preventive maintenance on the TSC outside air supply fan unit which affects the TSC emergency filter train and air handling unit. During a portion of the time these activities are being performed, this equipment will not be available for operation. As such, the TSC Ventilation will be rendered non-functional during the performance of portions of the work activity. "If an emergency condition occurs that requires activation of the Technical Support Center, during the time this work activity is being performed, it will take no more than 4 hours to return the equipment back to functional status, dependent on the stage of the work activity at the time an emergency occurs. Plans are to utilize the TSC for any declared emergency during the time this work activity is being performed as long as radiological conditions allow. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1107 EST ON 01/26/12 FROM RICHARD ROWE TO S. SANDIN * * * "Braidwood Nuclear Station TSC ventilation was restored to available status at 0635 CST on January 26, 2012. "The previously reported system preventative maintenance has been completed." The licensee notified the NRC Resident Inspector. Notified R3DO (L. Kozak). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-25
47621 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-01-25 13:50 | 2012-01-25 14:13 | 2012-01-25 | SAFEGUARDS SYSTEM HAS POTENTIAL VULNERABILITY FOR PERSONNEL ACCESS The safeguards system could have potentially allowed unauthorized access to the protected area for which compensatory measures were not in place. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-01-25
47620 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-01-23 10:40 | 2012-01-24 10:06 | 2012-01-24 | MEDICAL TREATMENT OF A POTENTIALLY CONTAMINATED INDIVIDUAL AT ONSITE FACILITY "10 CFR 70.50 (b)(3) requires a twenty-four hour report of an event that requires unplanned medical treatment at a medical facility of an individual with spreadable radioactive contamination on the individual's clothing or body. "An individual's fingers were potentially exposed to HF [hydrogen fluoride]. The potential HF exposure was believed to be caused by a pin hole in a glove-box glove. The glove was replaced and other glove-box gloves were inspected. The individual's fingers were rinsed and calcium gluconate cream was applied in the Radiological Control Area (RCA). As a precautionary measure, the individual was sent to the on-site medical area (within the Owner Controlled Area) for review/observation. Minor radioactive contamination, below minimum detectable activity (MDA) for the equipment, was removed from the individual's fingers at the medical area. The radioactive contamination was below radioactive release limits. In addition, at the medical area, the individual's finger was irrigated with water and additional calcium gluconate cream was applied. The individual was monitored and then released by medical personnel. No evidence of HF exposure was observed. "The licensee is making this report on a voluntary basis due to the ambiguous nature of the regulation [10 CFR 70.50 (b)(3)]. It should be noted that Part 50 guidance as well as internal licensee guidance refers to medical treatment at off-site medical facilities. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2012-01-24
47619 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2012-01-23 13:00 | 2012-01-23 20:59 | 2012-01-26 | BREACH IN HIGH ENERGY LINE BREAK BARRIER "At 1300 EST on 1/23/12, it was determined that an unanalyzed condition existed for the Unit 1 Cable Spreading Room. A high energy line break (HELB) barrier issue was discovered while performing a HELB inspection and the condition is believed to have existed from initial plant construction. A HELB barrier was found to have a breach in it that could allow steam from a high energy line break in the Unit 1 Turbine Building [into the cable spreading room and thus into the control room]. The Control Room is not analyzed for a steam environment. The degree of the impact could not be readily determined, but could likely affect the safety related equipment in the Cable Spreading Room. Therefore, an 8-hour report to the NRC is required under 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.'" The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 1/26/2012 AT 1339 EST FROM ROBERT MARTIN TO MARK ABRAMOVITZ * * * "Engineering performed an evaluation to address the impact of the degraded condition on the barrier's design functions. The evaluation concluded that the barrier remained capable of performing its design function with the degraded seal present. Therefore, this condition does not represent an unanalyzed condition that significantly degrades plant safety. The NRC Resident Inspector has been notified." Notified the R1DO (Dentel). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2012-01-23
47618 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-01-23 18:04 | 2012-01-23 18:51 | 2012-01-23 | UNSUAL EVENT DECLARED DUE TO FIRE INSIDE CONTAINMENT LASTING > 15 MINUTES At 1804 EST on 01/23/12, Unit 2 declared an Unusual Event due to an electrical fire in the control cabinet on the Polar Crane. The fire brigade responded, de-energized the equipment and confirmed that the fire was extinguished. There were no injuries as a result of this incident. At 1837 EST, the license terminated the Unusual Event classification. Unit 2 is currently in mode 5 (Cold Shutdown) for a Refueling Outage. The licensee informed state/local agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-01-23
47617 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2009-08-01 | 2012-01-23 18:11 | 2012-01-23 | AGREEMENT STATE REPORT - ABANDONED GENERALLY LICENSED SOURCES The following report was received from the Commonwealth of Pennsylvania via fax: "Event Description: International Communication Materials, Inc., (lCMI), a subsidiary of Nukote International, Inc., is a defunct manufacturer of toner and ink cartridges, which had operated a facility that closed in August 2009. This event wasn't discovered until the Department's [PA Bureau of Radiation Protection] Southwest Region inspected ICMI's factory in September 2010. The [ICMI] building was found unsecured, and [gauges were found with] the gauge shutters open and unlocked. The Department located two former ICMI employees, who secured the building and allowed the DEP to close and lock the shutters with padlocks. In August 2011, the SW Region again discovered the ICMI factory unsecure. The Department, with the Pennsylvania State Police, then conducted a joint inspection and discovered evidence that trespassers had entered the building and may have stolen copper pipes. After several unsuccessful attempts to contact Nukote International or ICMI, the Department then communicated with Nukote's largest creditor, CIT Group, and obtained their cooperation in securing both the building and the GL gauges. "Sources: Three (3) Kay-Ray / Sensail, Inc., Cs-137 GL sources, each 25 mCi "Serial Nos.: S96M1001, S96M1009, S96M1010 "CAUSE OF THE EVENT: Human Error - failure of ICMI to secure licensed material. "ACTIONS: As of January 18, 2012, the purchaser / transferee intends to dispose of the generally licensed unit's all together. The transferee has already received quotes from various licensed vendors and will be selecting a vendor as soon as possible. "Media attention: None at this time "PA Event Report ID No: PA090045" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-26
47616 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2012-01-05 | 2012-01-23 16:42 | 2012-01-23 | AGREEMENT STATE REPORT - MEDICAL RADIATION TREATMENT EXPOSURE TO WRONG TREATMENT SITE The following report was received from the State of North Carolina via email: "A cancer patient undergoing therapeutic radiation treatment for gastric cancer received an exposure to the wrong treatment site. This error occurred using a HDR afterloader device with a radioactive source containing Ir-192. "The event occurred after the dosimetrist made an error while correcting a change to dwell position due to catheter migration. The dwell position was mistakenly adjusted out rather than in. Two treatments were made prior to the error being detected. "The error resulted in an approximately 4 cm positioning error, which caused the source to stop short of the target so that the total prescribed dose was not delivered. "The patient was informed of the event, and received a correct third treatment as well as external beam therapy. "Additional information will be provided as it is provided by the licensee." The intended treatment site was a bile duct which was to receive 700 cGy in three (3) fractions. The first two (2) fractions were delivered on 1/5/2012 and 1/12/2012 with the source mispositioned as indicated above. The Regional Inspector for the State of NC is following up. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2012-01-29
47615 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-01-23 06:33 | 2012-01-23 12:43 | 2012-01-23 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "On January 23, 2012 at 0633 hours, planned routine preventive maintenance was initiated on the Technical Support Center/Operations Support Center (TSC/OSC) diesel generator. The planned maintenance includes fluid and filter replacements, damper inspections and cleaning and is scheduled to be complete on January 26, at 1500 hours. The normal TSC/OSC power supply and all other TSC/OSC functions remain available. During certain periods of the preventive maintenance the diesel generator would not be capable of being restored to service within one hour. "Under certain accident conditions the TSC/OSC may become unavailable as a result of the diesel generator not being available. Existing Emergency Procedures direct the responsible Emergency Plant Manager to relocate the TSC/OSC staff to the designated alternate location (EOF or main control room) as required. The affected Emergency Response Organization facility leads have been informed. "The USNRC Resident Inspector Staff has been notified. "This notification to the USNRC Operations Center is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF)." The licensee plans to notify the Commonwealth of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-23
47614 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2012-01-20 22:37 | 2012-01-21 04:00 | 2012-01-21 | LOSS OF ASSESSMENT CAPABILITY - SAFETY PARAMETER DISPLAY SYSTEM "At 2237 EST on Friday, January 20, 2012, with the reactor at 100% core thermal power, the Pilgrim Nuclear Power Station (PNPS) determined that portions of the in-plant Safety Parameter Display System (SPDS) were not functioning as designed due to potential problems with the plant process computer. Specifically, the SPDS, which provides numerous plant parameters, some of which are credited for emergency assessment capability, are not currently available. The initial investigation has determined that the failure has not impacted the entire SPDS, but has the potential to impair the licensee's safety assessment capability at this time. "Immediate actions are being taken to restore the system to functional status and applicable plant procedures have been entered to determine any further mitigating actions. "This event had no impact on the health and/or safety of the public. "The licensee has notified the NRC Resident Inspector. "This notification is conservatively being made in accordance with 10 CFR 50.72 (b)(3)(xiii)." There is no impact to plant operations. The licensee will be notifying the Commonwealth of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-21
47613 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-19 | 2012-01-20 20:00 | 2012-01-20 | AGREEMENT STATE REPORT - RADIUM-226 SOURCES DISCOVERED AT WASTE TRANSFER STATION The following event was received via facsimile from the Pennsylvania Department of Environmental Protection [DEP], Bureau of Radiation Protection: "Event Description: On Thursday, January 19, 2012, DEP's southeast regional office received a call from the Waste Management, Inc. Norristown solid waste transfer station stating that a roll-off container of waste had set off their radiation alarm. The facility's consulting health physicist investigated, along with representatives of the Department's Bureau of Radiation Protection. The radioactive material recovered from the roll-off was four (4) small cylinders identified as approximately one (1) curie [total] of radium-226 contained in what appeared to be a lead-lined box. The lead-lined box (with shiny exterior) was inside an old metal locking box that contained various other source holders, instruments and applicators, some containing the name 'Standard Chemical.' It is believed these Ra-226 sources are vintage circa 1920 medical radiation therapy capsules. Preliminary wipes revealed no significant removable contamination, thus, no leaking sources. The consultant HP was given a DOT Special Permit for transport, and [took] possession of the Ra-226 for safe and secure storage. Contact dose rates outside the closed shiny metal lead-lined box were as high as 2.0 R/hr. In an open configuration, dose rates were about 100 R/h in near contact with the sources. "The unlocked roll-off container was located for several weeks in a parking lot of an adult-only living community in West Chester, PA while a contractor performed work on townhomes in the development. Department personnel have been in touch with the contractor and will be interviewing workers, as well as nearby homeowners to determine if any people were significantly exposed to these sources. Local outreach is also planned to ensure similar sources are not in the public sector. "CAUSE OF THE EVENT: Suspected intentional abandonment of old medical radium sources in an open construction waste dumpster. "ACTIONS: The Department is in contact with DOE and a LLRW vendor for transfer or disposal of Ra-226 sources. Further investigations will be performed, as well as any needed dose reconstruction." Pennsylvania Report: PA120004 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-02-02
47612 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-20 14:09 | 2012-01-20 19:12 | 2012-01-20 | AGREEMENT STATE REPORT - MISADMINISTRATION OF DOSE TO PATIENT The following information was provided by the Commonwealth of Pennsylvania via facsimile: "On January 20, 2012, at 1409 EST, the Department's [PA Bureau of Radiation Protection] southeast regional office received notification via phone call about this ME [Medical Event]. "On January 19, 2012, a worksheet was prepared for two patients who were to be treated on the same day, close in time. The worksheets were switched and each patient received the other patient's dose. The first patient reached stasis before receiving the full amount and received a dose 35% above the planned dose. The second patient received 55% less than what was planned. "CAUSE OF THE EVENT: Human error. "ACTIONS: No adverse effects are expected from the overdose to the first patient. The second patient will receive a higher dose than planned at their next schedule treatment. The licensee plans on modifying their current procedures to prevent this event from occurring again. The Department plans to do a reactive inspection." Event Report 10 No: PA120005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-26
47611 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2012-01-20 08:33 | 2012-01-20 14:45 | 2012-01-20 | FITNESS FOR DUTY - CONFIRMED POSITIVE ALCOHOL TEST A non-licensed, employee supervisor had a confirmed positive test for alcohol. The individual's unescorted access has been administratively withdrawn. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2012-01-20
47610 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-19 13:15 | 2012-01-20 13:59 | 2012-01-20 | AGREEMENT STATE REPORT - FOUR NUCLEAR GAUGES FAILED SEMIANNUAL SHUTTER CHECK The following information was provided by the Commonwealth of Pennsylvania via email: "The Department's [PA Bureau of Radiation Protection] central office received an email on January 19, 2012. This event is reportable within 24-hours under 10CFR 30.50(b)(2). "EVENT DESCRIPTION: It was determined on January 19, 2012 during the six month shutter check that the remote actuator cables and one handle on four devices are inoperable. "The devices are identified as: Manufacturer Model Serial Isotope Activity Texas Nuclear 5197 81624 Cs-137 100 mCi Texas Nuclear 5197 81631 Cs-137 100 mCi Texas Nuclear 5197 81634 Cs-137 100 mCi Texas Nuclear 5197 81635 Cs-137 100 mCi "CAUSE OF THE EVENT: Normal wear and tear (30+ year old gauges) "ACTIONS: The shutters are in the locked and closed position and shall remain so until qualified repairs can be made. The gauges are planned to be removed and returned to the manufacturer. No employees were exposed to excess levels of radiation as a result of these failures. The Department plans to conduct a reactive inspection." Event Report ID No: PA120003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-25
47609 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2012-01-17 17:46 | 2012-01-18 17:12 | 2012-01-18 | 24-HOUR REPORT PER SECTION 2.G OF UNIT 1 OPERATING LICENSE "Surveillance Requirement 3.8.4.14 for LCO 3.8.4, "DC Sources - Operating," was performed on 02/10/11 for the 125 VDC Vital Battery 4 (VB4). The recorded capacity was 80.2% and VB4 was declared OPERABLE at that time. "On 06/27/11 VB4 failed the service test as required by SR 3.8.4.13. Prior to the test VB5 was aligned to Vital Battery Board IV. VB5 had previously passed its required SRs within the required surveillance frequency. With VB5 re-aligned to Vital Battery Board IV, the plant was in a configuration that would allow it to meet all design bases events including a four hour station blackout. The eight weakest cells in VB4 were replaced and VB4 re-tested in accordance with SR 3.8.4.13. VB4 passed its acceptance criteria and VB4 was returned to service on 07/06/11. "However, on 01/17/12, an independent analysis of the computer generated test data indicated that the actual battery capacity calculated on 02/10/11 was 79.87% which is less than the acceptance criteria of 80%. Therefore, between 02/10/11 and 06/27/11, VB4 was inoperable and the plant was in a condition prohibited by TS. "On 01/06/12 a functional test was performed on VB4. The functional test is a service test using a single unit load profile. The single unit load profile consists of Unit 1 loads, common loads, and loads transferred from Unit 2 to Unit 1. VB4 passed the acceptance criterion (105 Vdc) with a terminal voltage of 111.9 Vdc. This test indicates that VB4 was functional from 02/10/11 to 06/27/11. "VB4 has been replaced with new battery cells and the acceptance criteria for SR 3.8.4.13 and SR 3.8.4.14 were met." The error in the recorded capacity of 80.2% was discovered during a root cause investigation and attributed to arithmetical rounding errors. The licensee is continuing their investigation to determine extent of condition. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2012-01-18
47608 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-01-14 | 2012-01-18 16:50 | 2012-01-18 | AGREEMENT STATE REPORT - MISSING THEN RECOVERED THALLIUM-201 SOURCE "On January 17, 2011 the licensee's radiation safety officer called [the state] to advise that a portion of a shipment of radiological material to be used for medical purposes had not arrived at its intended destination. A package containing two doses of Thallium-201 of nominally 20 milliCi each was picked up by the Texas licensee, Pan Handle Nuclear, on January 14, 2012 in Amarillo. However, the package showed signs of repaired damage and when inspected, the third dose of Thallium-201 was missing from the package. The manufacturer was alerted on the morning of January 16th and they subsequently contacted the carrier, regarding the package. "HazMat Personnel from [the shipping company] conducted a trace of their facilities associated with the transfer which resulted in the missing vial being identified as 'found' in the Memphis 'Over goods' holding area. Apparently, the package had become damaged early in the morning on January 14th during the shipping process such that one of the three vials had escaped the packaging. The damage to the package was noted and repaired, however an accurate count of the contents was not conducted and, contrary to standing instructions from the manufacturer, the package was forwarded to the intended recipient rather than being returned to the manufacturer. "The 'missing' vial was subsequently found on the same day later that morning, some hours after the package was processed through the Memphis hub. The vial was identified as hazardous based on the trefoil which appeared on the shielded and intact container and the manufacturer's name. It was isolated and placed into an over pack that same day. The slightly damaged, but intact shielded container was then returned to the manufacturer as of January 18, 2012 after it was determined to be the 'missing' third vial. Surveys of the returned vial conducted by the manufacturer showed that there was no external contamination on the shielded vial, there was no damage to the vial and all the expected material remained present." Illinois Item Number: IL 12004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47607 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2012-01-18 | 2012-01-18 16:37 | 2012-01-18 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE The following report was received from the State of Florida via fax: A Troxler gauge, Model 3440, was run over and the housing cracked. The source was retracted at the time. The incident is currently under investigation. FL Incident Number: FL12-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47606 | -1 | U.S.ARMY TACOM LIFE CYCLE COMMAND |  |  |  |  | 2012-01-18 13:24 | 2012-01-18 15:41 | 2012-01-19 | POTENTIALLY DAMAGED RANGE INDICATOR CONTAINING 3.2 CURIES TRITIUM The U.S. Army Life Cycle Command was informed by the Combined Support Maintenance Shop in Richmond, Virginia that a range indicator containing 4 sources of 0.8 Curies each of Tritium may be damaged. Apparently, the range indicators appear cracked and are not illuminating properly. The range indicator is locked inside a secured area with no access allowed. The U.S. Army is waiting for results of swipe surveys to determine if there is an actual spread of contamination. * * * RETRACTION FROM THOMAS GIZICKI TO JOE O'HARA AT 1302 EST ON 1/19/12 * * * The licensee is retracting the event based upon swipe survey results being less than the lower limit of detectability. There was no spread of contamination and the device will be disposed of in the future. The licensee notified Bill Lin (Region 3). Notified R3DO(Peterson), R1DO(Bellamy) and FSME(McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2012-01-18
47605 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-17 08:00 | 2012-01-18 13:59 | 2012-01-18 | AGREEMENT STATE REPORT - BROKEN THERMO MEASURE TECH MODEL 5204 COLLIMATOR The following report was received via facsimile from the PA Department of Radiation Protection. "Notifications: The department's western regional office received a phone call on January 17, 2012 and then referred the matter to the central office via email and telephone on January 18, 2012. This event is reportable within 24 hours under 10 CFR 30.50(b)(2)(i). "Event Description: A collimator failure was discovered during a monthly routine maintenance check on January 17, 2012. The collimator had broken off of the shutter mechanism. "The device is identified as - Manufacturer: Thermo Measure Tech; Model 5204; Isotope: Cs-137; Activity: 4 Ci. "CAUSE OF THE EVENT: Equipment Failure "ACTIONS: Upon discovery, a service provider was contacted and repairs were made by replacing the collimator with a spare one. Surveys were performed to verify appropriate conditions. No employees were exposed to excess levels of radiation as a result of this failure. A 30 day licensee report is expected. The department plans to conduct a reactive inspection." Event Report ID No.: PA120002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47604 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2012-01-17 14:49 | 2012-01-18 12:30 | 2012-01-18 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACT EMPLOYEE SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for an illegal substance taken during a pre-access fitness-for-duty test. The contract employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2012-01-18
47603 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-09-29 08:00 | 2012-01-18 10:29 | 2012-01-18 | AGREEMENT STATE REPORT - SHUTTER FAILURE DUE TO DROPPING OF A BERTHOLD TECHNOLOGIES DENSITY GAUGE The following report was received via facsimile from the PA Department of Radiation Protection. "Notifications: On Friday January 13, 2012, the licensee sent notification via email after close of business to the central office about an event that took place on September 29, 2011. This email was received by central office on Tuesday, January 17, 2012. It is reportable within 24 hours under 10 CFR 30.50(b)(2). "Event Description: On September 29, 2011, a gauge with Serial Number 10153 was dropped, bending the shutter control handle, leaving the shutter stuck closed. The workers did not notify anyone of the incident and the gauge was put in storage. When the gauge was to be put back in service on November 10, 2011, it was then observed to be in the damaged condition. The gauge was then put back into a secured storage until the repair could be made. The gauge was repaired by replacing the shutter with a new Serial Number 10306 on December 1, 2011. "The device is identified as - Manufacturer: Berthold Technologies USA, LLC; Model: LB8010; Serial #: 10153 (replaced by 10306); Isotope: Cs-137; Activity: 20 mCi. "CAUSE OF THE EVENT: Human error. "ACTIONS: On December 1, 2011 repairs were made. This was discovered on an inspection by the Department on December 16, 2011." Event Report ID No.: PA110043. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47602 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-11-21 08:00 | 2012-01-18 10:29 | 2012-01-18 | AGREEMENT STATE REPORT - SHUTTER HANDLE FAILURE ON BERTHOLD TECHNOLOGIES DENSITY GAUGE The following report was received via facsimile from the PA Department of Radiation Protection. "Notifications: On Friday January 13, 2012, the licensee sent notification via email after close of business to the central office about an event that took place on approximately November 21, 2011. This email was received by central office on Tuesday, January 17, 2012. It is reportable within 24 hours under 10 CFR 30.50(b)(2). "Event Description: It was noticed during a job on approximately November 21, 2011, the shutter handle of Berthold Technologies density gauge, Serial Number 10049, had fallen off due to constant vibration and cavitation of the iron piping on the truck. This caused the roll pin that secures the rotary shutter handle to the shutter shaft to wear and eventually fall off. The gauge was temporarily repaired in the field, and reported on November 29, 2011 to the company's safety officer. The gauge was immediately taken out of service and scheduled for repair. "The device is identified as: Manufacturer: Berthold Technologies USA, LLC; Model: LB8010; Serial #: 10049; Isotope: Cs-137; Activity: 20 mCi. "CAUSE OF THE EVENT: Excessive vibration of the equipment. "ACTIONS: On December 1, 2011 repairs were made to Serial Number 10049. For preventative maintenance, the roll pin was replaced on Serial Number 10055 as well." Event Report ID No.: PA110042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47601 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-12-16 08:00 | 2012-01-18 10:29 | 2012-01-18 | AGREEMENT STATE REPORT - SHUTTER FAILURE ON BERTHOLD TECHNOLOGIES DETECTOR The following report was received via facsimile from the PA Department of Radiation Protection. "Notifications: On Friday January 13, 2012, the licensee sent notification via email after close of business, to the central office about an event that took place on March 18, 2011. This email was received by central office on Tuesday January 17, 2012. It is reportable within 24 hours under 10 CFR 30.50(b)(2). "Event Description: On March 18, 2011, a service vendor was at Universal Well Services to perform a change of the iron piping. At that time, they noticed an improper functioning shutter mechanism and it was temporarily fixed. On December 16, 2011, the licensee was inspected by Pennsylvania DEP (Dept. of Environmental Protection). It was found that the shutter on the Berthold Technologies Detector, Serial Number 10072 had been replaced on December 15, 2011 with a new shutter Serial Number 10275, permanently fixing the shutter failure. "The device is identified as: Manufacturer: Berthold Technologies USA, LLC; Serial #: 10072 (becoming 10275); Isotope: Cs-137; Activity: 20 mCi. "CAUSE OF THE EVENT: Excessive build-up of debris "ACTIONS: The licensee was directed to make the required notification immediately after receiving an NOV (Notice of Violation) from Pennsylvania DEP dated January 13, 2012 about the shutter failure discovered during an inspection on December 16, 2011." PA Report ID No.: PA110041. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2012-01-23
47600 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2012-01-17 18:14 | 2012-01-17 22:35 | 2012-01-17 | UNIT 2 COMMENCED A TECH SPEC REQUIRED SHUTDOWN AFTER DECLARING STATION BATTERY "B" INOPERABLE "At approximately 1814 hours (EST) on January 17, 2012, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, personnel confirmed that the Station Battery Performance Capacity Test (Five Year Interval), for station battery 'B' was not completed within its required periodicity plus grace period. Based upon this information, plant Operations personnel declared the 'B' battery inoperable and entered the required action for Improved Technical Specifications (ITS) 3.8.4, Condition 'A', which requires that the DC electrical power subsystem be restored to operable status in 2 hours. At 2014 hours (EST), Operations personnel entered the required action for ITS 3.8.4, Condition 'B' due to required actions and associated completion time for Condition 'A' not met. Condition 'B' requires the unit to be in Mode 3 within 6 hours AND be in Mode 5 within 36 hours. This report is being made in accordance with 10 CFR 50.72(b)(2)(i) based on the initiation of a plant shutdown required by the Technical Specifications. Following the shutdown, the unit will commence a refueling outage that was originally scheduled to begin at 0000 hours (EST) on January 21, 2012." The licensee informed the NRC Resident Inspector. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2012-01-17
47599 | 0 | AVERA MCKENNAN HOSPITAL |  |  |  |  | 2012-01-16 16:00 | 2012-01-17 13:04 | 2012-04-12 | MEDICAL EVENT DUE TO POTENTIAL DIFFERENT FRACTIONAL DOSE DELIVERED THAN PRESCRIBED The licensee provided notification that a patient received 2 occurrences of a dose less than prescribed when delivering ten fractions of a treatment. Each of the underdoses were approximately 50% of the 340 Gray prescribed fractional dose. The patient will receive additional dose fractions in order to achieve the written directive total dose. The Radiation Oncologist has notified the patient and attending physician. * * UPDATE FROM RICHARD MASSOTH TO JOHN KNOKE AT 1826 EST ON 01/31/12 * * "On January 17, 2012 the NRC Operations Center was verbally notified of two Therapeutic Underdose Occurrences discovered by the licensee on January 16 and 17, 2012. These occurrences involved a fractionated Breast High Dose Rate Afterloader (HDR) treatment with a SenoRx Contura multicatheter breast applicator. The first and third delivered treatment fractions were found to be less than 50% of the intended fractional dose. The entire course of the treatment in the written directive included ten equal-dose fractions of 3.4 Gray per fraction for a total dose of 34 Gray to the prescribed treatment site. To correct for the underdose occurrences, two additional treatment fractions were added and the treatment plan was modified to achieve the total dose specified in the written directive. "The licensee now believes that this medical event has also caused an unintended dose to skin outside of the prescribed treatment site, requiring notification under 10CFR35.3045(a)(3). The licensee has performed computer simulation, calculations and physical measurements using TLDs simulating the treatment geometry to model the unintended skin dose. The event delivered an unintended skin dose exceeding at least the skin erythema threshold (2 Gy). The licensee is continuing to monitor the patient response to the skin dose and is working to refine the unintended skin dose estimates. An NRC reactive inspection team is on-site." Notified R4DO (Jeff Clark) and FSME (Greg Suber) * * * UPDATE FROM TRACI HOLLINGSHEAD TO HOWIE CROUCH AT 1044 EDT ON 4/12/12 * * * The licensee confirmed that they agree with their medical consultants' findings that the patient received approximately 2720 rads of unintended skin dose. Notified R4DO (Gaddy) and FSME (McIntosh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-01-23
47598 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-14 13:30 | 2012-01-17 11:01 | 2012-01-17 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA The following report was received by fax: "On January 17, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee of a source disconnect event that occurred on January 14, 2012. The radiography crew was using a QSA 880D containing 54.9 Curies of iridium-192. The drive cables were also manufactured by QSA. The disconnect was caused by the drive cable snapping approximately four inches from the source connector. The radiographer noted the failure as he approached the camera after a shot and the dose rates indicated the source was still outside the camera. The radiographer notified his Radiation Safety Officer (RSO). The radiography crew set up new barriers and controlled access to the area. The RSO arrived at the site at 1630 hours. The RSO retrieved the source and it was returned to the fully shielded position by 1730 hours. The RSO stated that there was a section of the drive cable that looked like it may have been stretched, but he did not know when or how it could have happened. He stated that they had only had this set of drive cables for no more than eight months. No exposure limits were exceeded during this event. Additional information will be provided as it is received in accordance with SA-300." The event occurred on County Road 289 in Gonzales County. Texas incident: I-8922 * * * UPDATE AT 1321 EST ON 01/17/12 FROM ART TUCKER TO S. SANDIN * * * "The licensee has stated that the drive cable will be returned to the manufacturer for inspection and a cause for the failure [investigation]. Notified R4DO (Pick) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-20
47597 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2012-01-07 10:30 | 2012-01-17 10:12 | 2012-01-17 | AGREEMENT STATE REPORT - ATTEMPTED THEFT OF MEDICAL IMAGING EQUIPMENT The following information was received from the State of Georgia: On January 17, 2012 the State of Georgia received a fax dated January 13, 2012, from one of their licensees (PennTeck Diagnostics, Inc., license number GA 975-1) that one of their two mobile nuclear vans was broken into on Saturday, January 7, 2012, at 1030 EST, but nothing was stolen. PennTeck Diagnostics is located in Augusta, Georgia. The State contacted the licensee this morning to see if any further details or clarification on the incident could be gathered, but no additional information was given. The licensee reiterated that all of their calibration sealed sources and flood source were accounted for; they installed new locks on the rear lift gate on the mobile van where the thief entered, and the police are looking over the surveillance tapes. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2012-01-20
47596 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2012-01-16 03:30 | 2012-01-16 08:30 | 2012-01-16 | TECHNICAL SUPPORT CENTER VENTILATION DAMPER FAILURE "At 0330 EST on 01/16/12, it was discovered that due to the failure of the Technical Support Center (TSC) ventilation system to align during testing, the TSC was rendered non-functional. Repairs are underway. An update will be provided once the TSC ventilation has been restored to normal operation. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the potential loss of an emergency response facility. "The NRC Senior Resident Inspector has been informed." * * * UPDATE AT 1525 EST ON 01/16/12 FROM JORGE O'FARRILL TO S. SANDIN * * * "Corrective maintenance was completed 01/16/2012 at 1042 EST to restore the TSC filtered ventilation capability. Post maintenance testing was completed satisfactorily [on] 01/16/2012 [at] 1335 EST. JAF's TSC has been restored and is now functional." The licensee informed state/local agencies as a courtesy and the NRC Resident Inspector. Notified R1DO (Trapp). | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-16
47595 | -1 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-01-14 17:55 | 2012-01-14 21:37 | 2012-01-17 | OFFSITE NOTIFICATION DUE TO A CHLORINATED WATER DISCHARGE "Salem Generating Station made a 15 minute notification of a chemical discharge to the State of New Jersey Department of Environmental Protection at 1806 [EST]. The Salem Non-Rad Waste Chemical Treatment Building sump overflowed out of the building to a catch basin that discharges to the Delaware River. Approximately 100 gallons of chlorinated water was reported to the State of New Jersey as being discharged, which was terminated at 1806 [EST]. There were no personnel injuries associated with this event. There was no impact to any Salem Station Safety-Related systems and all Safety-Related systems are available. Investigation into the cause of the event is in progress." The licensee notified the NRC Resident Inspector and Lower Alloways Township. * * * RETRACTION FROM DAN MCHUGH TO JOE O'HARA AT 1031 ON 1/17/12 * * * "On 1/14/2012 Salem Generating Station made a 15 minute notification of a chemical discharge to the State of New Jersey Department of Environmental Protection at 1806. The Salem Non-Rad Waste Chemical Treatment Building sump overflowed out of the building to a catch basin that discharges to the Delaware River through DSN 488. Subsequent investigation has indicated that the spill was entirely contained within the onsite storm drainage system and that there was no discharge to the Delaware River. The storm drain system was plugged, flushed and pumped out for appropriate disposal of the waste water. Additionally, the spill to the ground was cleaned up within 24 hours." The licensee will notify the NRC Resident Inspector and has notified the New Jersey Department of Environmental Protection. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-01-14
47594 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2012-01-14 07:00 | 2012-01-14 10:18 | 2012-01-16 | EMERGENCY RESPONSE DATA SYSTEM REMOVED FROM SERVICE FOR MAINTENANCE "At 0700 EST on January 14, 2012, Fermi 2 removed the Emergency Response Data System (ERDS) from service to facilitate planned maintenance on the associated power bus. The Technical Support Center (TSC) will also be unavailable during the planned power outage. The duration of the outage is expected to be 11 hours. This loss in capability is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "Indications of related plant variables are available in the Main Control Center. The Visual Annunciator System (VAS) remains functional. Meteorological and process effluent radiological monitor indications are available and dose assessment capability is available. In the event TSC activation is required, the Emergency Operations Facility (EOF) will be used for the TSC function. Use of the EOF as the backup TSC is part of Fermi 2's Radiological Emergency Response Preparedness Plan. The Emergency Callout System (ECOS) is designed to, facilitate contacting TSC personnel to respond directly to the EOF. Information normally provided by ERDS can be transmitted via the notification system as described in the Radiological Emergency Response Preparedness Plan. "In the event of a plant emergency, the Emergency Plan can be implemented as assessment capabilities are available under alternate means." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL HIMEBAUCH TO VINCE KLCO ON 1/14/12 AT 2245 EST * * * "At 1835 EST, during restoration from planned maintenance, a failure of an electrical auto throwover device occurred, preventing restoration of power to ERDS and the TSC. Investigation of the failure and necessary repairs are in progress. At this time, it is unknown when availability of ERDS and the TSC will be restored. An update will be made to the NRC Operations Center when ERDS and the TSC are restored. The NRC Senior Resident Inspector has been notified." Notified the R3DO (Orth). * * * UPDATE AT 0127 EST ON 1/16/2012 FROM MICHAEL HIMEBAUCH TO MARK ABRAMOVITZ * * * "At 0127 EST on January 16, 2012 the Emergency Response Data System (ERDS) was restored and the Technical Support Center (TSC) is available as an emergency response facility, following restoration of the associated power bus." The licensee notified the NRC Resident Inspector. Notified the R3DO (Orth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-14
47593 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-13 | 2012-01-13 18:27 | 2012-01-17 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT A patient of Memorial Hermann in Houston received the wrong radioisotope. A dose of Gallium-67 was ordered, but a dose of Thallium-201 was delivered. Because the dose was improperly labeled as Gallium-67, the dose calibration process indicated an acceptable radioisotope and dose. The patient was injected with the wrong radioisotope on January 11, 2012. During patient imaging on January 13, 2012, it was realized that the patient received the wrong radioisotope. The pharmacy was notified of the error and admitted to delivery of the wrong isotope. The physicist at the hospital estimates that the patient received a dose of about 6 REM whole body. Texas Incident Number: I-8921 * * * UPDATED AT 1434 EST ON 01/17/12 FROM ROBERT FREE TO S. SANDIN * * * The following information was received as an update: "The licensee called to report that the wrong isotope was administered to a patient. Thallium 201 had been injected in a patient instead of Gallium 67 that was ordered. Apparently, the pharmacy sent the wrong isotope. 8 mCi of Gallium was ordered and a estimated 4.7 mCi of Thallium was delivered. Dose activities were similar and the dose calibrator didn't pick up the difference in isotope. Patient was injected on 1/11/12 and imaged 1/13/12. The mistake was discovered in imaging. The licensee will file a written report within 15 days." Notified R4DO (Pick) and FSME (McIntosh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-19
47592 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-01-06 10:48 | 2012-01-13 15:35 | 2012-01-13 | AGREEMENT STATE REPORT - LOST ANALYZER The following information was received via facsimile: "[The] Environmental Safety Manager of Louisiana Scrap Metal Recycling notified the [Louisiana] Department of Environmental Quality of a lost Niton XLI 818 Q/serial number 6066 analyzer with 30 mCi of Am-241 on January 6, 2012. "FINDINGS: The investigation was conducted at Louisiana Scrap Metal Recycling in Lafayette. Contact was made with the Environmental Safety Manager and the [Non-Ferrous Manager], who provided the following information of their internal investigation. "The facility's investigation revealed that on January 5, 2012, [Employee #1] was scanning a customer's trailer to identify the type metal in the load, with a Niton XLI 818Q/serial number 6066 analyzer with 30 mCi of Am-241. The analyzer was discovered missing the next morning, January 6, 2012 by [Employee #2] at approximately [0900 CST and notified the department at 1048 CST on January 6, 2012 of the missing source. [Employee #2] called [Employee #1] to try to reconstruct his actions of the previous day since he had signed out the analyzer on the utilization log. [Employee #1] stated that he believed that he must have left the analyzer on the trailer of a customer. [Employee #2] called the customer to ask if he had found the analyzer and also the route he took to go home. The customer stated that he had not found the analyzer. [Employee #2] then retraced the route to search for the missing analyzer for approximately eight hours but was not successful. The analyzer is still missing to date, however does not pose a health hazard to the general public. "In conclusion the licensee did not secure licensed radioactive material from unauthorized removal or access. The above area is contrary to LAC 33:XV.445.A. The licensee failed to maintain constant surveillance to prevent unauthorized use of licensed radioactive material that is in a controlled or unrestrictive area. The above area is contrary to LAC 33:XV.445.B. The licensee also failed to have the minimum of two independent physical controls that form a tangible barrier to secure portable gauges from unauthorized removal, whenever portable gauges are not under the control and constant surveillance of the licensee. The above area is contrary to LAC 33:XV.326.B." Louisiana Incident Number: LA120002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-01-18
47591 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2012-01-04 09:30 | 2012-01-13 15:34 | 2012-01-13 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA NOT PROPERLY SECURED The following information was received by facsimile: "This is a report of a transportation incident where an Industrial Radiography Camera was not properly secured. The RSO stated that two radiographers, one an instructor, conducted a radiography job in Bay St. Louis, Mississippi. On January 4, 2012, while returning to the Baton Rouge, LA office, they decided to meet with another radiographer who is an instructor on the radioactive materials license for Mistras and one of the other radiographer's father. The father offered to take the radiography camera to the office in Baton Rouge, LA. The instructor from the radiography job in Bay St. Louis agreed, but did not realize that the father did not have his radiography truck. The father put the camera in the trunk of his personal vehicle unsecured and unbraced. After noticing that the father and son did not have some of the required paperwork, the instructor pursued them. Approximately 2 miles down the road, the father and son in the same vehicle were pulled over for speeding. After they were pulled over, the son, who was driving, was suspected of intoxication and tested. The RSO received a call from the father regarding the impending arrest of the son for DUI at [2130 CST]. The son was arrested for DUI and the instructor from the radiography job secured the radiography camera. The father was arrested for outstanding warrants. Both the father and son were suspected of being under the influence, but the father refused to be tested by law enforcement. The RSO arrived to the site at [2200 CST]. The camera was placed in the Mistras storage vault around [0030 CST on January 5, 2012]. "Mistras is conducting an internal investigation. Louisiana Department of Environmental Quality is investigating. So far, the son's employment has been terminated. The father's Trustworthy and Reliability status has been suspended. All radiographers will be drug tested. Additional information will be forthcoming." Louisiana Incident Number: LA120001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2012-01-18
47590 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2012-01-13 14:03 | 2012-01-13 16:05 | 2012-01-13 | NOTIFICATION OF UNUSUAL EVENT AND REACTOR TRIP DUE TO LOSS OF OFFSITE POWER "At 1403 CST, Wolf Creek experienced a reactor trip due to loss of power in the switchyard. At 1415 CST, Wolf Creek declared a Notification of Unusual Event (NOUE) when it was determined that the switchyard would not be restored within 15 minutes. "All systems functioned as expected in response to this event and both Emergency Diesel Generators started and energized the safety-related buses. "The plant is currently stable in Mode 3 and investigation into the cause for loss of power in the switchyard is underway." During the trip, all rods inserted into the core. No primary relief valves lifted as a result of the transient. Decay heat is being removed via the atmospheric steam dumps with auxiliary feedwater supplying the steam generators. The plant is stable at NOP/NOT. No safety significant equipment is reported out of service. The licensee has notified state and local governments and the NRC Resident Inspector. * * * UPDATE FROM DAVE DEES TO VINCE KLCO AT 1851 EST ON 1/13/12 * * * At 1709 CST, the licensee exited the NOUE when power was restored to the east bus from offsite. Additionally, the licensee is reporting a loss of safe shutdown capability in accordance with 10CFR50.72(b)(3)(v)(A) due to the initial loss of offsite power. The licensee has notified state and local governments, the NRC Resident Inspector, and will be issuing a press release on the event. Notified R4DO (Powers), IRD (Marshall), NRR (Cheok), FEMA (Burckart) and DHS (Hill). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | POT UNABLE TO SAFE SD | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(A) | 0 | 2012-01-13
47589 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-10 | 2012-01-13 08:48 | 2012-01-13 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY SOURCE TO RETRACT The following information was received via E-mail: "On January 13, 2012, the Agency [Texas Department of State Health Services, Radiation Branch] was notified by the licensee that a source disconnect had occurred on January 10, 2012 at one of their job sites. The radiographer was using a Spec model 300 radiography camera containing a 116 curies cobalt-60 source. They had completed 20 exposures. After their last exposure, they approached the radiography camera and noted that their dose rate instrument was indicating that the source was not shielded. The radiographer returned to the end of the crank out device to make sure that he had retracted the source. The radiographer found that while the drive cable was completely retracted, the lock was not operating, and the source was still exposed. The radiographer contacted the company's Radiation Safety Officer (RSO). The radiographers set new boundaries at two millirem per hour and waited for the RSO. The RSO arrived at the location and determined that the source was located in the collimator. The RSO retrieved the source without incident. "An inspection of the connector on the source pig tail indicated that it had spread allowing it to disconnect. The licensee is sending the source to the manufacturer for inspection. No exposure limits were exceeded during this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-8919. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-18
47588 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2012-01-12 16:46 | 2012-01-13 00:50 | 2012-01-13 | DEGRADATION OF SAFEGUARD SYSTEM Degradation in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | ME | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2012-01-13
47587 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-04 06:09 | 2012-01-12 11:36 | 2012-01-12 | INVALID ACTUATION OF CONTAINMENT ISOLATION SIGNALS AND AN EMERGENCY SERVICE WATER PUMP "The following information is provided as a sixty (60) day telephone notification to the NRC in accordance with 50.73 (a)(1) in lieu of the submittal of a written LER to report a condition that resulted in an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system and emergency service water systems that normally do not run and that serve as ultimate heat sinks. NUREG-1022, Revision 2, identifies the information that needs to be reported as discussed below. "On December 4, 2011, Clinton Power Station was in Mode 5 (Refueling) conducting refueling outage activities, including the installation of a self test system power supply modification. During post-maintenance activities associated with the affected power supplies, an unexpected voltage reading was identified. While investigating the anomaly, one of the two nuclear system protection system essential logic power supplies was de-energized with the redundant power supply not yet restored. At 0609 [CST], the power supply was re-energized, resulting in an inadvertent actuation of the logic. "Containment isolation valves on the following systems automatically closed: Instrument Air, Service Air, and Containment Floor Drain. Additionally, the Division 1 Shutdown Service Water (SX) Pump started. These actuations were not valid since the actuations were associated with low reactor water level conditions (Level 1 and Level 2) which were non-existent at the time of the event. The associated actuations were successful had the actuations been valid. "This event is reportable in accordance with 10CFR50.73 (a)(2)(iv)(A) and has been entered into the Corrective Action Program." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-01-12
47586 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-12 09:00 | 2012-01-12 11:10 | 2012-01-12 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE "On January 12, 2012, the Agency [Texas Department of State Health Services] was notified by the licensee that a Troxler Model 3430 moisture/density gauge (SN 39547) containing 40 millicuries of americium-241 and 8 millicuries of cesium-137 had been stolen that morning at approximately 0900 hrs. CST from one of its vehicles while it was parked at a convenience store in McKinney, Texas. The gauge was secured in the bed of the pickup truck with two chains. While the licensee's technician was inside the store, both chains were cut and the gauge removed. Local law enforcement was notified. The Agency notified the Texas Association of Pawnbrokers. More information will be provided as it is obtained." Texas Incident # I-8918 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-17
47585 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2012-01-11 22:15 | 2012-01-12 04:27 | 2012-01-13 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On January 11, 2012 at 22:15 [EST], the High Pressure Coolant Injection System (HPCI) was declared inoperable due to a failure of the turbine governor valve to respond to demanded position. When demanded to travel to the full closed position, the governor valve remained full open rendering the speed and flow control system for the turbine inoperable. The failure was discovered as part of a planned maintenance evolution. "All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling (RCIC) system remain operable. The unit remains at 100% power. "The station has initiated an Event Response Team to identify and correct the cause of the failure. No personnel injuries resulted from the event. "The NRC Resident Inspector [has been notified] and Lower Alloway Creek Township will be notified." The unit is in a 14-day LCO for HPCI inoperability. * * * RETRACTION FROM JAMES PRIEST TO VINCE KLCO ON 1/13/12 AT 1644 EST * * * "The following is a retraction of ENS Notification #47585: On January 11, 2012, Hope Creek Generating Station reported to the NRC that High Pressure Coolant Injection System (HPCI) was declared inoperable due to a failure of the turbine governor valve to respond to demanded position. This condition was discovered when obtaining an oil sample from the HPCI system. According to the procedure, the HPCI flow controller automatic setpoint was lowered to zero. The procedure set the manual controller setpoint by having the operator lower the demand for a time period rather than verifying the setpoint at zero. The HPCI Auxiliary Oil Pump is then started. The governor valve was expected to start to open (intermediate position) and then close. Instead the valve went to the full open position and did not respond to attempts to close the valve from the flow controller. Accordingly, Control Room personnel conservatively initiated ENS reporting under 10CFR50.72(b)(3)(v) in response to the apparent loss of safety function for Unit 1. "Subsequent technical evaluation concluded that the performance and response of the HPCI turbine governor control valve was as expected based on the manual controller demand being at 35% when the HPCI Auxiliary Oil Pump was started to collect a HPCI oil sample. The Engineering review concluded that there are no problems with the HPCI turbine governor control valve response to controller demand. Operating procedures have been revised to provide guidance on verifying manual controller demand at 0% before placing the HPCI Auxiliary Oil Pump in service under standby conditions for oil sampling or similar evolutions. Since January 11th, 2012, HPCI has remained available to perform its required safety functions and only became inoperable during planned evolutions to either obtain oil samples or to investigate HPCI turbine governor control valve performance. On this basis, the HPCI system was capable of performing its function to mitigate the consequences of an accident and the issue described in Event #47585 is not reportable under 10 CFR 50.72(b)(3)(v). The NRC Resident Inspector and Lower Alloway Creek Township will be notified of this retraction." Notified R1DO (Trapp). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2012-01-12
47584 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2012-01-04 | 2012-01-10 17:02 | 2012-01-10 | AGREEMENT STATE REPORT - DOOR SAFETY INTERLOCK ON DRY IRRADIATOR FOUND TO BE NON-FUNCTIONAL The following report was received via e-mail from the Illinois Emergency Management Agency Radioactive Materials Section: "The licensee's radiation safety officer called the Agency to advise of a failure of a safety feature associated with the operation of their self shielded dry storage irradiator. This irradiator is used to conduct testing of samples prior processing. During the performance of routine weekly safety checks of the irradiator, it was discovered that the device could be operated without closing both shielded collar doors that allow access to the sample chamber. Further investigation showed that a proximity sensor associated with one of the doors failed in the 'on' configuration which gave a false indication that the unit was ready for operation and the irradiation sequence could be initiated. No samples were being irradiated in the unit at the time of the safety check and there were no exposures of personnel as a result of the failure, nor were any elevated radiation levels detected from the device. The device was subsequently locked out of service pending repair. The next day, the licensee obtained the necessary replacement part and repairs were affected by their trained technical staff according to the manufacturer's instructions. "The licensee has contacted the authorized service vendor, Best Industries, to discuss the matter as well as the irradiator manufacturer, MDS Nordion. This device contains an IAEA Category I quantity of radioactive material (Co-60) in a permanently shielded configuration." Illinois Report Number IL12001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2012-01-13
47583 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2012-01-10 11:30 | 2012-01-10 14:44 | 2012-01-10 | OFFSITE NOTIFICATION TO STATE OF FLORIDA DUE TO EXCEEDING WASTEWATER DISCHARGE PERMIT LIMIT "Florida Department of Environmental Protection was notified at 1130 EST on 01/10/12 that Stormwater Basin Discharge for the month of December exceeded the total monthly allowable limit for Total Suspended Solids (TSS). "The Monthly Average for TSS limit is 34 mg/l. The limit per the St. Lucie Plant DEP Discharge Permit is 30 mg/l for the month. This limit was exceeded due to rainfall and required pumping prior to an additional sample point. "While the basin was pumped, the Daily Maximum Limit of 100 ppm was not exceeded. "The FDEP representative concurred that there was no threat to the public as a result of this discharge. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the Offsite Notification to the Florida Department of Environmental Protection." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2012-01-10
47582 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2012-01-10 04:36 | 2012-01-10 04:49 | 2012-02-15 | EXCESSIVE LEAKAGE FROM RCP SEAL RETURN "Plant shutdown from 100% due to increased leakage from 21 RCP [Reactor Coolant Pump] seal return was commenced at 0100 EST. A manual reactor trip was actuated in accordance with plant procedures at 25% power. Auxiliary feedwater pump was placed in service prior to the reactor trip, per plant procedures. Decay heat is being removed via the condenser steam dumps. All offsite power sources are available. All equipment operated as expected." The licensee has notified the NRC Resident Inspector and other government agencies. * * * RETRACTION FROM CHARLES ROKES TO HOWIE CROUCH AT 0940 EST ON 2/15/12 * * * "Subsequent review concluded the condition did not meet reporting criteria. A normal plant shutdown was initiated in accordance with plant procedures for a known problem with the 21 RCP # 1 seal whose seal leakoff rate had reached an administrative alarm limit. Shutdown was not required by the Technical Specifications. On January 10, 2012, at 0100 hours [EST] a plant shutdown commenced per plant operating procedure 2-POP-2.1. At 0436 hours, the reactor was manually tripped in accordance with procedure 2-POP-3.1. This event is not reportable as the reactor trip was part of a normal shutdown for corrective maintenance." The licensee has notified the NRC Resident Inspector. Notified R1DO (Powell). | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2012-01-10
47581 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2012-01-09 17:22 | 2012-01-10 00:55 | 2012-01-10 | TECHNICAL SUPPORT CENTER DETERMINED TO BE NON-FUNCTIONAL "On January 09, 2012 the Technical Support Center(TSC) ventilation was discovered to be non-functional during system testing. At 1722 hours [EST], it was identified that control power was lost to four motor operated dampers. Investigation revealed that a control power fuse was blown. In addition, the TSC ventilation Supply Fan (AHU-1) was identified to have one of two fan belts failed. The fuses were replaced at 19:45 [EST] and the system was restored to service. However, the system has been removed from service this evening to replace the fan belts. An update will be provided when the system is restored to full functionality." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1744 EST ON 1/10/12 FROM JEFF MOORE TO HUFFMAN * * * Maintenance personnel installed two new belts on AHU-1 and aligned the motor/fan sheaves to ensure correct operation. TSC ventilation has been restored to the normal condition. The licensee will notify the NRC Resident Inspector. R1DO (Trapp) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-10
47580 | 0 | DIABLO CANYON |  |  |  | ISFSI | 2012-01-09 14:05 | 2012-01-09 23:44 | 2012-02-29 | NUT ON HOLD-DOWN STUD WAS FOUND LOOSE "On January 9, 2012, at 1405 [PST], plant personnel notified the Diablo Canyon shift manager that a nut on a hold-down stud on an Independent Spent Fuel Storage Installation(ISFSI) HISTORM spent fuel storage cask was loose to the touch. Plant personnel hand tightened the nut and verified that none of the other 16 casks in the facility had nuts that were loose to the touch. "The Diablo Canyon ISFSI design requires that each spent fuel storage cask be installed with the cask compressed against the embedment plate using 16, two-inch diameter, anchor studs. Each stud is pre-loaded to approximately 157,000 lbf. This design ensures the cask will remain stable during a seismic event. A manufacturer's analysis of the stability of the cask with all of the 16 hold down stud nuts installed with no pre-load concluded that the cask would maintain its stability during a seismic event. "PG&E has contracted the vendor to re-tension the stud and expect[s] completion [by] 1/13/2012. PG&E will assess the need to verify tension of the remaining studs based on the extent of condition evaluation. "Cause of the loose nut has not yet been determined. "The NRC Senior Resident Inspector has been informed." * * * UPDATE AT 2007 EST ON 1/11/2012 FROM PHILIPPE SOENEN TO VINCE KLCO * * * "On January 11, 2012, at 1325 PDT, plant personnel notified the Diablo Canyon shift manager that two additional nuts on hold-down studs for other ISFSI HISTORM spent fuel storage casks were discovered to be loose. The two additional nuts (one per cask) were discovered when the full effort of two hands was used on the nuts while performing an extent-of-condition evaluation. All 16 nuts on all 16 casks were tested for tightness using the full effort of two hands (i.e., no pre-load). "NRC senior resident inspector has been informed." Notified the R4DO (Powers), NRR EO (Cheok), and NMSS EO (Mohseni). * * * UPDATE AT 1915 EST ON 2/29/2012 FROM DAN STERMER TO CHARLES TEAL * * * "On February 29, 2012, at 1610 PST, plant personnel notified the Diablo Canyon shift manager that cause analysis of loose nuts on hold-down studs of ISFSI HISTORM spent fuel storage casks determined the cause is not a defect and this occurrence is not reportable. Accordingly, the reporting criteria for Event Notification 47580 is changed from '72.75(c)(1) Non-emergency condition' to 'Voluntary Report.' Pacific Gas and Electric (PG&E) plans to submit a voluntary, written report (licensee event report) to the NRC. PG&E personnel informed the NRC resident inspector." Notified R4DO (Lantz), NRR EO (Lee), and NMSS EO (Rubenstone). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | CA | ISF | [5 empty] | 0 | 2012-01-09
47579 | 0 | BENEFIS HEALTH CARE |  |  |  |  | 2012-01-05 | 2012-01-09 16:00 | 2012-01-18 | MEDICAL UNDEREXPOSURE TO TARGET AREA USING HIGH DOSE RATE AFTERLOADER DEVICE The licensee reported that a patient received only about 10% of the required dose to the target area during a treatment for esophageal cancer. The prescribed dose for the esophageal region was 700 centigray. The area was being treated with a Varian High Dose Rate Brachytherapy Afterloader device using a 6.344 Curie Ir-192 source. The location of the source is normally tracked by a radiographically opaque image near the source. In this case, the end of the catheter also appeared somewhat radiographically opaque and was mistaken for the source location. Consequently, the source was mispositioned about 4 cm back from the intended target area resulting in the underexposure. The physician and patient have been notified and no health effects are anticipated from the area that was unintentionally exposed due to the mispositioning of the source. * * * UPDATE AT 1345 EST ON 01/18/12 FROM KARI CANN TO S. SANDIN * * * The licensee is continuing their review of this incident and have determined that the source may have been mispositioned by as much as 29 cm back from the intended target area. This may have resulted in excessive exposure to portions of the upper neck and back of the patient. A physician has scheduled an anatomical examination of the patient tomorrow to assess if there are any adverse effects related to the treatment. NRC Region IV Inspectors are currently on-site. Notified R4DO (Pick) and FSME (McIntosh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2012-01-15
47578 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2012-01-09 11:55 | 2012-01-09 14:32 | 2012-01-09 | REPORT TO OFFSITE GOVERNMENT AGENCIES AND PRESS RELEASE DUE TO A CHEMICAL SPILL ONSITE The licensee reported that approximately 300 gallons of nitric acid spilled in the bulk chemical storage outdoor area from a storage tank. The nitric acid spilled into a dike that surrounds the tank. The leak was isolated and it is believed that no acid breached the dike and entered the environment. Due to fumes from the acid, the licensee shut down production activities and evacuated non-essential personnel from nearby buildings. The licensee is currently remediating the spill and evaluating when to permit personnel normal access to the onsite areas that were evacuated. This event did not involve any radiological material and did not meet emergency declaration criteria. There was no offsite impact from this event. Site security was maintained throughout. No injuries have been reported. The cause of the spill is still being investigated. This event is being reported to the NRC Operations Center as a "Concurrent Report" because the licensee has notified state, county, and local authorities and will be making a press release. The licensee has also notified the NRC Resident Inspector and Region 2 (Pelchat). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2012-01-10
47577 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2012-01-06 | 2012-01-06 16:41 | 2012-01-13 | AGREEMENT STATE REPORT INVOLVING A POTENTIAL MEDICAL EVENT DURING BRACHYTHERAPY The following information was received from the State of Ohio via email: "The Ohio Department of Health Bureau of Radiation Protection received a preliminary telephone report from the University of Toledo of a device malfunction with a Varian HDR with an Ir-192 source. A patient had received four treatments to the cervix. The physician noticed during examination reddening of the skin on the upper thigh. Upon reviewing the setup with the tandems, a constriction and blockage was identified in the catheters caused by wear debris. It is presumed at the time being that this caused the system to conclude the source had reached the end of the catheter when it had not. Dose calculations are in the process of being reviewed, however the licensee believes that the doses may be less than the quantities for a medical event. "The licensee is The University of Toledo, Ohio license number 02110 49 0006. "The licensee is preparing a written report. The Bureau will be sending an inspector to the site next week." Ohio Report # OH-12-001 * * * UPDATE FROM KARL VON AHN TO DONALD NORWOOD AT 1101 EST ON 1/13/2012 * * * The following information was received by email: "The Ohio Department of Health, Bureau of Radiation Protection is updating the event report to indicate that this is a medical event. "An Ohio Department of Health Bureau of Radiation Protection inspector investigated the incident at the licensee facility on Thursday Jan. 12, 2012. The Varian HDR (model number AL19000001, SN VS0054) had 4.01 Ci of Ir-192 at the time of the incident and was using the Brachyvision treatment system. "After the fourth of four fractions of 400 cGy each, the attending physician noticed an unusual skin reaction. After licensee was unable to find any errors in the treatment delivered, they began to investigate the hardware. The licensee found a 'corrosion' line in the entry of the Tandem used in the Fletcher Suite Device where the device narrows at is end. During the fourth fraction, apparently the catheter inserted into the tandem snagged on the 'corrosion' causing the starting point of fraction treatment to be misplaced 9 cm. The treatment began from this point, not at the intended treatment site. Preliminary dose calculations were made based on the assumption that the starting dwell position was at this point instead of being fully inserted. "Preliminary dose calculations indicate a skin dose of 1251 cGy to the right thigh, and 1273.9 cGy to the left thigh when no skin dose was intended. The dose to the prescribed treatment point for that fraction was 194.2 cGy instead of 400 cGy. The total dose for all fractions to the prescribed treatment site was 1394.2 cGy instead of the intended 1600 cGy. "The patient and the referring physician have been notified. The physician does not anticipate any adverse effects. "The original catheter used is no longer made by Varian, and the licensee was using a replacement catheter that that is slightly larger in diameter and is thicker than the original. The original catheter did not get caught on the 'corrosion' in the Tandem. This issue was found with two Tandems in three Fletcher Suite Device sets. The new catheter fully inserts as intended into the other Tandems. "The licensee's corrective action includes marking the new catheters to provide a visual indication that it has been fully inserted into the Tandem." Notified R3DO (Orth) and FSME EO (Turtil). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2012-01-12
47576 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-05 | 2012-01-06 14:31 | 2012-01-06 | AGREEMENT STATE REPORT INVOLVING A FIXED GAUGE WITH A STUCK SHUTTER The following information was received from the State of Texas via email: "On January 6, 2012 the Agency [Texas Department of Health] was notified by the licensee that while conducting routine maintenance check, the shutter on an Ohmart/Vega model SH-F2 was found stuck in the open position. The gauge contains 375 millicuries of cesium - 137. Open is the normal operating position for the gauge. The gauge does not pose an increased exposure hazard to the general public or to their workers. The licensee is contacting the manufacturer for repairs to the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-11
47575 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2012-01-05 16:00 | 2012-01-06 14:17 | 2012-01-06 | AGREEMENT STATE REPORT INVOLVING DETECTION OF CONTAMINATED MATERIAL The following information was received from the State of California via email: "Two [2] packages set off radiation alarms at Truckee, CA truck scales. Both packages indicated Cobalt 60. One package read 5.7 mr/hr and the other indicated 6.1 mr/hr using a Victoreen 450 CHP. The packages were enroute to Bed Bath and Beyond in Santa Clara and San Jose. "The shipment was authorized to proceed in a separate trailer to the Sacramento [the shippers] yard at 8200 Elder Creek Road where the shipment will be secured awaiting RHB inspector to determine the contents and disposition of the material. Surveys were requested of the CHP to document ALARA during this shipment. "Shipment contained four Model DR9M Dual Ridge Metal Boutique (Kleenex box holders). Contact reading 6.5 mr/hr, One foot 0.85 mr/hr with a Victoreen 450P ion chamber." The shipment originated in India with a port of entry at Newark, NJ and was shipped via common carrier to its final destination in California. CA 5010 #: 010512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2012-01-11
47574 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-01-05 | 2012-01-05 16:45 | 2012-01-05 | AGREEMENT STATE REPORT INVOLVING CONTAMINATION FROM A SUSPECTED BROKEN EXIT SIGN The following information was provided by the Commonwealth of Massachusetts via email: "Large area swipes reading up to 14,000 DPM H-3 were found in the loading dock area. No cause is known. Activity is distributed evenly on the floor and walls so airborne deposition is suspected. Current theorized cause is a broken exit sign. "Licensee has evacuated unnecessary personnel from loading dock and is trying to find the extent of contamination. "Since a broken exit sign could cause a release over 5 ALI, immediate notification was given to NRC over the phone." . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2012-01-10
47573 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2012-01-05 15:10 | 2012-01-05 15:58 | 2012-01-05 | ACTUAL ENTRY OF UNAUTHORIZED PERSON INTO PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2012-01-05
47572 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-11-07 09:44 | 2012-01-05 14:43 | 2012-01-05 | 60-DAY REPORT INVOLVING AN INVALID EDG ACTUATION DUE TO TECHNICIAN ERROR "This 60-day telephone notification is being made pursuant to the requirements specified in 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) in lieu of submitting a written Licensee Event Report due to invalid actuation of an emergency AC electrical power system while removed from service for testing. "On November 7, 2011 with the Station at 100% power, the Emergency Diesel Generator 'B' (EDG 'B') output breaker closed unexpectedly resulting in the EDG being paralleled to the grid out of phase during the performance of the semi-annual fast start test required by Technical Specifications. "The actuation of the EDG 'B' output breaker to close was determined to be invalid as it occurred while a technician was performing a required voltage check across a set of contacts in the output breaker circuit. The individual switched an analog multi-meter from the DC voltage range to resistance range while test leads were still in place across the test points. This action actuated the breaker closure relay, which caused the output breaker to close, placing the EDG 'B' in parallel to the grid. The EDG picked up load as expected until the output breaker was opened approximately 52 seconds later by an operator in the control room. A review of data from the event verified that the maximum rating of the EDG was not exceeded. "Subsequent inspection and testing of the EDG 'B' and output breaker found no abnormalities as a result of the out of phase paralleling of the EDG 'B' to the grid. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2012-01-05
47571 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-12-21 | 2012-01-05 14:26 | 2012-01-05 | AGREEMENT STATE REPORT INVOLVING A MISSING AMERICIUM-241 CHECK SOURCE The following report was received from the State of New Jersey via email: "Canberra is terminating their license and in reconciling their inventory, and on 12/21/11 they discovered that a 8uCi Am-241 source [used as a check source] was missing. The source was last used by an employee in June or August. That employee had a stroke and did not return to work. Other employees cleaned out his cube area, mailed his personal belongings to his house, and threw everything else in the garbage. NJDEP instructed Canberra to go to the former employee's home. They will send a technician to do a search/survey." This incident was reported by Canberra to the State of New Jersey on 1/4/12. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-01-10
47570 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2012-01-05 09:30 | 2012-01-05 11:52 | 2012-01-05 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email: At 10:45 a.m. today, 1/05/12, the [NJ] Bureau of Environmental Radiation (BER) received a call from the RSO for Nova QA Consulting to report that one of his inspector's car was stolen in front of the client's facility in Orange, NJ this morning between 09:30 and 10:00 a.m. In the locked car was a Troxler Model 4640 serial #2375 with less than 9 mCi of Cs-137. His inspector called the Orange police and the RSO is also in communication with the Orange police. At 11:05 a.m. the RSO said that he will call Trenton Dispatch. Trenton Dispatch called the BER at 11:25 a.m. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2012-01-10
47569 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2012-01-05 03:53 | 2012-01-05 05:18 | 2012-01-05 | SODIUM HYPOCHLORITE LEAK RESULTED IN AIRBORNE CONCENTRATIONS POTENTIALLY DANGEROUS TO LIFE AND HEALTH "A section of piping between sodium hypochlorite tanks[tanks 121 and 122] broke and resulted in a unisolable leak in one of the tanks. The spill was contained within the berm of the chlorine house. "The spill resulted in airborne concentrations exceeding Immediately Dangerous to Life and Health (IDLH) conditions in the chlorine house, which is contiguous to the plant screen house. "Alert declared based upon HA3.1 - Report or detection of toxic gases within or contiguous to Table H-1 areas in concentrations that may result in an atmosphere Immediately Dangerous to Life and Health (IDLH)." The licensee will remain in the Alert until IDLH conditions have been terminated. An offsite HAZMAT team has been notified and is expected to be on-site today at 0630 CST to clean up the spill. The licensee will notify the Resident Inspectors. * * * UPDATE FROM JOHN DUBOSE TO VINCE KLCO AT 0932 EST ON 1/5/2021 * * * The licensee reports that the HAZMAT contractor has arrived on-site. Licensee personnel are preparing a clearance for the sodium hypochlorite system in order to support HAZMAT contractor work. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Valos) * * * UPDATE FROM DARRELL LAPCINSKI TO CHARLES TEAL AT 1634 EST ON 1/5/2012 * * * "The Alert declaration due to HA3.1, Report or detection of toxic gases within or contiguous to Table H-1 areas in concentrations that may result in an atmosphere Immediately Dangerous to Life and Health (IDHL): "Prairie Island terminated from the Alert declaration at 1408 CST on Jan 5, 2012. "The following additional conditions were established prior to termination: 1. The permanent berm containing the sodium hypochlorite released by 121 Sodium Hypochlorite Tank piping break was pumped down. 2. Clean-up and remediation of the affected area is in progress. 3. Inspection of the unaffected sodium hypochlorite tank piping has been conducted to ensure satisfactory integrity. "NRC Resident has been informed." Notified NRR EO (Ruland), R3DO (Valos), IRD (Morris), DHS (Beach), FEMA (Blankenship), DOE (Jackson), USDA (Timmons), and HHS (Fajardo). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-01-05
47568 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2012-01-04 | 2012-01-04 16:24 | 2012-01-04 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILED IN CLOSED POSITION The following information was received via facsimile: "On January 4, 2012, the licensee reported to the Agency [Texas Department of State Health Services, Inspection Unit, Radiation Branch] that it had had a gauge shutter fail in the closed position during a routine shutter test on an Xact Ray, Model 5310, which houses a 1,000 millicurie Americium-241 source. The gauge is on a machine that is not in service and the shutter is kept closed. When the licensee attempted to open the shutter for the routine check, it would not open. More information will be provide as it is obtained." Texas Incident #: I-8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2012-01-09
47567 | 0 | ATC NUCLEAR |  |  |  |  | 2012-01-02 07:00 | 2012-01-03 16:19 | 2012-03-26 | PART 21 REPORT - DEFECTIVE 48 VOLT DC SAFETY RELATED POWER SUPPLIES The following was received via fax: "ATC Nuclear has identified a design defect associated with power supplies provided through ATC Nuclear, Schenectady, NY. The defect was identified during Failure Mode Analysis following return of one of the units from the customer. The 48 VDC Power Supplies, PIN DA265A1879P00/ST were provided as safety related components to Entergy's Pilgrim Station under Purchase Orders 10240621, 10282296 and 10308991. Entergy's Pilgrim Station is currently the only station in possession of these items. The failures are exhibited as a spurious overvoltage shutdown condition when power is applied or a spurious overvoltage shutdown condition if the overvoltage circuit becomes contaminated with particulate or other material. The design defect is related to the specific silicon control rectifier used in the over voltage protection circuit. An extent of condition review is ongoing to determine if other power supplies provided under these three purchase orders are affected. Currently none of the other power supplies provided have exhibited this condition. "The affected serial numbers are: 90922-1, 90922-2, 90922-3, 91013-1, 91013-2, 91013-3 under purchase orders 10240621 and 10282296. "The affected serial numbers are: 110512-1, 110512-2, 110512-3, 110512-4, 110512-5 under purchase orders 10308991. "ATC does not have sufficient information to evaluate the safety significance of the defect because the quantities and locations of the power supplies currently in use is not known. "Information Contact: Ray Chalifoux ATC Nuclear (865) 384-0124." * * * UPDATE FROM CHALIFOUX TO KLCO ON 3/26/12 AT 0841 EDT VIA FAX * * * "ATC Nuclear has identified an additional defective lot of power supplies provided through ATC Nuclear, Schenectady, NY to Xcel Energy's Monticello Station under Purchase Order #00037345. The defects were identified during Failure Mode Analysis following return of twelve units from the customer. The additional affected 115 VDC Power Supplies, P/N DA265A1313P001/ST, Serial Numbers 110713-1 through 110713-12 also were found to contain design flaws in the overvoltage protection circuitry similar to the 48 VDC power supplies. A design change was implemented to resolve the defective overvoltage protection circuit and the defects were resolved. No other additional customers are affected. The customer had not placed the power supplies into service." Notified the R3DO (Stone) and the Part 21 Reactor Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2012-01-03
47566 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-01-03 04:00 | 2012-01-03 03:33 | 2012-01-04 | UNAVAILABILITY OF TECHNICAL SUPPORT CENTER VENTILATION DUE TO SCHEDULED MAINTENANCE "At 0400 EST on Tuesday, January 3, 2012, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1500 EST on Tuesday, January 3, 2012. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM BEN HUFFMAN TO DONALD NORWOOD AT 1645 EST ON 1/3/12 * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1644 EST on 1/3/12." The licensee notified the NRC Resident Inspector. Notified R3DO (Valos). * * * UPDATE AT 0546 EST ON 1/4/12 FROM ESSIG TO HUFFMAN * * * "UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO DAMPER FAILURE "This is an update to EN #47566. "At 2300 EST on Tuesday, January 3, 2012, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration system volume damper 12-HV-TSC-SD-6, TSC Ventilation Normal Flow to and from Air Conditioner HV-TSC-AC-1 Volume Damper, did not reposition during surveillance 12-OHP-5030-028-007 TSC Ventilation Filtration System Functional Test. When the damper position was checked, damper remained open with system in Emergency mode. Per 12-OHP-5030-028-007, if any damper fails to reposition, the ventilation unit is considered non-functional. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. TSC ventilation system maintenance had previously been performed to clean, inspect, and lubricate linkages associated with this damper on 1-3-2012. That work was completed at approximately 1700 EST on 1-3-2012. "Following discovery, maintenance was contacted and discovered the linkage was loose for 12-HV-TSC-SD-6. Maintenance adjusted the linkage and damper was retested satisfactory at 0311 EST on 1-4-2012. TSC functionality has been restored. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." R3DO (Valos) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2012-01-03
47565 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2012-01-01 04:06 | 2012-01-01 05:00 | 2012-01-01 | NOTICE OF UNUSUAL EVENT DUE TO A SECURITY INCIDENT At approximately 0335 EST security observed an unauthorized individual climb over the owner controlled area fence. Site security responded and contacted local law enforcement. At 0406 EST, the site declared a Notice of Unusual Event. After turning the individual over to law enforcement and conducting a complete check of the area, the Unusual Event was terminated at 0502 EST. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2012-01-01
47564 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-12-31 02:00 | 2011-12-31 11:53 | 2012-01-04 | FIRE BARRIER RATING OF VITAL SWTICHGEAR WALLS MAY NOT MEET STANDARDS "On December 31, 2011 at 0200 PST, a plant employee indentified the fire barrier material in each unit was potentially not qualified as a 3 hour rated fire barrier as specified by the Diablo Canyon power plant fire protection program. The fire barrier material in question is installed between the block wall portion of the barrier and the door frames in the walls separating three of the 480 Volt switchgear buses and separating the three vital instrument AC inverters. The condition was discovered by a plant employee who questioned the configuration while performing a routine tour of that area. Operators confirmed existing fire watches were in place and established additional fire watches as compensatory measures as required by the Diablo Canyon fire protection program. "A review of the Appendix R fire protection analysis is in progress to confirm the rating of the installed configuration. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM CRAIG HARVEY TO DONALD NORWOOD At 1955 EST on 1/4/2012 * * * "This is an update to EN 47564 reported on 12/31/11 where it was reported that plant personnel had identified rated fire barriers were not qualified as a three hour rated barrier as required by the DCPP Fire Protection Program. "On 1/3/12 plant personnel provided barrier design drawings to the manufacturer of the DCPP fireproofing material. The manufacturer reviewed the design detail and confirmed that the barrier design depicted on the drawing is qualified as a 3 hour barrier. Therefore no unanalyzed condition that significantly degraded plant safety existed. This event is being retracted. "The licensee notified the NRC Resident Inspector." Notified R4DO (Vasquez). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-31
47563 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-12-30 21:00 | 2011-12-30 22:00 | 2011-12-30 | PRESS RELEASE BY COUNTY CONCERNING ERRORS IN THE 2012 EMERGENCY PLANNING ZONE CALENDAR The licensee has received information from Oswego County Emergency Management Office concerning errors in the 2012 edition of the Oswego County Public Emergency Response Information Calendar. The 2012 calendar mailed to residents within the 10-mile emergency planning zone near the Fitzpatrick and Nine Mile Point nuclear power plants contains errors in the maps depicting the individual Emergency Response Planning Areas (ERPAS). Oswego County notes that while its partners in emergency planning for the nuclear power plants work on a permanent solution, residents should retain their 2011 calendars and refer to them for the correct ERPA information if an emergency at one of the plants occurs. The calendar is a joint effort between Constellation Energy Nuclear Group, Entergy Nuclear, the Oswego County Emergency Management Office, the Oswego County Department of Community Development, Tourism and Planning, and the New York State Office of Emergency Management. It contains guidelines for public response to radiological and other types of emergencies for people that live within ten miles of the nuclear facilities at Nine Mile Point. Oswego County plans to repost the 2011 calendars (which contain accurate emergency response planning area maps) on its website, www.oswegocounty.com/emo. The 2011 calendars should be available on the website no later than Tuesday, January 3, 2012. Anyone with questions may call the Oswego County Emergency Management Office at 315-591-9150 or 1-800-962-2792. The licensee is providing this information as a courtesy notification to the NRC since the press release is being issued by Oswego County and not by the licensee. The NRC Resident Inspector has been notified. See related notification from Fitzpatrick - EN #47562. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2011-12-30
47562 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-12-30 21:00 | 2011-12-30 21:15 | 2011-12-30 | PRESS RELEASE BY COUNTY CONCERNING ERRORS IN THE 2012 EMERGENCY PLANNING ZONE CALENDAR The licensee has received information from Oswego County Emergency Management Office concerning errors in the 2012 edition of the Oswego County Public Emergency Response Information Calendar. The 2012 calendar mailed to residents within the 10-mile emergency planning zone near the Fitzpatrick and Nine Mile Point nuclear power plants contains errors in the maps depicting the individual Emergency Response Planning Areas (ERPAS). Oswego County notes that while partners in emergency planning for the nuclear power plants work on a permanent solution, residents should retain their 2011 calendars and refer to them for the correct ERPA information if an emergency at one of the plants occurs. The calendar is a joint effort between Constellation Energy Nuclear Group, Entergy Nuclear, the Oswego County Emergency Management Office, the Oswego County Department of Community Development, Tourism and Planning, and the New York State Office of Emergency Management. It contains guidelines for public response to radiological and other types of emergencies for people that live within ten miles of the nuclear facilities at Fitzpatrick. Oswego County plans to repost the 2011 calendars (which contain accurate emergency response planning area maps) on its website, www.oswegocounty.com/emo. The 2011 calendars should be available on the website no later than Tuesday, January 3, 2012. Anyone with questions may call the Oswego County Emergency Management Office at 315-591-9150 or 1-800-962-2792. The licensee is providing this information as a courtesy notification to the NRC since the press release is being issued by Oswego County and not by the licensee. The NRC Resident Inspector has been notified. See related notification from Nine Mile Point - EN #47563. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2011-12-30
47561 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-12-29 20:09 | 2011-12-30 02:34 | 2011-12-30 | LPCI INSTRUMENTATION REQUIRED REPAIR AND RECALIBRATION "Surveillance testing on Low Pressure Coolant Injection (LPCI) Loop Select logic yielded results requiring repairs to 3 of the 4 Recirculation Riser Differential Pressure instruments and calibration of all four. The instrument conditions were such that there was not reasonable assurance that the safety function of LPCI could be fulfilled during a design basis Loss Of Coolant Accident (LOCA). As such, this condition is reportable under 10 CFR 50.72(b)(3)(v)(D). "The four instruments support the LPCI Loop Select logic by providing input that successfully identifies and directs LPCI flow to the unbroken recirculation loop so that core reflooding is accomplished in time to ensure that the fuel peak cladding temperature remains below the limits of 10CFR50.46. The instruments are arranged in a one-out-of-two-twice logic. "The instruments were last calibrated September 26-29, 2011. At that time, pre-planned maintenance was performed to improve instrument reliability. Current testing indicates a repetitive issue with instrument drift. Repair and recalibration of each degraded instrument has been completed as the surveillance test has progressed such that the current status supports fulfillment of the safety function. "The instrument type (Barton) is used in several safety systems, but there has been no notable degradation in other applications." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-12-30
47560 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-12-21 | 2011-12-29 17:41 | 2011-12-29 | AGREEMENT STATE REPORT - IODINE-125 BRACHYTHERAPY SEED MISSING FROM TRANSPORTATION PACKAGE The following report was received by telephone from the State of Nevada. A representative of the State of Nevada Radiation Control Program was notified by a call from Cardinal Health and Summerlin Hospital in Las Vegas NV concerning a missing I-125 brachytherapy seed. Summerlin Hospital on or about 12/21/11 transferred 33 Iodine-125 brachytherapy seeds to Cardinal Health for shipment back to Bard Brachytherapy in Illinois. The 33 Iodine-125 seed shipment was packaged and sent by Cardinal Health to Bard via commercial carrier on or about 12/21/11. Upon receipt of the seeds by Bard, the top of the shipping pig was discovered to not be completely sealed. Some of the seeds were outside the pig but within the shipping package. After all the seeds were inventoried, a total of 32 seeds were received by Bard. At this time, one of the seeds appears to be unaccounted for. The missing I-125 seed had an activity of 0.23 milliCuries at the time of shipment. The half-life of Iodine-125 is approximately 60 days. Bard has surveyed the local carrier that transported the shipment to its facility. It has also surveyed the regional facility of the shipping carrier. Cardinal Health and Summerlin are still attempting to confirm the original inventory of seeds was 33. The State of Nevada is continuing its investigation of the missing seed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2012-01-03
47559 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2011-12-28 | 2011-12-29 16:40 | 2011-12-29 | AGREEMENT STATE REPORT - TWO NUCLEAR GAUGES FOUND AT METAL RECYCLING FACILITY The following report was received from the State of Colorado Radioactive Material Unit via facsimile: "This memo is to serve as a preliminary report for an incident concerning fixed nuclear gauges which were discovered at a Colorado scrap yard which is not licensed for that type of material. The Department [State of Colorado] was notified on December 28, 2011 that two gauges were identified at Rocky Mountain Recycling in Commerce City, Colorado. The initial notification indicated that they were both TN 5100 gauges [subsequently determined to be TN 5200 gauges] with an original activity of 20 mCi in 1986. "Rocky Mountain Recycling currently has a Colorado provisional radioactive materials license (Colo. 9016-01) and is licensed for six sections of scrap pipe which are contaminated with NORM in the form of pipe scale. For normal operations, Rocky Mountain Recycling does not possess a radioactive materials license. "The Department responded to Rocky Mountain Recycling on December 29, 2011. Two fixed gauges were at that location, both TN Technologies model 5200 gauges with serial numbers B1130 and B1131. Both gauges contain Cs-137 (verified using an ldentiFinder). Gauge B1130 contains 20 mCi as of December, 1986 and gauge B1131 contains 20 mCi as of October, 1986. The gauges were being stored in a steel drum away from public access. A wipe test was taken in the field on the drum prior to opening and no contamination appeared to be present. Wipe tests were also taken on the shutters of both gauges and no contamination appeared to be present. Both gauges appeared to be in good shape, there was some rust and weathering on the outside of the source housing but otherwise the source housing and shielding appeared to be in working condition. "The gauges were found without a lock to keep the shutter in the closed position. One gauge (B1131) was found with the shutter partially opened. Gauge B1130 could not have the shutter completely opened due to the steel mounting frame being bent. Both shutters could be manipulated by hand. Rocky Mountain Recycling provided padlocks to lock the shutter in the closed position for both gauges. "Dose rate measurements were taken around the shielding of the gauges. On contact, both gauges measured approximately 2.5 mRem/hour. With the shutter open, the highest reading in the beam of gauge B1130 was approximately 60 mRem/hour on contact, 15-20 mRem/hour at approximately 1 foot, and 3-3.5 mRem/hour at approximately 1 meter. With the shutter open, the highest reading in the beam of gauge B1131 was approximately 70 mRem/hour on contact, 10 mRem/hour at approximately 1 foot, and 1.5 mRem/hour at approximately 1 meter. "Around the drum the gauges were stored in, the highest reading on contact was 1.5 mRem/hour, the highest reading at one foot was 0.3 mRem/hour, and the highest reading at 1 meter was 0.08 mRem/hour." Colorado Report Number: I11-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2012-01-03
47558 | 0 | ST. VINCENT HOSPITAL |  |  |  |  | 2011-12-29 09:00 | 2011-12-29 11:50 | 2011-12-29 | RADIOPHARMACEUTICAL PACKAGE RECEIVED WITH EXTERNAL CONTAMINATION The Radiation Safety Officer of St. Vincent Hospital reported that the facility received a radiopharmaceutical shipment of I-131 with excess surface contamination on the outside of the shipping container. When the surface of the shipping container was initially swipe tested, the contamination was measured at 734 dpm per 100 sq centimeters. A follow-up swipe survey pinpointed the contamination to just one side of the shipping container and was found to be 581 dpm per 100 sq centimeters. Additional isotopic analysis determined that the radioactive contaminant was I-131. Integrity of the package was not compromised. The inside of the shipping container was tested and found to be clean. The two I-131 vials in the container were also verified to be intact and clean. The hospital called the radiopharmaceutical supplier, Cardinal Health Systems of Indianapolis, to notify them of the contamination found on the package. The shipping container has been isolated in a controlled area at St. Vincent Hospital. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2011-12-29
47557 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-12-29 09:10 | 2011-12-29 10:59 | 2011-12-29 | PLANNED MAINTENANCE ON PLANT PROCESS COMPUTER "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC} to replace power supplies in the plant process computer (Link 2) will result in a loss of some SPDS indications for a duration of less than 5 hours. No other indications or annunciators will be unavailable during this maintenance to affect the plant's ability to assess or monitor an accident of transient in progress." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT AREBAUGH TO JOHN KNOKE AT 1146 EST ON 12/29/11 * * * At 1006 CST on 12/29/11 the plant process computer (Link 2) was successfully restored and SPDS is functioning properly and returned to service. The licensee has notified the NRC Resident Inspector. Notified R3DO (Duncan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-29
47556 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-12-28 22:30 | 2011-12-29 02:00 | 2011-12-29 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY DUE TO A DISCHARGE INTO THE DELAWARE RIVER "At 2209 EST on 12/28/11 following a planned station service water (SSW) pump swap, a motor operated valve (MOV) failed to close in a water treatment system for the SSW pump that was secured. This was discovered shortly after the pump was removed from service by the field operators. The control room was notified at 2230 EST of the issue and ongoing efforts to troubleshoot and correct the malfunction. The release was terminated by closing a manual isolation valve at 2240 EST. This malfunction resulted in the discharge of approximately 17 gallons of 15% sodium hypochlorite (product) to the idle SSW pump intake which communicates with the Delaware river, The idle SSW pump was restarted at 2240 EST thus withdrawing all residual product from the intake and directing it to plant treatment systems (dechlorination on the cooling tower outfall). A sample was obtained from the Delaware river just outside the intake structure and there was no detectable chlorine in the sample and there were no abnormal conditions noted on the river. Based on Environmental Licensing review, this is reportable to the state of NJDEP [New Jersey Department of Environmental Protection] within 2 hours. The report to the state was initiated at 0017 EST on 12/29/11. "The HC Senior NRC Resident has been informed. Affected systems are limited to the Station Service Water (SSW) system and the Sodium Hypochlorite water treatment system. There were no actuations or initiating signals. There was no impact on plant operations and these systems remain fully operable. The failure was limited to the MOV which has been isolated via a manual valve. There was nothing unusual or not understood. All safety related equipment continues to function as required. There were no injuries or reported wildlife impact." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-12-29
47555 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2011-12-05 14:15 | 2011-12-28 12:05 | 2011-12-28 | AGREEMENT STATE REPORT - DAMAGED TRITIUM EXIT SIGN "Per the general license requirements stipulated in 10 CFR 31.5 (5), this letter is being sent to report a damaged Forever Lite model SLXTU1GB20 self-illuminating exit sign and the loss of one of its elements. The exit sign is owned by the Johns Hopkins University Applied Physics Laboratory (JHU/APL) and is possessed under a general license issued by the Nuclear Regulatory Commission (NRC). The general license requires the NRC to be notified of any damaged devices. A verbal notification was made to MDE [Maryland Department of the Environment] in a phone call on December 6, 2001 at 1:45 PM. "It has been determined that the damaged sign was removed from its mounted location during the demolition phase of a renovation project in Building 13 that started in May 2011. However, it along with three other signs from that project were not brought to JHU/APL's Hazardous Waste Accumulation Site (Building 10A) until Friday, December 2, 2011. The damaged sign was identified Monday, December 5, 2011 at 2:15 PM. It appears that the sign was damaged during removal from its mounted location and the missing element, along with the outer frame, was disposed of in the construction debris earlier this summer. "The total estimated tritium activity contained within the missing element is approximately 640 mCi of which about 90% (576 mCi) may be in the form of tritium gas and about 10% (64 mCi) may be in the form of tritiated water vapor. Contamination monitoring did not reveal any tritium contamination. This could be an indication that the tube did not break during the removal of the sign nor when it was caught up in the construction debris. Bioassay sampling of the potentially exposed personnel is unfortunately not possible due to the amount of time that has transpired since the removal of the sign (the most likely time when an exposure could have occurred). However, the possibility of an exposure is extremely unlikely since there is no indication of a broken element. In addition, the nature of a construction work environment and the use of personal protective equipment (work gloves, eyewear, ...) also minimizes the possibility of inhalation, ingestion and puncture wounds which are potential tritium exposure pathways from a broken element. "The damaged sign has been doubly sealed in plastic bags and is stored in JHU/APL's Hazardous Waste Accumulation Site awaiting proper disposal. "JHU/APL improved its control and oversight of the self-illuminating exit sign after the last damaged sign that was found in June 2007. Based on the current investigation, the following improvements will be made to improve JHU/APL control and accountability of the generally licensed exit signs: --Annual refresher training with revised self-illuminating exit sign handling and control procedures will be provided to all JHU/APL Technical Service Department (TSD) personnel. This will help ensure a greater awareness, particularly among managers and supervisors, of the handling and control requirements. Training up to this point has been provided to maintenance personnel, electricians and others on an as needed basis. --The training will place particular emphasis on the care required to remove these signs and the need to bring them to JHU/APL's Hazardous Waste Accumulation Site in a timely manner. --For better documentation of which signs are being turned in for disposal, a log will be maintained that documents such things as make, model serial number, former mount location (Bldg, Floor ...), person disposing the sign, date disposed, and the general condition of the sign. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2012-01-02
47554 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-12-27 08:00 | 2011-12-27 12:57 | 2011-12-27 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER MISSING The following information was received via email from the State of Iowa: "The RSO of Louisa Generating Station/MidAmerican located at 8602 172nd Street, Muscatine, Iowa 52761 reported to IDPH [Iowa Department of Public Health] at 0930 CST that at approximately 0800 [CST], the courtyard operator was performing rounds and noticed that the shutter on a Texas Nuclear device (model # 5192, serial # B-2724, 50 mCi, Cesium 137) in crusher feeder / hopper 1B was detached from the device and laying on the grating directly underneath the device. [The RSO] suspects that the shutter vibrated off. The shutter is usually in the open position as the hopper is operational 24/7 measuring coal as it moves through the hopper. There were no employees in the hopper and the device sits 10-12 feet above the ground. After [IDPH spoke] with [the RSO] and considering their license conditions, [the RSO] is calling the service provider to come to their location and assess the repositioning of the shutter." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-12-30
47553 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-12-26 12:50 | 2011-12-26 16:00 | 2011-12-26 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - SAFETY RELIEF VALVE DECLARED INOPERABLE "On Monday, December 26, 2011, at 1250 hours, with the reactor at 100% core thermal power, the station entered a 24-hour action statement to initiate a controlled shutdown and be less than 104 psig reactor pressure due to suspected leakage across the first stage of safety relief valve (SRV) RV-203-3D and subsequent declaration of the SRV inoperable due to criteria specified in Pilgrim plant procedure 2.2.23. "As background; the Pressure Relief System includes four (4) SRVs and two (2) spring safety valves (SSVs). The SRVs discharge through their individual discharge piping, terminating below the minimum suppression pool (torus) water level. The four SRVs and the two SSVs are installed on the Main Steam piping in containment between the reactor pressure vessel and the flow restrictors. "While at full power, indication of a steam leak across the first stage pilot of RV-203-3D was determined in accordance with criteria specified in procedure 2.2.23. Specifically, the SRV is inoperable if the pilot stage thermocouple temperature is 35 degrees F below its baseline temperature (with a lower decrease at the 2nd stage thermocouple) and cannot he explained by a corresponding downpower. The safety relief valve was subsequently declared inoperable and the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.6.D was entered. Due to the valve being declared inoperable, the station is required to be shutdown and reactor coolant pressure below 104 prig within 24 hours per T.S. 3.6.D.2. "Currently, preparations are being completed to conduct the reactor shutdown and to initiate safety relief valve repairs. "This event had no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-12-26
47552 | 0 | NIKE IHM, INC. |  |  |  |  | 2011-09-15 | 2011-12-24 20:36 | 2011-12-24 | LOSS OF CONTROL OF GENERAL LICENSED MATERIAL On August 1, 2011, the licensee removed an Ohmart Measurex Thickness Gauge from service. The gauge contained a Strontium-90 source which had an activity level in 1995 of 100 millicuries. On August 9, 2011, the radioactive source was removed from the gauge by Industrial Maintenance Engineering, Inc., an NRC licensed company. The source was then secured in a DOT-specification steel drum and sealed with a tamper-indicating device placed over the closure ring on the drum lid. The gauge was sold to HGR Industrial Surplus, Inc., a used industrial equipment vendor, who arranged for pick-up at Nike's facility and transportation to its warehouse in Euclid, Ohio. HGR Industrial Surplus, Inc. does not hold an NRC or an agreement state radioactive material license. On September 15, 2011, the gauge and containerized source were transported to HGR's warehouse. During the week of December 19, 2011, it was discovered that the source was not at the Nike facility. It was determined that the containerized source had been shipped with the gauge to HGR. HGR was immediately contacted by telephone. HGR confirmed that it had the containerized source and that the container had not been opened. The tamper indicating device was still on the closure ring and was still intact. HGR was instructed to not open the container and to place the container in a controlled access area until Nike could arrange return transportation to its facility. Nike has arranged for RM Wester and Associates, an NRC-licensed company, to retrieve the containerized source. RM Wester representatives will go to the HGR warehouse, prepare the source container for shipping and arrange shipping back to their facility where it will be recycled or disposed of appropriately. This is expected to occur during the week of December 25, 2011. Nike is conducting an investigation of this incident to determine root causes and will implement appropriate corrective actions to ensure that this does not happen again. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-12-24
47551 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-12-23 16:20 | 2011-12-23 16:54 | 2011-12-23 | ALERT DECLARED DUE TO HALON DISCHARGE DURING TESTING The licensee declared an alert condition based on the inadvertent discharge of Halon gas into their Emergency Bus Room during system testing. Plant operation was unaffected and the unit continued to operate at full power. There were no injuries or equipment damage due to the event. The licensee observed no fire or flames in the area. The licensee evacuated the area and provided ventilation to disperse the Halon. The licensee notified the NRC Resident Inspector. Also notified HHS (Jewel Wright). * * * UPDATE FROM BRIAN WALDSMITH TO DONALD NORWOOD ON 12/23/11 AT 1822 EST * * * At 1810 EST on 12/23/11, Robinson terminated the Alert condition based on a return to a habitable atmosphere in the Emergency Bus Room. "The cause for the Halon System actuation appears to have been a Human Performance Error. The test/inhibit switch was placed in the incorrect position." "There were no radiological releases for this event." The licensee notified state, local and other governmental agencies concerning this event. Notified R2DO (McCoy), NRR EO (Giitter), IR (Gott), DHS SWO (Arnold), FEMA (O'Connell), DOE (Jackson), USDA (Walters), and HHS(Wright). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 2 | SC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-12-23
47550 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2011-12-23 05:00 | 2011-12-23 15:18 | 2011-12-23 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE "At 0500 PST 12/23/2011, ERDS communication VPN (Virtual Private Network) link with the NRC was interrupted during an automatic swap between computer servers. "Restoration of the communication link is expected to be restored by 1430 PST." The licensee will notify the NRC Resident Inspector. | 0 | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-23
47549 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2011-12-23 06:10 | 2011-12-23 10:10 | 2011-12-23 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "At 0610 CST on 12/23/2011 with the reactor at 100% power, River Bend Station experienced an [automatic] reactor scram resulting from a RPS actuation. Following the scram, reactor water level briefly lowered below level 3, resulting in the automatic closure of containment isolation valves in the suppression pool cooling system. This isolation was confirmed to have occurred as designed. The reactor is stable with pressure and temperature being controlled by the feed water system and main steam bypass valves, respectively. The cause of the scram was due to a turbine trip. Initial indications are that the turbine tripped due to a loss speed sensor. All control rods inserted and Reactor Core Isolation Cooling was manually operated for approximately 1 minute and secured, "The plant is conducting causal investigations to fully understand the cause of the turbine trip. As information becomes available River Bend Station will provide additional information. "This event is being reported in accordance with 10CFR50.72(b)(iv)(B) as an automatic RPS actuation with the reactor critical." The safety relief valves momentarily lifted immediately following the scram. The plant electrical distribution system is in a normal shutdown configuration. The scram was uncomplicated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-12-23
47548 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-12-22 22:00 | 2011-12-23 09:41 | 2011-12-23 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECT AND RECOVERY The following information was received by e-mail: "On December 22, 2011, at 2102 hours, the Agency was notified by Harris County Hazmat that a radiography truck had been involved in an accident. The truck was carrying a Spec 150 camera serial # 153 containing a 32 curie Iridium 192 source. The radiographer informed the Hazmat officer that the source in the camera was not in the locked position. The radiographer stated that the source had separated from the drive cable and he had used a pair of pliers to insert the source into the camera backwards to shield it. The camera opening for the guide tube connection was covered with duct tape to prevent the source from coming out of the camera. The radiographer could not get the crank out device to separate from the camera so the camera and the crank out devices were placed between the transport container and the darkroom wall to transport them back to the storage location. The accident caused the source to move further to the back of the 'S' tube in the camera and the dose rates from the camera increased slightly. The crank out device was used to push the source back to the shielded position. Lead sheets were placed above the camera to help decrease the dose rates from the camera. The dose rates at this point were between two and four millirem at one meter. The radiographer took the camera and source to the licensee's storage location. The source was removed from the radiography camera and placed in a source changer shield. The radiographer stated that he had received 180 millirem for the event. No member of the general public received exposure due to this event. The licensee will return the source and camera to the manufacturer for inspection. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-12-28
47547 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-11-07 22:31 | 2011-12-23 03:03 | 2011-12-23 | INVALID SPECIFIED SYSTEM ACTUATION DUE TO A POSSIBLE FAULTY TEMPERATURE SWITCH "This 60-day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation signal affecting containment isolation valves in more than one system. "On November 7, 2011, Nine Mile Point Unit 2 (NMP2) received a Division 2 reactor building pipe chase high ambient temperature isolation signal, which resulted in closure of isolation valves in the reactor water cleanup (RWCU) system, the reactor core isolation cooling (RCIC) system, and the residual heat removal (RHR) system (isolation valve groups 5, 6, 7, and 10). All affected isolation valves responded as designed. "The Division reactor building pipe chase high ambient temperature isolation signal was generated by a new NUS/Scientech ambient temperature indicating switch that had recently been installed as a replacement for the original Riley temperature switch, which is no longer being manufactured. Two temperature switches (one for Division 1 and one for Division 2) monitor the reactor building pipe chase area to detect a rise in area temperature, which is indicative of a leak in the RWCU, RCIC, or RHR system piping that exists in the area. At the time of the event, operations personnel confirmed that conditions requiring isolation of the RWCU, RCIC, and RHR systems did not exist, based on a check of the Division 1 reactor building pipe chase high ambient temperature channel and area radiation monitors. Therefore, the isolation signal was determined to be invalid. The NUS/Scientech temperature switch was subsequently removed and the original Riley temperature switch was re-installed. The apparent cause for generation of the trip signal from the new temperature indicating switch was determined to be the presence of signal noise that was not adequately filtered. "This event was entered into the [Nine Mile Point] corrective action system as Condition Report (CR) 2011-010062. There were no safety consequences or impact on the health and safety of the public as a result of this event." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-12-23
47546 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-12-22 10:00 | 2011-12-22 09:56 | 2011-12-23 | TECHNICAL SUPPORT CENTER VENTILATION UNAVAILABLE DUE TO PREPLANNED MAINTENANCE "On December 22, 2011, at 1000 EST, due to pre-planned refueling outage maintenance, the Control Room Emergency Ventilation system on St. Lucie Unit 1 is inoperable. The Unit 1 Control Room Emergency Ventilation system provides filtered air to the Technical Support Center (TSC) ventilation system, therefore, the TSC ventilation system has been rendered unavailable during the course of the work activities. The Control Room Emergency Ventilation system is expected to be returned to service in 38 hours, and TSC filtered ventilation restored. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Should the TSC become uninhabitable, the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the Control Room Emergency Ventilation system has been restored to normal operation. The NRC Resident Inspector has been notified." Unit 1 is currently de-fueled. * * * UPDATE FROM CHUCK MONTANA TO VINCE KLCO AT 0459 EST ON 12/23/2011* * * "Update 12/23/2011, 0418 EST: The U1 Control Room Emergency Ventilation has been restored to operable [status] and the TSC filtered ventilation has been restored [to operable status]." The licensee notified the NRC Resident Inspector. Notified the R2DO (McCoy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-22
47545 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2011-12-21 13:59 | 2011-12-21 21:37 | 2012-02-15 | GROUNDWATER LEVEL MAY EXCEED DESIGN ASSUMPTIONS "On December 21, 2011, at 1359 hours EST, it was determined that the test instruction for the weekly groundwater level readings contained non-conservative acceptance criteria. The test instruction acceptance criteria for groundwater level exceeds the initial assumptions used in the Updated Safety Analysis Report (USAR) Chapter 15 accident analysis for 'Postulated Radioactive Releases due to Liquid Containing Tank Failures.' The issue was identified during the conduct of a prompt functionality assessment evaluating the plant underdrain system performance and to ensure all USAR described functions were being met. "The test instruction acceptance criteria is less than 575 feet. The calculation supporting the Chapter 15 accident analysis assumes an initial groundwater elevation of 568 feet in order to accumulate a sufficient volume of groundwater to dilute the tank inventory prior to exiting the underdrain system. The accumulation volume results in hold up time allowing for mixing and radioactive decay. With the degraded performance of the underdrain system pumps and high precipitation, the groundwater level had risen above 568 feet but was still less than 575 feet. A preliminary engineering evaluation has determined that significant margin exists in the calculation. A calculation revision is being pursued in parallel with this notification. "Compensatory actions involving the repair of 1 permanent non-safety pump and installation of temporary pumps were previously initiated and the groundwater levels are decreasing. Restoration of the remaining permanent plant pumps continues. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 2/15/12 AT 1315 EST FROM LLOYD ZERR TO ERIC SIMPSON * * * "The calculation supporting the USAR Chapter 15 accident analysis was reviewed and subsequently revised. The revised calculation verifies an initial groundwater elevation of 575 feet is consistent with the preliminary assessment that substantial margin existed in the calculation for the underdrain system. Because the condition reported in Event Number 47545 was not an event or condition that results in the nuclear power plant being in an unanalyzed condition that degrades safety, the condition is not reportable, and this notification is retracted. The evaluation for this condition is documented in condition report 2011-07169." The NRC Resident Inspector and R3DO (Passehl) were notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-21
47544 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-21 17:57 | 2011-12-21 19:56 | 2011-12-21 | UNUSUAL EVENT - HYDROGEN LEAK IN TURBINE BUILDING "At 1641 CST, during preparations to synchronize the generator, hydrogen pressure began to lower. Personnel were dispatched to identify the source of the leak. At 1752 CST reports from personnel in the turbine building identified high hydrogen levels and the turbine building was evacuated. An Unusual Event [HU7] was declared at 1757 CST and state notification was completed at 1809 CST. Turbine building roof vents were opened to ventilate the turbine building and all elevations were verified to be clear of hydrogen. Access to the turbine building was restored. "The Unusual Event was terminated at 1838 CST." The licensee has notified the NRC Resident Inspector. | 18 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-12-21
47543 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-12-21 12:00 | 2011-12-21 15:38 | 2011-12-21 | PLANT COMPUTER CALCULATION INCORRECT FOR BACK-UP METEOROLOGICAL DATA "During specification review of the computer points for the Monticello Nuclear Generating Plant backup meteorological tower (MET), it was identified by the station that the computer program software for the backup MET had not calculated the correct 15 minute average wind direction in all instances, A review and analysis of the historical data revealed that there were times that this condition existed when the site's primary MET had been out-of-service for maintenance or equipment issues. During those times the backup MET was relied on for determination of wind direction. Analysis determined that during those times the potential existed to incorrectly report affected sectors for Protective Action Recommendations. "Currently the station's primary MET has been verified to be in service and functioning properly. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-21
47542 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-12-21 15:15 | 2011-12-21 15:38 | 2011-12-21 | OFFSITE NOTIFICATION DUE TO WATER SAMPLE TESTING POSITIVE FOR LOW LEVEL OF TRITIUM "On December 20, 2011, Vermont Yankee (VY) was notified by its vendor laboratory that a water sample, taken from the Connecticut River on November 3, 2011, tested positive for a low level of tritium [1120 pCi/L]. This report is being made in accordance with 10 CFR50.72(b)(2)(xi) since VY is notifying government agencies and issuing a press release. The VY Off-Site Dose Calculation Manual contains effluent dose calculations that account for groundwater releases of this type. There is no impact on public health and safety as a result of this event." The licensee has notified the NRC Resident Inspector and the state of Vermont. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-12-21
47541 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2011-12-21 09:30 | 2011-12-21 11:52 | 2012-08-09 | OFFSITE NOTIFICATION FOR DETECTABLE LEVELS OF TRITIUM IN GROUNDWATER WELL "On Tuesday, December 20, 2011, technicians discovered detectable levels of tritium in an onsite groundwater well. The measured concentration of the isotope was approximately 48,000 picocuries per liter. This discovery was made during the conduct of the site's ongoing groundwater monitoring program. "The tritium concentration in the well sample exceeds the EPA established threshold for drinking water of 20,000 picocuries per liter. However, no groundwater wells on the River Bend site are used for drinking water. There has been no tritium identified in any wells downstream of, or surrounding, the affected well. "This test result does not indicate any threat to public health or safety, since the affected well is only used for groundwater monitoring, and not drinking water. Other onsite wells in the area were tested and will continue to be tested to ensure the tritium is not migrating offsite. The monitoring of the wells in the area immediately surrounding the affected well will be increased to a monthly frequency. "Voluntary notification of this discovery has been made to local and state governmental agencies, with the initial notification being made at 0930 CST today. This event is being voluntarily reported in accordance with 10CFR50.72(b)(2)(xi) as a condition related to health and safety of the public and onsite personnel for which a news release is planned." The licensee has notified the NRC Resident Inspector, state and local agencies and will be releasing information to the media. * * * UPDATE FROM DANNY WILLIAMSON TO JOHN KNOKE AT 1518 EDT ON 08/09/12 * * * "On August 7, 2012, one of the six new groundwater monitoring wells installed near the monitoring well which yielded the positive results on December 20, 2011, produced a groundwater sample containing 432,733 picocuries per liter of tritium. The investigation of the groundwater tritium activity is still ongoing, and the installation of these wells is part of that effort to determine the source. "The NRC Resident Inspector has been notified and officials with the Louisiana Department of Environmental Quality will be briefed." Notified R4DO (Michael Vasquez) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-12-21
47540 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-12-21 00:46 | 2011-12-21 06:14 | 2012-02-06 | BOTH UNIT TWO SECONDARY CONTAINMENT DOORS WERE INADVERTENTLY LEFT OPEN "On 12/21/11 at 0046 Secondary Containment integrity was lost when both U2 Reactor Building interlock doors were open simultaneously. Interlock door electrical checks were in progress. TS LCORA 3.6.4.1.Condition A was entered. Reactor Building differential pressure remained within Tech Spec limits. The doors were both open for approximately 9 seconds. "The cause of the event is being investigated." The NRC Resident Inspector has been notified. The State of Illinois Inspector will be notified. * * * RETRACTION FROM KATHARINE NETEMEYER TO CHARLES TEAL ON 2/6/12 AT 1243 EST * * * "On 12/21/2011, EN 47540 was made describing a condition where secondary containment was declared inoperable due to not meeting the surveillance requirement for having one access door closed. This was reported as a loss of safety function for the secondary containment. This condition occurred during a planned maintenance activity. "During a maintenance activity both doors unexpectedly opened. As a part of the maintenance, the inner door was opened by maintenance personnel using the normal control pushbutton. Upon personnel observing the outer door opening, the inner door button was released and the functional door automatically closed. Although both doors were briefly open, the negative pressure required to ensure secondary containment integrity was maintained at all times. Based on the door immediately closing and negative pressure being maintained, this is not considered a loss of safety function. Therefore this EN is being retracted." The NRC Resident Inspector has been notified. Notified R3DO (Giessner). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2011-12-21
47539 | -1 | DRESSER CONSOLIDATED |  |  |  |  | 2011-12-20 | 2011-12-20 14:26 | 2012-03-19 | PART 21 - CAPACITY FAILURE OF PRESSURE RELIEF VALVE The following information was received via facsimile: "A potential issue exists involving Dresser's pressure relief device model 1982. The Part 21 investigation was initiated because of a nameplate capacity failure during National Board certification testing. The Dresser model 1982 pressure relief device is used for system overpressure protection. Dresser's engineering and quality assurance departments are currently working to identify the root cause of this capacity failure and to determine if the equipment is being used in safety related applications subject to 10 CFR Part 21. Should it be determined that the equipment at issue is being used in safety related applications, a notification will be provided in accordance with the requirements of 10 CFR Part 21." * * * UPDATE AT 1431 EST ON 1/9/12 FROM PHILIP WALTZ TO HUFFMAN VIA FACSIMILE * * * The following is a summary of an interim report on this issue: "During the investigation process of 10 CFR Part 21, File No. 2011-02, in accordance with 10 CFR Part 21, GE Dresser has not been able to obtain the required flow capacity and does not have the required information regarding the system to determine the required flow capacity of the valve in question. "We have completed a Transfer of Information in accordance with 10 CFR Part 21.21 (b) to Entertech and Exelon to assist in the determination of Part 21 reportability. "The Transfer of Information letter [below] has been sent to Enertech and Exelon. "GE Dresser supplied a pressure relief valve dedicated as ASME Section VIII Safety Related to Enertech, which was then sold to Exelon and installed at the Dresden Nuclear Power Station, Unit 2. As a result of an investigation of the effect of outlet piping on the flow capacity of similar pressure relief valves it was noted that the pressure relief valve installed at Dresden, Unit 2 may not relieve its ASME certified flow capacity when installed with outlet piping. In order to determine if a reportable condition exists, the flow capacity provided by a pressure relief valve to prevent the protected system from exceeding a pressure 10% greater than systems design pressure is required. GE Dresser has not been able to obtain the required flow capacity and does not have the required information regarding the system to determine the required flow capacity. As such GE Dresser cannot determine if the identified deviation from technical requirements would create a reportable condition within the requirements of 10CFR Part 21. GE Dresser provides this Transfer of Information, in accordance with 10 CFR Part 21.21(b) to Enertech and Exelon to assist in the determination of Part 21 reportability." NRC R3DO (Orth) and R4DO (Lantz) have been notified. The NRC Part 21 Group has been sent a copy of this interim report. * * * RETRACTION AT 1315 ON 3/19/2012 FROM WILLIAM ALEXANDER TO MARK ABRAMOVITZ * * * The following report was received via fax: "During the investigation process of 10 CFR Part 21 File No. 2011-02, in accordance with 10CFR Part 21, GE Dresser was not able to obtain the required flow capacity and did not have the required information regarding the system to determine the required flow capacity of the valve in question. "We completed a Transfer of Information in accordance with 10CFR Part 21.21(b) to Enertech and Exelon to assist in the determination of Part 21 reportability. This information was attached to our previous Transfer of Information letter. "We have received updated information from Entertech and Exelon. Upon receiving 10CFR Part 21 notification from Dresser, Dresden Design Engineering performed an evaluation and has concluded that their system will produce a flow, for this valve, much less than the minimum flow valve determined by test of a representative valve. Upon receipt of system flow capacity from Dresden, GE Dresser's Engineering department has confirmed the valve in question will operate according to Dresden requirements. "The above information clears the one valve which was in question for this 10 CFR Part 21 reportable. "GE Dresser is filing this retraction letter to state we do not have a reportable issue involving a pressure relief device type 1982 valve and therefore closing our 10CFR Part 21 File No. 2011-02." Notified the R3DO (Kunowski) and Part-21 Group (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-12-20
47538 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-12-20 14:00 | 2011-12-20 15:01 | 2011-12-20 | UNPLANNED CONTAMINATION DUE TO MEDICAL TRANSPORT OFFSITE "An employee was complaining of chest pains this morning about 0830 CST. The plant nurse evaluated the employee and concurred with a decision to transport the employee to a regional hospital. The employee was transferred to a regional hospital while wearing his plant clothing. Contamination was present on the employees clothing. There was 2,250 dpm on a small area on the back pocket. The coveralls were collected and placed in a plastic bag at the hospital. The gurney, ambulance, and hospital facility was surveyed and no contamination was detected. "The employee's plant clothing was returned to the plant for disposal." Contamination was from uranium ore concentrates. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-12-20
47537 | 0 | USEC |  |  |  |  | 2011-12-20 | 2011-12-20 14:22 | 2011-12-20 | PART 21 - UF6 ACCUMULATOR TANK HAD THROUGH WALL CRACKS THAT CAUSED LEAKAGE The following information was received via facsimile: "On October 26, 2011, the discovery of two (2) defects (cracks) was identified on the north head of the Building C-310A side accumulator vessel. The accumulator is a tank used to provide a storage volume for liquid Uranium Hexafluoride (UF6) during the product withdrawal process, and it can hold up to 20,000 pounds of UF6 liquid. The defects in the 48" UF6 side accumulator allowed a small release of material which produced a process gas leak detection alarm on October 21, 2011 "Investigation to determine the cause of the cracks has revealed that the base metal contained stress defects which allowed multiple cracks to form with some of the cracks penetrating through the outer wall causing the vessel to leak. These cracks were a result of fabrication deficiencies and not the use of the vessel. There are nine (9) similar basic components used in Buildings C-310 and C-315. However, the other nine (9) vessels were not manufactured by Westerman Companies, the firm which designed and fabricated the defective vessel. "The C-310A side accumulator has been repaired by cutting out the area of the defect extending into the unaffected areas of the base metal in accordance with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1. USEC held a meeting with a representative of Westerman Companies on November 22. 2011, to discuss the defect." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MD | OTH | PAR | 21.21 |  |  |  | 0 | 2011-12-21
47536 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-12-19 | 2011-12-20 13:07 | 2011-12-20 | AGREEMENT STATE REPORT - SCRAP METAL FACILITY REJECTED LOAD The following information was provided by the state via email: "Nucor-Yamato Steel in Blytheville, Arkansas reported to the Arkansas Radiation Control Program on December 19, 2011, that a sealed source containing radioactive material had been found in a load of scrap metal received at their facility. The broker for this load of scrap metal was The David J. Joseph Company. The load of scrap originated in Louisiana. "Survey readings on contact with the source using a sodium iodide detector were 1.0 mR/hr. Smears taken and counted using a thin window GM detector in the field indicates that the source does not appear to be leaking. "The source has a glass covered flange end approximately 1.125" diameter, with a fitting on the back side of approximately 0.5" diameter. Overall length is approximately 1.0". No identifying marks have been found at this time. "The source was contained within a small can, secured within a locked storage room. The steel mill is awaiting a consultant to pick-up, identify and dispose of the source." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2011-12-23
47535 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-12-19 11:30 | 2011-12-20 08:14 | 2011-12-20 | AGREEMENT STATE REPORT - SHUTTER FAILURE ON OHMART SH-100 PROCESS GAUGE "At 11:30 AM December 19, 2011, the licensee's radiation safety officer provided a 24-hour telephone report notification of a shutter failure on a gauge. The gauge involved was an Ohmart SH-100, serial number 70230, containing 10 mCi of CS-137, with an assay date of Aug 1981. The shutter mechanism is a lead block screwed to a sliding aluminum plate. The licensee was removing the gauge from its mounting to replace it with a different new gauge as permitted by their license. When the licensee removed the gauge from its mounting, the lead block separated from the aluminum plate. The licensee replaced the lead shielding and secured it in place. The licensee secured the gauge from unauthorized access and will return it to the manufacturer for disposal with other gauges they are replacing. The licensee states that no personnel received radiation doses during this event." Ohio Report #OH110005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2011-12-23
47534 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-12-19 16:44 | 2011-12-19 17:25 | 2011-12-19 | OFFSITE NOTIFICATION DUE TO TRITIUM LEVELS EXCEEDING THRESHOLD FOR DRINKING WATER "At 1644 EST, on 12/19/11, TVA's Sequoyah Nuclear Plant made voluntary offsite notifications to the Tennessee Radiological Health Department Director and the Tennessee Department of Environmental Conservation - Senior Director Water Programs, to inform them of the following: "On October 31, 2011, Sequoyah proactively installed two new groundwater monitoring wells in an area known to have contained previously reported releases of tritium in an effort to further characterize and validate the scope of the plume. These releases were reported in 2006 as part of NEI's [Nuclear Energy Institute] groundwater initiative. On December 16, 2011, elevated levels of tritium were identified in water samples taken from one new onsite monitoring well. The tritium levels were confirmed to be greater than 20,000 pCi/L which is the threshold for drinking water. No groundwater monitoring wells are used for drinking or irrigation purposes onsite. The highest level sampled was 22,760 pCi/L. "Samples taken in the discharge channel located 30 yards from this groundwater monitoring well confirmed no detectable tritium. Refueling Water Storage Tank levels are being monitored and no active leak is in progress. Samples of adjacent wells have been taken and confirmed no unexpected changes in tritium levels of these wells. Additionally, Sequoyah has sampled at the station discharge to the Tennessee River and confirmed no detectable levels in any sample. "In a conservative decision making process and in accordance with the groundwater protection initiative established by the nuclear industry, Sequoyah is voluntarily communicating sample results likely attributed to a previously reported tritium spill. The plant is continuing to review the sample results to confirm this is related to the historical tritium plume. The plant will take appropriate actions as outlined in the Groundwater Tritium Action Plan, which has been initiated to address this issue. Sequoyah Nuclear Plant has had an extensive groundwater monitoring program in place since 2008. The environmental sampling program consists of sixteen groundwater wells which are periodically sampled in accordance with industry standards. "The NRC Resident Inspector has been notified. The following agencies have been, or will be updated: Hamilton County, State of Tennessee, Nuclear Energy Institute and American Nuclear Insurers. Tennessee Valley Authority plans a media notification for this issue." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-12-19
47533 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-18 09:30 | 2011-12-18 18:08 | 2011-12-18 | LOSS OF RHR COOLING DUE TO INCORRECT REACTOR WATER LEVEL INDICATION "On 12/18/11 at approximately 0930 CST, with the plant in Mode 4, while Operations was lowering reactor water level as part of restoration activities following the Reactor Pressure Vessel hydrostatic test, an automatic reactor scram and Residual Heat Removal (RHR) 'A' pump trip occurred due to a valid Reactor Water Level Low (Level 3) signal. The cause of the low level appears to be due a significant disparity between the Upset and Shutdown Range level instrumentation and the Level 3 RPS [Reactor Protection System] instrumentation. No rod motion occurred during the reactor scram as all control rods were fully inserted at the time of the event. Operations immediately entered the station off-normal procedures for Loss of Shutdown Cooling and Reactor Scram. The 'A' RHR pump was restored at 0956 CST. Reactor coolant temperature increased from approximately 128.7 deg F to 131.7 deg F during the event. At 1112 CST, the scram was reset and at 1216 CST, the off-normal procedures were exited. "Following the event as part of trouble shooting, maintenance personnel performed a fill and vent of reactor water level transmitter, 1B21N027. At the completion of this fill and vent, indicated water level changed from 195" to 86" on Shutdown Range and from off-scale high (>180") to 103"on Upset Range. No change in other reactor water level indication was observed. "This event is reportable under 10 CFR 50.72 (b)(3)(v)(B), as an event or condition that could have prevented the fulfillment of a safety function needed to remove residual heat, and 10 CFR 50.72 (b)(3)(iv)(A), event or condition that results in a valid actuation of the reactor protection system (RPS)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT RHR INOP |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2011-12-18
47532 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-18 01:19 | 2011-12-18 09:47 | 2011-12-18 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE "On 12/18/11 at approximately 0119 CST, Clinton Power Station commenced work to repair a failed hard drive on the server that provides data to the Emergency Response Data System (ERDS) link. At 0130, it was determined that the server had a hardware issue. IT personnel are currently in the process of making repairs to re-establish the link. It is estimated that this link will be restored at approximately 1030 CST. "This event is reportable due to the major loss of emergency assessment capability per 10CFR50.72 (b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE AT 1229 EST ON 12/18/2011 FROM JIM PETERSON TO MARK ABRAMOVITZ * * * ERDS was restored at 1122 CST on 12/18/2011. Notified R3DO (Dickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-18
47531 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-12-17 00:01 | 2011-12-17 12:59 | 2011-12-17 | POSSIBLE DEGRADATION IN HIGH PRESSURE FIRE WATER SPRINKLER HEADS "At 0001 CST, on 12-17-2011, the Plant Shift Superintendent was notified that the C-310 High Pressure Fire Water (HPFW) Sprinkler System #2 had been inspected by Fire Services and thirty-two (32) sprinkler heads had visible corrosion on them. The system configuration was evaluated using EN-C-822-99-047, 'Effects of Impaired Sprinkler Heads on System Operability' and determined that with these heads potentially impaired, a portion of the building would not have sufficient sprinkler coverage. The HPFW system is required to be operable according to TSR LCO 2.4.4.5. C-310 HPFW system #2 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. Based on past testing results, there is a possibility that the heads would have been able to perform their specified safety function. Once the heads are removed from the system, testing will be performed to determine the actual affect on operability. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed." The site instituted compensatory measures included performing a fire patrol walkdown of the area within the first two hours after discovery of the potential degradation and hourly fire patrols thereafter. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2011-12-17
47530 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2011-12-16 10:17 | 2011-12-16 16:37 | 2011-12-17 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM AND EMERGENCY RESPONSE DATA SYSTEM "At 1017 EST on December 16, 2011, a loss of the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) occurred due to a process computer malfunction. This loss in capability is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "Indications of related plant variable are available in the Main Control Center. The Visual Annunciator System (VAS) remains functional. Meteorological and process effluent radiological monitor indications are available and dose assessment capability is available and tested functional. "In the event of a plant emergency, the Emergency Plan can be implemented as assessment capabilities are available under alternate means." The NRC Resident Inspector has been informed. * * * UPDATE AT 0022 EST ON 12/17/11 FROM GROFF TO HUFFMAN * * * "At 2235 EST on December 16, 2011, the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) were restored following the correction of the process computer malfunction. This loss in capability was reported under a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). " The licensee has notified the NRC Resident Inspector. R3DO (Dickson) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-16
47529 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2011-12-13 19:00 | 2011-12-15 18:27 | 2011-12-15 | HELICOPTER INTEGRATED BLADE INSPECTION SYSTEM SOURCE LOST On 12/13/11, after a Marine Corps CH53 Helicopter training flight at 1900 PST it was determined during a post flight inspection that the 500 micro-Curie Sr-90 integrated blade inspection system (IBIS) source was missing. The flight originated on Marine Corps Air Station Miramar. During the flight the helicopter flew over the pacific ocean then to and over Camp Pendleton before returning to Miramar. An investigation into the event is ongoing. The results of the investigation will determine what actions are taken to recover the source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-12-15
47528 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2011-12-06 19:00 | 2011-12-15 17:43 | 2011-12-23 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT The following was received from the State of Minnesota via email: "Minnesota Department of Health (MDH) was initially notified on December 14, 2011, by a representative from the University of Minnesota about a possible HDR [High Dose Rate] medical event. As of December 15, 2011 MDH was notified of the determination of a medical event that resulted in a 50% overexposure to an unintended area." * * * UPDATE FROM BRANDON JURAN TO DONALD NORWOOD AT 1149 EST ON 12/23/2011 VIA E-MAIL * * * "This notification is to provide follow-up information to the medical event initially reported on 12/15/2011 by Lynn Dunbar of the Minnesota Department of Health. "The patient was being treated for uterine cancer using iridium 192 high dose-rate (HDR) brachytherapy. The written directive called for treating the target area to approximately 600 cGy per fraction for five fractions. Instrumentation consisted of four plastic Heyman capsules, a tandem, and a pair of ovoids. Of the seven pathway options, five were identified to be used in the treatment plan for delivering the dose, and catheters were inserted into these instruments. "The first fraction of five was delivered with the tandem catheter not fully inserted into the tandem. The second of five fractions was delivered according to the original written directive. The 3rd, 4th, 5th fractions were modified to give the treatment volume the originally intended total dose. The dose to the rectum would have been 157.5 cGy if all five fractions were completed according to the original written directive. The dose to the rectum as treated was 256.2 cGy, about 63% more than intended." The Event Date provided in the initial report was changed (from 12/15/2011 to 12/6/2011) and the number given as the 'MDH #' (MDH #: 1049-206-27) was re-assigned as the licensee's license number based on information provided in the update. Notified R3DO (Pelke) and FSME EO (Einberg). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2011-12-21
47527 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-12-14 | 2011-12-15 11:43 | 2012-01-30 | AGREEMENT STATE REPORT - POSSIBLE EXTREMITY DOSE EXCEEDING ANNUAL LIMIT "On 12/14/11, the licensee reported to Agency [Ma. Radiation Control Program] a potential dose exceeding the adult occupational shallow dose equivalent limit of 50 Rem to the extremities. Situation involved a researcher handling microcurie quantities of phosphorus-32. Licensee's initial estimate of worker extremity exposure is in the range of 47-59 rem during the previous six months. Worker monitored with a whole body dosimeter but not with an extremity dosimeter. Licensee investigation of researcher's experimental procedures and handling techniques, after researcher observed left index finger skin discoloration, led to the conclusion of potential dose exceeding annual regulatory limit. Individual restricted from further radioactive material handling. Experimental procedure changes implemented by licensee. "An investigation is ongoing." MA Event: 12-9924 * * * UPDATE FROM TONY CARPENITO TO VINCE KLCO AT 1132 EST ON 12/21/2011* * * The following information was received from the Commonwealth by email: "On 12/19/11, the licensee reported a revised worker extremity exposure estimate of 40.15 rem. The Commonwealth [Massachusetts Radiation Control Program] considers this event to still be open." Notified the R1DO (Perry) and the FSME EO (Burgess). * * RETRACTION FROM TONY CARPENTINO TO JOE O'HARA AT 0955 EST ON 1/30/2012 * * "The Agency [Commonwealth of Massachusetts] inspection of 1/13/12 consisted of interviews with subject worker and other licensee personnel, observation of subject work area, and review of reports and representative records. Licensee determined subject worker's assigned 2011 shallow dose equivalent to the extremity to be 43.41 rem. Agency and subject worker accepts licensee's determination that subject worker's exposure did not exceed annual occupational dose limit for adults. Skin discoloration no longer visible. "The Agency considers this event to be NON-REPORTABLE and CLOSED." Notified R1DO(Cook) and FSME EO(McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-12-20
47526 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-12-14 | 2011-12-15 11:39 | 2011-12-15 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED PROCESS GAUGE The following was received from the State of Texas via email: "On December 14, 2011, the Agency [Texas Department of State Health Services] received a report from a licensee that a shutter had failed on one of its Kay-Ray Model KR7062P fixed density gauges, which contains a 100 millicurie Cesium (Cs)-137 source. The shutter failed in the open position, which is its normal operating position. There is no increased exposure risk. The licensee is placing an information tag advising of the malfunction on the gauge until it can be replaced by a service company. Additional information will be provided as it is obtained." Texas Case #: I-8910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-12-20
47525 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-12-15 07:39 | 2011-12-15 10:41 | 2011-12-15 | DUAL UNIT TECHNICAL SPECIFICATION 3.0.3 REQUIRED SHUTDOWN DUE TO LOSS OF CONTROL ROOM CHILLERS "Control room area chilled water system 'B' train tripped while control room area chilled water system 'A' train was isolated for maintenance. Unit 1 and Unit 2 entered technical specification 3.0.3 at 0739 EST. Unit 1 shutdown commenced at 1030 EST. Unit 2 shutdown is scheduled to commence at 1100 EST. This plant condition also requires a notification under 10CFR50.72(b)(3)(v)." The licensee is investigating the cause of the trip on the 'B' train and is taking actions to restore the 'A' train to service and exit the shutdown. The electrical lineup is normal and all safety systems are operable. The NRC Resident Inspector has been notified. The states of North Carolina and South Carolina will be notified. Local county governments of York, Gaston, and Mecklenberg counties will also be notified. | 99 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-12-15
47524 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2011-12-15 09:00 | 2011-12-15 07:30 | 2012-03-14 | ERDADS OUT OF SERVICE FOR PLANNED MAINTENANCE "The St. Lucie Unit 1 Emergency Response Data Acquisition and Display System (ERDADS) will be removed from service for system modification following completion of core offload for the current cycle 24 refueling outage, currently scheduled for 12/15/2011 at 0900. The ERDADS system will be functional prior to core reload (Mode 6) and fully operational prior to the plant startup. This is an informational notification of a planned loss of emergency assessment capability. Control room indications including annunciators are available as alternate means to monitor critical data. An update to this notification will be provided when the system is restored to service." The NRC Resident Inspector has been notified. * * * UPDATE FROM PORRO TO CROUCH AT 1703 EDT ON 3/14/12 * * * "The St. Lucie Unit 1 Emergency Response Data Acquisition and Display System (ERDADS) has been restored to service. Some area rad monitoring functional testing remains in progress; however full assessment capability is functional via the control room indications and alarms. All ERDS link data points provided by the Emergency Response Data Acquisition and Display System have been restored to service and fully operational to support plant start up." The licensee has notified the NRC Resident Inspector. Notified R2DO (Guthrie). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-15
47523 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-12-14 15:10 | 2011-12-14 16:40 | 2011-12-14 | MANUAL REACTOR TRIP DUE TO LOSS OF BOTH MAIN FEEDPUMPS "The reactor was manually tripped at 1510 EST on 12/14/11 due to loss of both main feedpumps. Both feedpumps tripped on low suction pressure due to an apparent unplanned opening of the 'A' main feedpump recirculation valve. The cause of the main feedpump recirculation valve opening has not been determined. All full length control rods fully inserted. Auxiliary feed pump P-8A automatically started at 1511 EST on steam generator level as designed (10CFR50.72(b)(3)(iv)(A)). The turbine bypass valve is in service maintaining reactor coolant system temperature [by directing steam flow to the main condenser]. The plant is stable in mode 3 [and the reactor trip was considered uncomplicated]. "The Van Buren County Sherriff was notified [per other plant requirements] concerning use of the atmospheric steam dump causing excessive noise in the vicinity of the plant [immediately following the plant trip]." The plant electric power is in the normal shutdown configuration. There was no primary to secondary leakage. A press release is planned for the local media. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OTHER UNSPEC REQMNT |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-12-14
47522 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-12-09 11:59 | 2011-12-13 19:43 | 2012-01-26 | UNANALYZED CONDITION- DEGRADED FIRE BARRIER BETWEEN FIRE AREAS "A degraded fire barrier between Fire Area (FA) 118 (Bus 26 Room) and FA 128 (Bus 27 Room) has existed during the last three years. The top of the wall between the Bus 26 and Bus 27 room had a missing/degraded fire barrier. At the time of discovery on December 9, 2011 a fire watch was in place. However, it was determined that at various times during the last three years a fire watch was not established. "Bus 27 has been conservatively aligned to Bus 26 to provide the required degree of separation for redundant safe shutdown trains (between Bus 26 and Bus 25). The fire watch will remain in place as a compensatory measure until the fire barrier is repaired. "[The] NRC Resident [Inspector] has been informed." * * * RETRACTION FROM BRIAN JOHNSON TO JOE O'HARA AT 1555 EST ON 1/26/12 * * * "An eight hour report per 10 CFR 50.72(b)(3)(ii)(B) was reported on December 13, 2011 for a degraded fire barrier between Fire Area (FA) 118 (Bus 26 Room) and FA 128 (Bus 27 Room.) 'Subsequent engineering analysis determined that the degraded fire barrier maintained the required degree of separation for redundant safe shutdown trains and plant safety was not significantly degraded. The 10 CFR 50.72(b)(3)(ii)(B) report is retracted. "The NRC Resident Inspector has been informed." Notified R3DO (L. Kozak) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-13
47521 | -1 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2011-10-13 12:00 | 2011-12-13 16:55 | 2012-01-23 | FISHER CONTROLS PART 21 NOTIFICATION INTERIM REPORT - POSSIBLE DISC PIN ISSUE ON A TYPE A11 BUTTERFLY VALVE The following information was received by facsimile: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International, LLC (Fisher) is providing the required written interim notification of a possible deviation or failure to comply. On October 13, 2011, Fisher became aware of a possible issue with the disc pin engagement of a 20" type A11 butterfly Valve, serial number 19102243. The affected valve was returned to Fisher for evaluation and correction and, upon correction, was returned to the customer [Clinton Power Station] on November 21, 2011. "Fisher expects to complete its evaluation by January 31, 2012. At that time, if the evaluation reveals that a potential issue exists with the disc pin engagement, Fisher will issue a notification per the requirements of 10 CFR 21.21(b)." * * * UPDATE AT 1539 EST ON 01/23/121 FROM GEORGE BAITINGER TO S. SANDIN * * * This report is retracted based on the following: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International LLC (Fisher) is providing the required written final notification of a possible deviation or failure to comply. "On December 13, 2011, Fisher provided an interim notification of a possible deviation or failure to comply concerning a possible issue with the disc pin engagement of a 20 inch Type A 11 butterfly valve, serial number 19102243. The affected valve was returned to Fisher for evaluation and correction and, upon correction, was returned to the customer on November 21, 2011. "Fisher has completed the review of the valve design and has determined that this potential issue would not have negatively affected the subject valve or its performance. Therefore, Fisher will not be issuing a notification per the requirements of 10 CFR 21 21.21(b)." Notified R3DO (Kozak) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-12-13
47520 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2011-12-12 16:50 | 2011-12-12 18:06 | 2011-12-12 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY DUE TO HIGH OPACITY OF DIESEL EXHAUST "At 1447 [EST] Oyster Creek experienced a failure of a discharge flange on a fire protection pond pump. The fire system backup fire diesel started in response to low system pressure. At 1540 [EST], it was noted that the fire diesel had higher than expected opacity from its exhaust. High exhaust opacity (equal to or greater than 20% for more than 3 minutes in any consecutive 30 minute period) is reportable to the State of New Jersey in accordance with the Auxiliary Boiler Air Pollution Control Permit. At 1650 [EST], high opacity from the fire diesel was reported to the State of New Jersey via the NJ Department of Environmental Protection hotline. "In accordance with 10 CFR 50.72 (b)(2)(xi) this event is being reported due to Offsite Notification." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-12-12
47519 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-12-10 19:00 | 2011-12-12 14:38 | 2012-06-21 | AGREEMENT STATE REPORT - NUCLEAR GAUGES DAMAGED DUE TO FIRE The following information was provided from the state via email: "On December 12, 2011, the Agency was notified by a licensee that on Saturday, December 10, 2011, at approximately 1900 CST, there was a fire in the coker unit at their facility in Pasadena, TX. The RSO reported there were 4 fixed nuclear gauges on drums in the area of the fire. The gauges were Ohmart-Vega Model SH1G-1 and each contained a 300 milliCurie Cesium-137 source. Two gauges were directly in the fire and were damaged. The other two gauges were shielded from the fire by the drum they were mounted on and it has not yet been determined if they sustained any damage. The area was barricaded to prevent entry due to unsafe conditions caused by the fire (i.e. structural damage that has to be assessed, heat, ash/hydrocarbons). There were no radiation levels above background found during initial surveys from the barricade line and subsequent surveys conducted under the drums on the ground level and second level (areas where people will begin working). Higher levels will be surveyed prior to entry. The licensee has made arrangements with Ohmart-Vega for service to remove all 4 gauges once the area is safe. "Gauge and Source Information: Gauges: All Ohmart-Vega Model SH1G-1 Serial numbers:13543162, 13543163, 13543164 (in fire), 13543165 (in fire) Sources: Cesium-137, 300 milliCuries each, SN same as gauge Gauges installed March, 2010. "More information will be provided as it is obtained." * * * UPDATE FROM ART TUCKER TO JOHN KNOKE AT1612 EDT ON 06/21/12 * * * The following information was provided from the state via email: "On June 13, 2012, the Agency was notified by the licensee that the four gauges involved in the fire on December 12, 2011, had been removed from the vessel and sent to their service provider. Prior to being shipped a source leak test was performed on all four gauges. The results for all the sources was less than the acceptable limit. A second source leak test was performed on the gauges once they were received at the service providers facility. The results were reported as less than the acceptable limit. On June 19, 2012, the service provider contacted the Agency and stated that while repairing one of the gauges containing 300 milliCuries of cesium - 137, their technician, the floor in the work area, and the work bench became contaminated. The area and the technician were decontaminated to background that same day. The service provider has not provided the contamination levels, but stated that they were low enough that they did not believe there was any risk to the worker of internal contamination. They also reported that the gauge was void of lead shielding. The service provider is trying to determine how the source failed. Additional information will be provided as it is received in accordance with SA 300." Texas Incident #: I-8909 Notified R1DO (Geoffrey Miller), FSME via email | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-12-15
47518 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-12-08 14:30 | 2011-12-12 12:31 | 2011-12-12 | AGREEMENT STATE REPORT- LINEN TRANSPORT TRUCK DETAINED AFTER SETTING OFF RADIATION ALARM The following information was provided via email: "On 12/8/11 at 1430 PST, the Nevada Radiation Control Program (NRCP) received a call from the Alternate Radiation Safety Officer (ARSO) for Renown South Meadows Medical Center, that a truck carrying linen had been detained by the California Highway Patrol (CHP) at the Truckee inspection station after setting off a radiation alarm. The ARSO explained that the truck was not carrying any materials from the Nuclear Medicine Department or decay room and she knew of no reason that it would be radioactive. She provided the name and number for the CHP at Truckee. "The NRCP contacted the CHP and were told that they had surveyed the truck with a Ludlum meter and measured .400 millirem per hour (or 400 microR/hour) outside the trailer. The CHP said that their protocols dictate that anything above three times background is treated as a hazmat incident and must have proper packaging and manifest. They had not run an identification spectrum on the truck. They had no capability to unload a trailer on site for further investigation. They were holding the vehicle pending instructions from their departmental radiation specialist and agreed to call [the NRCP] when they had a decision. "The Aramark (linen service) representative confirmed that the vehicle in question was a tractor trailer and was carrying only linen from Renown. "At approximately 1545 PST, the CHP called and indicated that they had released the trailer with orders to return to Renown Medical Center. They were unable to identify the radioisotope present and the dose rate reading was now .100 millirem per hour (100 micro R/hr). "The NRCP Incident Response Supervisor arrived at Renown Medical center at approximately 1645 PST, shortly after the truck, and met with Renown staff. After conducting a radiation survey on the outside of the truck, he determined the general location of the high radiation and identified Technetium-99m (Tc-99m) as a suspected isotope. Linens are transported in large plastic bins, which were removed with a pallet jack, by the staff at Renown. When the radioactive bin was identified, it was segregated, a thorough survey was done and the radioisotope was positively identified as Tc-99m. The bin was placed in Renown's decay room where it will remain for 2 to10 days until the Tc-99m decays. "The most likely cause of this contamination was that a recently treated patient soiled the sheets and the possibility of radioactive contamination was not recognized by floor staff. Linens are not routinely screened for radiation. Aramark recently began transporting linens to Sacramento, rather than processing locally, so they are now subject to inspection upon entering California. The RCP will assist Renown with some procedure changes that will minimize the chances of this happening in the future. "Dose rate readings were one order of magnitude lower than what CHP reported. It is unknown why CHP was unable to obtain an accurate identification of the isotope. "Radiation readings: RadEye - Background 6 uR/hr; at bin 48 uR/hr; Ortec MicroDetective - Background 65 counts per second; at bin 1800 counts per second; Renown 451P Ion Chamber - Background 6 uR/hr; at bin 52 uR/hr; Ludlum 14c with pancake G-M detector - at bin 1800 counts per minute." Nevada Report Number: NV110024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2011-12-15
47517 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-12-11 12:58 | 2011-12-11 16:45 | 2011-12-11 | INTERMEDIATE RANGE NUCLEAR INSTRUMENT HIGH FLUX TRIP SET POINTS SET INCORRECTLY "This 8 hour notification is being made in accordance with 10 CFR50.72 (b)(3)(v)(A). "On November 24, 2011, 1N35 and 1N36 Intermediate Range Nuclear Instruments High Flux Trip set points were adjusted while Unit 1 was at approximately 55% reactor power following the 1R21 Refueling outage, On December 11, 2011, at 1258 EST Salem Unit 1 entered Technical Specification 3.0.3, after determining the set points were set incorrectly. "A review of the Reactor Engineering Manual, which contains the trip set points, showed that the trip set points for 1N35 and 1N36 were 2.69E-4 and 2.37E-4 respectively. These values equate to approximately 125% thermal power. The Intermediate Range Trip set point is normally set to 25% thermal power. Both channels were declared inoperable and preparations were made to install the correct set points. At 1628 [EST] 1N35 was declared operable and Technical Specification 3.0.3 was exited following installation of the correct set point and retest of the channel. "There was no out-of-service safety related equipment that contributed to this event. No one was injured as a result of this event." The licensee will notify the NRC Resident Inspector and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2011-12-11
47516 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-12-10 04:56 | 2011-12-10 14:36 | 2011-12-10 | SECONDARY CONTAINMENT INOPERABLE DUE TO ICING OF REACTOR BUILDING INTAKE FILTERS "Secondary containment pressure exceeded atmospheric pressure which does not meet the surveillance requirement to have secondary containment vacuum greater than or equal to 0.25 inches of water vacuum. Secondary containment was declared inoperable and the Limiting Condition for Operation (LCO) Action Statement was entered. Manual control of the reactor building pressure control system was taken. Vacuum was less than 0.25 inches of water for approximately 1 minute. Secondary containment is [now] operable. "There were no actual radiological releases associated with the event. "Actual secondary containment integrity was not challenged. The secondary containment pressure excursion was a result of icing of the reactor building intake filters which caused the automatic reactor building pressure control system to function improperly. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-12-10
47515 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2011-12-09 18:35 | 2011-12-09 22:41 | 2012-02-06 | PART 21 ISSUE WITH SEISMIC CLIPS ON RCIC SYSTEM CONTROLLERS RESULTS IN SYSTEM INOPERABILITY "On December 7, 2011, a 10 CFR 21 report (reference NRC EN No. 47498) was received from a vendor for a defect with NUS Controllers. The defect involves spring clips that form part of the seismic restraints for the controllers. The controllers referenced in the report are installed for the Reactor Core Isolation Cooling (RCIC) system in the control room and remote shutdown panel. Based on initial information provided by the vendor, it was determined that the RCIC system remained operable. On December 9, 2011, additional information provided by the vendor did not support the immediate operability determination and the RCIC system was declared inoperable for Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3 Condition A at 1835 hours [EST]. At 1932 hours [EST], the High Pressure Core Spray system was verified operable per TS LCO 3.5.3 Required Action A.1. TS LCO 3.5.3 Required Action A2 requires restoration of the RCIC system to operable status within 14 days. Qualified spring clips have been obtained and will be installed on the controllers. This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(B) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to remove residual heat. "The NRC Resident Inspector has been notified." * * * UPDATE FROM CHARLES ELBERFELD TO JOHN KNOKE AT 1415 EST ON 12/10/11 * * * "As a follow-up to the condition reported above, we have replaced the affected seismic clips on the controllers and the Reactor Core Isolation Cooling system is now operable as of 0734 on December 10, 2011. "The NRC Resident Inspector has been notified." R3DO (Skokowski) notified. * * * RETRACTION FROM LLOYD ZERR TO CHARLES TEAL ON 2/6/12 AT 1504 EST * * * "The vendor provided a seismic report to the station. This report showed that the seismic clips holding the Reactor Core Isolation Cooling (RCIC) controller meet the Operating Basis Earthquake (OBE) test requirements and design requirements for a Safe Shutdown Earthquake (SSE) for Perry. Based on this review, it was determined that the spring clips would function properly during and OBE and SSE. Because the condition reported in Event Number 47515 would not have prevented the fulfillment of the safety function of a system needed to remove residual heat, the condition is not reportable, and this notification is being retracted. The evaluation for this condition is documented in condition report 2011-06531. The NRC Resident Inspector has been informed." Notified R3DO (Giessner) and Part 21 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-12-09
47514 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-12-09 10:46 | 2011-12-09 13:45 | 2011-12-09 | UNIDENTIFIED RCS LEAKAGE GREATER THAN 2 GPM INCREASE WITHIN 24 HOURS "At 0908 [EST] Nine Mile Point Unit 2 received alert alarms for containment monitoring particulate channels. These alarms were accompanied by a rise in drywell floor drain leakage and drywell pressure. "At 0915 [EST] Nine Mile Point Unit 2 entered technical specification action statement (TS 3.4.5 B) due to unidentified leakage rise of greater than 2 gpm within 24 hours. "At 1046 [EST] the control room commenced power reduction for shutdown of the plant. "Peak drywell pressure was approximately 0.16 psig and is lowering since the commencement of plant shutdown. Peak drywell floor drain leakage was approximately 3.7 gpm and is also lowering since the commencement of the plant shutdown. The cause of the rise in unidentified drywell leakage is unknown at this time." The licensee has notified the NRC Resident Inspector and the state. | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-12-09
47513 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-12-05 09:45 | 2011-12-05 09:35 | 2011-12-09 | UNAVAILABILITY OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) FOR SCHEDULED UPGRADE "At approximately 0945 hours on December 5, 2011, the Beaver Valley Power Station Units 1 & 2 (BVPS) Emergency Response Data System (ERDS) electronic data link to the NRC will be taken out of service to implement planned system upgrades which include the improvements requested by Regulatory Information Summary 2009-13. The duration of the upgrade work is expected to be approximately 5 days. "During the upgrade, the Emergency Response Data System (ERDS) data link to the NRC will not be available ERDS parameters will be available to be monitored by control board indications or plant computer systems. An emergency plan procedure has instructions for providing data to the NRC, if needed, when ERDS is out of service. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified. An update will be provided when the ERDS data link to the NRC has been returned to service." [The above report was originally logged by the NRC Headquarters Operations Officer at approximately 0935 on December 5, 2011 and was converted to an event report upon receipt of the updated information below] * * * UPDATE FROM SHARBAUGH TO HUFFMAN ON 12/9/11 AT 0948 EST * * * "Testing of the Beaver Valley Power Station Emergency Response Data System (ERDS) upgrade has been completed and the ERDS data link to the NRC has been returned to service. The NRC Resident has been notified." R1DO (Cahill) notified. NRC ERDS Program Manager (Alemu) and ERDS Help Desk informed via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-09
47512 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-12-08 17:55 | 2011-12-09 00:21 | 2012-02-07 | UNANALYZED CONDITION POTENTIALLY COULD AFFECT THE COMMON CONTROL ROOM "At 1755 on 12/8/11, it was determined that an unanalyzed condition existed for the common Control Room for both Units. A high energy line break (HELB) barrier issue was discovered while performing a fire barrier surveillance and the condition is believed to have existed from initial plant construction. A HELB barrier was found to have a significant breach in it that could allow steam from a HELB in the Unit 2 Steam Generator Blowdown system to potentially impact equipment in the Control Room. The Control Room is not analyzed for a steam environment. The degree of the impact could not be readily determined, but could likely affect the safety related equipment in the Control Room. At 1803 on 12/8/11, Unit 2 Steam Generator Blowdown was secured to eliminate the potential for a HELB in the affected area which eliminated the potential unanalyzed condition. Therefore, an 8 hour report to the NRC is required under 10 CFR 50.72(b)(3)(ii)(B) 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety' since there was not a reasonable expectation that the Control Room environment could support operation of safety related equipment with Unit 2 Steam Generator Blowdown in service. Further analysis is underway." The licensee will notify the NRC Resident Inspector * * * RETRACTION AT 0059 EST ON 2/7/12 FROM KENT MILLS TO HUFFMAN * * * "Engineering performed an evaluation to address the impact of the degraded condition on the barrier's design functions. The evaluation concluded that the barrier remained capable of performing its design function with the degraded seal present. Therefore, this condition does not represent an unanalyzed condition that significantly degrades plant safety." The licensee will notify the NRC Resident Inspector. R1DO (Burritt) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-09
47511 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-12-02 13:11 | 2011-12-08 14:33 | 2011-12-08 | LOW PRESSURE COOLANT INJECTION INOPERABLE "This condition is being reported in accordance with 10CFR50.72(b)(3)(v) as a condition that could have prevented fulfillment of a safety function. "On 12/02/2011 at 1311 CST, the Low Pressure Coolant Injection (LPCI) was declared inoperable when voiding was discovered in the 'B' Residual Heat Removal (RHR) inject vent line. "Initial review of this condition for immediate reportability under 50.72(b)(3)(v), event or condition that could have prevented fulfillment of a safety function, concluded the condition was not reportable based on the availability of other Emergency Core Cooling Systems (ECCS). Specifically, Core Spray and HPCI were both available to perform the function of emergency core cooling. On 12/03/2011 at 1650 CST, LPCI was declared operable based on further examinations to determine extent of voiding, system filling and venting and completion of supporting engineering evaluations. Subsequent reviews determined that the reportability decision under 50.72(b)(3)(v) as a event or condition that could have prevented fulfillment of a safety function should be based on safety function at the system level, rather than at the ECCS function level. The decision to report the inoperability of LPCI under 50.72(b)(3)(v) was made at 1319 CST on 12/08/2011. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-12-08
47510 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-08 05:00 | 2011-12-08 13:30 | 2011-12-08 | UNANALYZED CONDITION - NON FUSED DC BUS AMMETERS COULD SHORT AND CAUSE A FIRE "During Operating Experience (OPEX) review of Browns Ferry Fire Protection ENS 47374, 'Deficiency Identified in Transition to Performance Based Standard for Fire Protection,' a similar condition was identified at Clinton Power Station. "During site review, it was determined that original plant wiring design for the station battery ammeter contains a 'shunt' in the current flow from each direct current (DC) battery. Bolted on the shunt bar are two IEEE 383 qualified leads to a current meter in the main control room (MCR). The small difference in voltage between the two taps on the shunt is enough to deflect the current gauge in the MCR when current flows from the battery through the shunt. The ammeter wiring attached to the shunt does not have fuses, and if one of these ammeter wires shorts to ground at the same time another DC wire from the opposite polarity on the same battery also shorts to ground, a ground loop through the unfused ammeter cable could occur. With enough current going through the cable, the potential exists that a fire in the raceway system or MCR could occur wherever the cable is routed. "This design condition exists in Divisions 1, 2, 3, and 4. This condition is reportable in accordance with 10CFR50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' Compensatory fire watch measures have been implemented for affected areas of the plant. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-08
47509 | -1 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2011-12-07 14:58 | 2011-12-07 20:40 | 2011-12-22 | REACTOR BUILDING VENTILATION DIFFERENTIAL PRESSURE ABOVE TECHNICAL SPECIFICATIONS "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C) and (D), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and mitigate the consequences of an accident. Following initial troubleshooting of the reactor building ventilation (VR) differential pressure (DP) control loop, the Unit 1 VR DP controller was left in manual per the troubleshooting steps. It was noted at 1458 CST, on 12/7/11, that building DP was above the TS SR 3.6.4.1.1 required value of -0.25" H20. This rendered the secondary containment inoperable. Reactor building DP was returned to within the TS requirements within 14 minutes, and following system walkdowns, secondary containment was declared operable at 1615 [CST, on] 12/7/11. Troubleshooting will continue with other excursions above -0.25" H2O possible until repairs are complete (anticipated being complete week of 12/12/11)." This condition requires the licensee to comply with technical specifications values within 4 hours or be in Mode 3 within 12 hours. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM R. DRAPER TO P. SNYDER ON 12/22/11 AT 1440 EST * * * "On December 7, 2011, following initial troubleshooting of the reactor building ventilation (VR) differential pressure (DP) control loop, the building DP was above the TS SR 3.6.4.1.1 value of -0.25 inch of vacuum water gauge. The secondary containment was declared inoperable and determined to be a loss of safety function. During the investigation it was determined that the event occurred due to a failure in the non-safety reactor building ventilation differential pressure control loop. The safety related function of the secondary containment and the non-safely reactor building ventilation differential pressure control loop are completely independent from one another. It is recognized that reactor building DP may exceed the TS SR [Technical Specification Surveillance Requirement] 3.6.4.1.1 value due to non-safety related component failures such as system fan trips, pressure controller malfunctions, rapid air temperature changes due to blast heater trips, or station heat recovery coil issues. A failure of a non-safety component does not result in a loss of safety function. The safely function of the secondary containment is maintained by adequate leak tightness and the operable ventilation equipment required to maintain the negative pressure requirements of TS SR 3.6.4.1.1. The safety related Stand-By Gas Treatment (SGT) ventilation system performs the negative pressure safety function. The secondary containment isolation safety function, isolation dampers and SGT systems remained operable throughout the event. Therefore this event did not constitute a loss of safety function of secondary containment and this event is not reportable." The licensee notified the NRC Resident Inspector. Notified R3DO (Pelke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-12-07
47508 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-11-16 20:00 | 2011-12-07 18:29 | 2011-12-10 | POSTULATED FLOODING SCENARIO RESULTS IN UNANALYZED CONDITION "On November 16, 2011, at 2000 hours (EST), control room operators accepted the results of an immediate investigation related to the adequacy of a calculation related to the flooding analysis for service water piping in the control complex. The conclusions of the original analysis assumed operator actions to mitigate the flooding. The existing procedural guidance at that time lacked specificity for the required operator actions. This was identified as a non-conforming condition with respect to a USAR flooding analysis. The immediate investigation determined that significant margin exists for mitigation of the service water leakage crack compared to the 30 minute actions required in the original analysis. A preliminary strategy for flood mitigation was identified in the immediate investigation. Guidance was provided to the operators for a leak mitigation strategy in a night order, and a prompt functionality assessment was requested for the control complex building with respect to the flooding analysis. On November 22, 2011, at 1957 hours (EST), the prompt functionality assessment was accepted by the control room operators. The assessment included compensatory measures that simplified guidance for mitigating the flooding from the service water system. The compensatory measures were implemented. On December 2, 2011, the NRC Component Design Basis Inspection team debriefed that the condition identified should have been called in to the NRC Operations Center within eight hours and that missing the call was a violation of 10 CFR 50.72(b)(3)(ii)(B). On December 7, 2011, at 1320 hours (EST), a call was received from the NRC Region III informing the compliance supervisor that the eight-hour notification should still be made. "The NRC Resident Inspector has been notified." * * * UPDATE FROM CHARLES ELBERFELD TO JOHN KNOKE AT 1412 EST ON 12/10/11 * * * The licensee added further clarification to the event reported above as follows: "Given that an unanalyzed condition existed until the appropriate measures were implemented, an eight-hour call in accordance with the aforementioned section of 10 CFR 50.72 should have been made. After further consideration, station management decided the eight-hour call was missed and it is being reported as required. "The NRC Resident Inspector has been notified." R3DO (Skokowski) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-12-07
47507 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2010-04-10 21:00 | 2011-12-07 15:40 | 2011-12-07 | AGREEMENT STATE REPORT - SHUTTER SOLENOID FAILURE ON GAUGE The following report was received from the Kentucky Department of Public Health - Radiation Health Branch via facsimile: "The state (Kentucky Radiation Health Branch) was notified on 4/12/10, by a representative from Temple-Inland, of the failure in the shutter (in the closed position) on one of their gauges. The gauge is a Honeywell, Model 4000, scanner (Honeywell system number 8465) containing a 1 Ci Kr-85 source, model number 4201, serial number 4991BXV. This event occurred on the evening of 4/10/10 and a representative from Honeywell was called in for repair. The scanner was back online at 2349 CST on 4/10/10 for a total downtime of 2.25 hours." Kentucky Report ID Number: KY1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-12-12
47506 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-12-07 | 2011-12-07 09:59 | 2011-12-07 | AGREEMENT STATE - SHUTTER FAILURE The following was received from the Commonwealth of Pennsylvania via facsimile: "On December 6, 2011, the Department's Southwest Regional Office [Pennsylvania Bureau of Radiation Protection (PBRP)] received notification via email about an event that took place on December 2, 2011. It is reportable within 24 hours under 10 CFR 30.50(b)(2). "A radiological consultant was completing the six month leak testing and shutter checks of thickness gauges. During the testing, it was discovered that the pneumatic system for this gauge did not completely close the shutter. The device is identified as: Manufacturer: DMC Model: AM-5A Serial #: 0404LV Isotope: Am-241 Activity: 100 mCi "CAUSE OF EVENT: Failure of the pneumatic system to completely close the shutter. "ACTIONS: Maintenance personnel were able to drain the air line of accumulated moisture and close the shutter later that day. The Bagdad facility shall investigate this matter and determine what is necessary to prevent recurrence. The Department [PBRP] plans to conduct a reactive inspection." Event Report ID No: PA11039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-12-12
47505 | 0 | FLOWSERVE LIMITORQUE ACTUATORS |  |  |  |  | 2011-12-05 | 2011-12-06 16:43 | 2012-06-27 | LIMITORQUE PART 21 NOTIFICATION INTERIM REPORT - POTENTIAL DEFECTIVE PART IN SMB-0 HEAVY SPRING PACK The following information was received via fax: Background: During in-house production testing of Limitorque SMB-0 actuators, test lab personnel reported an inability to maintain consistent torque output at the various torque switch settings. Investigation revealed that the actuator torque spring pack assembly had lost preload during the test. Component inspection determined that the loss of preload was due to disc springs that had experienced an excessive permanent relaxation of free height during actuator testing. Components Affected: Only SMB/SB/SBD-0 actuators with heavy spring pack assemblies shipped between September 15, 2011 and November 7, 2011 could possibly be affected. No parts orders for SMB/SB/SBD-0 replacement heavy spring packs were built in this time period. Potential Impact on Safety Related Operation: A significant loss of preload on the actuator torque spring pack assembly could result in the actuator producing insufficient output torque thereby affecting proper valve function. Cause and Corrective Action: Communications with the spring manufacturer revealed that Limitorque was shipped a single lot of springs that were not in accordance with our parts requirements. These springs were incorrectly shipped to Limitorque due to a manufacturer backorder on our normally requested product. Vendor controls have been implemented to prevent reoccurrence of this issue. Limitorque has identified the problem springs and purged them from inventory. On November 14, 2011 Limitorque notified all affected customers who received the actuators which shipped during the time period identified above. The serial numbers and locations of the potentially affected actuators are provided in the table below. Limitorque has requested that the actuator spring packs be returned for detailed inspection and replacement if needed. After inspection of the spring pack assembly of all actuators listed below, Flowserve-Limitorque will issue a follow-up to this interim report on or before February 3, 2012. Affected Customers/Locations: Customer - Velan Valve Corp. Location of Actuator - Velan Valve, Montreal Limitorque Order No. 110309.001 Quantity - 6 Actuator Serial # 909476-909481 Customer - Velan Valve Corp. Location of Actuator - Velan Valve, Montreal Limitorque Order No. 115055.001 Quantity - 1 Actuator Serial # 926332 Customer - Weir Valve Corp. Location of Actuator - Weir Valve, Ipswich, MA Limitorque Order No. 106839.008 Quantity - 4 Actuator Serial # 911621-911624 Customer - Weir Valve Corp. Location of Actuator - Weir Valve, Ipswich, MA Limitorque Order No. 106839.009 Quantity - 4 Actuator Serial # 911625-911628 Customer - Weir Valve Corp. Location of Actuator - Weir Valve, Ipswich, MA Limitorque Order No. 106930.012 Quantity - 4 Actuator Serial # 912769-912772 Customer - Areva NP Location of Actuator - Exelon, Braidwood NGS Limitorque Order No. 112724.001 Quantity - 1 Actuator Serial # 917953 * * * UPDATE FROM JEFF MCCONKEY TO PETE SNYDER ON 6/27/12 AT 1714 EDT * * * The following update was received via fax: "Pursuant to 10 CFR 21.21, Flowserve Corp is providing notification of the identification of a defect. This information was originally reported to the NRC Operations Center on 12/6/2011 (Event # 47505). This document is a follow-up to the interim Part 21 report. "Nineteen of the twenty actuators identified in the interim report as potentially suspect have been returned to Limitorque for inspection of the spring pack. All nineteen of these actuators were returned from two different valve manufacturer's facilities and bad not been shipped to any utilities for installation. Six of the actuators returned from Velan Valve Corporation were found to contain defective springs. The spring packs were replaced and the actuators were returned to Velan Valve. The actuators returned from Weir Valve Corporation did not contain defective springs. "The remaining actuator (serial number 917953) identified in the interim report which has not been returned to Limitorque is at Exelon Braidwood NGS. Exelon reported the following with regards to this actuator. The actuator is installed on a 36" quarter-turn MOV that is normally open and de-energized. This MOV has no safety related function to close. The MOV is position limit controlled and the valve functioned properly during operational testing after installation. Exelon Braidwood NGS is aware of the potential spring defect and plans to change the spring pack on this MOV at the first available maintenance cycle. "Flowserve's investigation of this issue concluded that this was an isolated incident and that all defective components have been identified." Notified R3DO (Valos) and Part 21 Group (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-12-06
47504 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-12-05 | 2011-12-06 16:11 | 2011-12-06 | AGREEMENT STATE REPORT - MISSING THORIUM-229 SOURCE The following information was received from the State of California via email: "UCLA notified RHB on December 5, 2011 that they discovered a single missing Thorium-229 source. Its activity is approximately 4.73 microcuries and is contained in a flame sealed ampoule. The responsible researcher claims that they transferred the source to EH&S for storage, but a search of EH&S records showed it was returned to the researcher in June 2011. A continued search of the Principal Investigator's lab and EH&S storage locations is ongoing. "10 CFR 20 Appendix C for Th-229 = 0.001 uCi, and 10CFR 20. 2201(a) requires reporting losses that exceed 1000 times the Appendix C level. Activity of > 1 microcuries is a reportable quantity. "No serial number was reported to RHB [Radiologic Health Branch]. Potential exposure to individuals is expected to be extremely low. "This investigation is on-going." CA 5010 Number: 120511 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-12-09
47503 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-03-08 | 2011-12-06 12:24 | 2011-12-06 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENTS INVOLVING CARDIOGEN-82 RADIOISOTOPE GENERATORS USED FOR CARDIAC STRESS TESTING The following information was received from the State of Nevada via email: "Description: A patient who received a Rubidium stress test on March 8th 2011 was detected at a security checkpoint upon reentry to the United States. The patient was determined to have higher than expected levels of strontium. The patient was referred to Oak Ridge National Laboratory to undergo sensitive whole body counting. The whole body counting indicated an expected dose of 4.9 rem. Additional testing conducted by the Nevada Radiation Control Program was performed on 203 patients. The result of each scan was compared to the patient who received the whole body counting at Oak Ridge National Laboratory. The definition of a medical event is '[a] dose that differs from the prescribed dose or dose that would have resulted from the prescribed dosage by more than 0.05 Sv (5 rem)' and that 'differs from the prescribed dose by 20 percent or more.' [10 CFR º 35.3045]. Because the patient who received the whole body counting at Oak Ridge received 4.9 rem any patient who had more activity when compared to the Oak Ridge patient may qualify as a medical event. The analysis of the scans indicates 38 patients had an exposure that may constitute a medical event. The following table identifies the date, number of patients on a specific date, and the total number of patients that may have received Sr-82 and Sr-85 in sufficient quantities to constitute a medical event. The investigation is ongoing and includes the Nevada Radiation Control Program, Food and Drug Administration ('FDA'), BRACCO, and Nevada Heart and Vascular. As information becomes available the actual number of medical events may change and will be updated at that time. "Date Of Injection # Of Patients 2/11/2011 6 3/7/2011 2 3/8/2011 5 3/9/2011 3 3/10/2011 5 3/11/2011 2 3/12/2011 3 3/13/2011 4 3/14/2011 1 3/15/2011 2 4/5/2011 1 4/7/2011 4 Total Patients 38 "Why The Event Occurred: The events are still under investigation. The events may be related to manufacturing defects, inadequate training procedures, or a combination of both. 'Based on further investigation, FDA has determined that the current CardioGen-82 manufacturing procedures are not sufficient to ensure reliable performance of the generator used to produce the Rb-82 chloride injection' (FDA, 7-26-2011). "The Effect, if any, on the Individuals Who Received the Administration: The exposure is still under investigation. However, no deleterious effects are expected as a result to the exposure. Concerning this issue, 'Oak Ridge National Laboratory determined the estimated amount of unexpected radiation to be minimal and similar to what other patients may receive with cumulative exposure to certain other types of cardiac imaging procedures' (Giordano, K. & McDaniel, K., 2011). "What Actions, if any, Have Been Taken, or are Planned to Prevent Recurrence: The FDA alerted healthcare professionals to stop use of CardioGen-82 for Cardiac PET scans and BRACCO decided to voluntarily recall CardioGen-82 and this will prevent recurrence. (FDA, 7-26-2011). In addition, all technologists have undergone retraining by BRACCO and shall adopt BRACCO's updated policy concerning breakthrough testing. An online worksheet has been constructed to simplify and monitor the breakthrough recording process. "Additional actions may be implemented based on the investigation's findings. "Certification that the licensee notified the individual (or the individual's responsible relative or guardian), and if not, why not. "All patients who received studies on the dates referenced above have met with their referring physician concerning the elevated exposure to strontium. This is included in the patient's chart as part as their medical record. The Nevada Radiation Control Program has also contacted patients concerning the elevated strontium exposure. "Event Cause: Equipment Failure "Corrective Action: Reevaluation of CardioGen-82 design, training procedures and quality control. "Device/Associated Equipment: CardioGen-82 manufactured by BRACCO Diagnostics." NV Report No.: NV110023 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2011-12-12
47502 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-12-06 13:06 | 2011-12-06 17:07 | 2011-12-06 | LOSS OF COMMUNICATIONS CAPABILITY DUE TO A MAJOR CABLE CUT "On 12/06/2011 at approximately 1306 CST, a major offsite underground communications line was severed, cutting telephone lines to Clinton Power Station. The lost communications include the Health Physics Network (HPN), Emergency Notification System (ENS) and the ability to send Emergency Response Data System (ERDS) data to the NRC. Alternate communications have been established with the NRC and other agencies. This event is reportable due to the major loss of emergency assessment capability per 10CFR50.72 (b)(3)(xiii). The time to repair the lines and restore communications is unknown at this time. The NRC Resident Inspector has been notified. * * * UPDATE AT 1624 EST ON 12/6/11 FROM BOB RUSH TO S. SANDIN * * * The communication lines have been repaired and HPN, ENS, and ERDS have been restored. Notified R3DO (Skokowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-06
47501 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-12-06 09:00 | 2011-12-06 13:54 | 2011-12-09 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 0900 hours EST, on December 6, 2011, Emergency Preparedness personnel determined that the Unusual Event and Alert EAL criteria for the Liquid Waste Disposal Effluent could not be achieved due to the monitor range capability. Specifically, the R-18 effluent monitor instrument range has a maximum range of 1.0E+06 with the alarm set at 1.0E+06. The UE and Alert criteria, which are 2 times the alarm and 200 times the alarm respectively, both exceed the instrument range. "The NRC Resident Inspector has been notified." This condition has existed for some time (at least three years) and was discovered during a review of the Operating Experience database involving a similar condition reported by Crystal River-3. The licensee maintains the ability to perform grab samples of the liquid effluent for assessment. * * * UPDATE ON 12/08/11 AT 2330 EST FROM RAY BUZARD TO JOHN KNOKE * * * As a follow-up to the condition reported above, the licensee inspected other discharge and effluent radiation monitors for similar conditions and provided the following update: "At 2250 hours EST, on December 8, 2011, it was determined that the Alert EAL classification criteria for the Steam Generator Blowdown radiation monitors and the Condensate Polisher Sump discharge radiation monitor could not be achieved due to the monitors range capability. Specifically, the R-19 A, B, C and the R-37 monitors instrument range have a maximum range of 1.6E+06 which is less than the Alert EAL classification criteria. This information was validated as a follow-up to a similar event which was reported on December 6, 2011 in EN# 47501. "The NRC Resident Inspector has been notified." R2DO (Musser) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-06
47500 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-10-11 16:29 | 2011-12-06 10:15 | 2011-12-06 | LOSS OF VITAL AC POWER WHILE SHUTDOWN "This 60-day telephone notification is being made pursuant to 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to describe an invalid actuation of a containment heat removal system. "On October 11, 2011, with the reactor shutdown for refueling, a partial loss of vital AC power was experienced which resulted in a loss of shutdown cooling as well as PCIS group 2, 3, 4, and 5 half isolations. The actuation was determined to be invalid as it occurred because a breaker supplying power to the 'A' vital AC was manually opened, resulting in actuation of the associated PCIS logic circuitry. The Group 4 actuation resulted in a complete isolation of the single train Residual Heat Removal shutdown cooling suction path. The shutdown cooling path was isolated for approximately 12 minutes resulting in a coolant temperature increase of approximately 2 degrees F. At the time of the event, the reactor cavity was flooded with the spent fuel pool gates removed and the normal fuel pool cooling system in operation to provide reactor cavity cooling. Based on this, there was no impact on public health and safety." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-12-06
47499 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2011-12-06 09:30 | 2011-12-06 09:51 | 2012-01-11 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO PLANNED MAINTENANCE "Between December 6, 2011 and January 13, 2012, a sequence of activities are planned that will render the Technical Support Center (TSC) non-functional at times by removing the emergency ventilation system from service. These activities are being performed in support of planned preventive maintenance and extended power uprate facility upgrades. In preparation for these emergency ventilation system outages, the TSC emergency responders were notified that if an emergency occurred during these outages the Emergency Coordinator and the TSC staff involved with classification, notification and PARS should report to the control room. All other TSC personnel should report to the Operational Support Center. The duration for each of these TSC outages is expected to be less than 24 hours. The NRC Operations Center will be provided an update to this notification when the TSC emergency ventilation has been removed from service and following restoration for each time period. This 8 hour notification in accordance with 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector, and State and local governments. * * * UPDATE FROM CHRISTOPHER TRENT TO JOE O'HARA AT 1900 EST ON 12/7/11 * * * The TSC is functional at this time. The NRC Resident Inspector will be notified. * * * UPDATE FROM BILL BURROWS TO CHARLES TEAL AT 0313 EST ON 12/14/11 * * * The TSC has been removed from operation to continue planned maintenance. The NRC Resident Inspector has been notified. Notified R2DO (Bartley). * * * UPDATE FROM ROBERT STRUSINSKI TO JOHN KNOKE AT 0330 EST ON 12/15/11 * * * The TSC is functional at this time. The NRC Resident Inspector will be notified. Notified R2DO (Scott Freeman) via email. * * * UPDATE FROM SEAN BLOOM TO BILL HUFFMAN AT 0306 EST ON 12/20/11 * * * The TSC will be removed from operation to continue planned maintenance at 0330 EST today. The NRC Resident Inspector will be notified. Notified R2DO (Freeman). * * * UPDATE FROM SEAN BLOOM TO VINCE KLCO AT 0335 EST ON 12/21/11 * * * The TSC has been returned to service at 0130 EST on 12/21/11. The NRC Resident Inspector will be notified. Notified the R2DO (McCoy). * * * UPDATE ON 12/26/2012 AT 2333 FROM JOSE VASQUEZ TO MARK ABRAMOVITZ * * * The TSC was taken out of service at 2330 and will be out of service for several weeks. The NRC Resident Inspector was notified. Notified the R2DO (McCoy). * * * UPDATE ON 12/27/2011 AT 2000 EST FROM RICHARD RUTGERSON TO MARK ABRAMOVITZ * * * The TSC has been returned to service at 1955 EST on 12/27/2011. The NRC Resident Inspector will be notified. Notified the R2DO (Blamey). * * * UPDATE ON 1/11/2011 AT 2349 EST FROM NICK DESANTIS TO JOE O'HARA * * * The TSC will be taken out of service at 0200 for approximately 18 hours to replace a damper motor on the emergency ventilation system. The NRC Resident Inspector will be notified. Notified the R2DO (Haag). * * * UPDATE FROM TRENT TO KLCO ON 1/1/12 AT 1906 EST* * * TSC ventilation is operable and an operation test was completed satisfactory. The TSC has been returned to service. Other TSC modification work continues. The NRC Resident Inspector will be notified. Notified the R2DO (Haag). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-12-06
47498 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2011-12-05 | 2011-12-05 14:55 | 2011-12-05 | PART 21 INVOLVING DEFECTIVE SPRING CLIPS USED AS SEISMIC RESTRAINTS ON TWO SCIENTIFIC MODULES The following information was received via fax: "The purpose of this letter is to notify you of a defect in spring clips that form part of the seismic restraint for Scientech CON2000-701 and RTD2100-7403 modules. Details of the defect are provided below and in the attached Technical Bulletin Volume 38, CON2000 and RTD2100 Spring Clips, dated December 2011. "The written report shall include, but need not be limited to, the following information, to the extent known: (i) Name and address of the individual or individuals informing the Commission. Michael Weinstein Director of Quality Operations Scientech, a business of Curtiss-Wright Flow Control Corporation 44 Shelter Rock Road Danbury, CT 06810 Scott Robuck General Manager Scientech, a business unit of Curtiss-Wright Flow Control Corporation 200 S. Woodruff Avenue Idaho Falls, ID 83401 (ii) Identification of the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. PID controller, manufactured by Scientech, Model CON2000-701, Part No. NUS-A056PA RTD converter, manufactured by Scientech, Model RTD2100-7403, Part No. NUS-A121PA (iii) Identification of the firm supplying the basic component which fails to comply or contains a defect. Scientech, a business unit of Curtiss-Wright Flow control Corporation 200 S. Woodruff Avenue Idaho Falls, ID 83401 (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. The CON2000-701 is replacement for the obsolete Bailey Meter Company 701 PID controller. It is a panel mounted module that is retained in the panel during seismic events by a spring clip on the top of the modules (part number NUS-P089DB-13) that engages a detent in the panel. The module can be pulled out about one inch out of the rack before the spring clip prevents further movement; full removal requires pressure on the spring clip to disengage the detent. The module was seismically tested as documented in Qualification Report NUS-A056QA Rev 2. During the CON2000 test, a minor anomaly occurred and was accepted by Scientech as not affecting the qualification results. Recently a client questioned Scientech's acceptance of the anomaly and requested a retest. Scientech agreed to retest the module; the RRS used is attached. During the retest, the spring clip failed to adequately restrain the module. The balance of the replacements for the Bailey 7000 series - the NUSI 2000 series - are cabinet mounted modules. When they are reconfigured for shelf or panel mounting they become part of the NUSI 2100 series, and the seismically qualified units use the same spring clip. The RTD2100-7403 is the only safety related panel mounted module sold as of December 2011 with the deficient spring clip. Investigation revealed that the original clip was made of 0.025" thick spring steel. After the seismic qualification test was performed, Revision 4 to NUS-F089DB-13 altered the characteristics of the retaining clip, reducing the force required to disengage the detent. The metal was changed to SS301 stainless steel and the thickness reduced to 0.015" thick. Scientech's design change process required an evaluation of the impact of the change; the evaluation was complet4ed, but did not address the impact on seismic qualification adequately. These controllers could be mounted in the in the main control room control panels. The failure of the seismic clip could result in the controllers coming out of the panels, impacting other safety related equipment or personnel, and failing to properly control their actuated devices during a seismic event. (v) The date on which the information of such defect or failure to comply was obtained. Submitted for evaluation 11/30/11; evaluation completed 12/2/11. (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. PLANT CON2000-701 RTD2100-7403 Clinton 4 0 Davis Besse 8 0 Monticello 2 0 Perry 4 0 Susquehanna 20 7 TOTALS 38 7 (vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. 1. All five plants were notified and provided with a technical bulletin addressing the problem and the proposed solution. 2. Scientech is expedition procurement of the correct spring clips and will supply them to all affected plants. They can be readily changed out on site. 3. Scientech had previously strengthened its design review process to specifically remind reviewers to evaluate the impact on and need for additional qualifications testing. 4. Scientech will review this event with all engineering staff and emphasize the need for correct reviews. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. See attached Technical Bulletin. (provided separately) (ix) In the case of an early site permit, the entities to whom an early site permit was transferred. Not applicable. "Should you have any questions regarding this matter, please contact Robert Queenan, Operations Manager, Scientech/NUS Instruments, at (208) 524-9311." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21 |  |  |  | 0 | 2011-12-05
47497 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2011-12-05 08:47 | 2011-12-05 09:35 | 2011-12-05 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - UNUSUAL EVENT "At approximately 0847 EST, Unit 1 Letdown Pressure Control Valve, 1-CH-PCV-1145, began acting erratically which resulted in the Letdown Relief Valve, 1-CH-RV-1203, lifting and flowing to the Pressurizer Relief Tank. "At 0848 EST, the relief valve reseated and the leakage stopped. Approximately 42 gpm leakage resulted from the relief valve lifting. "This identified flow rate exceeded the threshold for entry into a Notice of Unusual Event under EAL tab SU6.1 due to identified leakage greater than 25 gpm." The licensee is troubleshooting the Letdown Pressure Control Valve. The licensee notified the NRC Resident Inspector and will notify State and local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2011-12-05
47496 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2011-12-03 12:35 | 2011-12-03 16:53 | 2011-12-03 | SECONDARY CONTAINMENT INOPERABLE DUE TO A DEGRADED DOOR SEAL "On December 3, 2011 during operator rounds, it was discovered that an Enclosure Building (secondary containment) door sweep had failed and was not providing an adequate seal. "Technical Specification (TS) 3.6.5.2, 'Secondary Containment Enclosure Building', is applicable in Modes 1,2,3, and 4 was entered at 1235 [EST]. Since secondary containment was rendered inoperable, Dominion is reporting this as a condition that could have prevented the fulfillment of the safety function to control the release of radioactive material. The door has subsequently been repaired, the Enclosure Building declared OPERABLE and the TS Action Statement exited at 1524 [EST]. Further engineering review will be conducted to more fully evaluate the impact on radiological controls. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C)." The licensee has notified the Connecticut Department of Environmental Protection, surrounding towns and the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2011-12-03
47495 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-12-02 09:45 | 2011-12-02 13:28 | 2011-12-02 | WRONG TRAIN EMERGENCY DIESEL FUEL RACK TRIP "While hanging tags on the 'B' Diesel Generator, which was tagged out for maintenance, the operator mistakenly entered the 'A' Diesel Generator Room and tripped the 'A' Diesel Generator fuel rack, making it inoperable. At this time both diesels were inoperable placing the plant in a 24 Hour LCO. "When the fuel rack was tripped alarms were received in the control room, the operator was immediately contacted and the problem was identified and corrected. Total LCO time was approximately 2 minutes." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-12-02
47494 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2011-12-02 08:29 | 2011-12-02 13:21 | 2011-12-02 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE SUPERVISOR A non-licensed employee supervisor had a confirmed positive drug test during random testing. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2011-12-02
47493 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-12-01 13:44 | 2011-12-01 16:05 | 2011-12-01 | CONTROL ROOM AIR CONDITIONING AND CONTROL ROOM EMERGENCY VENTILATION SYSTEMS INOPERABLE "At 1344 hours (EST) on December 1, 2011, the Control Building Instrument Air Dryer failed resulting in loss of control air. As a result, the three Control Room Air Conditioning subsystems required by Technical Specification (TS) 3.7.4, 'Control Room Air Conditioning (AC) System,' and the two Control Room Emergency Ventilation [CREV] subsystems required by TS 3.7.3, 'Control Room Emergency Ventilation (CREV) System,' became inoperable. As a result, this condition could have prevented the fulfillment of the safety function for these systems. Because Brunswick has a shared control room, Unit 1 and Unit 2 entered TS 3.7.3 Required Action C.1, for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours) and TS 3.7.4, Required Action E.1, for three Control Room AC subsystems inoperable (i.e., enter LCO 3.0.3 immediately). "Operability of two Control Room AC subsystems and one CREV subsystem was restored and LCO 3.0.3 was exited, at 1410 hours, when the Instrument Air Dryer was bypassed. "No power reduction took place as a result of the LCO 3.0.3 entry. This report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition existed for approximately 26 minutes. Plant staff took immediate actions to return the equipment to service. For the brief time the Control Room AC and CREV systems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected. The maximum Control Room back panel temperature during this event was approximately 68 degrees F. Troubleshooting activities are under way to determine the cause of the Instrument Air Dryer failure." The licensee notified the NRC Resident Inspector. | 100 | 5 | 0 | 100 | 5 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Startup |  | Power Operation | Startup |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-12-01
47492 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-11-30 17:47 | 2011-11-30 22:09 | 2011-11-30 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "On November 30, 2011, at 1747 hours [EST], with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) declared the High Pressure Coolant Injection (HPCI) system inoperable due to the HPCI turbine control valve (HPCI-24) failing to go open during planned post-maintenance testing. The HPCI-24 is a hydraulically operated control valve and its normal position is closed. The HPCI-24 valve has a safety function to open on a demand signal during certain event mitigation scenarios requiring the HPCI system operation. "Based on the turbine control valve failing to open during post-maintenance testing and a subsequent check out run per PNPS Procedure 8.5.4.1, the HPCI system was declared inoperable at 1747 hours and the appropriate LCO was entered. An investigation of the event is underway and continuing. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector bas been notified. "This is an 8-hour notification made in accordance with 50.72(b)(3)(v)(D)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-11-30
47491 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-11-20 05:46 | 2011-11-30 16:13 | 2011-11-30 | TURBINE TRIP PROTECTION DISABLED WHILE IN MODE 3 "On November 20, 2011 at 0546 hours [CST], STP Unit 2 transitioned modes from Mode 4 to Mode 3. Prior to the mode change, all Solid State Protection System (SSPS) generated turbine trip signals were defeated by a maintenance work activity that installed a jumper in both channels (Train R and S) of non-class relays to the turbine trip circuit. The SSPS signals to the non-class relays that were defeated by the jumpers included the turbine trip from reactor trip breakers open (P4), turbine trip from a reactor trip signal (P-16), and the turbine trip from Steam Generator HI- HI (P-14). T.S. 3.3.2 Items 5a (P4) and 5b (P-14) are required in Modes 1, 2, and 3. The jumpers were removed around 0930 on November 20, 2011 with U2 still in Mode 3. "Both the UFSAR and TS bases identify that the turbine trip mitigates the consequences of an accident. The TS bases states that an ESFAS initiated turbine trip mitigates the consequences of a steam line break or loss of coolant accident. The accident analysis for SGTR also assumes a turbine trip on a reactor trip to isolate the steam path. "Although Unit 2 was in Mode 3, with the reactor trip breakers open, and turbine throttle valves closed while the jumpers were installed, this condition is conservatively considered to be a safety system functional failure. If not corrected, this condition could have prevented the fulfillment of the accident mitigating and control of the release of radiation safety functions. A review of the performance of this activity in previous outages was conducted. It was identified that during 2RE14 in April of 2010, a work package for this activity was not closed until after Mode 3. The 60 day LER will address if the jumpers were installed in Mode 3 in April, 2010. "This was determined to be reportable within 8 hours as required by 10 CFR 50.72(b)(3)(v) parts (C) and (D)." The licensee did not determine the reportability of this event until 1415 CST on 11/30/11. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Hot Shutdown; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-11-30
47490 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-11-30 09:35 | 2011-11-30 11:39 | 2011-11-30 | PLANT PROCESS COMPUTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) to replace power supplies in the plant process computer will result in a loss of some Safety Parameter Display System (SPDS) indications for a duration of less than 5 hours. No other indicators or annunciators will be unavailable during this maintenance to affect the plant's ability to assess or monitor an accident or transient in progress. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE ON 11/30/11 AT 1442 EST FROM GILBERT TO HUFFMAN * * * The licensee reports that the plant process computer work has been completed and SPDS has been functionally tested and returned to an operable status. The licensee will notify the NRC Resident Inspector. R3DO (Riemer) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-30
47489 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-11-29 17:28 | 2011-11-29 21:47 | 2011-11-29 | UNIT EXPERIENCED AN AUTOMATIC REACTOR SCRAM DURING A PLANNED SHUTDOWN "During a planned shutdown in preparation for refueling outage C1R13, shortly after tripping the main turbine, an automatic reactor scram occurred due to high reactor steam dome pressure. Preliminarily, per the plant process computer, the reactor pressure was observed to reach approximately 1074 psig approximately 26 seconds after main steam bypass valves unexpectedly closed. An investigation will be conducted to determine the cause of the bypass valve closure and reactor scram. No safety relief valves lifted as a result of the pressure increase. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(B) as an event or condition that results in actuation of the reactor protection system when the reactor was critical." The licensee is manually controlling the steam bypass valves to remove decay heat via the main condenser. All control rods fully inserted. The Unit is in a normal shutdown electrical lineup. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-11-29
47488 | 0 | FLOWSERVE |  |  |  |  | 2011-08-02 | 2011-11-29 17:25 | 2011-11-29 | PART 21 NOTIFICATION ON LIMITORQUE SMB-5T ACTUATOR CLUTCH LUG FAILURE The following is a summary of information was received from Limitorque via facsimile: "On August 2, 2011, Flowserve-Limitorque was notified by Browns Ferry Nuclear (BFN) Generating Station that a Limitorque SMB-5T valve actuator (1-MVOP-074-052) had failed to run open automatically during the performance of a stroke test. Electrical maintenance personnel working at the valve reported an abnormal mechanical noise. Upon disassembly, it was found that the driving lugs on both the sliding clutch gear and the flexible clutch were seriously worn with a significant amount of deformation. Further investigation by BFN showed that the declutch mechanism would not allow full engagement of the drive lugs on the sliding clutch and flexible clutch. These lugs must be engaged for motor operation to take place. The declutch mechanism required adjustment to allow full drive lug engagement. "Following reassembly of the SMB-5T on 1-MVOP-074-052, an inspection was performed of the SMB-5T on valve 1-MVOP-074-066 which was manufactured and supplied to TVA at the same time. This actuator was functioning normally at the time of the inspection. Disassembly of the clutch compartment revealed evidence of deformation of the clutch drive lugs. To better evaluate the operation of the clutch components, the grease was cleaned out of the compartment and a boroscope used so that the action of the clutch could be seen. Boroscope examination of several declutching and re-clutching tests showed that the clutch lugs would not engage fully. The major contributing factor in this issue was found to be the external declutch lever stop screw adjustment. Adjustment of the lever stop screw significantly improved the lug engagement. Subsequently, BFN personnel inspected four additional SMB-5T actuators. The declutch components were found to be adjusted correctly and no indications of abnormal clutch lug wear were found. "The potential for this issue is limited to SMB-5 and SMB-5T actuators only. Other sizes of SMB/SB/SBD actuators are not affected. This issue, when it occurs can affect the safety related function of the actuator by preventing proper motorized operation. Indications of the issue can include failure to complete valve stroke, failure to remain in motorized operation, intermittent motorized operation resulting in longer than expected stroke time, and/or abnormal noise in the clutch compartment. "Limitorque performed an investigation per the guidelines of 10 CFR Part 21. The failure of 1-MVOP-074-052 to operate was due to damage to the drive lug interface between the sliding clutch and the flexible clutch which resulted in the actuator disengaging from electric motor operation in mid-stroke of the valve. This lug damage occurred over time during normal operation of the actuator and is directly attributable to an assembly set-up error resulting in partial lug engagement. The actuators which were investigated at BFN Unit 1 were of relatively recent manufacture, having been shipped from the Limitorque factory in 2004. Limitorque's review of existing SMB-5/5T assembly procedures followed by interviews with assembly personnel led to the conclusion that the root cause of this event was that the Limitorque factory assembly procedure documents for the SMB-5/5T lack adequate detail to ensure reliable long term functionality of the clutching mechanism. "Limitorque's review of previous industry operating experience did not show any history of problems related to drive lug engagement and/or declutch components in SMB-5/5T actuators. However to address the potential issue of insufficient drive lug engagement, Limitorque will issue a Maintenance Update to the MOV Users Group for distribution to the utilities (on or before January 15, 2012) containing recommendations for site inspection of the SMB-5/5T clutch mechanism as well as detailed instructions for set-up, adjustment and verification of proper clutch operation. As part of our internal corrective action, Limitorque will develop enhanced assembly and service procedures for the SMB-5/5T to include sufficient detail to ensure the proper set-up and function of the clutching mechanism. Limitorque assembly, field service, and QC personnel will be trained in the enhanced procedures." Technical contacts: John Thilking 434-522-9862 Jeff McConkey 434-845-9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-11-29
47487 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-11-29 07:22 | 2011-11-29 08:58 | 2011-11-29 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 11/29/11 AT 1941 EST FROM IHLENFELDT TO HUFFMAN * * * The licensee has retracted this report based on further investigation revealing the attempted introduction was inadvertent and that the contraband was interdicted prior to entry into the protected area. Contact the Headquarters Operations Officer for additional details. The licensee has notified state and local authorities and the NRC Resident Inspector. R3DO (Riemer) notified. The NRC 73.71 Group was notified via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-11-29
47486 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-04-25 12:00 | 2011-11-29 08:05 | 2011-11-29 | PENNSYLVANIA AGREEMENT STATE REPORT - UNSECURED RADIOACTIVE SOURCE The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "On April 25, 2011, an Ir-192 source (SN# D36C-5591), 3.36 Ci activity, was removed from a Nucletron microSelectron HDR unit, placed into an approved Type A source storage and transportation container, and moved to a secure designated HDR source storage location, awaiting return to the manufacturer. However, due to miscommunication, the source was never shipped back to the manufacturer and as a result, the source was relocated by contractors approximately a month later to an unoccupied storage room in an uncontrolled area of the building. The source was estimated to have decayed to 2.5 Ci. On October 10, 2011, the unoccupied storage room became the office of a new full-time physicist. The activity was estimated to be 0.69 Ci at this time. On October 27, 2011, the source was discovered during a routine inspection by the Department of Environmental Protection and immediately placed back into the permanent storage area within the HDR storage location. It was determined that the badged physicist who occupied the office received 5.6 mrem, however, his subsequent dosimeter reading indicated no measureable radiation exposure. The unmonitored contractor who moved the source was estimated to have received 0.6 mrem. "The source was returned to the manufacturer via [a national shipper] on November 10, 2011. In the future, the new full-time physicist will maintain control of all sources, as well as document when the sources actually leave the facility to be returned to the manufacturers. The licensee has also modified their policies and procedures. The Department [Pennsylvania Department of Environmental Protection] plans another reactive inspection." PA Event Report ID: PA110037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-12-02
47485 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-11-29 03:29 | 2011-11-29 06:55 | 2011-11-29 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON GENERATOR LOCKOUT "At 0329 CST on 11/29/2011, Unit 2 experienced an automatic Reactor Trip while the plant was stable at 100% power in Mode 1. All systems actuated as designed. The reactor trip was caused by Generator Lockout. "All ESF systems actuated as designed. The following systems actuated: Auxiliary Feedwater [AFW] and Feedwater Isolation. "All control rods fully inserted. Steam Dump system valve FV 7485 failed open and was manually isolated. This caused a letdown isolation that was restored. No primary/secondary relief valves lifted. There were no electrical bus transfer problems. Normal operating temperature and pressure [of] 567 degrees F and 2235 psig [is being maintained]. There were no significant TS LCOs entered." The electrical grid is stable and is supplying power to the plant via a normal shutdown electrical line-up. Decay heat is being removed via steam dumps to the condenser with AFW supplying the steam generators. There was no effect on Unit 1. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 11/29/11 AT 1312 EST FROM BRINKLY TO HUFFMAN * * * The licensee has issued a press release concerning this event. The NRC Resident Inspector will be notified. R4DO (Farnholtz) informed. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-11-29
47484 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-11-25 | 2011-11-28 19:52 | 2011-11-28 | AGREEMENT STATE REPORT - PACKAGE CONTAINING RADIOACTIVE MATERIAL LEFT UNATTENDED The following was received from the State of California via email: "During the holiday weekend, November 26, 2011, [a carrier] delivered a source containing 11.35 Ci of Ir-192 to Saint Joseph Hospital in Eureka, CA. There were no radiation safety personnel on site to receive the package and [the carrier] left the package with the receptionist, who is not authorized to receive radioactive material. The package was stored in the shipping and receiving area over the weekend. On Monday, November 28, 2011, the RSO became aware that the package had been sitting unsecured in the shipping and receiving area all weekend and notified the CA/RHB (California Radiation Health Branch)." CA 5010 Number: 112811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-12-01
47483 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-11-28 09:30 | 2011-11-28 19:12 | 2011-11-28 | 24-HOUR REPORT CONCERNING A LOCALIZED LOSS OF A GEOMETRY CRITICALITY CONTROL CONTINGENCY "At 0930 CST on 11-28-11, during annual inspection of the C-400/C-409 floor drains and sumps according to procedure CP4-CU-CH6021, a chemical operator identified that an eye wash drain was no longer properly sealed around the concrete base and would not prevent solutions from entering the drain if challenged. NCSA [Nuclear Criticality Safety Assessment] CHM-001 requires specific drains to be sealed to prevent the accumulation of fissile material in the unsafe geometry drain system. In violation of NCSA CHM-001, the poured concrete base surrounding the eye wash drain #147 in C-400 was discovered to be broken loose from the floor so that it could no longer provide a seal against spilled uranium solution getting into the drain system. SAFETY SIGNIFICANCE OF EVENTS "Although the concrete block has broken loose from the floor, only a small crack exists at the base of the concrete block which would present a torturous solution path to the drain. Therefore, a large release will be prevented from transporting a significant amount of solution to the drain system. While the Safety Related Item failed, no fissile material was released onto the C-400 building floor and no fissile material entered the drain system through this drain. POTENTIAL CRITICALITY PATHWAYS INVOLVED "In order for a criticality to occur a release of greater than a safe mass of uranium onto the floor of C-400 would have to occur. A solution containing greater than a safe mass would then have to migrate to the drain, leak into the drain system, and accumulate in an unfavorable geometry. CONTROLLED PARAMETERS "The two process conditions relied upon for double contingency for this scenario are mass and geometry. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL "Process is designed to handle uranium contaminated solutions with a maximum assay of 5.5 wt.% U235. NUCLEAR CRITICALITY SAFETY CONTROL AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "The first leg of double contingency is based on the mass of uranium in solution form that leaks out of the system. The analysis credits both the integrity of the system and the fact that the tanks and piping are inspected for leakage. Small leaks will be identified and fixed before they have leaked enough uranium mass in solution to be a concern. Since no leakage has occurred, this control was not violated. The second leg of double contingency relies on the integrity of the floor drain seals to prevent uranium solution from getting into the unsafe geometry drain system. Since a pathway from the floor to the drain system exists, this control was violated and the parameter was not maintained. Because the parameter was not maintained double contingency was not maintained. Double contingency was not maintained because the geometry parameter was not maintained. CORRECTIVE ACTIONS "1. Stop fissile solution operations in the vicinity of the eyewash drain. This was completed at 1000 CST on 11-28-11. 2. Restore the seal to this drain. Pending 3. Upon successful restoration of the seal for the eyewash drain #147, fissile solution operations may be resumed. Pending "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-11-3171 and PGDP Event Report No. PAD-2011-20." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2011-11-28
47482 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-11-28 16:50 | 2011-11-28 18:40 | 2011-11-28 | OFFSITE NOTIFICATION OF OIL SHEEN IN DISCHARGE CANAL "At approximately 1650 EST on 11/28/2011 an oil sheen of about 20 ft. in diameter was observed in the Unit 2 discharge canal. The source of the oil is unknown at this time. There is no adverse impact on the plant. All required notifications have been made, including the New York State Dept. of Environmental Conservation, Westchester County Dept. of Health, and the U.S. Coast Guard National Response Center." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-11-28
47481 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2011-11-28 06:00 | 2011-11-28 12:34 | 2011-11-28 | OFFSITE NOTIFICATION OF UNPLANNED ACIDIC SOLUTION DISCHARGE "During the regeneration of the Unit 2 full flow condensate polishing demineralizer (FFCPD) resin, 5 percent sulfuric acid briefly overflowed from the bermed area. The majority of the acid went into the floor drains in the FFCPD area and then to the turbine building sump system. "An estimated quantity of 2 gallons of sulfuric acid was released into the storm drains that discharged into the circulating water system. The quantity released was well below the reportable quantity. The fire department and environmental/hazmat team were contacted and responded. "Precautionary notifications were made by SCE to: - California Emergency Management Agency - San Diego Dept. of Environmental Health." The cause of the leak has been corrected and no additional discharge is anticipated. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-11-28
47480 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-11-18 07:00 | 2011-11-28 09:17 | 2011-11-28 | NORTH CAROLINA AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was obtained from the State of North Carolina via email: "On November 18, 2011, the RSO of Research Triangle Institute (RTI), License Number 032-0131-1, performed a leak test on a sealed source. The results of the leak test revealed greater than 0.005 microcuries of removable contamination. The leak test showed 0.00517 microcuries of removable contamination. Subsequent surveys continued to show elevated results. "The survey was performed with a Packard 1900 TR liquid scintillation counter, S/N 103761, calibrated Aug. 24, 2011. "The source was a Ni-63 Electron Capture source. It had been removed from service and placed in storage in 2008. The source was being leak tested to prepare for disposal. Upon determination that the source was leaking, the RSO double-bagged the source, removed it from storage and segregated it, and contacted the waste broker for instructions on source disposal. The RSO performed contamination surveys of the storage area and the area is clean. "Source information: "Isotope: Ni-63, Quantity: 11.3 mCi, Mfg: Franklin GNO Corporation, Drawing No: 801-023, Serial Number: 37, Source date: October 20, 1975 "The licensee met all reporting requirements for the 5-day notification of a leaking source and is preparing a report with additional information." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-12-01
47479 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-11-27 16:57 | 2011-11-28 01:04 | 2011-11-28 | ROD WORTH MINIMIZER CONTROL SWITCH FOUND OUT OF REQUIRED POSITION "After transitioning to Mode 2 from Mode 4, while performing the Rod Worth Minimizer (RWM) operability test, it was discovered that the RWM control switch was in the BYPASS position. The RWM enforces predetermined control rod withdrawal and insertion sequences. Complying with these predetermined sequences ensures a Control Rod Drop Accident does not exceed analytical limits. With the control switch in the BYPASS position, the RWM was inoperable and would not have enforced the predetermined control rod withdrawal sequence. The RWM control switch was restored to the OPERATE position and the RWM was verified to be operable. "This issue is being reported under 50.72(b)(3)(v)(D) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of the RWM, which is a system needed to mitigate the consequences of the Control Rod Drop Accident." The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-11-28
47478 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2011-11-27 02:38 | 2011-11-27 04:22 | 2011-11-27 | UNUSUAL EVENT DUE TO A LOSS OF OFFSITE POWER DURING SWITCHING OPERATIONS "At 0238, Point Beach Unit 1, classified an Unusual Event based on CU3.1, loss of power to or from the 1X-04 transformer that results in a loss of all offsite power to both safety-related busses 1A-05 and 1A-06 for greater than 15 minutes and at least one emergency [diesel] generator is supplying power to an emergency bus." The licensee was restoring transformer 1X-03 when the upset occurred that tripped the 1X-04 transformer. The 1X-03 transformer converts 345kV to 13.8kV. The 1X-04 transformer converts 13.8kV to 4160V. Both Emergency Diesel Generators are running supplying the safety-related busses. The licensee notified State and local agencies and the NRC Resident Inspector. * * * UPDATE FROM KARL COSSEY TO JOHN KNOKE AT 0843 EST ON 11/27/11 * * * "Off-site power to Unit 1A-05 and 1A-06 Safeguards Busses has been restored via Unit 2 2X-03 High Voltage Station Transformer and 1X-04 Low Voltage Station Transformer. "During the transient, all four Emergency Diesel Generators (EDGs) started as expected with G-01 EDG supplying the Unit 1 1A-05 Safeguards Bus and G-03 EDG supplying 1A-06 Safeguards Bus. Off-site power to the Unit 2 Safeguards Buses was not affected. The start of the EDGs is also reportable under 10CFR 50.72 (b)(3)(iv)(A). "All systems responded as designed during the transient and operators performed in accordance with procedures and their training. Unit 1 is stable in Mode 5 within normal operating bands. Unit 2 remains operating at 100% power. The Unusual Event was terminated at 0700 [CST] on November 27, 2011. A press release is planned." The licensee has notified State and local agencies and the NRC Resident Inspector. Notified R3DO (Julio Lara), IRD MOC (Jane Marshall), NRR EO (Sher Bahadur), DHS (Rickerson), and FEMA (Hollis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-11-27
47477 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-11-25 05:23 | 2011-11-25 06:32 | 2011-11-25 | AUX FEEDWATER PUMP START AFTER MAIN FEEDWATER PUMP TRIP "At 0522 EST on November 25, 2011, operators manually started all Auxiliary Feedwater (AFW) pumps in response to a manual trip of the Unit 1 East Main Feedwater Pump due to bearing failure. "Operators were responding to increasing vibrations on the East Main Feedwater Pump and reducing turbine load when the East Main Feedwater Pump was manually tripped [at approximately 90% power] due to high vibrations. Operators entered the abnormal operating procedure for Loss of One Main Feedwater Pump, which directs starting all three AFW pumps. "Plant power was stabilized at approximately 58%. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A) due to the valid actuation of the AFW system in response to equipment failure." | 58 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-11-25
47476 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-11-24 03:15 | 2011-11-24 11:17 | 2012-01-18 | EMERGENCY 4160 VOLT AC BUSSES DECLARED INOPERABLE "On Thursday, November 24, 2011, at 0315 CST, with the reactor at 100% steady state thermal power, Kewaunee Power Station declared both emergency 4160 Volt AC busses inoperable due to voltages being high outside of the procedurally directed voltage band. As a result, in accordance with Technical Specification 3.8.9, Distribution Sources - Operating, Kewaunee entered Technical Specification LCO 3.0.3 to, within 1 hour, initiate shutdown of the unit. At 0410 [CST], per management direction, the load tap changers for the supply transformers were adjusted to reduce the emergency bus voltages to within their procedural operating band. At this time, both emergency busses were declared Operable and LCO 3.0.3 was exited. Minimum required accident voltages were met at all times. "The NRC Resident Inspector has been notified." * * * RETRACTED AT 1515 EST ON 01/18/12 FROM RICHARD REPSHAS TO S. SANDIN * * * "On November 24, 2011, EN # 47476 provided notification that both emergency 4160 Volt AC busses were inoperable based on voltages being high outside of a procedurally directed voltage band. "Subsequent investigation and analysis determined that unnecessary conservatisms were used in the development of the voltage values used in procedure, OSP-MISC-002, Electrical Power System Weekly Surveillance Test. Review of the actual voltages present during the event determined that the voltages did not exceed the required values to support bus operability. "Therefore, the busses remained operable and this condition did not meet the reportability criteria identified in 10 CFR 50.72. As a result, the notification made on 11/24/2011 is hereby retracted." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-24
47475 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-11-03 03:48 | 2011-11-24 00:05 | 2011-11-24 | INVALID ACTUATION OF A SAFETY INJECTION VALVE "This telephone notification is being made in lieu of submitting a written LER under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of MOV 8803A, High Head Safety Injection (HHSI) to RCS Cold Leg, resulting in ECCS injection into the RCS. "On November 3, 2011 at 03:48 CST, during a maintenance replacement activity for the K604 slave relay in Solid State Protection System, MOV 8803A unexpectedly opened. The relay was not recognized to be in a latched condition when the lead associated with MOV 8803A was landed causing it to stroke open. This actuation was invalid since the stroke signal was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. MOV 8803A was subsequently closed from the control room in approximately 2 minutes and power was removed at 03:57 CST to prevent another stroke. After investigation, the relay was installed in the correct configuration and system tested to restore operability. This event did not adversely affect the safe operation of the plant or health and safety of the public. "The following required information is being submitted per NUREG-1022, Rev. 2: (a) MOV 8803A is an 'A' Train component. (b) The stroke open of MOV 8803A and ECCS injection is a partial train actuation. (c) Given the conditions, MOV 8803A functioned as expected and all other systems functioned per design." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-11-24
47474 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-11-23 | 2011-11-23 16:53 | 2011-11-23 | AGREEMENT STATE REPORT - LOST OR MISSING IODINE-125 PLAQUE SEED "On November 23, 2011, during a physical inventory of iodine-125 seeds to be returned to the vendor, it was determined that one (1) iodine-125 eye plaque seed was missing. The patient and room surveys were conducted at the time of the eye plaque procedure (late May) to verify no seed had been left in the patient or the room, and that all sources were returned from the procedure to the source storage room. The manufacturer's assay was 2.94 mCi per seed on May 20, 2011. The assay at the time of the procedure was within 3% of the manufacturer's assay. All attempts to identify the time, location, or the passage of disposal did not produce a definite result. "The Wisconsin Department of Health Services (DHS) followed up with the licensee by phone and will conduct an investigation the first week of December." Event Report No.: WI110020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-11-28
47473 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-11-22 17:00 | 2011-11-23 01:43 | 2011-12-16 | TEMPORARY LOSS OF SHUTDOWN COOLING "During walkdown of scheduled work it was discovered that HCV-335 (Shutdown Cooling Heat Exchanger Inlet Header Isolation Valve) would not be able to be manually positioned open due to a missing idler gear key. "Upon a loss of instrument air, HCV-335 would have failed closed, interrupting shutdown cooling flow with no ability to open HCV-335 manually. "Alternate shutdown cooling pump and paths were available at the time of discovery. No loss of instrument air or interruption in shutdown cooling flow occurred while preparing to align alternate shutdown cooling. An 8 hour LCO under Technical Specification 2.8.1(3)2 was entered at 1700 CST. Alternate shutdown cooling was established on a containment spray pump as allowed by procedure. The 8 hour LCO was exited at 2306 CST. A replacement idler key has been fabricated for HCV-335." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO PETE SNYDER AT 1654 EST ON 12/16/11 * * * "Additional analysis has determined that the shutdown cooling system was capable of performing its design safety functions during the time that the idler key was missing. Therefore this event is being retracted." The licensee notified the NRC Resident Inspector. Notified R4DO (Walker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-11-23
47472 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2011-11-22 19:25 | 2011-11-22 23:03 | 2011-11-22 | MANUAL REACTOR TRIP DUE TO CONTROL ELEMENT DEVIATION "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "PVNGS [Palo Verde Nuclear Generating Station] [Unit 1 was in the process of Low Power Physics Testing following a refueling outage. The Unit was at 0.4 percent power and performing individual CEA [Control Element Assembly] group worth testing. Specifically Regulating Group (RG) 2 was being inserted while RG 4 was being withdrawn. During the CEA manipulations, it was identified that there was a CEA deviation on RG 2 subgroup 17 that exceeded 6 inches from the remainder of the RG. RG 2 subgroup 18 was at 134 inches withdrawn and RG 2 subgroup 17 had two CEAs at 124 inches, one CEA at 122 inches and one CEA at 118 inches withdrawn. The CEA Malfunctions abnormal operating procedure 40AO-9ZZ11 was entered and a manual reactor trip was directed by the Control Room Supervisor. The reactor was tripped at 1925 hours. "Unit 1 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 1 reactor trip and this notification." | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-11-22
47471 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-11-22 13:53 | 2011-11-22 18:50 | 2011-11-22 | INADVERTENT ACTUATION OF A DRYWELL-TO-SUPPRESSION CHAMBER VACUUM RELIEF VALVE "This report is being made pursuant to 10CFR50.72 criteria (b)(3)(v)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "At time 1353 CST on 11/22/11, a licensed operator inadvertently bumped the Torus-to-Drywell vacuum relief Master Control Switch for the Drywell-to-Suppression Chamber vacuum relief valves from the 'close' position to the 'open' position. One of the twelve vacuum relief valves controlled by the Master Control Switch indicated an open indication. The other eleven vacuum relief valves did not operate due to having the pneumatics secured to the operator. Immediately upon recognizing the condition, the licensed operator returned the switch to the closed position. The open vacuum relief valve indication changed to the closed indication. From automatic alarm logging, the time that the vacuum relief was open was recorded as six seconds. The vacuum relief valve has a safety function in the closed position to limit the amount of bypass flow to ensure proper containment response on a postulated LOCA event and an open safety function post-LOCA to limit negative differential pressure between the drywell and the suppression chamber. With the valve partially open, the LOCA containment response cannot be assured. This results in declaring the primary containment inoperable. "The vacuum relief valve manual operators have air secured during normal operation. With air secured, only one of the twelve valves operated versus all twelve. A valve line-up was performed and all pneumatic supply valves were in the proper line-up. Currently, the only unusual occurrence is why there was sufficient air to the individual vacuum relief valve that caused it to operate in the open direction. This will be resolved within the corrective action program. "Currently, all twelve Drywell-to-Suppression Chamber vacuum relief valves are closed and in the normal line-up. "[The] NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-11-22
47470 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-08-15 | 2011-11-22 18:20 | 2011-11-22 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via telephone: On or about August 15, 2011, Lighting Systems, Inc. shipped three tritium exit signs to a customer via UPS. Upon delivery, the customer refused receipt of the signs. UPS retained possession of the signs. UPS has not returned the signs to Lighting Systems, Inc. and has been unable to locate the signs. Each sign contained 7.5 Curies of tritium. Model number: SLX-60. Serial numbers: 11-14985, 11-14986, and 11-14987. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-11-25
47469 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-18 07:00 | 2011-11-22 18:03 | 2011-11-22 | TEXAS AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE The following information was obtained from the State of Texas via email: "On November 18, 2011, the Agency [Texas Department of State Health Services] was notified that a licensee had lost, and subsequently abandoned, a logging tool containing a 20 milliCurie cobalt (Co)-60 sealed source at a depth of approximately 5,100 feet down a well in Matagorda County, Texas. The well is a brine solution well that was converted to gas storage; it is a domed salt cavern. There is no rig on the well and the source is at the bottom of the cavern. There is no danger of rupture or exposure. There are no plans to enter the well or cavern in the near future with tubing or wire line. No further action will be taken to retrieve the tool. "Source information: 20 milliCurie Cobalt-60 "Manufacturer: Eckert and Ziegler "Model: HEG-060 "SN: CZ3507" Texas Incident No.: I-8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-25
47468 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2011-11-14 07:00 | 2011-11-22 16:53 | 2011-11-22 | NEW YORK AGREEMENT STATE REPORT - GAMMAKNIFE THERAPY UNDERDOSE DUE TO MECHANICAL FAILURE OF DEVICE The following information was obtained from the New York City Office of Radiological Health via email: "Type of event: Therapy, gammaknife "Description of event: Patient was being treated by gammaknife Model C-23004 for a meningioma. Halfway through, the treatment was automatically terminated. It was discovered that the latch that fastens the immobilizing frame of the head to the couch failed. Termination of treatment resulted in an underdose of more than 50% below the prescribed dose for that fraction. This was the third of three patients who were being treated at about that time. The first two patients were treated without incident. "Discovery of Event: Event was discovered when treatment was automatically terminated in the course of treatment. "Effect on Patient: In the opinion of the responsible physician, there are no expected sequelae for this patient as a result of this event. "Root Cause of Event: The root cause of this event was mechanical failure. There was not found to be any computer failure involved. "Actions Taken to Prevent Recurrence of Event: Replacement of latch mechanism. "Inspection Results: An inspector from the [NYC] Office of Radiological Health conducted an inspection on 11/17/11. The inspector found the circumstances of the event to be as described above. "Any Issuance of Violations: No formal violation was issued. "This case is considered closed." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-11-28
47467 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-11-16 07:00 | 2011-11-22 16:28 | 2011-11-22 | KENTUCKY AGREEMENT STATE REPORT - WRONG BRACHYTHERAPY TREATMENT PLAN PERFORMED ON WRONG PATIENT The following information was obtained from the Commonwealth of Kentucky via email: "Kentucky RHB [Radiation Health Branch] was notified via e-mail on 11/17/11 at 10:30 a.m. [EST] and via telephone call on 11/17/11 at 10:45 a.m. of a possible medical event occurring on 11/16/11. The medical event involved using the wrong permanent prostate brachytherapy implant treatment plan on the wrong patient. The facility performed back to back procedures on two patients on two consecutive days and the implant procedure used on the second patient was actually developed for the first patient. The RSO reported that immediately after completing the procedure, the mishap was noted by the Radiation Oncologist and a post implant CT and MRI were performed immediately. The Radiation Oncologist who developed the treatment plan and performed the procedure determined the dose delivered to the target organ based on D90 was 90%. According to the RSO, written directives for both patients called for the same number of seeds of the same radionuclide and same activity and both called for the same prescribed dose thus accounting for the oversight on the part of the Radiation Oncologist. These similarities however, allowed for a D90 of 90% despite the wrong treatment plan being used. The State will continue to keep NRC informed of the status of their investigation." The patient was given 79 seeds with 0.0406 mCi of I-125 per seed (STM 1251). The manufacturer was Bard Brachytherapy Inc. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-11-28
47466 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2011-11-21 17:00 | 2011-11-22 14:43 | 2011-11-22 | CONFINEMENT NOT MAINTAINED AS REQUIRED BY TECHNICAL SPECIFICATIONS Yesterday afternoon, while performing retests on replacement control shim arm switches, reactor operators placed the reactor in a condition that would allow more than one shim control rod to be withdrawn. This violated Technical Specification 3.4.1, "Operations that require confinement." The reactor facility did not have full confinement in place at that time. The specific language of Technical Specification 3.4.1 is "Confinement shall be maintained when changes of components or equipment within the confines of the thermal shield, other than rod drop tests or movement of experiments, are being made which could cause a significant change in reactivity." Although the shim control rods were not withdrawn and the rod bottom lights never cleared, the circumstances, in the licensee's opinion, were that they could have caused a significant change in reactivity, allowing more than one control rod to be withdrawn when the reactor was not in full confinement. The licensee notified the NRC Reactor Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MD | NPR | [5 empty] | 0 | 2011-11-22
47465 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2011-11-09 08:30 | 2011-11-21 18:19 | 2011-11-21 | UTAH AGREEMENT STATE REPORT - AUTOMATIC LOCKING MECHANISM FAILED ON RADIOGRAPHY CAMERA The following information was obtained from the State of Utah via facsimile: "On November 9, 2011 at about 8:30 AM [MST], [the licensee RSO] was contacted by one of [their] radiographers and told that the self locking mechanism on one of [their] cameras was not working. The camera was SN D7217 manufactured by Sentinel. The model is a 880 Delta which was purchased new in January of this year and put into service February 4, 2011. Though the camera did not automatically lock when the source had been returned to the shielded position, the lock slide had been manually returned to the locked position after retracting the source and a survey by the radiographer showed that the source was shielded and the camera was then locked. [The radiographer] is a level II IRRSP [Industrial Radiography and Radiation Safety Personnel] certified radiographer who was working in [the facility's] permanent installation B cell when the incident occurred. The entrance and area alarm for B cell were working properly at the time of the event and confirmed what the survey showed which was that the source was in the shielded position. [The radiographer] demonstrated that the lock slide was not coming back over to lock the camera automatically when the source was returned to the camera as it was designed to do. After the demonstration, the camera was surveyed to ensure the source was in the shielded position, the slide lock was then slid to the lock position manually, the camera locked and [was] removed from service. The radiographer did not receive any radiation exposure associated with the failure of the slide lock mechanism. "[The RSO] contacted the manufacturer the same day and was instructed to return the camera for repair. The camera had a 13.7 Ci Ir-192 source in it. The camera was sent overnight to Sentinel/QSA Global in Baton Rouge, La.. [The RSO] was contacted by the service technician the next afternoon, November 10, 2011. He informed [the RSO] that one of the springs had broken and that was the cause of the malfunction of the slide lock. A new rear plate assembly was installed by Sentinel and the camera was then returned to [the licensee] facility with a new Ir-192 source of 97 curies. The camera was put back into service on Monday November 14, 2011 and has been operating properly since." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2011-11-24
47464 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-11-21 16:06 | 2011-11-21 17:51 | 2011-11-21 | OFFSITE NOTIFICATION DUE TO FISH KILL "At 1606 Central Standard Time, Xcel Energy Environmental Services made a report to the State of MN regarding 190 fish killed from the discharge canal temperature transient during the reactor scram on 11/20/11. The report was made verbally with a follow-up email message detailing the species of fish killed. "This is a notification being made under 50.72(b)(2)(xi) as an event related to the environment for which notification to other government agencies have or will be made." The licensee has notified the NRC Resident Inspector and the State and will notify local authorities of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-11-21
47463 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-17 07:00 | 2011-11-21 15:23 | 2011-11-21 | TEXAS AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING Y-90 MICROSPHERES The following information was obtained from the State of Texas via email: "On November 21, 2011, the Agency [Texas Department of State Health Services] was notified by one of its licensees that it had determined that a therapy event had occurred on November 17, 2011, during an administration of Yttrium-90 microspheres. The patient was prescribed a dose of 135 gray to the target tissue. Surveys of the administration equipment following the procedure indicated readings that were higher than expected if the full dose had injected into the patient. Initial estimates by the licensee are that a dose of 95.8 gray was administered to the target tissue, approximately a 29% variation from the prescribed dose. The licensee will confirm the dose administered and investigate to determine the cause of the event. Information on this event will be updated as it becomes available." Texas Incident #: I-8904 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-27
47462 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-11-21 09:00 | 2011-11-21 15:15 | 2011-11-21 | UNPLANNED MEDICAL TREATMENT OF A CONTAMINATED INDIVIDUAL "On November 21, 2011, at 0900 [CST] a Honeywell employee entered the plant's dispensary for unplanned medical treatment for chest pain. [The] employee's plant shoes and coveralls were contaminated. After [the] individual's boots were removed and coveralls were cut off, he was surveyed . Upon decontamination, all readings on the patient did not exceed background. The patient was sent by ambulance to Baptist Hospital for evaluation. "Reporting Requirement: 10 CFR 40.60(b)(3), Unplanned medical treatment in a medical facility of an individual with spreadable contamination. "Isotope, Quantities and Chemical Form: Uranium Ore Concentrate, U3O8." The licensee informed NRC Region II (Joe Calle). The licensee stated that there was no contamination elsewhere in the facility as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-11-21
47461 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2011-11-20 17:58 | 2011-11-20 20:37 | 2011-11-20 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM DURING STARTUP Millstone Unit 3 was manually tripped at low power during startup following the loss of condenser vacuum. The loss of vacuum was caused by the loss of the auxiliary steam boiler. The auxiliary steam boiler supplies gland seal steam to the turbine at low power and without the gland seal steam, the licensee could not maintain a condenser vacuum. All rods fully inserted and there were no complications during the trip. All systems functioned as required and the unit is stable in Mode 3. There was no impact on Unit 2. The licensee has notified state and local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Startup; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-11-20
47460 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-11-19 23:12 | 2011-11-20 02:10 | 2011-11-20 | AUTOMATIC REACTOR SCRAM WHILE PERFORMING TURBINE BYPASS VALVE TESTING "While performing a regularly scheduled Turbine Bypass Valve surveillance, prior to Turbine Bypass Valve movement, a 'B' half scram [signal] was received. Operators immediately suspended testing. Approximately 10 seconds later, a full Reactor Protection System actuation occurred. Following the reactor scram, reactor water level lowered below the Group II isolation initiation setpoint of +9 inches, [resulting in containment valve isolations]. There were no radioactive releases associated with this event. "No other alarms were received prior to the RPS actuation. The cause of the reactor scram is under investigation at this time. "Also, due to the reactor scram, discharge canal temperature rate of change exceeded plant requirements. As a result, the State of Minnesota, and appropriate local agencies will be notified." All control rods inserted and the scram is considered uncomplicated. The plant is in a normal shutdown electrical configuration. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2011-11-20
47459 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2011-11-19 08:28 | 2011-11-19 16:48 | 2011-12-15 | THE LOW PRESSURE SAFETY INJECTION SYSTEM WAS SUBJECTED TO HIGH PRESSURE RESULTING IN BOTH TRAINS BEING DECLARED INOPERABLE "On November 19, 2011, Unit 1 was in Mode 3. Boration of the four reactor coolant system (RCS) cold leg injection lines was in progress using High Pressure Safety Injection pump 'A'. "During this activity, 'SI CHK VLV Leak Pressure Hi' alarms were received at 0828 [MST]. The 'A' and 'B' Low Pressure Safety Injection (LPSI) subsystems were declared inoperable because the pressure downstream of the motor operated LPSI injection valves was above 1525 psia. This elevated pressure potentially impacts the ability of the LPSI RCS loop injection valves to open. The high differential pressure may exceed the capability of the motor operator. All four injection line pressures were found above 1525 psia and LCO 3.0.3 was entered due to both trains of LPSI being inoperable. At 0839 [MST], pressure in the 'A' train injection lines was lowered below 1525 psia and 'A' LPSI subsystem was declared operable and LCO 3.0.3 was exited. At 0842 [MST], pressure was reduced below 1525 psia on the 'B' train injection lines and the 'B' LPSI subsystem was declared operable and LCO 3.5.3 condition A was exited. "This call is being made to report a condition that could have prevented the fulfillment of a safety function required to mitigate the consequences of an accident and unanalyzed condition that existed for 11 minutes while both LPSI subsystems were inoperable. "The NRC Resident Inspector has been notified." * * * RETRACTION RECEIVED FROM DANIEL HAUTALA TO CHARLES TEAL AT 1546 EST ON 12/15/11 * * * "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via ENS or under the reporting requirements of 10CFR50.73. "This notification is a retraction of ENS 47459 which was made by Arizona Public Service to report a condition that could have prevented the fulfillment of a safety function required to mitigate the consequences of an accident and an unanalyzed condition that existed for 11 minutes while both LPSI subsystems were declared inoperable when pressure downstream of the motor operated injection valves for safety injection subsystem were declared inoperable. An engineering review of the motor operated valves thrust and torque calculations determined that the affected valves would have been fully capable of performing their intended safety function at the time of the pressure excursion. "The NRC Resident Inspector has been notified of this retraction." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-11-19
47458 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-11-17 15:48 | 2011-11-18 15:45 | 2011-11-18 | AGREEMENT STATE REPORT - PATIENT RECEIVED GREATER THAN THE PRESCRIBED DOSE A patient had a mass surgically removed from both sides of the nose and was undergoing a topical treatment for microscopic disease using a Nucletron HDR containing 8.52 curies of Ir-192 with a Valencia Model H3 skin applicator containing a platinum filter. The planned administration was 7 fractions of 600 centigrays each on both the left and right side of the nose. During the initial planning for the treatment, an error was made in calculating the dwell time for each location and this incorrect data was entered into the HDR system. As a result of the error, the patient received 54% during each fraction (treatment) during two of the seven fractions on each side of the nose. Prior to the third fraction, the medical team is required per procedure to check calculations and caught the error before the third fraction (treatment) was performed. The patient and prescribing physician have been informed, and there is no long range medical concern for disease as a result of this error. The total dose treatment has not been exceeded. The state's licensee is revising procedures in order to prevent recurrence, and the state will be submitting an NMED report. New Jersey Incident Number: #410674 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-11-24
47457 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-11-18 13:30 | 2011-11-18 15:21 | 2011-11-18 | LOCAL POWER RANGE MONITOR (LPRM) STORED IN SPENT FUEL POOL CANNOT BE LOCATED "At 1330 [CST] on 11/18/11, Nuclear Engineering reported to Operations that during a Special Nuclear Material (SNM) Physical Inventory they were unable to locate an individual LPRM [Local Power Range Monitor] detector that was believed to be loose in the bottom of the Spent Fuel Pool. Efforts remain in progress to locate the material in the pool." The licensee stated that during a previous refueling, a 4-detector LPRM string had been removed from the core and placed in the spent fuel pool. At the time, the string had been cut and a single detector at the bottom of the string had fallen to the bottom of the spent fuel pool under the fuel racks. Today, the licensee attempted to retrieve the LPRM detector for placement in a special storage canister in a controlled location that could be easily inventoried. During the retrieval attempt, the licensee could not locate the LPRM detector. There is no indication at this time that the detector has been inadvertently removed from the spent fuel pool and disposed of. The licensee believes that the detector is still in the pool and just needs to be located. The specific information on the detector was not available at the time of this report but the licensee is conservatively assuming the it contained greater than 1 gram of Uranium-233 and is therefore reportable under 10 CFR 74.11. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 74.11(a) |  |  |  | 0 | 2011-11-18
47456 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2011-10-27 | 2011-11-18 13:35 | 2011-11-18 | AGREEMENT STATE REPORT - EXTREMITY OVEREXPOSURE FROM FLUORINE-18 The Kansas Department of Health and Environmental Services provided a notification via facsimile concerning an employee working for a State licensee (PFI LLC) who apparently received an extremity overexposure of 53,010 mrem during the month of September while processing the radiopharmaceutical Fluorine-18. No additional details concerning the circumstance of how the overexposure occurred was provided in the State's report. The Headquarters Operations Officer was unable to contact the originator of the report for additional information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2011-11-23
47455 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2011-11-18 05:30 | 2011-11-18 12:13 | 2011-11-18 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) DISCOVERED TO BE OUT OF SERVICE "At 0530 EST on 11/18/11, it was identified that communication capability to the NRC ERDS link from the Emergency Response Data Acquisition and Display System (ERDADS) was disabled for St. Lucie Unit 2. The loss of communication occurred due to an issue within the FPL network that was resolved at 1024 EST on 11/18/11. The loss [of the ERDS link was determined to have] occurred on 11/15/11 and is under investigation. The details of this investigation will be documented via the corrective action process. St. Lucie Unit 1 communication capability was maintained by the ERDS modem." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-18
47454 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-11-17 15:15 | 2011-11-17 18:00 | 2011-11-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE FEEDWATER CHECK VALVE "On Thursday, November 17, 2011, at 1515 hours, with the reactor at approximately 50% core thermal power, the station entered a 24 hour cold shutdown action statement due to the inability to provide a manual isolation for a main feedwater line check valve that had been declared inoperable due to a leak. As background, the reactor was at reduced power in order to perform a planned main condenser thermal backwash. While at reduced power an inspection of the main steam tunnel (a normally locked closed high radiation area) was performed as part of a scheduled system inspection. The inspection identified a leak on the feedwater line 'B' outboard check valve (6-CK-62B). The feedwater check valve was declared inoperable and the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.7.A.2.a.5 was entered. Because there is no ability to manually isolate the primary containment penetration the station is required to be in cold shutdown within 24 hours per TS 3.7.A.5. "Currently, preparations are being completed to conduct the reactor shutdown and to initiate check valve repairs. "This event had no impact on the health and safety of the public. The USNRC Senior Resident Inspector was onsite and has been notified." The electrical lineup is normal and all safety related equipment required for shutdown and cooldown are operable. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-11-17
47453 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-11-17 14:20 | 2011-11-17 17:17 | 2011-11-17 | OFFSITE NOTIFICATION DUE TO DIESEL FUEL OIL SPILL "A notification was made to the National Response Center and the Kansas Department of Health and Environment of a 7-10 gallon release of diesel fuel oil to the environment. The leak originated from a temporary diesel fueled heater in place for freeze protection for a temporary fire pump. The fuel oil was not released to surface water, and has been isolated." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-11-17
47452 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-11-17 13:45 | 2011-11-17 16:58 | 2011-11-17 | UNANALYZED CONDITION ON STARTUP FOLLOWING MAINTENANCE OUTAGE "On November 17, 2011, at 1345 Eastern Standard Time (EST), it was determined that an unanalyzed condition that significantly degraded plant safety existed on Unit 2 following a mid-cycle maintenance outage which required reactor vessel disassembly. Unit 2 had reached Mode 2 (i.e., Startup) during the power ascension, when elevated drywell leakage was identified and the plant was shutdown (see EN#47444). Unit 2 was subsequently operating in Mode 4 (i.e., Cold Shutdown) to allow for drywell entry. During leak investigation activities, it was determined that the reactor pressure vessel (RPV) head was not fully tensioned. This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition of the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "The safety significance of this event was minimal. Unit 2 was in power ascension operating at a maximum of approximately 7% of rated thermal power. Control Room Operators took appropriate action to shutdown the Unit when elevated drywell leakage was identified. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-17
47451 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2011-11-14 18:20 | 2011-11-17 16:31 | 2011-11-17 | AGREEMENT STATE REPORT - THEFT OF A TROXLER DENSITY GAUGE The following report was received from the Mississippi Division of Radiological Health (DHR) via e-mail: "The licensee's RSO contacted DRH to report the theft of their Troxler Model 3440 (S/N 22563) nuclear gauge that was secured in the back of their white marked pick-up truck parked six spaces from the front entrance of the Wal-Mart [located in Meridian, MS]. The two gauge cables were cut and the gauge was taken out of the truck bed. All required shipping documentation was stolen out of the unlocked cab of the truck. The gauge and gauge paperwork were estimated to have been stolen around 1820 [CST]. The gauge was stored in the yellow plastic transport case with Radioactive Yellow II labels attached. The yellow plastic transport case had two locks on the outer container and two cables threaded through the top handle and locked with two separate locks on each separate eye hook. "Meridian City Police were immediately notified by the licensee. Licensee notified Mississippi Emergency Management Agency (MEMA) at 1940 [CST]. MEMA contacted DRH at 1955 [CST]. DRH notified Department of Homeland Security (DHS) who then notified FBI. "DRH performed an inspection and investigation on November 16, 2011 at Terracon Consultants, Inc., in Ridgeland." The gauge contained the following sources: Cs-137 (S/N 75-4297) (8 mCi); Am-241:Be (S/N 47-18403) (40 mCi) Mississippi Report MS-11006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-11-22
47450 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-09-19 10:00 | 2011-11-17 13:53 | 2011-11-17 | INVALID GROUP 6 ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation signal affecting more than one system. "On September 19, 2011, at 1000 hours Central Daylight Time (CDT), during the performance of a maintenance activity on the Reactor/Refueling Zone Ventilation Radiation Monitor BFN-3-RM-090-0141/143, Browns Ferry Unit 3 received a Primary Containment Isolation System (PCIS) Group 6 isolation. This resulted in isolation of the reactor and refuel zone ventilation systems, initiation of the Standby Gas Treatment System (Trains A, B and C), and the initiation of the Control Room Emergency Ventilation System (Trains A and B). All plant systems responded as designed. "There are two divisions of Reactor/Refueling Zone Ventilation Radiation Monitors: BFN-3-RM-090-0140/142 and BFN-3-RM-090-0141/143. A downscale or inoperable signal in both divisions will initiate the PCIS Group 6 isolation. Prior to the performance of the maintenance activity, BFN-3-RM-090-0140/142 was functional. However, during a field walkdown after the PCIS Group 6 isolation, relay BFN-3-RLY-064-16AK62A for BFN-3-RM-090-0140/142 was discovered to be chattering. A chattering relay could cause momentary loss of continuity between the contacts which would effectively generate a spurious isolation signal from that division. Thus, when 3-RM-090-0141/143 was made inoperable by the surveillance, the PCIS Group 6 logic was made-up. "The PCIS Group 6 isolation was reset at 1008 CDT. This event was entered in the Corrective Action Program as Problem Evaluation Report (PER) 434799. There were no safety consequences or impact on the health and safety of the public as a result of these events. The NRC Senior Resident Inspector was notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-11-17
47449 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-11-16 17:00 | 2011-11-16 23:16 | 2012-01-16 | HPCI DECLARED INOPERABLE DUE TO DUAL POSITION INDICATION ON CLOSED STEAM ADMISSION ISOLATION VALVE "On November 16, 2011, at 1600 hours [EST], with the reactor at 100% core thermal power and steady state conditions, the High Pressure Coolant Injection (HPCI) system was removed from service for planned testing and the appropriate Limiting Condition for Operation was entered (14 days per TS 3.5.C.2). At 1700 hours during restoration from the testing, the normally closed HPCI steam admission isolation valve (HPCI-2301-3) displayed dual indication (not full closed). The HPCI-2301-3 is a motor-operated valve (MOV) whose safety function is to open upon a HPCI injection/actuation signal. "The Limiting Condition for Operation (LCO) that had been entered in a planned manner was continued as of 1700 hours due to the apparent degraded performance of the HPCI-2301-3 valve. Currently, troubleshooting into the cause of the anomalous dual indication on HPCI-2301-3 is in progress. However, it is projected that the troubleshooting will not be complete within reportability assessment requirements. Therefore, in accordance with 50.72(b)(3)(v)(D), Pilgrim Nuclear Power Station is providing an 8 hour non-emergency notification that the HPCI System is inoperable. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1715 EST ON 01/16/12 FROM JOSEPH BRACKEN TO S. SANDIN * * * The licensee is retracting this report based on the following: "Event Notification Number 47449 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were satisfied pending further evaluation of HPCI system operability due to dual valve position indication when the HPCI Turbine Steam Supply Valve (MO-2301-3) valve was taken to the fully closed position after HPCI system surveillance testing from the Alternate Shutdown Panel. "Evaluation of the MO-2301-3 valve condition was performed. The dual position indication from the valve position instrumentation was determined to be valid based on the as-found valve position. The valve did not fully close because the torque switch opened prematurely due to high stem torque. The apparent cause evaluation identified that a lack of grease due to a tight stem to valve configuration and inadequate guidance to perform proper periodic stem lubrication were the apparent cause of the valve closure failure. "The valve is limit switch controlled in the open direction and torque switch controlled in the closed direction. The valve is normally closed and has no automatic closing function necessary to ensure HPCI System safety functions are satisfied. The valve has an active safety function to open to allow steam to the HPCI Turbine. The surveillance test that was performed verified capability of the valve to open on demand. Based on the surveillance test, failure of the HPCI Turbine Steam Supply Valve to close would not have prevented the HPCI System from operating and meeting required safety functions. "Therefore, the initial 50.72(b)(3)(v)(D) report is being retracted." The licensee will inform the NRC Resident Inspector. Notified R1DO (Trapp). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-11-16
47448 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-11-16 16:22 | 2011-11-16 19:04 | 2012-01-16 | RHR CAPABILITY AFFECTED DUE TO BOTH TRAINS OF RIVER WATER SUPPLY HVAC SYSTEMS INOPERABLE "At 1622 [CST] on November 16, 2011, NextEra Energy Duane Arnold declared the 'A' River Water Supply inoperable following discovery that the HVAC damper controller was installed in reverse. This would have closed the HVAC intake dampers on high temperature instead of opening them. At this time, the 'B' River Water Supply system was already inoperable for HVAC damper maintenance. This resulted in entering TS 3.7.2 Condition B for both River Water Supply systems inoperable [required action to restore a train or be shutdown in 12 hours]. Both trains of River Water Supply inoperability potentially affect the plant capability to remove residual heat. Therefore, this event is being reported pursuant to the requirements of 10CFR 50.72(b)(3)(v)(B). "At 1735 [CST] on November 16, 2011 Post Maintenance testing on the 'B' River Water Supply HVAC Dampers was completed and 'B' River Water Supply was declared operable, restoring the capability to remove residual heat. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1440 EST ON 01/16/12 FROM BOB MURRELL TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract a previous report made on 11/16/2011 at 19:04 (ET) (EN 47448). Notification of the event to the NRC was initially made as a result of declaring both trains of the River Water Supply (RWS) system inoperable following the discovery that the HVAC damper controller was installed incorrectly. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the RWS system was capable of performing its safety function and was fully operable during the period that the HVAC controller was incorrectly configured. Specifically, based on the environmental conditions that existed during the period from November 8, 2011 to November 16, 2011, the non-TS RWS Intake HVAC system was Functional, but Degraded. "This event is not considered a Safety System Functional Failure or a Condition Prohibited by TS and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Senior Resident Inspector has been notified." Notified R3DO (Orth). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-11-16
47447 | 0 | NASA GODDARD |  |  |  |  | 2011-11-16 11:09 | 2011-11-16 16:37 | 2011-11-17 | IRRADIATOR SOURCE STUCK IN UNSHIELDED POSITION On November 16, 2011 at 1637 EST, the licensee's Radiation Safety Officer called the NRC Operations Center, as required by 10 CFR 36.83, to report a source not being able to be returned to its normal down position inside a J.L. Shepherd Model 81-24Q Beam Irradiator. At approximately 1109 EST on November 16, 2011 the source, located inside the right side of the irradiator, was not able to be returned to the down position. An emergency shutter built into the system was deployed, which reduced the radiation intensity surrounding the irradiator, permitting access into the irradiator room. Upon entering the room, it was noted that the source position indicator found on the operating tower mounted on the top of the irradiator showed that the source was about halfway up from its normal down position. A radiation survey taken around the irradiator found one point in front of the emergency shutter to be less than 10 mR/hr at one foot from the irradiator. Further shielding was added at this point which reduced it down to about 0.3 mR/hr. Contact was made to J. L. Shepherd and arrangements are being made to have a representative come onsite to help return the source to its normal down position. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | GEN | 36.83(a)(1) |  |  |  | 0 | 2011-11-17
47446 | 0 | NORTH ANNA | 3 |  |  | (3) M-4-LP, (4) M-4-LP | 2011-09-13 09:00 | 2011-11-16 11:35 | 2011-11-16 | EARLY SITE PERMIT POSTULATED SEISMIC ACCELERATION IS LESS THAN PROJECTED BASED ON NEW INFORMATION "On August 23, 2011, an earthquake occurred with an epicenter 11 miles from the North Anna Unit 3 site. Instruments recorded earthquake data at the North Anna Unit 1 containment structure base mat. Certified data regarding the earthquake was received on September 13, 2011 and a Condition Report was initiated. This best available earthquake data exceeded at low frequencies the Safe-Shutdown Earthquake (SSE) response spectra established in the North Anna Early Site Permit (ESP-003). The event data also exceeded the site 250 foot elevation Ground Motion Response Spectra (GMRS) and the hard rock SSE developed for the North Anna Unit 3 Combined Operating License Application (COLA) based on the ESP SSE spectra. "The US-APWR standard plant (i.e., Reactor Building Complex and Power Source Building) Certified Seismic Design Response Spectra (CSDRS) envelops the actual seismic response recorded on August 23, 2011. However, the site-specific Seismic Category I Ultimate Heat Sink Related Structures, Essential Service Water Pipe Tunnel and Power Source Fuel Storage Vault use design inputs presented in the ESP. The recorded seismic response on August 23, 2011 exceeded the seismic design spectra presented in the ESP and COLA. "As defined in 10 CFR 21, this condition represents a 'deviation' in the seismic design information contained in the ESP and a 'defect' in that it involves a 'basic component' that could result in a major design deficiency that has safety implications, if it were to remain uncorrected. Therefore, NRC notification of this condition is required pursuant to 10 CFR 21.21(d)(1). The basis for this conclusion is discussed in the following paragraph. "In August 2007, the NRC amended the regulations applicable to the licensing and approval processes for nuclear power plants (e.g., ESP, COLA) to clarify various requirements, and made conforming amendments to other related regulations, including 10 CFR21. The discussion of changes to 10 CFR 21 (Federal Register / Vol. 72, No. 166, Page 49424) states that: 'services that are required to support an early site permit application (e.g., geologic or seismic analyses, etc.) that are safety-related and could be relied upon in the siting, design, and construction of a nuclear power plant, are to be treated as basic components as defined in part 21.' The discussion also states: 'if the ESP holder becomes aware of a significant safety concern with respect to its site (e.g., that the specified site characteristics for seismic acceleration is less than the projected acceleration due to new information), the concern should be reported to the NRC so that it may be considered in the review of any future application referencing the ESP.' Based on these statements of consideration, the analyses supporting the seismic design information in the ESP would be considered a 'basic component' and the recorded response data from the August 23, 2011 seismic event represents new information that impacts the seismic analyses. "This defect resulted from new data, not an error in the performance of the seismic analyses for the ESP. While there was no error in the performance of the seismic analyses, Dominion is assessing whether any changes should be made to the North Anna Unit 3 COLA." The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Under Construction; FMode1: Under Construction | NON EMERGENCY | 2 | VA | POW |  | 21.21 |  |  |  | 0 | 2011-11-16
47445 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-10-24 | 2011-11-16 10:11 | 2011-11-16 | AGREEMENT STATE - SHUTTER FELL OFF FIXED PROCESS GAUGE "The licensee's two fixed gauges were locked out because of maintenance on refractory equipment occurring the weekend of 10/22/11. On the morning of 10/24/11 it was discovered that the shutter had fallen. The exact timing of when the shutter fell is under investigation. This event resulted in a possible overexposure of members of the public. "Staff from the NJDEP (New Jersey Department of Environmental Protection) is visiting the site today, 11/15/11." The gauge is a TN Technologies Model #5204, S/N B585, fixed gauge containing 8 Ci of Cs-137. NJ Incident #: 410183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-11-21
47444 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-11-16 03:01 | 2011-11-16 03:33 | 2011-11-16 | UNUSUAL EVENT DUE TO DRYWELL LEAKAGE GREATER THAN 10 GPM "On 11/16/11 at 0208 EST, Brunswick Nuclear Plant, Unit 2 calculated a drywall floor drain 42 minute leak rate of 5.88 gpm, following several hours of gradually rising floor drain leakage during a plant startup. Tech Spec 3.4.4 A was entered, requiring floor drain leakage to be restored below 5 gpm within 8 hours. At 0253 EST, a 45 minute leak rate of 10.11 gpm was calculated. At 0301 EST, Unusual Event SU 6.1 was declared for unidentified leakage exceeding 10 gpm, and at 0309 EST, a manual reactor scram was inserted from approximately 7% power [10 CFR 50.72(b)(2)(iv)(B)]. Following the scram, the reactor was depressurized at a maximum cooldown rate of 92.5 deg F/hr, and the unidentified leak rate fell less than 10 gpm within 1 hour and less than 5 gpm within 2 hours. Leak rate at 0614 EST on 11/16/11 is 3.82 gpm with reactor pressure at 228 psig. "The exact nature of the leak is unknown at this time. The current plan is to continue to depressurize and cool down the reactor to Mode 4, such that a full drywall inspection can commence. At present, Brunswick has not terminated the Unusual Event." Level control is currently being maintained with control rod drives (CRD). The MSIVs were manually closed to control cooldown. The maximum cooldown was observed to be 92.5 F/hour. The plant plans to reopen MISIVs and depressurized to condensate booster pump injection pressure of 350 psig. The plan is to achieve Mode 4 for a leak inspection. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DAVID FASHCHER TO CHARLES TEAL AT 0550 EST ON 11/16/11 * * * The leakage rate is currently 3.73 gpm. The decrease is due to lower pressure which is currently at 258 psig. There are no additional changes. The leakage source is not identified at this time. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO JOHN SHOEMAKER AT 0648 EST ON 11/16/11 * * * The leakage rate is currently below the T.S. limit due to lower pressure which is currently at 210 psig. There are no additional changes. The plant will remain in an Unusual Event (UE) until further notice. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO CHARLES TEAL AT 0749 EST ON 11/16/11 * * * The leakage rate is stable. The leak rate is calculated at 3.04 gpm at 183 psig at 0708 EST. The current reactor pressure is 162 psig. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). * * * UPDATE FROM DUSTIN LUPTON TO JOHN KNOKE AT 0832 EST ON 11/16/11 * * * The licensee terminated from their Unusual Event at 0815 EST. The leakage is still unidentified. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias). | 0 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2011-11-16
47443 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2011-11-16 02:22 | 2011-11-16 03:04 | 2011-11-16 | ALERT DUE TO FIRE IN ELECTRICAL BUS AFFECTING SAFETY RELATED EQUIPMENT At 0222 EST on November 16, 2011, an ALERT was declared due to an electrical fire in the auxiliary building which houses safety related equipment. The apparent cause of the fire was due to an unknown source of water leaking on a breaker, thus causing an arc. The electrical fire is out. The plant was at 0% power and will remain shutdown in Mode 5. There was no impact on core cooling, or emergency power supplies. The licensee has notified the NRC Resident Inspector and state and local agencies. * * * UPDATE FROM JANE MALLERNEE TO JOHN KNOKE AT 0449 EST ON 11/16/11 * * * At 0443 EST on November 16, 2011, Davis Besse, Unit 1 exited their ALERT. The electrical short affected the Control Room Emergency Ventilation Fan #1 Damper. The licensee has notified the NRC Resident Inspector. Notified R3DO (Hills) and Canada Nuclear Safety Commission (Jim Sandlef). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | ALERT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-11-16
47442 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2011-11-15 19:52 | 2011-11-15 22:19 | 2011-11-15 | HIGH PRESSURE COOLANT INJECTION STEAM SUPPLY VALVE CABLE UNPROTECTED DURING POSTULATED FIRE "On 11/15/2011 at 1952 [EST], while performing a Fire Protection Program review, it was determined that one of the 'Multiple Spurious Operation' (MSO) modifications implemented during the P3R18 refueling outage adversely impacted Peach Bottom's fire safe shutdown analysis conclusions. New cabling that was routed for the Unit 3 High Pressure Coolant Injection (HPCI) system steam supply valve lacks appropriate fire barrier protection in the event of a postulated fire-induced damage to this cable. This cable is routed through a fire area in which the only credited and protected method of reactor level control for a fire in this area is HPCI. Postulated fire-induced damage in the cable could prevent the steam supply valve from opening, thereby causing the HPCI pump to be unavailable for an Appendix R fire. An hourly fire watch has been established as a compensatory action." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-15
47441 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-11-05 12:30 | 2011-11-15 20:54 | 2011-11-15 | MAJOR LOSS OF EMERGENCY PREPAREDNESS CAPABILITY DUE TO NETWORK ISOLATION DEVICE FAILURE "At 12:30 PDT on 11-5-2011, a network isolation device failed, resulting in interruption of the feed of plant data to emergency response facilities as well as loss of Emergency Response Data System (ERDS) transmission capabilities. At approximately 05:00 PST on 11-6-11, actions were initiated to reboot the system and capability was restored at 06:30 PST on 11-6-11. On 11-15-11, the time of the original device failure was identified and it was determined the total outage time was approximately 19 hours (including accounting for the change from daylight to standard time). It was further concluded this represents a major loss of emergency preparedness capability. Emergency assessment equipment in the control room was available throughout the event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-15
47440 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-11-15 16:00 | 2011-11-15 19:28 | 2011-11-15 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following report was received via e-mail: "Stuck 37 Curie radiographic source in an INC IR100 camera. The magnet holding the collimator to the tank came loose and fell on the guide tube, kinking the guide tube. Operators placed lead bags on the source and repaired the kink so that the source could be retrieved. The radiographer received 42 mRem. The RSO received 39 mRem and the assistant received 10 mRem." California report number: 5010-111411 This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-11-18
47439 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-15 | 2011-11-15 16:45 | 2011-11-15 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received via e-mail: "On November 15, 2011, the Agency [Texas Department of Health] was notified by the licensee that a Troxler model 3440 moisture/density gauge containing 9 millicuries of cesium-137 and 40 millicuries of americium-241 was stolen. The gauge was locked in the back of a company truck and the truck was parked at the technicians home overnight. When the technician went to the truck to leave, he found the gauge, one lock, and a chain missing. The licensee has notified local law enforcement of the theft. Additional information will be provided in accordance with SA - 300." Texas Incident: I-8903 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-18
47438 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-11-15 | 2011-11-15 15:27 | 2011-11-15 | AGREEMENT STATE REPORT - SUSPECTED CONTAMINATED PACKAGE The following report was received from the state via fax: "The State of Florida received report of potentially breached package that had arrived from Singapore to Jacksonville Florida. Jacksonville Fire Department was initially called and surveyed item, no contamination found. Item was then shipped to repair facility in Jacksonville (Unisom) License #3942-1. This office was contacted by State Warning Point, which sent an Investigator, he found an oily stain on a White 1 labeled package approximately 80cm2. His survey of packaging material and ignition exciters indicated no detectable radiation. Oily substance appeared to only on the outside of shipping container and was not from ignition exciters. No further action will be taken on this incident." Florida Incident No.: FL11-096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-11-18
47437 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-01-01 | 2011-11-15 14:41 | 2011-11-15 | AGREEMENT STATE REPORT - LOSS OF A TRITIUM SIGN The following report was received from the state via e-mail: "Safety Light Model 2040-50-20, Serial Number A10 1821 with 12 Ci of H-3 was shipped in July of 1991 to the facility. In 2002-2003, the facility was remodeled. The facility was sold in 2004. The new owner assumed that they still had the sign and continued to pay the annual fee. This year, one of the owners sold his portion of the business and new staff questioned where the sign was when they received the annual fee notice. The staff believes that the sign was removed at the time of remodeling in 2002-2003." Nebraska Item Number: NE110009 The licensee determined the sign was lost on 11/4/2011 and reported it to the state on 11/14/2011. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2011-11-18
47436 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-11-15 06:15 | 2011-11-15 08:03 | 2011-11-15 | SAFEGUARDS DEGRADATION RELATED TO SECURITY EQUIPMENT Safeguards system degradation related to security equipment. Compensatory actions were taken upon discovery. Call the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM D. GARD TO HOWIE CROUCH AT 2159 EST ON 11/15/11 * * * Safeguard system has been returned to service. Compensatory measures have been suspended. Call the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. Notified R2DO (Vias) and 73.71 Group via email. | 100 | 88 | 0 | 100 | 88 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-11-15
47435 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-11-10 07:00 | 2011-11-14 18:49 | 2011-11-14 | AGREEMENT STATE REPORT - UNDERDOSAGE OF THERASPHERES The following report was received via facsimile: "Event type: A medical event (ME) involving Y-90 TheraSpheres where the patient received an under-dose of 36%, which is reportable under 10CFR35.3045 (a) (1) (ii). "Notifications: On November 11, 2011, at 0849, the Department's [Pennsylvania Department of Environmental Protection] Southeast Regional Office received notification via email about the ME. "Event Description: The patient was being treated with MDS Nordion Y-90 TheraSpheres« for disease of the liver and received only 36% of the intended dose. The licensee has notified the patient. No more information is available at this time. "Cause of the Event: Is unknown at this time and is currently under investigation. "Actions: The licensee will be submitting a written report within 15 days. The department [Pennsylvania Bureau of Radiation Protection] has planned a reactive inspection for November 17, 2011." PA Event Report Identification Number: PA110036 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-20
47434 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-11-14 06:19 | 2011-11-14 10:14 | 2011-11-14 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-11-14
47433 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-11-13 10:58 | 2011-11-14 10:07 | 2011-11-14 | AGREEMENT STATE REPORT - CABLE DISCONNECTED FROM RADIOGRAPHY SOURCE The State of Kentucky reported a source containing 39 Curies of Ir-192 disconnect from a QSA model 660A radiography camera during radiography of a boiler. There was no leakage or personnel exposure during this event. The licensee contacted a contractor for retrieval. The source was secured and placed inside the camera. The State will follow up with additional details. Kentucky Report #: 110008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-11-17
47432 | -1 | WATERFORD | 3 |  |  | [3] CE | 2011-11-12 05:25 | 2011-11-12 08:58 | 2011-11-23 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM WILLIAM HARDIN TO HOWIE CROUCH ON 11/23/11 AT 1649 EST * * * Based on further investigation, the licensee determined that the incident was not reportable and is retracting this event. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. Notified R4DO (Azua) and 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-11-12
47431 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-11-11 10:21 | 2011-11-11 13:17 | 2011-11-11 | TECHNICAL SUPPORT CENTER INOPERABLE DUE TO PLANNED MAINTENANCE "At 1021 hrs. (CST) on November 11, 2011, the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) Ventilation Fan 1VAC070 was removed from service for pre-planned maintenance. The expected duration of the maintenance is 6 hours. The backup plan is to relocate key TSC personnel to the Control Room where the Standby Filter Units protect personnel. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) due to a loss of emergency response facility." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM HAN OLSON TO PETE SNYDER AT 1907 EST ON 11/11/11 * * * The TSC Ventilation Fan 1VAC070 has been returned to service and functionally tested so the TSC has been returned to service. The licensee notified the NRC Resident Inspector. Notified R3DO (Giessner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-11
47430 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-11-10 12:00 | 2011-11-11 10:01 | 2011-11-11 | SUPERVISOR ATTEMPTED TO SUBVERT THE FITNESS FOR DUTY PROCESS This event is being reported because a non-licensed contractor employee's direct supervisor authorized the individual to return home instead of initiating a for cause Fitness For Duty test. Both the direct supervisor and the contractor employee had their unescorted access to the protected area terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2011-11-11
47429 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-11-10 14:39 | 2011-11-10 21:54 | 2011-11-12 | LOSS OF TECHNICAL SUPPORT CENTER EMERGENCY FILTRATION SYSTEM DURING MAINTENANCE "At 1439 PST on 11-10-2011, while performing maintenance on the Technical Support Center (TSC) emergency filtration system, it was discovered that replacement gaskets required to restore the system were undersized and that the system could not be restored. Specifically the replacement gaskets were determined to be too small. All spare gaskets onsite were examined and determined to suffer from the same undersized condition. Prior to discovery of the undersized gaskets, the maintenance plan allowed for prompt system restoration in the event of an emergency. "The current lack of a suitable replacement gasket has resulted in a condition which represents a major loss of emergency preparedness capability per 10 CFR 50.72(b)(3)(xiii) in that TSC habitability might not be sustainable during certain events due to the inability of the filtration system to maintain a habitable atmosphere. Station procedures provide instructions to relocate the TSC if monitoring during an emergency event indicates that habitability cannot be maintained. Compensatory measures are being developed (while the restoration work is ongoing) to heighten awareness of responsible TSC staff following ERO activation to monitor TSC habitability in accordance with procedures and to consider potential TSC relocation as necessary as described in the station emergency plan. "Work is underway to return the TSC filtration system to functional status with a high priority." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL STODICK TO HOWIE CROUCH AT 2039 EST ON 11/12/11 * * * "Maintenance work on the TSC emergency filtration system has been completed. A post functional test has been performed and it has been evaluated that the TSC emergency filtration system's function has been restored as of 1718 PST on 11/12/2011. The NRC Resident Inspector will be notified." Notified R4DO (Hay). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-10
47428 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2011-11-10 11:10 | 2011-11-10 20:10 | 2011-11-10 | RADIOGRAPHY CAMERA SOURCE FAILS TO COMPLETELY RETRACT "On November 10th, the radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device (serial number 6774). "During the shift, the source was cranked in and the camera was surveyed per the proper procedure. There were no abnormal readings observed during the survey and the key was turned to the lock position. When the crank assembly was removed it was noted that the pigtail was not fully seated. "The 2 mR/hr boundary was reconfirmed and the Foreman and Supervisor were notified. The camera was surveyed and noted as being safe to transport. The camera was tagged out and placed in the Permanent Storage facility. A trained radiographer removed and cleaned the locking system. The locking system was successfully reinstalled. The camera has been returned to service. "Exposure Device: Industrial Nuclear IR-100 "Device S/N: 6774 "Source S/N: 70129B "Source Activity: 63.4 curies "Source Type: Ir-192 "Source Model # QSA 87703 "There was no exposure to the crew or the general public during this incident." See similar events: 47418, 46533, 46323, 46233, 46052, 46051, 45669, 45648, 45609, 45544, 45524, 45496, 45469, 45384. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-11-10
47427 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2011-11-10 01:00 | 2011-11-10 00:59 | 2011-11-10 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "'This telephone notification is provided in accordance with 10CFR50.72(b)(3)(xiii), loss of emergency assessment capability. "On 11-10-11 at 0100 Central Standard Time, the Technical Support Center Emergency Diesel Generator and Technical Support Center regular lighting will be taken Out of Service to support a scheduled temporary power supply return to normal configuration. The temporary power had been in place since the last refueling outage in support of planned bus maintenance. The Technical Support Center Emergency Diesel Generator and regular lighting are scheduled to be restored at 1100 [CST] on 11-10-11. "The licensee has notified the Senior Resident Inspector of this scheduled work." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-10
47426 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-11-09 17:50 | 2011-11-09 21:43 | 2011-11-09 | POTENTIAL FAILURE OF HIGH DENSITY POLYETHYLENE PIPING IN ESW SYSTEM "On November 9, 2011 at 1715, Callaway Plant staff determined that a postulated design basis fire event in Fire Area C-1, (Control Building, elevation 1974, ESW Pipe Space, Room 3101) could result in failure of the High Density Polyethylene (HDPE) piping in the Essential Service Water (ESW) system. "In 2008-2009 timeframe, Callaway Plant implemented a modification which replaced underground large bore carbon steel ESW piping with HDPE piping. Four short sections of this HDPE piping enter the Control Building and interface with steel piping in Room 3101. During the design of the modification, it was not recognized that a fire barrier should be installed to protect the HDPE piping from the consequences of a fire. As a result of the missing fire barrier, a postulated fire could cause a failure of one train of the large bore HDPE piping located within the fire area. The resultant pipe failure could lead to flooding in the fire area that could adversely affect both trains of ESW equipment required to achieve and maintain safe shutdown. "An hourly fire watch has been imposed as a compensatory measure for this condition in accordance with the approved fire protection program. "This condition is reported in accordance with 10 CFR 50.72 (b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-09
47425 | 0 | BALDOR ELECTRIC CO. |  |  |  |  | 2011-11-08 | 2011-11-09 16:19 | 2011-11-09 | PART 21 NOTIFICATION - MOTOR POWER LEADS UNDERSIZED The following information was provided by Baldor Electric via facsimile: "Description of Defect: Motor power leads are undersized, #12AWG should be #8AWG. [Baldor] corrected the electrical design where the lead size is specified. "Advice Related to Defect: Motors in service are not at risk unless held at locked rotor for more than 8 seconds. Normal operation, with instantaneous inrush while starting and running at loads as high as 40% locked rotor torque as name-plated, will not result in a failure. Holding the shaft blocked for 10 seconds could result in lead failure. Baldor-Reliance recommends changing the motors out as soon as convenient, i.e. during next outage. Any motors in storage should be replaced ASAP for future use. "Part/Component Name: Actuator Motors Limitorque P/N R-402-FO6-582100A20 "Location Of All Units: 1) AREVA or PSE&G 2) AREVA or PSE&G 3) Baldor Electric, Gainesville, GA" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-11-09
47424 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-11-09 05:30 | 2011-11-09 16:02 | 2011-11-09 | AGREEMENT STATE REPORT - EXTERNAL RADIATION READINGS ON SHIPPED PACKAGE EXCEEDED LIMITS The following information was received via fax: "Medi-Physics, Inc. d/b/a GE Healthcare reported they had received a package from Lantheus Medical Imaging containing a Mo-99/Tc-99m generator (serial #M312111D60), which had a contact radiation reading of >200 mR/hour. The Transport Index (TI) on the labeling was stated at 4.2, while the actual TI upon receiving the package was 8. Contamination wipes were completed with no contamination on the outside of the package. When the package was opened, contamination wipes were completed with no contamination on the inside of the package. The generator was manufactured on 11/8/11 and delivered to GE Healthcare on 11/9/11. The packaging surrounding the generator was entirely composed of styrofoam. At this point, it was determined the secondary lead shielding surrounding the generator was absent. The generator was removed from the packaging and eluted, there was no damage to the generator and the eluted material passed all quality control testing. "The Wisconsin Department of Health Services (DHS) followed up with the licensee by phone, and also contacted the State of Massachusetts to notify them of the event." Wisconsin Report ID: WI110019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-11-14
47423 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-11-09 | 2011-11-09 14:16 | 2012-02-15 | AGREEMENT STATE REPORT - DAMAGED SOURCE ROD ON MOISTURE DENSITY GAUGE The following information was provided by the state via email: "On 11/9/11 [EST], the licensee reported to the Agency [Massachusetts Radiation Control Program] that a portable moisture density gauge had been damaged by a construction vehicle at a temporary job site. The source rod was bent and extended outside of the shielded gauge body so that it could not be returned to the closed position. The extended rod was left within the measuring hole so that the surrounding soil could provide shielding. A 15-plus-foot radius area was segregated around the damaged gauge. The licensee's radiation safety officer and radiation safety consultant were en route to the site to conduct and oversee the source recovery operation at the time of this report. "The Agency [Massachusetts Radiation Control Program] considers this event to be open and ongoing. "Manufacturer: Humboldt Scientific Inc, 5001 Series; Isotopes: Cs-137/ .011 Ci; Am-241/ .044 Ci." * * * UPDATE ON 1/26/2012 AT 1307 EST FROM TONY CARPENITO TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "The consultant and licensee submitted follow-up reports. An authorized gauge user was attending to the gauge and could not get the attention of the driver of the vehicle being driven in reverse just before gauge damage occurred. The source rod retracted into the gauge body successfully and the gauge was returned in its transport case to the licensee's facility on 11/9/11. A post-retrieval survey determined no residual contamination in the area. Personnel dosimeters worn during retrieval indicated minimal personnel exposure. The licensee presented employees retraining related to construction site safety on 11/10/11. Leak test results indicated no sealed source leakage. The gauge was returned to manufacturer for repairs. Manufacturer : Humboldt Scientific, inc. Model Number : 5001 EZ Serial Number : 3544 Cesium-137 Source Serial Number : 9433GQ Americium-241 Be Source Serial Number : NJ03832 "The Agency considers this event to be CLOSED." Notified the R1DO (Dentel) and FSME (McIntosh). * * * UPDATE ON 2/15/12 AT 0921 EST FROM ANTHONY CARPENITO TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "The Cesium-137 source is an AEA Technology/QSA Model CDC.805, Capsule Type X8. "The Americium-241 source is an AEA Technology/QSA Model AMN.V997, Capsule Type X1. "The Agency still considers this event to be CLOSED." Notified FSME (McIntosh) and R1DO (Powell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-11-14
47422 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-11-08 17:18 | 2011-11-08 17:18 | 2011-11-10 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "On November 8, 2011, at 1718 EST, the Technical Support Center (TSC) will be unavailable due to pre-planned maintenance to maintain the Technical Support Center and Emergency Response Data Acquisition and Display System ventilation system. The TSC is expected to be restored to available status at approximately 2300 on November 10, 2011. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures, and the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC has been restored to normal operation. The NRC Resident Inspector has been notified." The TSC ventilation will be out of service for two days for ducting modifications and flow testing. * * * UPDATE AT 2249 EST ON 11/10/11 FROM TIMOTHY KUDO TO PETE SNYDER * * * As of 2200 EST the TSC is restored and is fully functional. The licensee notified the NRC Resident Inspector. Notified R2DO (Hopper). | 81 | 100 | 0 | 81 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-08
47421 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-11-08 07:55 | 2011-11-08 16:53 | 2011-11-08 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed supervisor (contractor) tested positive for alcohol. The contractor had not entered the protected area after reporting to work. The contractor had his badge pulled and his access to the site was terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2011-11-08
47420 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-11-02 | 2011-11-07 13:16 | 2011-11-07 | AGREEMENT STATE REPORT - NUCLEAR GAUGE DISLODGED FROM MOUNTING The following report was received via e-mail: "Curwood, Inc. reported an incident involving a NDC Infrared Engineering, Inc. thickness gauge, model 103, serial number 13457, containing 150 mCi's of Americium-241 that occurred on November 2, 2011. A sample of film was cut from the web on a production line and as the sample passed the device, the tail snagged the gauge and dislodged it from the mounting bracket. The gauge fell approximately 40 inches to the treater deck platform. The fall caused the shutter to become dislodged from the device and the crystal lens was cracked. Curwood contacted NDC and was instructed to perform a survey and wipe test of the device. The survey and wipe test indicated that the source was intact and no removable contamination was present. The device is currently packaged and in storage awaiting shipment to NDC for repair. The cause of this incident was the fact that the sample was taken prior to the device and that one of the two screws mounting the device was missing. Corrective actions include now taking the samples at a location on the production line after the device, replacing and securing the missing screw, [performing] a daily spot check of the mounting screws, and a weekly check of the screws to ensure that they are secure." Iowa Event: IA110006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-11-10
47419 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-11-06 20:03 | 2011-11-06 22:30 | 2011-11-06 | LOSS OF SPDS AND PLANT PROCESS COMPUTER DUE TO PLANNED MAINTENANCE "At 1203 EST on 11/06/2011, the Safety Parameter Display System (SPDS) was removed from service for planned maintenance of the Plant Process Computer. The Plant Process Computer and the SPDS function were restored at 2015 EST on 11/06/2011. This event is reportable per 10 CFR 50.72(b)(3)(xiii) since the SPDS was out of service for greater than 8 hours resulting in a major loss of emergency assessment capability." The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-06
47418 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2011-11-05 22:00 | 2011-11-06 13:04 | 2011-11-07 | RADIOGRAPHY CAMERA SOURCE LOCK MALFUNCTION A radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunction of the locking system on an INC IR-100 exposure device. After completing radiography activities, the source was cranked in however, the source was still 1/4 to 1/2 inch from the fully retracted position. There were no abnormal readings observed and the key was turned to the locked position. The crew has been trained for this type of situation. They dismantled the lock, cleaned it, rebuilt it, and retracted the source to its fully retracted position. Exposure Device: Industrial Nuclear IR-100 Device S/N: 6774 Source S/N: 70129B Source Activity: 80 curies Source Type: Ir192 There was no exposure from this event. * * * UPDATE AT 1548 EST ON 11/7/2011 FROM KEENAN REMELE TO MARK ABRAMOVITZ * * * The following report was received via fax: "On November 5th, the radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device (serial number 6774). "During the shift, the source was cranked in and the camera was surveyed per the proper procedure. There were no abnormal readings observed during the survey and the key was turned to the lock position. When the crank assembly was removed it was noted that the pigtail was not fully seated. "The 2 mR/hr boundary was reconfirmed and the Foreman and Supervisor were notified. The camera was surveyed and noted as being safe to transport. The camera was tagged out and placed in the Permanent Storage facility. A trained radiographer removed and cleaned the locking system. The locking system was successfully reinstalled. The camera has been returned to service. "Exposure Device: Industrial Nuclear IR-100 Device S/N: 6774 Source S/N: 70129B Source Activity: 63.4 curies Source Type: Ir-192 Source Model # QSA 87703" There was no exposure to the crew or the general public during this incident. Notified the R4DO (Hay) and FSME (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-11-06
47417 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-11-04 16:30 | 2011-11-05 18:56 | 2011-11-05 | AGREEMENT STATE REPORT - THEFT OF A MOISTURE DENSITY GAUGE "On 11/4/2011, at 1630, the licensee reported to [State of California] Radiologic Health Branch [RHB], Brea (and by voice mail to Sacramento) the theft of one of its portable nuclear gauges, a Troxler, Model 3440, # 34646. The theft took place from the licensee's permanent storage location, sometime in the last six weeks. The gauge was in the authorized permanent storage area and had not been used at a temporary job location for two years. The RSO stated that some employees had been recently laid off and may have been disgruntled. There was no evidence of tampering with the storage location locks. The gauge contained 0.3 GBq (9 mCi) of Cs-137 and 1.48 GBq (44 mCi) of Am-241/Be. The RSO was instructed to notify the local low enforcement agency to report the theft and place a reward notice in the local newspaper. The RSO will be providing a written report and supporting documentation to RHB within 30 days. RHB is initiating an investigation." California Report: 5010-110411 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-11-09
47416 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-11-05 09:00 | 2011-11-05 12:18 | 2011-11-10 | TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "Maintenance activities are being performed on the Hatch Nuclear Plant's Technical Support Center (TSC) Emergency Ventilation System starting on November 5, 2011 at 0900. These maintenance activities include the replacing the TSC HVAC cooling coils, condensing unit and controls. The maintenance activity will be worked 24 hours per day until completion. The scheduled completion date is November 10, 2011. "During the time these activities are being performed, the TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of this work activity. If an emergency is declared requiring activation of the TSC during the time these work activities are being performed, then the contingency plans call for utilization of the TSC during the time of these work activities, as long as environmental and radiological habitability conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev.1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM CHUCK VONIER TO HOWIE CROUCH AT 1655 EDT ON 11/10/11 * * * The TSC was returned to service at 1621 EDT. The licensee has notified the NRC Resident Inspector. Notified R2DO (Hopper). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-11-05
47415 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-11-03 16:00 | 2011-11-04 18:49 | 2011-11-04 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILS TO RETRACT The following report was received via e-mail: "Valley Industrial X-ray and Inspection Services radiographers were unable to retract an Ir-192 source assembly into its fully shielded position and secure it in this position. The device is an Industrial Nuclear Co, Model IR-100 s/n 4100 camera which contained 49 Ci of Ir-192. Emergency procedures were enacted by evacuating the area 200 yards around the exposure device and calling the RSO for assistance. Radiation safety personnel were able to retract the source into the shield and the device was secured by 1600 [PDT]. The licensee removed the Ir-192 source from the camera and placed it into a spare shield. The IR-100 camera (without a source assembly) was sent to Industrial Nuclear Co. in San Leandro, CA for evaluation. No personnel overexposure occurred due to this event. RHB [Radiologic Health Branch] is following up with the licensee as to the cause of the event." California Report: 5010-110311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-11-09
47414 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-11-03 15:50 | 2011-11-03 23:51 | 2011-11-04 | UNANALYZED CONDITION - CONTROL ROOM VENTILATION SINGLE POINT VULNERABILITY "On November 3, 2011, at 1550 PDT, operators determined that control room ventilation system (CRVS) contained a single failure vulnerability whereby unfiltered air supplied to the control room could exceed the flowrates used in the licensing basis analyses of design basis accident (DBA) consequences. This vulnerability was discovered during performance of control room inleakage testing required by TS SR 3.7.10.5. "It was determined that the control room pressurization system airflow could bypass the supply filter if the CRVS booster fan in the associated train was not operating. This would allow as much as 800 cubic feet per minute of unfiltered air to be delivered to the control room following an accident that results in initiation of the CRVS pressurization mode. Operators would correct the condition approximately 10 minutes after a safety injection by manually selecting the train's redundant booster fan in accordance with existing proceduralized actions specified in the DCPP emergency procedure E-0 Appendix E. This period of unfiltered air supply to the control room due to a single failure of a CRVS booster fan had not been previously analyzed and could have potentially resulted in operator dose greater than contained in plant analyses. "Plant staff verified that all components and redundant components in each ventilation train are currently OPERABLE. Plant staff has implemented additional compensatory measures by issuing a shift order to require that TS Action 3.7.10.A be entered for unavailability of either of the two CRVS booster fans in each CRVS train. Additionally, evaluation of the new unfiltered inleakage may result in more restrictive administrative controls to ensure operator doses are maintained less than the FSAR accident analyses." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-04
47413 | -1 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2011-11-03 18:00 | 2011-11-03 23:26 | 2011-12-29 | DIESEL GENERATOR STARTING AIR NOT COMPLIANT WITH APPENDIX R REQUIREMENTS "During the conduct of a system vulnerability assessment by Engineering on the emergency diesel system. a discussion was held regarding the impact of a fire on the DG starting air system. "Subsequently it was recognized that components of the system were vulnerable to damage during a fire. A review of the Appendix R analysis was conducted and it was determined that this vulnerability was not analyzed in the evaluation. "This is reportable to Unit 2, as Unit 1 has a separate diesel building for the 1-Alpha emergency diesel." The NRC Resident Inspector has been notified. * * * RETRACTION ON 12/29/11 AT 1556 EST FROM GIOFFRE TO HUFFMAN * * * "The Appendix R analysis was updated and no changes to the plant or procedures resulted. Therefore, no unanalyzed condition that significantly degraded plant safety existed. This event is being retracted. The NRC Resident Inspector has been notified." R1DO (Joustra) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-03
47412 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-11-03 16:00 | 2011-11-03 19:06 | 2011-11-03 | UNANALYZED CONDITION FOR A POSTULATED CONTROL ROOM FIRE "During the 2011 Triennial fire protection inspection, it was determined that the off normal procedure for control room evacuation due to fire has two defects. It does not adequately protect the steam generators from overfilling and possibly damaging the turbine driven auxiliary feedwater pump. In addition it does not protect the reactor coolant system pressurizer from filling to above 100% indicated water level, possibly causing the primary system to go solid. Both of these issues are results of inadequate assumptions used in the Post Fire Safe Shutdown Analysis of a fire in the Control Room. "Compensatory measure of hourly fire watch for the control room is in place. The procedure for control room evacuation due to fire is being revised to include compensatory actions that will address the above events." The NRC Resident Inspector has been notified. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-03
47411 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-02 | 2011-11-03 16:23 | 2011-11-03 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK OPEN The following was received via email: "On November 3, 2011, the agency [Texas Department of Health] was notified by the licensee that the shutter on an Ohmart Vega model SH-F2 containing 500 milliCurie of cesium-137 failed to close during the required maintenance check done on November 2, 2011. The gauge shutter is stuck in the open position, which is the normal operating position for the gauge and does not pose an increased exposure risk to any individual. The licensee stated that the pin attaching the operating handle to the shutter operating arm was found broken. They had not determined when the pin was broken. On November 3, 2011, the licensee determined that they could not repair the gauge. The reactor vessel the gauge is attached to is not accessed during system operation. The licensee stated that they were in the process of contacting the manufacturer for repairs or replacement of the gauge. Additional information will be provided as it is received in accordance with SA-300" Texas Report: I-8898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-08
47410 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-02 | 2011-11-03 16:10 | 2011-11-03 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK OPEN The following was received via email: "On November 3, 2011, the Agency [Texas Department of Health] was notified by the licensee that the shutter on an Ohmart Vega model SH-F1A containing 50 milliCuries of cesium - 137 failed to close during the required maintenance check done on November 2, 2011. The gauge shutter is stuck in the open position, which is the normal operating position for the gauge and does not pose an increased exposure risk to any individual. The licensee stated that the pin attaching the operating handle to the shutter operating arm was found broken. They had not determined when the pin was broken. On November 3, 2011, the license determined that they could not repair the gauge. The vessel the gauge is attached to is not accessed during system operation. The licensee stated that they were in the process of contacting the manufacturer for repairs or replacement of the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-08
47409 | 0 | BARNES-JEWISH HOSPITAL |  |  |  |  | 2011-11-02 14:00 | 2011-11-03 15:05 | 2011-11-03 | MEDICAL DOSE LESS THAN INTENDED DUE TO A LEAKING CONNECTOR The patient had a written directive to receive 81 mCi of Sm-153 (Quadramet) as a whole body exposure for bone metastases. The administered dose was 29 mCi with the rest leaking out of a connector onto the tubing and absorbent pads. Any residual contamination was cleaned up. Both the doctor and patient were notified of the underdose and a follow-on treatment has been scheduled for next week. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2011-11-09
47408 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2011-11-03 | 2011-11-03 14:29 | 2011-11-03 | AGREEMENT STATE REPORT - GADOLINIUM SOURCE LOST The following report was received via e-mail: "On November 3, 2011, at approximately 9:30AM, a 709.36 mCi Gadolinium-153 sealed source was discovered to be missing from the back of a LIXI, Inc. employee's RV in Phoenix, Arizona. The source was last seen on Monday, October 31st at approximately 8PM in Abilene, Texas. "The investigation into this event is ongoing. "The U.S. NRC, AZ governor's office, Texas, and Illinois have been notified." Arizona Report: 11-012 * * * UPDATE ON 11/3/2011 AT 1541 FROM AUBREY GODWIN TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "At 11:45AM, the licensee was notified that the source was left at the PepsiCo in Abilene, Texas. The licensee is flying back to Texas to pick up the source at approximately 7:30PM tonight. "The U.S. NRC, AZ Governor's Office, Texas, and Illinois have been notified." Notified the R4DO (Gaddy) and FSME (Camper). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-11-08
47407 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-11-01 15:00 | 2011-11-03 14:24 | 2011-11-03 | AGREEMENT STATE REPORT - SHUTTER ACTUATOR FAILED TO CLOSE SHUTTER The following was received from the Commonwealth of Pennsylvania via facsimile: "During the monthly shutter test, the licensee recognized the actuator that controls the shutter failed on both gauges. The handle that connects the actuator to the shutter snapped on both, rendering the shutter inoperable and in an open position, which is the normal operating position. A service provider was contacted to make necessary repairs. No exposure have been reported and none are expected. The device is identified as: Manufacturer (BSI Instruments), Model (7224), Serial # (ED355A), Isotope (Co-60), Activity (100 mCi), and Model (7440), Serial # (2498-11-87), Isotope (Cesium-137), Activity (20 mCi). "A service provider has been contacted and they are planning on making repairs as soon as parts are available. A departmental reactive inspection is planned to investigate this event further." PA Report #: PA110035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-08
47406 | 0 | FORT SAINT VRAIN ISFSI |  |  |  | ISFSI | 2011-11-03 10:39 | 2011-11-03 13:15 | 2011-11-04 | ISFSI BUILDING AIR VENT BLOCKED FOR 12 MINUTES "At 1009 (all times MDT) today, 11/3/11, a Security Officer performing routine rounds noted 95-100% blockage on the inlet screens at the Fort St. Vrain Independent Spent Fuel Storage Installation (FSV ISFSI). The FSV ISFSI is located near Platteville, Colorado. The FSV ISFSI safely stores used fuel from the Fort St. Vrain Nuclear Generating Station (FSV NGS). The NGS has been decommissioned and released for unrestricted use. The fuel is stored at the ISFSI under NRC license SNM-2504. The inlet screens are in place to provide a cooling path for the used fuel. "The Security Officer immediately notified the Emergency Coordinator, who directed the screens to be cleared of the blockage at 1010. The blockage was removed at 1021, at which time the event was terminated. The blockage was caused by frost, which built up due to dense fog, high humidity, and low temperatures. Removal was accomplished by lightly hitting the screens by hand. No further action is necessary. "Per FSV ISFSI Limiting Condition for Operation (LCO) 3.1, inlet screen blockage which equals or exceeds 95 percent must be cleared within 24 hours. The blockage was cleared in 12 minutes. Thus the REQUIRED ACTION was satisfactorily completed, and the CONDITION was exited. "Per the FSV ISFSI Emergency Plan Implementing Procedure (EPI)-102, Emergency Action Level 1NE.6, 95% or greater blockage of the inlet screens constitutes a 1 hour NON-EMERGENCY event. Required notifications were made by the Warning Communications Center (WCC) in Idaho." There was no increase in building temperature during this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [9 empty] | NON EMERGENCY | 4 | CO | FUE |  | 72.75(d)(1) |  |  |  | 0 | 2011-11-04
47405 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-11-02 03:00 | 2011-11-03 12:33 | 2011-11-03 | AGREEMENT STATE REPORT - THICKNESS GAUGE WARNING LIGHTS LOST POWER The following was received from the Commonwealth of Pennsylvania via facsimile: "A licensee's thickness gauge warning lights lost power. The problem was found to be in the wiring circuitry to the gauge. Repairs were made to wiring with the shutter remaining closed throughout the event. No radiation exposure to personnel ensued. The device is identified as: Manufacturer (AccuRay), Model (U-3), Serial # (771353031), isotope (Americium-241, Activity (1000 mCi). "Repairs were made to the wiring. A 30-day licensee report is expected. The department plans to do a reactive inspection." PA Event #: PA110034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-08
47404 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-11-02 15:50 | 2011-11-03 10:29 | 2011-11-03 | AGREEMENT STATE REPORT - UNDERDOSAGE OF Y-90 THERASPHERES The following was received from the Commonwealth of Pennsylvania via fax: "Event type: A medical event (ME) involving Y-90 TheraSpheres where the patient received an under-dose of 63%, which is reportable under 10CFR35.3045(a)(1)(ii). "Notifications: On November 2, 2011, at 1550, the Department's Southeast Regional Office received notification via phone message about the ME. "Event Description: A patient who was being treated with MDS Nordion Y-90 TheraSpheres, received only 37% of the intended dose based on the before and after survey readings of the TheraSphere accoutrements (5.8mR/hr vs. 3.8mR/hr). The licensee is in the process of notifying the patient. No more information is available at this time. "Cause of the Event: The licensee suspects that procedural changes led to the problem. Nordion recently changed the procedure to clamp the priming line with a hemostat because the original clamp is hard to manipulate. This was their first procedure using the hemostat. "Actions: Nordion has been contacted. The licensee will be submitting a written report within 15 days. The Department plans to do a reactive inspection." Event Report ID No. PA 110033 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-09
47403 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2011-11-02 14:30 | 2011-11-02 20:41 | 2011-11-02 | UNANALYZED CONDITION CAUSED BY NON-CONFORMING FIRE BARRIERS "Ongoing field inspections as a result of Industry Operating Experience have identified certain fire barriers that are not in conformance with required tested configurations. Specifically, some of the flexible conduit that penetrates these barriers has a coating that does not exhibit flame retardant characteristics and therefore does not meet the requirements for fire barriers at Beaver Valley Power Station, Unit 1. "In the event of a postulated fire, this non-conformance has the potential to affect fire barriers separating the two independent trains required for post fire Safe Shutdown equipment. This issue is being reported per 10CFR 50.72(b)(3)(ii)(B). "Compensatory actions have been established in accordance with the approved Fire Protection Program. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-11-02
47402 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-11-01 | 2011-11-02 16:45 | 2011-11-02 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK CLOSED The following information was received via fax: "On November 2, 2011, the Agency [Texas Department of Health] was notified by a general licensee that the shutter on a NITON XLp818 nuclear gauge containing 30 milliCuries of americium (Am) - 241 used for metal analysis was stuck in the closed position. The gauge appeared to have suffered an impact locking the shutter closed. The screen displays this error. The licensee has sent gauge to the manufacturer for repairs. The serial number is #7625. There is no exposure since the shutter failed in the closed position. The investigation in to this incident is ongoing. Further details will be provided in accordance with SA 300." Texas report: I-8896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-07
47401 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-11-01 14:50 | 2011-11-01 18:08 | 2011-11-01 | ALERT DECLARED DUE TO AN AMMONIA LEAK On November 1, 2011 at 1450 PDT, San Onofre Unit 3 declared an ALERT and entered EAL HA3.1 due to an ammonia leak that prevented access to local areas. The plant is in a stable condition while the leakage is being secured. The turbine building on Unit 3 has been evacuated. Plant personnel are in the process of verifying no presence of ammonia in the turbine building. There was no impact on Unit 2. * * * UPDATE FROM KEN HOUSEMAN TO JOHN KNOKE AT 2115 EDT ON 11/01/11 * * * At 1807 PDT licensee exited the ALERT and EAL HA3.1. The leak was at the Ammonia day tank and was flowing through an overflow vent into the berm. The high level in the Ammonia day tank was due to a leaking closed valve between the Demineralizer system and the ammonia bulk storage. The berm area was drained of all fluids. The wind direction caused the ammonia fumes to travel to the Unit 3 turbine deck. No off-site HAZMAT personnel came on-site. At 1756 PDT the precautionary evacuation of on-site personnel was terminated. Unit 2 was not affected from this event. The NRC Resident Inspector was notified. Notified NRR EO (Fredrick Brown), R4DO (Vincent Gaddy, IRDMOC (Jeff Grant), DHS (Hill), DOE (Doyle), USDA (Krauf), FEMA (Fuller) and HHS (Fajardo). * * * UPDATE FROM LEE KELLY TO VINCE KLCO AT 2228 EDT ON 11/01/11 * * * "On November 1, 2011, Southern California Edison notified the California Emergency Management Agency at 1755 PDT and the San Diego Department of Environmental Health at 1810 PDT that approximately 25 gallons of Ammonium Hydroxide was spilled under the Ammonium Hydroxide day tank located outside the Unit 3 turbine building. The spill was contained in a berm under the tank and subsequently cleaned up. "Both Units 2 and 3 were at approximately 100% power at the time of the event." Notified the R4DO (Gaddy). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode3: Power Operation; FMode3: Power Operation | ALERT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-11-01
47400 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-10-26 12:00 | 2011-11-01 16:06 | 2011-11-03 | AGREEMENT STATE REPORT - EQUIPMENT MALFUNCTION The following information was received by e-mail: "On 10/31/11, the ARSO [Alternate Radiation Safety Officer] at TC Inspection informed RHB [California Radiation Health Branch] via email of an incident occurring on 10/26/11 at Valero Refinery in Benicia, CA during one of their radiography operations. The email written by the ARSO is as follows: "On October 26, 2011, there was an incident involving RAM material; one of [the licensee's crew was] performing radiography at the Valero refinery when, while cranking out the source, the trainer noticed the crank handle started free-spinning. When he tried to crank the source back in it was still free spinning so the source was stuck out of the shielded position. When the trainer called, [the licensee] advised him to loosen one of the nuts on the crank assembly, pull back the tube and then grab the cable and pull the source back into the exposure device and into the shielded position and that [the licensee was on his way]. When [the trainer] did this he noticed that the end of the cable was inside the tube, he was able to grab it with a pair of needle nose pliers and retrieve the source back into the shielded position. "Two things happened here, the first; the trainer or assistant (still not sure which one) did not fully connect the guide tube to the camera. This allowed the source and cable to go out of the camera into air, thus allowing the cable to reach the end where the stop at the end of the cable did not stop the cable from coming out of the crank assembly. After further investigation [the licensee] found that the aluminum body of the crank assembly was worn right at the exit hole thus allowing the stop to go through. [The licensee] just did a maintenance inspection on those cranks on 10/1/11 and saw some wear on it but not as much as was there this time. [The licensee has] been in the process of replacing the aluminum body on all of [the licensee's] INC crank assemblies with stainless steel bodies when the techs tell [the ARSO] their cranks are getting hard to crank (That is usually the first sign that the aluminum body is wearing). [The apparent cause of the event is a technician forgetting to connect all of the equipment pieces due to production pressures or] equipment failure." CA 5010 Number: 103111 * * * UPDATE FROM KEN PRENDERGAST TO CHARLES TEAL ON 11/3/11 AT 1513 EDT * * * The following was received via email: "On the day of the event, the operators pocket dosimeters indicated 10 mR. "Camera information: INC IR-100, S/N 4301, with a source activity of 40.8 Ci. "The crank assembly has been sent to INC and we'll be visiting INC today. "We requested written statements from the trainer assistant. The ARSO already received them and he'll be sending a copy to RHB today. "TC was requested to process the dosimetry badges worn by trainer and the assistant." Notified R4DO (Gaddy) and FSME EO (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-11-04
47399 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-10-28 12:00 | 2011-11-01 14:52 | 2011-11-01 | AGREEMENT STATE REPORT - EMPLOYEE OVEREXPOSURE The following information was received by facsimile: "On Friday, October 28th, two NVI [Nondestructive and Visual Inspection, LLC] employees were performing radiography on a pipeline project in Wyalusing, PA. While performing radiography on a main line the crew approached the pipe after cranking in the source to set-up and mount for their next shot. While strapping the next weld with film, one of the crew noticed the indicator which shows full retraction of the source on their Amersham Model D880 had not popped out. At this time both crew members confirmed their survey meters read zero. However, also at this point they realized one member's rate alarm was chirping, but not very loudly and the other's rate alarm was not chirping at all. It was noted both rate alarms were inspected and working properly at the beginning of the shift. The crew then approached the crank controls where one was able to make approximately one turn with the crank, fully retracting the source back into the camera. They inspected their dosimeters which were both off-scale. They informed the RSO and were immediately removed from work. The badges were sent for emergency processing and whole body dosimetry results were 5133mR and 1447mR. "CAUSE OF THE EVENT: Undetermined at this time, expected faulty equipment. "ACTIONS: The licensee will be submitting a written report within 30 days. The Department [PA DEP Bureau of Radiation Protection] plans to do a reactive inspection." Pennsylvania Event Report: PA110032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-04
47398 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-11-01 08:45 | 2011-11-01 13:56 | 2011-11-01 | UNPLANNED MEDICAL TREATMENT OF AN INDIVIDUAL INVOLVING CONTAMINATION "A person working in an office area began feeling excessive heartburn and nausea. The individual was taken to the site dispensary for evaluation. An ambulance was requested to take the employee to the hospital for further evaluation. The employee had contamination on his coveralls and boots. Before leaving the site for the hospital, the employee's plant clothing was removed and the individual was surveyed. There was no detectable contamination on the employee when he was transferred to the hospital. "Isotope, Quantities and Chemical Form: Uranium Ore Concentrates, U308 "NRC Region II informed: Richard Gibson- Senior Fuel Cycle Inspector" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-11-01
47397 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2011-10-28 12:00 | 2011-11-01 12:34 | 2011-11-01 | AGREEMENT STATE REPORT - ORPHANED SOURCE DISCOVERED AT A SCRAP METAL FACILITY An outgoing shipment of scrap metal from the Yaffe Iron and Metal Company detected a radioactive source when going through the monitoring process. It is thought an orphaned radioactive source entered the scrap metal yard with an unmonitored shipment of aluminum. Upon further investigation, a radioactive metal rod of about 15 inches long was discovered in the outgoing shipment of scrap metal. Initial readings indicate a dose about a 200 mRem at 2 inches from a metal box that contains the source. Based on the use of a G-M detector, the activity is estimated to be 3.75 Ci. The metal box is constructed of one quarter inch steel. Initial portable gamma spectrometry indicates the source is Radium-226. The source is currently locked in the metal box. The State of Oklahoma is currently on the scene investigating and will determine a list of potential individuals who may have been exposed to the source. A preliminary assessment has determined that one individual received about 600 mRem to the hand. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2011-11-04
47396 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2011-10-13 12:00 | 2011-11-01 11:11 | 2011-11-01 | AGREEMENT STATE REPORT - DOSE MISADMINISTRATION The following information was received by facsimile: "NYS Incident 935 - On 10/31/2011 a NY radioactive materials licensee reported a diagnostic misadministration which occurred on 10/13/2011 and discovered on 10/28/2011. A patient undergoing diagnostic imaging of the thyroid using Iodine-123 was administered 4.21 mCi instead of the intended 400 uCi. The estimated dose to the patient's thyroid is 58 rem. "This is a preliminary 24 hour notification report. "The facility is performing an investigation and root cause analysis. "Telephone communications with the facility [and the State of New York] are ongoing. "The facility is required to submit a written report within 15 days." New York Event: NY-11-25 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-11-07
47395 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2011-10-31 18:00 | 2011-11-01 09:38 | 2011-11-01 | GENERAL ELECTRIC CR-120B RELAYS SUPPLIED BY NATIONAL TECHNICAL SYSTEMS FAIL BENCH TEST "On October 31, 2011, NextEra Energy Seabrook, LLC completed a 10 CFR 21 evaluation of a condition associated with General Electric (GE)-CR-120B relays supplied by National Technical Systems, Inc. and intended for use at Seabrook. Six (6) Quality Level 1 GE-CR-120B relays failed bench testing. During bench testing, the subject relays failed to reset when de-energized. An evaluation was performed to determine the applications where these relays could have been and were installed and to determine if the failure of the subject relays could result in a Substantial Safety Hazard as defined in 10 CFR 21.3. The evaluation concluded that there is one safety significant application relative to the failure of the GE-CR-120B relays to reset in the Seabrook Diesel Air Handling System (DAH). "Each DAH system train (includes one supply fan and one exhaust fan per train) has one relay that provides a start permissive for the ventilation fans. An analysis of the failure of a GE-CR-120B relay in the DAH system determined that, if the relays were installed, the condition could create a substantial safety hazard due to a subsequent loss of the emergency power function. Therefore, this report is being submitted pursuant to the requirements of 10 CFR 21.21(d)(3)(i). A written notification will be made to the NRC within 30 days pursuant to 10 CFR 21.21(d)(3)(ii). "No actual safety consequences resulted from this condition because the GE-CR-120B relays were not installed in the plant in this safety significant application." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 21.21 |  |  |  | 0 | 2011-11-01
47394 | 0 | PROVIDENCE PARK HOSPITAL |  |  |  |  | 2011-11-01 08:10 | 2011-11-01 08:45 | 2011-11-01 | CONTAMINATED PACKAGE Providence Park Hospital received an externally contaminated package from Hot Shots Nuclear Pharmacy (HSNP). Upon receipt of the package, the Nuclear Medical Technologist (NMT) performed a routine wipe test and determined the package was externally contaminated. Wipe test indicated surface contamination of 60,608 dpm (disintegrations per minute). The Radiation Safety Officer (RSO) was notified and the package was bagged and stored in a hot lab for decay. The package contained approximately 70 mCi of technetium-99m. There was no indication of any personnel contamination or exposure. The package will be shipped back to HSNP, after isotope decay is complete, for follow up investigation and recommendation. HOO Note: See EN #47392 for similar report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2011-11-01
47393 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2011-06-29 | 2011-10-31 15:46 | 2011-10-31 | OVERDOSE TO PATIENT OF 48% DURING GAMMAMED HIGH DOSE RATE TREATMENT "Patient was treated intraoperatively following surgical removal of a metastatic lesion in the sacral region. Treatment involved Ir-192 in a Gammamed HDR (High Dose Rate). "In standard cases implant geometry calls for a single-plane treatment, and entry of treatment plan into a commercial planning treatment system to control stopping positions of dwell times of source catheter. Size of treatment volume was such in this case that two treatment planes were required. Decision was made to select a single plane midway between the two treatment planes so that both treated regions would receive required dose. "Prescribed dose was 15 Gray at a position 1cm away from the source plane on either side, thus simulating a volume source implant. Treatment plan in this case required manual input of treatment parameters. "Physicist incorrectly entered distance between treatment planes as 3 cm, instead of 3 mm. A treatment plan was generated using the larger distance, and corresponding source stopping positions and dwell times for this separation. The result was incorrectly large dwell times and an overdose to the two treatment planes separated in fact by 3 mm. It was calculated that the dose delivered was 22.2 Gray rather than the prescribed 15 Gy, an overdose of 48%. "Discovery of Event: Event was discovered during chart rounds when a supervising physicist noticed the difference between prescribed dose and the iCheck results. After discovery of the event, it became evident upon reconstructing the timeline of events that treatment planning sheets in the patient's record had been altered. "Effect on Patient: In the opinion of the attending radiation oncologist, it is unlikely that there will be any medical consequences. "Root Cause of Event: An analysis concluded that the root cause of the event included: * Incorrect entry of data; * Failure to follow specifics of quality assurance procedure; * Inappropriate chart alterations; * Perception of some members of the staff that people who make or find a mistake will be punished regardless of the specifics of the event. "Actions Taken to Prevent Recurrence of Event: * Training to reverse perception of some members of the staff that people who make or find a mistake will necessarily be punished, regardless. * Retraining in actions to be taken in cases of non-standard geometry. * Disciplinary actions against physicist and dosimetrist involved. * Annual documented training of medical physicists, dosimetrists and radiation oncology physicians on appropriate quality assurance procedures. * Change in cover sheet for brachytherapy radiation treatments to include iCheck calculations including quality assurance verifications. "Inspection Results: An inspector from the Office of Radiological Health conducted an inspection on 9/21/11. The inspector found the circumstances of the event to be as described above. In addition, the inspector found that: * Upon check of the initial treatment plan by the physicist, the dosimetrist calculated a dose of 22.29 Gray rather than the prescribed 15 Gy. * The dosimetrist informed the physicist of the discrepancy. * The physicist told the dosimetrist that the iCheck results may be wrong. The reason was that the ABACUS program used by the physicist knows that there are two treatment planes, and that the iCheck which assumes one plane may be wrong. * Dosimetrist at this point failed to follow proper QA by stopping treatment and informing the radiation oncology attending. * After seeing the 15 Gy calculated dose at 1 cm from source plane, the attending oncology physician concluded that isodose distribution was correct. * The dosimetrist left the OR and treatment proceeded with the incorrect dwell times. "The inspector found licensee to be highly cooperative and believes that actions taken in the wake of this event were satisfactory. No formal violation was issued." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-11-06
47392 | 0 | INGHAM REGIONAL MEDICAL CENTER |  |  |  |  | 2011-10-31 11:20 | 2011-10-31 15:30 | 2011-10-31 | PACKAGE RECEIVED WITH SURFACE CONTAMINATION ABOVE LIMITS "Package marked container 1 from Hot Shots Nuclear Medicine (license #21-26597-01md) had a wipe test of 4700 dpm. Background was re-measured and the second wipe was 5900 dpm. The package was thoroughly wiped with alcohol. The third wipe revealed a count of 510.0 dpm. The package was then opened. An inside wipe of the package was 678 dpm. The package was considered safe for use. The doses were used. Notifications were made to personnel from Medical Physics Consultants and Hot Shots Nuclear Medicine. The Ingham Regional Medical Center Radiation Safety Officer was also notified." The package contained Technetium-99m, a gamma emitter. The licensee believes that the package was transported via a Hot Shots Nuclear Medicine courier. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2011-10-31
47391 | 0 | HOSPITAL METROPOLITAN DR. PILA |  |  |  |  | 2011-08-17 | 2011-10-31 12:15 | 2011-10-31 | DOSE TO AN EMBRYO "On 8/17/2011, an oral dose of 100.2 mCi of NaI-131 (sodium iodide) was administered to a female patient of childbearing age for radioablation of papillary thyroid carcinoma post thyroidectomy. The patient became pregnant approximately a week after dose administration, despite proper pre-therapy orientation and against medical advice. This was brought to [the licensee's] attention by the patient's OB/GYN physician on 9/28/2011. On that same date, the patient was contacted via telephone and was alerted and oriented as to the possibility of harmful effects of radiation to the embryo. On 10/4/2011, that same orientation was performed more thoroughly in person. Full dosimetric analysis was performed by [the licensee's] medical physicist on 10/5/2011. A complete medical report, including possible effects and complications was given to the patient and referring OB/GYN physician on 10/19/11. The list of possible complications included: Miscarriage, neurologic system damage, intrauterine growth retardation, mental retardation, and increased risk of development of cancer. "To prevent recurrence of this incident, [the licensee has] created a barrier system, where the department secretary and then the nuclear technologist verifies the patient's paperwork before the physician. We have also revised our patient instructions for childbearing age patients." The licensee has verbally discussed this incident with R2 (Bermudez). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | PR | HOS |  | 35.3047(a) |  |  |  | 0 | 2011-11-06
47390 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-10-29 19:18 | 2011-10-29 19:46 | 2011-10-29 | LOSS OF GREATER THAN 25% OF EMERGENCY NOTIFICATION SYSTEM SIRENS DUE TO WEATHER CONDITIONS "At approximately 1818 EDT on October 29, 2011, Three Mile Island Nuclear Generating Station received notification that 25 of 96 emergency notification system offsite sirens were not functional. The loss of >25% of the sirens is considered a Major Loss of Emergency Preparedness Capabilities (10CFR50.72(b)(3)(xiii)). The loss of offsite sirens was due to loss of electrical power caused by significant heavy snowfall in the area. Efforts are in place to restore offsite sirens to service." The licensee stated that compensatory measures are in place should their be a need to notify the areas affected by the lost sirens. The licensee has notified State and local authorities. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-29
47389 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-29 15:15 | 2011-10-29 15:39 | 2011-10-29 | LOSS OF GREATER THAN 25% OF EPZ SIRENS DUE TO WEATHER "Limerick Generating Station reports a loss of >25% of the EPZ sirens for greater than 1 hour. Forty eight of the 165 offsite sirens are not functioning due to loss of power related to the recent storm." The licensee has notified the NRC Resident Inspector, and state and local government. A press release may be issued. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-29
47388 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-10-28 16:44 | 2011-10-28 22:11 | 2011-10-28 | FITNESS FOR DUTY INVOLVING A EMPLOYEE SUPERVISOR A non-licensed supervisor was arrested for possession of a controlled substance with the intent to distribute. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2011-10-28
47387 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2011-10-28 14:30 | 2011-10-28 19:09 | 2011-12-14 | TSC UNAVAILABLE FOR EMERGENCY CONDITIONS "At 1430 [EDT] on 10/28/11, it was discovered that due to an Equipment Clearance Order (ECO), the HVAC recirculation capability of the Technical Support Center (TSC) was lost. The TSC dampers were deenergized in the non-emergency position while the ECO was in effect. The ECO was put into effect on 10/10/11. The ECO was released at 1630 [EDT] on 10/28/2011 and functionally tested restoring TSC HVAC recirculation capability. "While the ECO was in effect and under certain accident conditions, the TSC may have been unavailable due to the inability of the charcoal filtration system to maintain a habitable atmosphere. The alternate TSC remained available, during the time the ECO was in effect, as defined in the Emergency Plan Implementing Procedures. This 8 hour notification is required per 10 CFR 50.72(b)(3)(xiii)." The alternate TSC remained available during this period. The NRC Resident Inspector has been notified. * * * RETRACTION FROM JOSE VASQUEZ TO VINCE KLCO ON 12/14/2011 AT 1852 EST * * * "A Functionality Assessment (FA) has concluded that the Turkey Point TSC was able to perform it's intended function of ensuring habitability to TSC responders during the period 10/10/11 through 10/28/11 with the TSC ventilation system in the degraded condition. A dose analysis was performed, modeled after the design basis LOCA analysis for the TSC, using alternate source term, no filtration, containment leakage based on the most recent ILRTs, current data on ECCS leakage, and meteorological conditions existent during the period. Dose to TSC responders would have been less than the general design criterion limit of 5 REM." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-28
47386 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-10-27 | 2011-10-28 16:28 | 2011-10-28 | DAMAGED PACKAGING CONTAINING RADIOACTIVE MATERIAL "The purpose of this report is to notify the NRC of a breach of a package containing a limited quantity of radioactive material. This breach was considered 'breakage' in accordance with Title 49 of the Code of Federal Regulations, Transportation. In accordance with 49 CFR 171.15, Duke Energy contacted the National Response Center at 1350 [EDT] on October 28, 2011, Report Number 993866. The National Response Center then contacted Mecklenburg County, NC, Emergency Management. "Although the packaging of the radioactive material was damaged during transportation, the package was transported in an enclosed van. The radioactive material itself has not been released, and the damage did not result in radioactive contamination or any radiation exposure. This event is being reported because notification to other government agencies has been made." The NRC Resident Inspector has been notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-28
47385 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-10-06 | 2011-10-28 16:02 | 2011-10-28 | AGREEMENT STATE REPORT - FETUS EXPOSED TO RADIATION DURING THYROID THERAPY TREATMENT The following was received from the state via facsimile: "The patient took a pregnancy test on October 5, 2011 and the results were negative. The patient was then treated with 73.7mCi of I-131 thyroid therapy treatment on October 6, 2011. The patient discovered she was pregnant and contacted the licensee on October 26, 2011. The estimated dose to the fetus is 17.4 Rads. It has been determined that the fetus was 10 days old when the therapy was given to the patient. "The licensee will be submitting a written report within 15 days. The Department plans to do a reactive inspection to review licensee's procedures and response to this ME." Event Report ID No. PA110031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-03
47384 | -1 | JEPPESEN RADIATION ONCOLOGY |  |  |  |  | 2011-01-11 07:00 | 2011-10-28 15:26 | 2011-12-01 | MEDICAL EVENT - MISADMINISTRATION OF PROSTATE CANCER SEEDS During a recent inspection, an NRC inspector noted two cases which occurred on 8/23/11 and 1/11/11, respectively in which two separate patients were under dosed by greater than 20% during prostate cancer treatment using Iodine 125 seeds. The underdose was determined during post operative treatments. The same physician administered the procedure in both cases. The licensee has informed the prescribing physician, and is investigating the cause of the events. There is no long term permanent functional damage suspected to any organ in either case. The licensee discussed the issue with NRC Region 3 (Gattone). * * * UPDATE FROM DENNIS KEHOE TO VINCE KLCO ON 11/01/11 AT 1841 EDT * * * After the licensee reviewed 3 years of medical reports, fourteen patents were found to have been under-dosed greater than 20% of the prescribed dose. Specific under-dose dates were: 4/10/08; 4/21/08; 4/25/08; 9/15/08; 10/17/08; 11/03/08; 2/17/09; 8/27/09; 1/05/10; 1/14/10; 5/25/10; 10/12/10; 5/03/11 and 5/19/11. The licensee discussed the issue with NRC Region 3 (Gattone). Notified the R3DO (Valos) and the FSME EO (Camper). * * * RETRACTION FROM DENNIS KEHOE TO VINCE KLCO ON 12/1/2011 AT 1440 EDT * * * The licensee is retracting this event due to the fact that the prostate seed implant for all the above 16 referenced events are planned intra-operatively within the operation. The licensee evaluates the seed implants at the end of the implant operation. Notified the R3DO (Riemer) and FSME (McIntosh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2011-11-03
47383 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2011-10-27 17:15 | 2011-10-27 19:08 | 2011-10-27 | ACCIDENTAL DISCHARGE OF FIREARM "At approximately 1715 EDT on 10/27/11, a Security Officer accidentally discharged his weapon and wounded himself in the foot. An ambulance and Monroe County Sheriff reported to the site. The officer was transported offsite to a local hospital. This is being reported under 10CFR50.72(b)(2)(xi)." The officer was clearing his weapon following his shift when the accident occurred. No other individuals were hurt. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-27
47382 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-10-26 20:05 | 2011-10-27 15:35 | 2011-10-27 | FITNESS FOR DUTY - NON-SUPERVISORY TECHNICIAN TESTED POSITIVE FOR ALCOHOL A non-supervisory technician (vendor) had a confirmed positive test for alcohol during a random fitness-for-duty test. Plant access for the individual involved has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2011-10-27
47381 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-10-13 07:00 | 2011-10-27 15:26 | 2011-10-27 | AGREEMENT STATE REPORT - BROKEN HANDLE ON BERTHOLD NUCLEAR GAUGE The following was received from the state via e-mail: "On October 13, 2011, the Agency [Texas Department of State Health Services] was notified by the licensee that while exercising the shutter handle on a Berthold nuclear gauge containing 20 milliCuries of cesium - 137 the handle broke off flush with the gauge housing. The gauge shutter is in the open position, which is the normal operating position of the shutter. No individual will receive any additional exposure due to the failure. The manufacture has been contacted to repair the gauge. The licensee stated that no entry to the vessel will be allowed until the gauge has been repaired. The cause for the failure is unknown at this time. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident Number: I-8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-01
47380 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-10-26 15:00 | 2011-10-27 14:33 | 2011-10-27 | LOSS OF DOUBLE CONTINGENCY "On October 26, 2011 at approximately 3:00 p.m., a deficiency was identified during a routine criticality safety review of a proposed revision to an operating procedure for transporting and storing 3-gallon cans. One of the controls needed to meet double contingency was not available to restrict the movement of cans that exceed the specified mass limit for these storage locations. This resulted in a condition where the mass control documented in the criticality safety analysis had not been maintained. The second control, geometry, was maintained. "There are no uranium cans of this particular material type currently in these storage locations and no unsafe condition is present. All movement of this material type to these designated storage locations has been suspended. "Additional corrective actions and extent of condition are being evaluated. "This event is being reported pursuant to GNF-A internal procedure reporting requirements due to a loss of double contingency." The licensee will notify Region 2, North Carolina Radiation Protection, and New Hanover County Emergency Management. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2011-10-27
47379 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-10-26 11:25 | 2011-10-27 13:15 | 2011-10-27 | OFFSITE NOTIFICATION TO STATE AND LOCAL OFFICIALS DUE TO INADVERTENT SIREN ACTIVATION "On 10/26/11 at approximately 11:25 a.m., while performing siren encoder maintenance and testing, the siren vendor inadvertently activated the EPZ sirens. New Hampshire, Massachusetts, Vermont and local emergency management directors were notified of the event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-27
47378 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-10-27 10:27 | 2011-10-27 12:12 | 2011-10-27 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR CONTAINING 10 MILLICURIES POLONIUM 210 The state's licensee reported that they lost a NRD Nuclecel Device Model P-2021-8201, serial number A2HH880, which was shipped to the company on 09/01/10. The company noticed the device was missing on October 4th. However, the company also believes it could be installed somewhere in the facility in a location where it cannot be seen. The State's licensee has implemented the following corrective actions: "1) We will assign 1 device to its own machine cell and it will not be moved. 2) We have stopped the use of quick push/pull connections and replaced with threaded connections. 3) All Nuclecel devices are attached with yellow air hose ... and we don't use yellow air hoses on anything else. 4) We have added the devices to our month end inventory count." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-11-01
47377 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-10-12 | 2011-10-27 11:37 | 2011-10-27 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHER OVEREXPOSURE The following was received from the state via email: "On October 17, 2011, the Agency [Texas Department of State Health Services] was notified by a licensee that one of its radiographers had climbed a ladder to remove the guide tube from a SA Model 880 radiography camera containing a 49.3 curie Iridium (IR)-192 source that was suspended by a rope. Another employee walked by the area and observed the survey meter needle was pegged high. He yelled at the radiographer who climbed down the ladder and attempted to crank the source back into the camera. The source would not move so he cranked it all the way out and then retracted it successfully. The radiographer's badge was sent for processing. The badge had a whole-body dose reading of 4,192 millirem, bringing his total for the year to 5,196 millirem, exceeding the annual limit. The radiographer was unable to ascertain where the source had been in the guide tube. The radiographer did not carry the dose rate instrument to the camera because the safety rules for the facility he was working at does not allow an individual to climb a ladder with any articles in their hand. On October 27, 2011, the Agency [Texas Department of State Health Services] was informed by the licensee that they had completed their investigation and had calculated the dose to the radiographers left hand, which had been on the guide tube, to be between 51 and 58 rem for the event exceeding the annual limit. The licensee stated that they had not observed any changes in appearance in the radiographer's hand. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-11-01
47376 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-10-26 13:20 | 2011-10-26 21:24 | 2011-10-26 | 24 HOUR REPORT DUE TO DETECTION OF LINEAR DEFECT IN SURGE VOLUME ACCUMULATOR "At 1320 CDT, on 10-26-11 the Plant Shift Superintendent (PSS) was notified that the C-310 Side Accumulator had a linear defect in the vessel shell that caused a UF6 release on 10-21-2011. The UF6 liquid accumulators serve the product withdrawal system. The side accumulator is a monel tank used in the product withdrawal system to provide a surge volume. The safety function of the side accumulator is to provide UF6 primary system integrity for the withdrawal process that contains a gaseous and liquid UF6. TSR 2.3.5.6 is a design feature that requires the withdrawal area UF6 condensers and accumulator vessels to have a minimum required metal thickness in accordance with ASME requirements to prevent UF6 releases. There are no LCO actions associated with this TSR but there is a 5 year surveillance requirement to perform a visual inspection including thickness measurements. The side accumulator was in service when a small UF6 release occurred on 10-21-2011. The release was contained to the immediate area and the side accumulator was taken out of service for investigation and subsequent repairs. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-11-2856; PDGP Event Report No. PAD-2011-19. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2011-10-26
47375 | 0 | RHODE ISLAND ATOMIC ENERGY COMM |  |  |  | 2000 KW POOL | 2011-10-25 11:15 | 2011-10-25 13:07 | 2011-10-26 | 24 HOUR TECHNICAL SPECIFICATION REQUIRED REPORT BASED ON A POTENTIAL OVER-EXPOSURE EVENT At approximately 1115 EDT on 10/25/11 an intern entered the dry gamma room at the Rhode Island Nuclear Science Center Facility during an ion probe calibration procedure. The intern received an estimated unplanned dose of between 2-3 rem based on a stay time of 5 minutes in a 500 mr/min field. His dosimetry, an OSL (Optically Stimulated Luminescence) badge, has been sent to Landauer for expedited processing. The dry gamma room is properly posted as a high radiation area with administrative controls in effect to limit access. The assistant Director of the facility is performing an investigation including event reconstruction to determine the cause. * * * UPDATE FROM JEFF DAVIS (LICENSEE) TO HUFFMAN ON 10/26/11 AT 10:03 EDT * * * The licensee clarified that the call to the Operations Center made on 10/25/11 was a 24 hour notification required by the facility's Technical Specification 1.25.8 based on the potential for over-exposure. NRR Backup Project Manager (Hardesty) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | RI | NPR | [5 empty] | 0 | 2011-10-26
47374 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-10-25 15:34 | 2011-10-25 23:49 | 2011-10-26 | DEFICIENCY IDENTIFIED IN TRANSITION TO PERFORMANCE BASED STANDARD FOR FIRE PROTECTION "At 1534 on 10/25/11 Site Engineering and Licensing reported the following to the Operations Department: "The following deficiency was identified during reviews for NFPA 805 Transition: Cable 1B11 (#12 awg - Fire Area Route 16, 17) from the shunt in the 250 VDC Battery Board 1 (0-BDDD-280-0001) compartment #1, to the control room ammeter 1-EI-57-38 mounted on Control Room Panel 1-9-8, is not fused or otherwise protected against an electrical fault. The 250 VDC Battery 1 is an un-grounded DC system. However, in a scenario where the 250 VDC Battery Board system negative becomes grounded at the same time the ammeter cable 1B11 has a fault to ground, the cable may not be protected and the cable could auto-ignite anywhere along the cables length from the ground fault location back to the battery source. For example, in a Fire Area 16 (Control Bay) scenario, these ground faults could result in a fire being spread from Fire Area 16 to Fire Area 17 (Battery Board 1). Fuses should be added to protect these cable conductors. "A similar condition exists for the remote ammeters on Unit Battery Board 2 (Cable 2B11 - Fire Area Route 16, 18), Unit Battery Board 3 (Cable 3B11 - Fire Area Route 16, 19), Unit Battery Board 4 (Cable 2B4018 - Fire Area Route 16, 26), Unit Battery Board 5 (Cable 1B383 - Fire Area Route 16, 26), and Unit Battery Board 6 (Cable 3B336 - Fire Area Route 16, 26). "This condition is reportable as an 8 hour notification to the NRC IAW 10CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "This is also reportable as 60 day written report IAW 10CFR 50.73(a)(2)(ii)(B). "Fire watch compensatory measures are in place for the Fire Areas of concern. Ref. FPIP#09-1920 "The NRC resident has been notified of this event. "This event was entered into the licensee's Corrective Action Program as PER# 452185." | 50 | 100 | 100 | 50 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-10-26
47373 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-10-19 15:45 | 2011-10-25 16:00 | 2011-10-25 | AGREEMENT STATE REPORT INVOLVING FOUR MISSING TRITIUM EXIT SIGNS The following report was received from the California Radiation Control Program via email: "During a inspection/inventory, by NCIS [National Center for International Schools] personnel, of tritium exit signs it was discovered that 4 of the signs had been vandalized and the EXIT portion and /or the tritium tubes had been removed from the unit with the mounting bracket still attached to the wall." The initial notification was forwarded to the California Radiation Control Program by the NRC State Programs Office on 10/19/11. The actual event date is unknown. CA 5010 Number (Date Notified): 102011 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-10-28
47372 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-24 17:15 | 2011-10-24 20:14 | 2011-10-24 | EMERGENCY OPERATION FACILITY OUT OF SERVICE DUE TO PLANNED MAINTENANCE ACTIVITY " At 1715 hours on 10/24/2011, replacement of a router and circuit at the Emergency Operation Facility (EOF) commenced. This action will cause a temporary outage of network devices such as personal computers, telephones, printers, routers, switches, alarm panels, and wireless communications. The duration of work is expected to be approximately 8 hours. If use of the EOF is subsequently required, this condition may delay activation of the EOF until equipment is restored. Restoration of the equipment will take less than one hour. "This is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the State of Pennsylvania, Luzerne and Columbia Counties and the NRC Resident Inspector. * * * UPDATE FROM ROBINSON TO KLCO ON 10/24/2011 AT 2252 * * * Systems have been restored and the EOF is operable. The licensee has notified the NRC Resident Inspector. Notified the R1DO (DeFrancisco). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-24
47371 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-10-21 | 2011-10-24 18:07 | 2011-10-24 | AGREEMENT STATE REPORT INVOLVING APPARENT STOLEN DENSITY GAUGES WITH CS-137 SOURCES "On October 22, 2011, at approximately 12:05 AM, the [Pennsylvania] Department's Director of the Bureau of Radiation Protection received notification via a phone call and email from the Pennsylvania Emergency Management Agency's Duty Officer of two 'densitometers' with radiation symbols that were found on the side of the road. It appears that the devices were stolen. This event is reportable under 10 CFR 20.2201(a)(1)(i). "On Friday, October 21, 2011 evening (time unknown), two 'densitometers,' sealed source make and model currently unknown, each containing approximately 200 millicuries (mCi) of Cs-137, were reported found on the side of the road in Montoursville, PA in Lycoming County. A Fire Department and Emergency Response Team were deployed, and the two devices were isolated - one at or near Fairview Drive & Cherry Street, and the other on Maple Street in the same general area. Radiation measurements in the range of 30 to 40 micro-roentgens per hour at six feet were noted. The licensee was contacted and quickly recovered the two devices (Serial No. 8-7176 and 8-6891) and the Cs-137 sources at around 1:00 AM on October 22, 2011. [The devices] are now back in [the licensee's] possession. The DEP BRP Director spoke to the licensee's representative around this same time and was informed the sources were found in a shielded configuration, and, they could (now) account for all their radioactive sources. From the information known at this time, there were no noteworthy radiation exposures to the general public or any responding personnel. "A reactive inspection is planned by the Department's Radiation Protection Program along with the PA DEP Bureau of Investigations. More details will be added as they become known. "Media attention: None at this time Pennsylvania Event Report ID No: PA110028 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-11-01
47370 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-10-24 10:35 | 2011-10-24 17:24 | 2011-10-24 | ACCIDENT MITIGATION SYSTEMS OUT OF SERVICE DUE TO MAINTENANCE ERROR "On 10/24/11 at 1035 CDT, a maintenance technician performing a field walk-down of a clearance order inadvertently opened the bus potential fuse drawer for Unit 2 Safety Related Bus 23. This caused all loads of Bus 23 to receive an undervoltage (UV) load shed signal. Division I Containment Cooling Service Water (CCSW) pumps are powered from Bus 23 and are currently aligned to the Main Control Room Emergency Ventilation (CREV) Air Conditioning system. On a loss of CCSW, the CREV Air Conditioning system is inoperable due to a loss of its emergency cooling water supply. This condition affects both Dresden Units 2 and 3. This condition lasted for approximately 7 seconds before the bus potential fuse drawer was reinserted and the Bus 23 UV condition cleared. "This event is reportable under 10CFR50.72(b)(3)(v)(D) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-10-24
47369 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-24 16:11 | 2011-10-24 17:01 | 2011-10-24 | MANUAL REACTOR SCRAM DUE TO ERRATIC IRM INDICATIONS DURING STARTUP "While performing a startup of HNP-2, after reaching criticality, the crew observed erratic indications on two Intermediate Range Monitors (IRMs), 2C51K601A and 2C51K601C. IRM 2C51K601A had been spiking and was subsequently bypassed. The 2C51K601C was spiking downscale and could not be bypassed due to the 2C51K601A being bypassed already. Both IRMs are in the 'A' RPS trip system. At the time when the second IRM was acting erratic, the crew identified the condition as both IRMs in the same quadrant and did not continue withdrawal of control rods. As a result of not withdrawing control rods, reactor power began to decrease and the crew conservatively inserted a manual reactor scram to shutdown the reactor. All rods did fully insert into the core. No PCIS [Primary Containment Isolation System] actuations occurred and none were expected to occur based on plant conditions following the scram. "At this time, investigation is in progress, but the investigation and corrective actions have not yet been completed. "The crew is maintaining HNP-2 in Hot Standby [Mode 3] at this time." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-10-24
47368 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-10-24 01:52 | 2011-10-24 09:38 | 2011-10-24 | BOTH DIVISIONS OF THE RWCU HIGH DIFFERENTIAL FLOW ISOLATION FUNCTION REMOVED FROM SERVICE "This event is being reported in accordance with 10CFR50.72(b)(3)(v)(C). On October 23, 2011 at 0915 EDT, the Division 1 Reactor Water Cleanup (RWCU) system differential flow - high channel was declared inoperable due to failing its channel check. A troubleshooting plan was developed to determine the cause for the failed channel check. In accordance with this troubleshooting plan, at three separate times (October 24, 2011 at 0152, 0258, and 0519), both the Division 1 and Division 2 RWCU differential flow timers were placed in bypass, and Technical Specification (TS) 3.3.6.1, Condition B was entered for one or more automatic functions with isolation capability not maintained. In each of the three instances, one channel of the RWCU differential flow - high function was restored to Operable status within 1 hour as required by TS 3.3.6.1 Required Action B.1. It was believed at the time of the troubleshooting evolutions that this condition was not reportable because it was a planned maintenance evolution performed in accordance with approved procedures and the plant TS; however, further review has concluded that disabling both divisions of the RWCU differential flow - high function constitutes a reportable condition in accordance with 10CFR50.72(b)(3)(v), as an event or condition that could have prevented fulfillment of a safety function." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2011-10-24
47367 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-21 08:57 | 2011-10-22 01:56 | 2011-10-22 | FITNESS FOR DUTY RULE NOT MET "At 0857 on 10/21/2011 a condition was reported identifying that 10CFR Part 26 requirement for the FFD Lab Director to be subject to the FFD Rule was not met for the period of 12/12/2010 to 4/28/2011. "10CFR 26.4(g), 'FFD program applicability to categories of individuals,' provides specific requirements for FFD program personnel. "Contrary to the above, the FFD Lab Director was not included in the [licensee's] random drug testing program as required by the regulation. "This event is reportable under 10CFR26.719(b)4 requiring a 24 hour ENS notification." The NRC Resident Inspector has been notified. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2011-10-22
47366 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-10-21 17:20 | 2011-10-21 20:25 | 2011-10-21 | OFFSITE NOTIFICATION DUE TO FUEL OIL SPILL "This event is being reported in accordance with 10CFR50.72(b)(2)(xi). On October 21, 2011, at approximately 1723 hours EDT, notification of a fuel oil spill was made to the US Environmental Protection Agency (EPA), National Response Center. At the time of the event, the plant was in Mode 1 at 100 percent rated thermal power. The fuel oil spill was caused by a leak in an underground pipe outside the protected area, but inside the owner controlled area. The spill is estimated between 1000 to 1500 gallons and is contained onsite. However, a certified wetlands specialist was contacted and determined the area met the criteria for wetlands designation, which in turn made the event reportable. Clean Harbors Incorporated is assisting with the onsite clean-up and remediation. "Additionally, the Ohio EPA: State Emergency Response Commission, Perry Township Fire Department, Lake County Emergency Planning Committee, and the U.S. Coast Guard were notified in accordance with plant procedures. This event is also being reported in accordance with the plant's Operating License, Appendix B, Environmental Protection Plan, which states, in part, that any occurrence of an unusual or important event that indicates or could result in significant environmental impact causally related to plant operation shall be recorded and reported to the NRC within 24 hours followed by a written report." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-21
47365 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2011-08-24 | 2011-10-21 17:05 | 2011-10-21 | POTENTIALLY UNDERSIZED WELDS ON CENTRIFUGE T-COLUMN BASE PLATE CONNECTORS Name of the firm constructing or supplying the basic component which contains the deviation or fails to comply: Engineered Products Department PO Box 2138 Carlsbad, NM 88221 Description of the deviation or failure to comply which is being evaluated : Undersized welds were identified on centrifuge T-column to base plate connectors which are still in construction. The welds do not comply with AWS 01.1 and are currently being evaluated for the potential to cause substantial safety hazards. An extent of condition is in progress to identify any further conditions and to provide weld dimensions to the design agent for engineering analysis. This analysis will determine the ability of the steelwork to perform per design requirements. The date on which the information of suspect deviation defect or failure to comply was obtained: 24 August, 2011 The date on which the evaluation is expected to be complete: 23 November, 2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 21.21 |  |  |  | 0 | 2011-10-21
47364 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-10-21 12:50 | 2011-10-21 16:42 | 2011-11-01 | AUTOMATIC REACTOR SCRAM DUE TO LOCKOUT OF AUXILIARY POWER TRANSFORMER "The station experienced a lockout of the 2R Auxiliary Power Transformer. The resulting transient caused an automatic actuation of the RPS system. All control rods fully inserted. A Group 2 Primary Containment isolation occurred. Both 11 and 12 Emergency Diesel Generators started on a loss of voltage signal. Equipment response was that the 11 ESW [Emergency Service Water] pump (cooling for the #11 Emergency Diesel) failed to develop required pressure. The #13-4160V non-safety related bus failed to restore after the transient [and feed the Division 1 Essential Bus]. Additionally, the #15 bus transferred to the 1AR transformer [and is feeding the Essential Bus]." The #11 Emergency Diesel Generator is currently tagged out of service. Electrical supply is being provided by offsite power. Reactor heat is being removed through the main steam line to the main condenser and reactor water inventory is being provided by the feedwater system. The SRVs lifted and reseated. The HPCI system was manually place into a pressure control mode. The Minnesota Pollution Control Agency is being notified due to the licensee violating the site discharge canal temperature rate of change limit. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RYAN RICHARDS TO JOHN KNOKE AT 1730 EDT ON 11/01/2011 * * * "Prior to this event the 'B' Control Room Emergency Filtration (CREF) and 'B' Control Room Ventilation (CRV) Systems were inoperable for planned maintenance. On 10-21-11 at 1325 CDT, the #11 EDG ESW Pump was declared inoperable due to low cooling water pump flow, resulting in the #11 EDG being inoperable, which in turn resulted in the 'A' CREF and 'A' CRV being inoperable. "Contrary to reporting requirements this condition was not identified and reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as required within 8-hours in the previous event notification. This condition resulted in a loss of safety function for both divisions of CREF and CRV. This update amends the 10-21-11 event notification to include this as an 8-hour non-emergency event pursuant to 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified the R3DO (Nick Valos) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2011-10-21
47363 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-10-21 03:30 | 2011-10-21 11:13 | 2011-10-21 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE STRUCK BY VEHICLE AT CONSTRUCTION SITE The following was received from the state via fax: "The on-duty State Response Coordinator (SRC) for the Wisconsin Department of Health Services (DHS) received a phone call at approximately 3:30 am that a moisture density gauge had been struck by a motor vehicle. The incident occurred at a road construction site near 1221 Northport Drive, Madison, WI. The gauge was in use with the operator in contact with it, when a car veered out of traffic into the construction lane. The operator was forced to jump out of the path of the vehicle, leaving the gauge. The vehicle struck the gauge, shattering the housing. The source rod with the Cesium-137 source detached from the housing. The Americium/Beryllium source remained within the housing. The SRC and licensee's RSO responded to the scene to supervise source recovery. "The Cesium source was leak tested in-situ and determined to be intact. Surveys were performed in the affected area, with no contamination detected. A portion of the housing designed to hold the retracted Cesium source rod was found partially intact. The Cesium source was placed within the cavity and securely taped. The housing assembly was placed in the transport container for transport back to a licensed service provider for assistance with disposal. "The driver who struck the gauge has yet to be located by the police. The licensee will be submitting a 30 day written report concerning this event." Event Report ID Number: WI110017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-10-26
47362 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-10-20 16:50 | 2011-10-20 20:38 | 2011-10-20 | OFFSITE NOTIFICATION DUE TO THE OFFSITE FATALITY OF AN EMPLOYEE "On October 20, 2011 at approximately 1335 hours, a South Texas Project employee suffered an apparent heart attack offsite while attending a fire brigade training exercise. The person was transported to Matagorda County Regional hospital. The individual was evaluated by emergency room personnel and later pronounced deceased. "OSHA is being notified pursuant to the requirements of 29CFR1904.39. This ENS report is being made in accordance with 50.72(b)(2)(xi). "There was no radioactive contamination involved in this event. The licensee does not plan any media or press release. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-20
47361 | 0 | WATERFORD | 3 |  |  | [3] CE | 2011-10-20 08:00 | 2011-10-20 14:32 | 2011-10-20 | INOPERABLE EMERGENCY FEEDWATER PUMP POTENTIALLY IMPACTS RHR SAFETY FUNCTION "At 08:00 CDT on 10/20/2011 Essential Chilled Water Loop B was declared inoperable while turbine driven Emergency Feedwater Pump AB was out of service for planned maintenance. Operability of Essential Chilled Water Loop B was restored at 08:50. During this time period, the application of cascading technical specifications rendered motor driven Emergency Feedwater Pump B inoperable. The remaining operable Emergency Feedwater Pump A is a design rated 50 percent pump; therefore, this event could have prevented fulfillment of the Residual Heat Removal safety function. Offsite power and Train A safety related equipment and systems were verified operable. "Essential Chilled Water Loop B was declared inoperable because Essential Chiller B failed to automatically restart from a load recycle. The shift crew took action to align Essential Chiller AB to restore operability to Essential Chilled Water Loop B. The cause for the failure of Essential Chiller B is not yet known. Restoration of operability to Essential Chilled Water Loop B concurrently restored operability to Emergency Feedwater Pump B. "No plant transient or safety system actuations occurred. Plant operation continues stable at 100 percent power." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-10-20
47360 | -1 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2011-10-20 09:10 | 2011-10-20 13:03 | 2011-11-23 | ONE HOUR REPORT DUE TO A FAILED ITEM RELIED ON FOR SAFETY "At approximately 0910 [PST] on 10/20/2011, during discussions with an NRC inspector, the AREVA Richland NCS Manager concluded that a previous determination made on Friday, 7/22/2011 that an IROFS (a criticality drain on a HEPA filter housing) declared to be in a degraded state was, in fact, failed in that a pre-filter in the HEPA housing was sitting on the drain and could have prevented it from performing the required safety function. This original discovery was made during a routine PM of the system (a management measure prescribed to this IROFS). On 7/22/2011 (the initial day of discovery) the criticality drain was modified so that it would remain unobstructed and free flowing. "At 1303 EDT, AREVA's EHS&L Manager notified the NRC Operations Center of this condition per the requirements of 10CFR70 Appendix A criterion (a)(5) (1 hour report) which requires reporting if '... only one IROFS remains available and reliable to prevent a nuclear criticality and has been in that state for greater than 8 hours,' and indicated that potentially criterion (b)(1) (24 hour report) was also met. This 24 hour criterion requires reporting '... the facility being improperly analyzed, or different than analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR 70.61.' Subsequent to the initial report, AREVA has concluded that the performance requirements of 10CFR 70.61 were met and the 24 hour reporting criteria (b)(1) do not apply. "Safety Significance of Event: The safety significance of this event is low. This process is used to recover incinerator ash and the ISA team was unable to identify any mechanism whereby a critical concentration of approximately 285 g U/liter of solution could be created in the process connected to the duct work. "Potential Nuclear Criticality Pathways Involved: The only potential pathway is for uranium bearing liquids that exceed 285 g U/liter to gradual build up in the HEPA filter housing. "Controlled Parameters (Mass, Moderation, Geometry, Concentration, Etc.): Uranium mass/concentration is controlled. "Nuclear Criticality Safety Control(s) or Control System(s) and description of the failures or deficiencies: No control system failures occurred. "Corrective Actions to Restore Safety Systems and When Each Was Implemented: A grate was installed over the criticality drain inlet on July 22, 2011 and has been present since that time." * * * RETRACTION FROM ROBERT LINK TO HOWIE CROUCH ON 11/23/11 AT 1205 EST * * * "After careful consideration of the guidance contained in FCSS ISG-12 and NUREG 1520, Rev. 1, AREVA has concluded that this condition did not meet the reporting requirements set forth in 10CFR70 Appendix A and formally retracts the previously made report." Notified R2DO (Freeman) and NMSS EO (Hiltz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2011-10-20
47359 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-10-20 10:50 | 2011-10-20 13:46 | 2011-10-20 | FLOOD BARRIER PENETRATIONS NOT WATER TIGHT "During follow-up inspections of flood barrier penetrations into two rooms in the plant it was determined that some of the water tight conduit fittings were not filled with the material required to make them water tight. Inspection caps were removed from the fittings to perform the inspections. Three fittings into room 19 (auxiliary feedwater and plant air compressors) and fittings into room 56E (electrical switchgear) were found to contain no filling material. One additional fitting into room 56E that was thought to be capped was found to be open with a sheet metal box covering the inside access thereby obscuring inspections. "All of the affected penetrations have modifications in progress to assure that they are modified and qualified for design basis flood levels. "Of the 16 penetrations 6 have been verified to be made water tight by other means, specifically fire foam barrier installed in the conduit from the room 56E side. "The remaining 10 penetrations will leak with a 1014 flood, although the plate will restrict flow to some degree. The stations auxiliary feedwater and safety related electrical switch gear could be affected. "This eight-hour notification is being made pursuant to 10CFR50.72 (b)(3)(v)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-10-20
47358 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-10-10 | 2011-10-20 09:55 | 2011-10-20 | LOSS OF CONTROL OF AN I-125 BRACHYTHERAPY SEED On October 10, 2011, North Carolina Radiation Protection (NCRP) received a call from the Radiation Safety Officer (RSO) at Marion L. Shepard Cancer Center in Washington, NC, informing them that on September 26, 2011, while working with I-125 brachytherapy seeds for calibration, they had discovered the loss of one of the seeds. The lost seed was a 0.346 mCi brachytherapy seed that had been received on September 23, 2011. According to the RSO, they had made every effort to locate the seed but could not find it. At that time, it was believed that the seed must have gone behind an un-movable counter in the hot lab at the hospital nuclear medicine department. The well counter they use is kept at the cancer center and taken to the hospital's nuclear medicine department when needed to assay the seeds. According to North Carolina section .1645 of the rules, this amount did not require immediate phone notification but does require notification within 30 days by phone and a written report within 30 days of the phone notification. On October 19, 2011, NCRP received a call from the State of Wisconsin to notify them that a licensee at the University of Wisconsin had received a well counter from NC that contained a brachytherapy seed. It has not been the policy of the Cancer Center licensee to survey a well counter prior to shipment, since it should not contain any radioactive material, but in the future, well counters will be surveyed. The well counter belonging to the licensee was sent to Wisconsin for calibration and will be shipped back to the Marion L Shepard Cancer Center. No personnel exposures occurred during this event. North Carolina Incident: 11-56 Wisconsin Item Number: WI 110066 (This item received via North Carolina) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-10-25
47357 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-10-19 20:02 | 2011-10-19 23:35 | 2011-10-19 | UNANALYZED CONDITION DUE TO PRESSURE INSTRUMENTS CONTAINING ALUMINUM MATERIAL "With Unit 1 in Mode 4 and Unit 2 in Mode 1 an issue was identified with the body material of existing installed pressure instruments for both the Personnel and Emergency Airlocks of both units. The pressure instruments were determined to have an aluminum body which is not suited for safety related use in containment. "Aluminum is a restricted/limited material in containment because it is not compatible with accident conditions and has failures with multiple adverse effects. Due to this condition, the pressure instruments would potentially lose pressure integrity during a LOCA with containment spray actuation. "These pressure instruments are located inside containment and are connected to tubing that penetrates the airlock barrel. In event of a failure of any pressure instrument the integrity of the airlock would be compromised. The containment air locks form part of the containment pressure boundary and, as such, a loss of pressure boundary integrity would no longer meet general design criteria. "Compensatory measures have been taken to prevent a failure of the airlock integrity due to containment spray actuation and at this time the airlock is operable. "Luminant power determined this to be reportable at 2002 [CDT] on 10/19/11 per 50.72(b)(3)(ii)(B) Comanche Peak Units 1 and 2 being in an unanalyzed condition that significantly degrades plant safety." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Hot Shutdown | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-10-19
47356 | 0 | FAIRBANKS GOLD MINING INC. |  |  |  |  | 2011-10-19 08:00 | 2011-10-19 19:17 | 2011-10-19 | SHUTTER STUCK OPEN ON DENSITY GAUGE Fairbanks Gold Mining Inc. discovered a density gauge for the number 2 South Cyclo-Pac Area of its Fort Knox Gold Mine had its shutter stuck open. There is no personnel radiation hazard with the situation of the gauge. The gauge is a Ronan Model SA1-C5 with a 1000 millicurie Cs-137 source. The source serial number is 0606GK. All on-contact readings were less than 5 millirem per hour. Fairbanks Gold Mining has contacted Ronan who will send a representative to the site to repair the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-10-19
47355 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-10-19 12:44 | 2011-10-19 16:42 | 2011-10-19 | OPENED ALCOHOLIC BEVERAGE CONTAINER IN PROTECTED AREA "At 1244 CST a prohibited substance (can of beer) was discovered open in the protected area. The non-supervisory, non-licensed individual involved did not consume any alcohol and was tested under the FFD program. The prohibited substance (alcohol) has been confiscated and FFD test results were negative for consumption. The can of beer was inadvertently brought in the person's lunch box and opened before the individual realized the error. "This report is being made in accordance Significant Fitness-Far-Duty Events 10 CFR 26.719 (b) Significant FFD policy violations or programmatic failures. The following significant FFD policy violations and programmatic failures must be reported to the NRC Operations Center by telephone within 24 hours after the licensee or other entity discovers the violation: '(1) The use, sale, distribution, possession, or presence of illegal drugs, or the consumption or presence of alcohol within a protected area.' "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2011-10-19
47354 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-10-19 10:00 | 2011-10-19 16:22 | 2011-10-21 | TECHNICAL SUPPORT CENTER EMERGENCY DIESEL NON-FUNCTIONAL "At 1000 (CDT), on October 19, 2011, the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) Emergency Diesel Generator (EDG) was declared non-functional due to its failure to maintain required voltage during routine testing. The plant is currently in the process of determining the cause of the failure. Normal power to the TSC is currently available." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM KEVIN HUBER TO VINCE KLCO ON 10/21/2011 AT 1502 EDT * * * "The TSC Emergency Diesel Generator failure has been identified and corrected. The unit has been successfully tested, restoring the TSC Emergency Diesel Generator and TSC to a functional status." The licensee has notified the NRC Resident Inspector. Notified the R3DO (Hills). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-19
47353 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2011-10-19 05:28 | 2011-10-19 07:32 | 2011-10-19 | MANUAL REACTOR TRIP ON LOSS OF CONDENSER VACUUM "On October 19, 2011, at 0528, Unit 1 was manually tripped due to rising condenser backpressure. All (Control Element Assembly) CEAs fully inserted into the core. Decay Heat Removal is from Main Feedwater and Steam Bypass to the Main Condenser. The cause of the rising backpressure was an unplanned trip the Circulating Water Pump 1A1, which degraded the Circulating Water System performance. At the time of the trip, an additional Circulating Water Pump 1A2 was secured for planned maintenance. "The cause of the Circulating Water Pump 1A1 trip is under investigation. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip." The plant is stable at normal operating temperature and pressure. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-10-19
47352 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-10-18 15:45 | 2011-10-18 18:21 | 2011-10-18 | ALUMINUM VALVE DISCOVERED INSTALLED IN CONTAINMENT "While Unit 1 was in Mode 5, for the 15th refueling outage, an issue was identified with the valve material of an existing installed airlock hydraulic system valve. The valve was determined to have an aluminum body which is not suitable for safety related use in containment. "The Unit 1 airlock hydraulic system penetrates the containment pressure boundary. The airlock hydraulic system achieves containment integrity by being a closed system under GDC-57. A loss of pressure boundary integrity would no longer meet General Design Criteria 57 (GDC-57) for a closed system. "Aluminum is a restricted/limited material in containment because it is not compatible with accident conditions and has failures with multiple adverse effects. Due to this condition, the valve would potentially lose pressure integrity during a LOCA with containment spray actuation. "Compensatory measures have been taken to prevent containment spray from affecting this valve and at this time, the airlock is operable. "Luminant Power determined this issue to be reportable at 1545 [CDT] on 10/18 per 50.72(b)(3)(ii)(B) Comanche peak Unit 1 being in an unanalyzed condition that significantly degrades plant safety. "The Unit 2 airlock is a different design and this condition does not apply to Unit 2." This material was installed during original construction and discovered during a licensee self-assessment. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-10-18
47351 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-10-18 09:39 | 2011-10-18 17:36 | 2011-10-18 | RANDOM FITNESS FOR DUTY TEST FAILURE A non-licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2011-10-18
47350 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-10-18 04:50 | 2011-10-18 05:59 | 2011-10-18 | TECHNICAL SUPPORT CENTER EMERGENCY DIESEL GENERATOR OUT OF SERVICE "At 0450 (CDT), on October 18, 2011, the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) Emergency Diesel Generator (EDG) was removed from service for preplanned maintenance. The expected duration of the maintenance is 12 hours. Normal power to the TSC will be available for the duration of the maintenance. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) "The NRC Resident Inspector has been notified." * * * UPDATE AT 1739 EDT ON 10/18/11 FROM STEVE BREWER TO S. SANDIN * * * The Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) Emergency Diesel Generator (EDG) was returned to service at 1637 CDT on 10/18/11. The licensee informed the NRC Resident Inspector. Notified R3DO (Daley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-18
47349 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2011-10-18 00:56 | 2011-10-18 03:20 | 2011-10-18 | OFFSITE NOTIFICATION DUE TO WASTE WATER SPILL "This is a four (4) hour Non-Emergency notification to the NRC Operations Center for a notification to other government agency in accordance with 10CFR50.72(b)(2)(xi). "On 10/18/2011 at 0056 EDT, the Miami-Dade County Department of Environmental Resource Management (DERM) was notified of a spill of approximately 50 gallons of waste water (ash-water sluice) from Turkey Point Units 1 and 2 fossil power plants. This spill is not related to Turkey Point Units 3 and 4 nuclear power plant operations." The licensee notified the NRC Resident Inspector. | 55 | 100 | 0 | 55 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-18
47348 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-10-17 20:50 | 2011-10-17 21:33 | 2011-10-18 | UNIT 1 DECLARED AN UNUSUAL EVENT BASED ON AMMONIA LEVELS EXCEEDING OSHA LIMITS "Normal Operation of WBN [Watts Bar Nuclear] Unit 1 impeded in the Turbine Building, El. 685, West side of the Unit 1 Main condenser due to Toxic Gas (ammonia) concentrations of 75-79 ppm exceeding the OSHA Permissible Exposure Limit (PEL) of 50 ppm, and the ACGIH [American Conference of Governmental Industrial Hygienists] limit of 25 ppm. WBN Unit 1 returned to approximately 100% RTP on Monday, October 17, 2011, following a maintenance outage. Suspect excessive ammonia concentrations due to condenser vacuum pump continuous drains which may need throttling open to increase drain flow, following Unit startup. (Ammonia is used to treat feedwater for secondary chemistry control). There have been no injuries from this event. NRC Senior Resident [Inspector] has been notified. (Event Class 4.4.A, Toxic Gas, Unusual Event)." The licensee informed both the State and local agencies. Notified FEMA (Blankenship) and DHS (Konopka). * * * UPDATE FROM BILL SPRINKLE TO DONALD NORWOOD AT 0052 EDT ON 10/18/2011 * * * At 0047 EDT on 10/18/2011, the licensee terminated the Notification of Unusual Event condition based on ammonia concentrations having been reduced to approximately 6 ppm. Normal personnel access to the affected area has been restored. Unit 1 remained at 100% power during this event with no changes or challenges to plant operations. During the event there were no additional EAL designators. During the event there were no significant changes in plant conditions. During the event there were no significant changes in plant radiological conditions. During the event there were no offsite protective recommendations made by the licensee. The licensee notified the NRC Resident Inspector and State and local agencies. Notified R2DO (Lesser), NRR EO (Brown), IRD (Morris), DHS (Gates), and FEMA (Blankenship). * * * UPDATE AT 1354 EDT ON 10/18/11 FROM BILLY JOHNSON TO S. SANDIN * * * "This information is being provided to the NRC for a 10CFR50.72(b)(2)(xi) notification. "TVA is planning on making a news release to local media affiliates and posting the news release on TVA's website. This news release is in reference to the Notification of Unusual Event (NOUE) Watts Bar Nuclear Plant recently entered and exited for ammonia levels exceeding OSHA limits (reference EN 47348 and update). "The licensee notified the NRC Senior Resident Inspector." Notified R2DO (Lesser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-10-17
47347 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2011-10-11 | 2011-10-17 17:19 | 2011-10-17 | PART 21 NOTIFICATION - EMERGENCY DIESEL GENERATOR PISTON DELAMINATION "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 08/12/11 upon receipt of four piston assemblies returned from Perry Nuclear Plant. It was reported that Perry had performed a maintenance activity whereby they replaced four of their piston assemblies with four refurbished pistons provided by ESI. Following installation of the replacement pistons, it was found that large portions of the tin plating were flaking or smearing off. "The evaluation was concluded on 10/11/11 and determined the piston tin plating delamination to be a reportable defect as defined by 10CFR21 . The delamination was attributed to residual oil impregnated in the ductile cast iron base material of the skirts. The piston assemblies had previously been in service on the emergency diesel generators and were later refurbished by ESI in 2007. A portion of the refurbishment activity consisted of re-tin plating the piston skirts. "ESI is not aware of any absolute methods for ensuring all oils have been removed (or at least to the point that it will not interfere with tin plating adhesion). As a result of this finding, it is ESI's recommendation that piston skirts which have been in service should no longer be re-tin plated." ESI Internal Report Number: 10CFR21-0103, Rev. 0 Potentially affected power plants: Perry, River Bend, Comanche Peak, and Catawba | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-10-17
47346 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-10-14 07:15 | 2011-10-14 17:43 | 2011-10-14 | CALIFORNIA AGREEMENT STATE REPORT - TROXLER GAUGE LOST AND SUBSEQUENTLY RECOVERED The following is a summary of information received from the California Department of Health - Radiologic Health Branch via e-mail: "On October 14, 2011 Construction Testing and Engineering, Inc., contacted [the California Department of Health Radiologic Health Branch] about a portable moisture/density gauge (Troxler Model 3411B, S/N 8349, 8 mCi Cs-137, 40 mCi Am:Be-241) that was lost while being transported to a jobsite at California State University, Channel Islands. The gauge operator had picked up the gauge at their facility around 6:45-7:15 A.M. and left for the jobsite, which is approximately 8-12 miles east of their facility. When nearing the jobsite, while travelling on Laguna Rd., around 7:15 and 7:30 A.M., the gauge operator noticed that the lid on the gauge transport box was open, the operator stopped the vehicle and noticed that the gauge was gone. He immediately contacted his office and Ventura County Sherriff's to report the incident. After filing a report with the police, the gauge operator then proceeded to search for the gauge. "[The licensee] stated that the fire department and police were also searching for the gauge. [The licensee] stated that their employees had also looked for the gauge inside and outside of their facility and asked their neighbors if they had seen the gauge and to look out for the gauge. The gauge had been used by the same operator at the same jobsite for the last few weeks, and had used it the day before. [The licensee] also stated that the gauge should have been chained to the truck bed and should have had two locks in place. "[Shortly after 10:00 A.M, Oxnard Fire Department reported that] the gauge had been found and one of their trucks was enroute to verify that the gauge was intact. [The] gauge had been found intact with the handle securely locked and minor scratches and that the police/fire department verified that there was no unusual radiation readings. The gauge was found in the vicinity of 601 E. Bard Rd., Oxnard, approximately 2 miles from Pacific Coast Highway. The individual who found the gauge, who works for another construction company, brought the gauge to 601 E. Bard Rd. and notified the police. The Oxnard Police and Fire Department and the gauge operator arrived at the scene and verified the gauge was intact. "[The California Department of Health - Radiologic Health Branch informed the licensee] that a leak test was needed to be done prior to using the gauge again and that a written report needed to be provided within 30 days. While the investigation is still ongoing, pending licensee's findings in their 30 day report, the licensee is likely to be cited for improperly securing the gauge, and loss of control of the gauge. Also a site visit will be conducted to verify the licensee is properly securing their gauges during transport." California Report Number: 101411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-10-19
47345 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-10-14 14:40 | 2011-10-14 15:30 | 2011-10-14 | BEARING COOLING WATER DISCHARGE INTO LAKE "On 10/14/2011 at 0322 [EDT], Operations identified during operator rounds that the bearing cooling tower basin was overflowing. Earlier in the night the control room had received a bearing cooling basin high level alarm, verified that the bearing cooling tower basin was not overflowing and was monitoring the level from control room indications. The Control Room indications of bearing cooling basin level had remained steady. The overflow condition was due to leak by from a motor operated valve (MOV) which had been used earlier to add water to the bearing cooling basin. The leaking MOV was manually torqued shut which isolated the overflow discharge. Investigation of the inaccurate level indication is ongoing. "Samples of the bearing cooling water were analyzed by Chemistry. All chemical parameters analyzed were within VPDES (Virginia Pollutant Discharge Elimination System) limits. Bearing Cooling chemistry is maintained to ensure compliance with the North Anna VPDES permit. It is estimated that 272 gallons may have been discharged to the lake. "At 1440 hours on October 14, 2011, a 24-hour notification of the unusual discharge was made to the Virginia Department of Environmental Quality In accordance with the North Anna VPDES permit. "This issue is being reported per 10CFR50.72(b)(2)(xi) as an event where notification of other government agencies has been made." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-14
47344 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-10-14 | 2011-10-14 12:10 | 2011-10-14 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following report was received by the Texas Dept of State Health Services Investigations Unit Radiation Branch via e-mail: "On October 14, 2011, the Agency [Texas Dept of State Health Services] was notified by the licensee that on October 14, 2011, a radiography team was unable to retract a 32 curie Iridium - 192 source to the exposure device. The QSA model 880 D exposure device was set on a pipe to perform radiography on an adjacent pipe. The exposure device fell off the pipe approximately 18 inches and the return portion of the crankout tube was crimped preventing the radiographer from fully retracting the source. The radiographer contacted his Radiation Safety Officer and notified them of the event. The radiographer is qualified to perform source recoveries, so he dismantled the crankout device, pulled the drive cable out of the crankout device, and manually retracted the source to its fully retracted and locked position. No member of the general public received any exposure during this event. The radiographer received a total of 20 millirem for the day. Visual inspection of the exposure device did not find any damage to the camera. The licensee has removed the exposure device and crankout device from service and will send them back to the manufacturer for inspection and repair. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-10-19
47343 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-10-11 09:50 | 2011-10-13 20:21 | 2011-10-16 | EMERGENCY RESPONSE DATA SYSTEM INOPERABLE "At 0915 on 10-11-2011, Columbia Generating Station's (CGS) Emergency Response Data System (ERDS) system was taken out of service for planned maintenance activities. Assessment of the ERDS outage considered the anticipated duration of the outage along with the knowledge that the system would not be recoverable within an hour of a declared event (Alert or higher) during this maintenance period. Station personnel concluded the planned maintenance to be reportable under 10 CFR 50.72(b)(3)(xiii) as 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).' To that end, a call was made to the NRC's Headquarters Operational Office (HOO) at 09:22 PDT on 10-11-2011. Feedback received during that call was that the event was a loggable entry but not recordable and no EN number was assigned. "Efforts to fully restore ERDS following the maintenance have not yet been successful and the actual duration of the work has substantially exceeded initial estimates for planned duration. Work is ongoing to restore the system to full capability. Restoration plans include a functional test coordinated with the NRC ERDS center to demonstrate the system performs as required. "This follow-up call is made to update the original call placed 10-11-2011 and to affirm that the current lack of a functional ERDS system represents a major loss of emergency preparedness capability consistent with 10 CFR 50.72(b)(3)(xiii). Previously credited compensatory measures remain in effect and rely on existing CGS Emergency Response procedures to provide plant data via the Emergency Notification System to the NRC Operations Center until the ERDS can be returned to service. Members of the CGS Emergency Response Organization have been trained on contingencies required during an Emergency Plan activation with loss of ERDS capability. No other emergency response functions are impacted by this ongoing work. The resident inspector has been briefed. A follow up notification will be made when the maintenance work has been completed." * * * UPDATE FROM BRUCE HUGO TO DONALD NORWOOD AT 0601 EDT ON 10/16/2011 * * * The licensee returned ERDS to service at 0245 PDT on 10/16/2011. The licensee notified the NRC Resident Inspector. Notified R4DO (Whitten). | 100 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-13
47342 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2011-10-13 11:50 | 2011-10-13 17:46 | 2011-10-13 | EMERGENCY RESPONSE DATA SYSTEM INOPERABLE "The Unit 3 Emergency Response Data System (ERDS) communications link failed its engineering performance test. Troubleshooting [of the problem] is to commence on 10/14/11 during normal business hours." The license has compensatory measures in place should ERDS be needed by Unit 3 prior to completion of repairs. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-13
47341 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-13 10:00 | 2011-10-13 16:28 | 2011-10-13 | FIRE RELATED UNANALYZED CONDITION THAT COULD IMPACT EQUIPMENT CREDITED IN SAFE SHUTDOWN ANALYSIS "In preparation for converting from 10 CFR 50, Appendix R, to NFPA (National Fire Protection Association) 805, a review of the Brunswick Steam Electric Plant (BSEP) Safe Shutdown Analysis identified conditions that may not ensure a protected train of equipment remains available under certain postulated fire scenarios. The analysis determined that a postulated fire in specific fire areas could cause spurious actuation of critical components, potentially resulting in loss of equipment required for Safe Shutdown. A fire in one of the specified fire areas could potentially adversely affect the following; Suppression Pool level instrument 2-CAC-LT-2602, Residual Heat Removal net positive suction head (i.e., Drywell Containment Overpressure), Reactor Core Isolation Cooling (RCIC), Emergency bus E-1, and Emergency bus E-3. "The initial safety significance of this event is minimal. Fire watches have been established for the affected portions of fire areas RB2-01, RB1-01, TB1, CB-02, and CB-23E. Additionally, fire detection and suppression equipment in the affected areas is fully functional. "Fire watches have been established for the affected portions of fire areas RB2-01, RB1-01, TB1, CB-02, and CB-23E. This condition has been entered Into the Corrective Action Program (i.e., CR 493784). "This is reportable as an unanalyzed condition that significantly degrades plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). Compensatory measures have been established to provide an hourly fire watch for the affected fire areas." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-10-13
47340 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-10-12 14:30 | 2011-10-13 14:45 | 2011-10-13 | AGREEMENT STATE REPORT - MALFUNCTION OF IRRADIATOR SOURCE DRIVE MECHANISM The following information was received from the Texas Dept of Health Services Investigation Unit Radiation Branch via email: "On October 12, 2011, at 1552 hours CDT, the Agency was notified by the licensee's Radiation Safety Officer (RSO) that there had been a malfunction identified with [a self contained] irradiator, at the licensee's facility in Houston, Texas. The source was, and had been, in the fully shielded position and therefore did not present a risk of exposure to any individual. The owner/operator within the facility reported to the RSO's staff that the compressor failed on Friday, October 7, 2011, and they were going to get it repaired or replaced. While working to replace/repair the compressor, it was determined that the problem was not the compressor. The licensee was able to open and close the door to the irradiation chamber and apparently make up all the interlocks, but the source failed to move. Finally, it was determined on Wednesday, October 12th at approximately 1430 hrs that the source drive mechanism was failing to move the source. The owner/operator has been in contact with Shepherd to make arrangements for repair. More information will be provided as it is obtained. The irradiator has been posted as out of service. The source is properly shielded as shown by dose rate surveys conducted in the room." Texas Incident Number: I-8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-10-18
47339 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-10-10 07:00 | 2011-10-12 08:30 | 2011-10-12 | AGREEMENT STATE REPORT - MISALIGNMENT IN THE CRANKOUT DEVICE The following was received via fax: "On October 11, 2011, the Agency [state] was notified by the licensee that on October 10, 2011 while performing radiography operations in one of their shooting bays, they were unable to retract an 89 Curie Iridium - 192 source into a SPEC model 150 camera. The licensee used their video surveillance cameras to verify that nothing had fallen on the guide tube to prevent movement of the source. No obstructions were observed. A technician approved for source retrieval inspected the camera and associate equipment and determined that the crankout being used was not working correctly. The crankout was disassembled and the drive cable was pulled by hand until the source returned to the fully shielded and locked position. The licensee inspected the crankout device and found that there was a slight misalignment between the drive cable and the gear. The device was adjusted, tested and operates smoothly. The crankout device will be sent to the manufacturer for further evaluation. No additional exposure was received by any individual during this event." Texas Incident No. I-8890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-10-17
47338 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-10-11 23:28 | 2011-10-12 02:33 | 2011-10-12 | AUTOMATIC REACTOR TRIP DUE TO TURBINE AUTO STOP VALVE CLOSURE "Automatic Reactor Trip due to Turbine Auto Stop Valve Closure and Actuation of Auxiliary Feedwater System. "At 2328 on 10/11/2011, the reactor tripped due to a RPS actuation Signal from a turbine trip, which was caused by a Turbine Auto Stop signal. All control rods inserted on the trip, RCS pressure is currently 2235 psig and stable, and RCS average temperature is 547 degrees and stable. Decay heat removal is being controlled by auxiliary feedwater which auto started as expected and steam generator atmospheric relief valves. The licensee is investigating the cause of the Auto Stop Signal. The plant will be maintained in MODE 3 until the cause of trip is determined. "The licensee has notified the NRC Resident Inspector." There is no primary to secondary leakage. Offsite power is normal and all EDG's are available. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-10-12
47337 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-12 05:03 | 2011-10-11 12:50 | 2011-10-11 | 60 DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID SPECIFIED SYSTEM ACTUATION "On August 12, 2011, while removing the Unit 2, Division II 24/48 volt DC Cabinet 2B from service for planned maintenance, Unit 2 secondary containment and partial Group II primary containment isolation signals were initiated upon disconnecting the battery with the following systems and components successfully started and actuated as designed: - Unit 1 and 2 Standby Gas Treatment (SGT) systems automatically started - Complete actuation of Unit 2 secondary containment isolation devices in system 2T41 - Partial Group 2 primary containment isolation devices in systems in Division II associated with the 2D11, 2P33, and 2T48 systems. "The procedure for rotating the affected battery chargers did not contain adequate direction to ensure the charger was functioning properly before disconnecting the associated battery in preparation for its replacement. This actuation was confirmed to be an invalid actuation as an unplanned response associated with this maintenance activity. Therefore, the event is not reportable under 10CFR50.72(b)(3)(iv), since it was not a valid actuation. In accordance with 10CFR50.73(a)(1) the option of reporting this event as a telephone notification within 60 days is being used. The event is reportable under 10CFR50.73(a)(2)(iv)(A) because the actuations were not planned and were not expected to occur. In this case the systems to which the requirements of 10CFR50.73(a)(2)(iv)(A) apply are general containment (primary and secondary) isolation signals as described in 10CFR50.73(a)(2)(iv)(B)(2) for the 'B' logic resulting in isolation of the associated valves on Unit 2, thereby affecting containment isolation valves in more than one system. Control room personnel restored the Unit 2, Division II 24/48 volt DC Cabinet 2B and the condition was cleared." The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-10-11
47336 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2011-10-10 11:00 | 2011-10-10 13:52 | 2011-10-10 | FITNESS FOR DUTY - NON-LICENSED EMPLOYEE HAS A POSITIVE CONFIRMED TEST FOR AN ILLEGAL DRUG A non-licensed employee supervisor had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2011-10-10
47335 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-10-08 10:00 | 2011-10-09 14:49 | 2011-10-09 | AGREEMENT STATE REPORT - POTENTIAL OVER EXPOSURE OF RADIATION WORKERS The following is a compilation of information received from a verbal report from the State of New Jersey; an e-mail from the State of California; and discussions with the RSO involved in the incident: On October 8, 2011 at approximately 1000 EDT, three contractor personnel were loading Co-60 sources on a GammaCell 220 irradiator at a Johnson & Johnson facility located in Raritan, New Jersey. During the activity, an 8 inch 1210 Curie Co-60 source was somehow dislodged from its shielded position and approximately 4 inches of the source were exposed in an unshielded configuration. In addition, the insertion tool prevented the workers from re-inserting the source quickly. The workers were able to take a titanium shield and force the source into place by breaking off the insertion tool. The source was then confirmed to be in a shielded configuration and safely secured. The total time the source was exposed was estimated to be 25 to 30 seconds. The two individuals loading the source are employed by Foss Therapy, a California Agreement State licensed service provider. The third individual involved in the activity was the RSO employed by Gamma Irradiator Service (GIS) under a Pennsylvania Agreement State license. Based on readings from the electronic dosimetry being used by the workers, the two Foss Therapy employees are estimated to have received whole body doses of 8.1 R and 7.7 R respectively. The RSO working for GIS is estimated to have received a dose of 8.5 R. Extremity exposure has been estimated at between 50 R to 60 R for the two Foss Therapy workers. The workers were also wearing fresh TLDs and finger badging. More detailed dose information will be forthcoming after analysis of this dosimetry. See event report from the State of New Jersey: EN # 47334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-10-12
47334 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-10-08 10:00 | 2011-10-09 10:27 | 2011-10-09 | AGREEMENT STATE REPORT - POTENTIAL OVER EXPOSURE OF RADIATION WORKERS The following is a compilation of information received from a verbal report from the State of New Jersey; an e-mail from the State of California; and discussions with the RSO involved in the incident: On October 8, 2011 at approximately 1000 EDT, three contractor personnel were loading Co-60 sources on a GammaCell 220 irradiator at a Johnson & Johnson facility located in Raritan, New Jersey. During the activity, an 8 inch 1210 Curie Co-60 source was somehow dislodged from its shielded position and approximately 4 inches of the source were exposed in an unshielded configuration. In addition, the insertion tool prevented the workers from re-inserting the source quickly. The workers were able to take a titanium shield and force the source into place by breaking off the insertion tool. The source was then confirmed to be in a shielded configuration and safely secured. The total time the source was exposed was estimated to be 25 to 30 seconds. The two individuals loading the source are employed by Foss Therapy, a California Agreement State licensed service provider. The third individual involved in the activity was the RSO employed by Gamma Irradiator Service (GIS) under a Pennsylvania Agreement State license. Based on readings from the electronic dosimetry being used by the workers, the two Foss Therapy employees are estimated to have received whole body doses of 8.1 R and 7.7 R respectively. The RSO working for GIS is estimated to have received a dose of 8.5 R. Extremity exposure has been estimated at between 50 R to 60 R for the two Foss Therapy workers. The workers were also wearing fresh TLDs and finger badging. More detailed dose information will be forthcoming after analysis of this dosimetry. See event report from the State of California: EN # 47335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-10-12
47333 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2011-10-08 16:19 | 2011-10-08 20:09 | 2011-10-08 | NOTIFICATION OF UNUSUAL EVENT DUE TO SEVERE ELECTRICAL FAULT IN RCP JUNCTION BOX "Reactor Coolant Pump 2A tripped at approximately 1535 MST, resulting in numerous simultaneous electrical distribution alarms. A walkdown of containment was performed and at 1609 MST it was determined that a junction box, supplying power to the 2A Reactor Coolant Pump, had failed, resulting in the pump tripping on overcurrent protection and an 86 lockout. The plant was operating in forced circulation and had one train of shutdown cooling in service. As a result, an Emergency Classification of HU2.2, Explosion was declared due to the junction box failure and noise that had been heard in containment. "The plant is currently stable with one train of shutdown cooling in service, the opposite train of shutdown cooling is available to be placed in service. The Unit 1 Reactor Coolant System is currently at 160 degrees Fahrenheit and 375 psia with the 1A Reactor coolant pump in service for forced circulation. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." The licensee has notified appropriate state and local agencies. * * * UPDATE FROM DAN DAILEY TO DONALD NORWOOD AT 2306 EDT ON 10/8/2011 * * * The Notification of Unusual Event at Palo Verde Unit 1 was terminated at 1916 MST on 10/8/2011. The termination was based on conducting inspections which did not reveal any additional damage or plant impact as a result of this event. Unit 1 remains stable in Mode 5 with RCPs 1A and 1B in service along with one train of RHR in service. The licensee notified the NRC Resident Inspector and appropriate state and local agencies. Notified R1DO (Gray), NRR EO (Hiland), IRD (Grant), DHS (Flinter), and FEMA (Castro). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-10-08
47332 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-10-07 13:20 | 2011-10-07 21:14 | 2011-10-08 | LOSS OF COMMUNICATIONS SYSTEMS DUE TO CUT FIBER OPTIC CABLE "At 1320 on October 7, 2011, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, a vehicle accident on NYS Rte 104 resulted in a loss of Communications equipment at the site. The JAF dedicated Emergency Notification System (ENS) and Health Physics Network (HPN) phone lines are not functioning as a result of this accident. The Radiological Emergency Communications System (RECS) phone connection to the Nine Mile Point 1 and Nine Mile Point Unit 2 units is also lost as a result of this failure, but communications with the county and state has been verified to function. Nine Mile Point units have also reported a loss of ENS capability. "This communication failure impacts the ability to readily receive and transmit information to the NRC for the JAF Nuclear Power Plant. The loss of both the ENS and the HPN constitutes a major loss of communications capability and meats NRC 8 hour reporting criterion 10CFR50.72(b)(3)(xiii). "Alternate commercial telephone lines remain available and have been verified to function to support communications between NRC headquarters and JAF. "The Communications provider has been contacted to enact repairs to the affected communications circuit. "The NRC Resident Inspector has been briefed." See related event notification EN #47331. * * * UPDATE FROM STEVE DEFILLIPPO TO PETE SNYDER AT 0356 EDT ON 10/8/11 * * * All communications systems previously identified as out of service have been restored. Notified R1DO(Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-07
47331 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-10-07 13:20 | 2011-10-07 20:55 | 2011-10-07 | LOSS OF COMMUNICATIONS SYSTEMS DUE TO CUT FIBER OPTIC CABLE "On 10/07/11, at approximately 1320 EDT, Nine Mile Point Unit 1 received multiple annunciators related to the offsite power tone monitoring system. These annunciators were subsequently determined to have been caused by damage to an offsite fiber optic cable line. The damaged fiber optic cable also disabled the Emergency Notification System (ENS) and Radiological Emergency Communication System (RECS) communication lines, which is reportable under 10 CFR 50.72(3)(b)(xiii). "ENS is the Control Room's primary method for communicating with the NRC headquarters during emergency conditions. If an emergency is declared with the ENS line inoperable, the Control Room maintains the ability to make notification to offsite agencies using commercial telephone lines. "Control Room personnel have been briefed on the required contingent actions with the ENS line inoperable." The licensee notified the NRC Resident Inspector and State and local agencies. See related event notification EN #47332. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-07
47330 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2011-10-07 16:15 | 2011-10-07 17:23 | 2011-10-07 | DIMENSION OF SNM CARRYING PAILS DIFFERENT FROM VALUE IN SAFETY ANALYSIS "It was reported to [the licensee's Environmental Health and Safety organization] on Oct 7, 2011 that the measurements on the 1.5 gallon pails used in the facility were found to be non-compliant with the governing Criticality Safety Evaluation, CSE-16-K Rev. 3, 'Common Containers.' This CSE authorized the deployment of 1.5-gal steel pails for miscellaneous use with SNM-bearing liquids. The safety basis for the design of these pails is addressed in credible scenario 4.1.4 in CSE-16-K. The primary contingency is passive engineered control FLOOR-115 which specifies the following dimensional requirements for the pails: Top ID : 8.059 to 8.559" Bottom ID: less than or equal to 6.309" Inner Height: less than or equal to 8.217" Wall Thickness No Limit "The controls, PROCUR-901 and -902, cover the ordering and inspection upon receipt for the pails, to meet the criteria of FLOOR-114. In June 2011 all of the pails were inspected by the Product Assurance (PA) department and judged to meet the dimensional requirements. The pails were then deployed to the floor and have been in use since then. "On October 7, 2011, NCS Engineering was informed that the PA department had determined that their measurement methodology for the pails was incorrect. As a result, the actual top ID of the pail exceeded the IROFS limit by a margin of [approximately] 0.25 [inch]. This results in the facility being in a state that is different from that analyzed in the Integrated Safety Analysis (i.e. the governing CSE). All other dimensions specified by the control FLOOR-115 are met, but the diameter aberration appears to affect all pails. As a result, the passive engineered IROFS FLOOR-115 is judged to have failed, eliminating the primary contingency. "Calculation results modeling an infinite array of in tolerance pails containing oil-moderated UO2 with 6 [inch] S/S spacing for this condition results in a 95/95 Keff of 0.8569. Preliminary calculation results with the increased diameter case results in a 95/95 Keff of 0.8610. Therefore, with the proper spacing maintained (12 [inch] per control FLOOR-116), with no stacking (control FLOOR-104), an infinite array of the as-built pails would not exceed the SNM-1107 license 0.95 criterion. "This event is being reported pursuant to the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery due to the facility being in a state that is different from that analyzed in the Integrated Safety Analysis (i.e. the governing CSE). The performance requirements for this accident sequence require the Overall Likelihood Index (OLI) be Highly Unlikely. With this failure the sequence is Unlikely. "Immediate Corrective Actions: -- Upon identification of the issue operations staff removed the pails from the main process areas and segregated to prevent use. -- The event is being entered into the Corrective Action Process and a casual analysis initiated. "The Columbia Fuel Fabrication Facility is subject to Subpart H of 10 CFR 70 and this issue is addressed in the corresponding Integrated Safety Analysis." The licensee will notify NRC Region 2 and state authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2011-10-07
47329 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-10-06 11:25 | 2011-10-06 17:34 | 2011-10-06 | MEDICAL TREATMENT OF EMPLOYEES WITH CONTAMINATION ON CLOTHING "Two maintenance employees were exposed to anhydrous hydrogen fluoride while working on a chemical storage tank. The two employees were taken to the plant dispensary for first aid treatment. Both employees were treated and released to return to work. Radiological surveys of the employees in the dispensary showed contamination on both of the employees work shoes and one of the employee coveralls. "[The contamination was from] U3O8 Uranium Ore Concentrate, Natural Uranium. "[This event is reportable under] 40.60(b)(3) - Unplanned Medical Treatment at a Medical Facility of an individual with spreadable contamination." The licensee has notified appropriate local authorities and NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-10-06
47328 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-06 11:40 | 2011-10-06 16:47 | 2011-10-06 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "On 10/06/2011 the control room was notified of an oscillation occurring on the output of Unit 2 High Pressure Coolant Injection (HPCI) pump electronic governor. These oscillations are occurring while the system is in standby and is an early indication of potential governor failure. The governor oscillations were discovered on 10/06/2011 at 1140 EDT by the system engineer while performing system trending analysis via plant computer points. "HPCI was declared inoperable and LCO 3.5.1 was entered at 1140 EDT on 10/06/2011. "An investigation is in progress. Unit 1 HPCI and both Unit 1 and Unit 2 RCIC (Reactor Core Isolation Cooling) systems are unaffected as the electronic governor outputs for this equipment is stable and trending as expected. "This is being reported as a loss of an entire safety function condition in accordance with 10CFR50.72(b)(3)(V)(D)." The licensee notified the NRC Resident Inspector. | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-10-06
47327 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2011-10-06 12:26 | 2011-10-06 15:17 | 2011-10-06 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR WATER LEVEL "At 1226 [EDT] today, Seabrook experienced an automatic reactor trip on low steam generator water levels. The low steam generator levels resulted following a trip of one of the two operating main feed pumps. Main feed pump 'A' tripped on low suction pressure while a condensate pump was being returned to service following maintenance on the pump. The emergency feedwater system actuated automatically and recovered steam generator levels. All systems actuated and functioned as designed. The wide range level indication on steam generator 'C' indicated erratically and was declared inoperable. The plant is stable and being maintained in Mode 3. The station plans to cool the plant to Mode 5 for a previously planned forced outage. "This notification provides a four-hour report for an actuation of the reactor protection system while the reactor is critical and an eight-hour report for a valid actuation of the emergency feedwater system." All rods fully inserted. Emergency feedwater has been secured and placed in standby and startup feedwater is supplying the steam generators. Decay heat is being removed to the condenser via the turbine bypass valves. Electrical systems are in a normal shutdown alignment. There is nothing unusual or not understood and all systems functioned as required. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-10-06
47326 | 0 | ATC NUCLEAR |  |  |  |  | 2011-10-06 | 2011-10-06 13:35 | 2012-07-07 | PART 21 NOTIFICATION CONCERNING MOORE PROCESS CONTROLLERS The following information was received from ATC Nuclear via facsimile: "This notification is in accordance with U.S. Nuclear Regulatory Regulation 10 CFR 21.21(a)(3)(ii)(b). "Exelon Corporation Clinton and LaSalle Stations have identified common mode failures associated with Moore 535 Controllers (Part Number 535-000000HOST-SSTRV) provided through ATC Nuclear Tennessee. These items were provided as safety related components to Exelon under Clinton Purchase Order 00461980 and LaSalle Purchase Order 00462363. All safety related failures to date appear to originate from these specific purchase orders. The failures have been evaluated with the original equipment manufacturer and appear to be isolated to controllers containing a main processor board containing 'Revision F' labeling manufactured in early 2010 (Date Code 1310). These items all passed an extended burn-in during testing. The failures may manifest themselves as process variable (PV) drift, controller reset with loss of controller function, or create nuisance alarm conditions after a relatively short period (less than 1 year) following installation. "Because the end-use application of each item is not known by ATC Nuclear, the safety hazard evaluation has been deferred to the customer. The Licensees above have been formally notified of the defect." * * * UPDATE FROM RAY CHALIFOUX TO DONG PARK AT 1638 EDT ON 7/2/12 VIA FACSIMILE * * * "A failure analysis has been concluded to determine the causes for Moore Industries International (MII) 535 Single Loop Process (SLP) Controller failures, initially reported October 6, 2011 and provided by ATC Nuclear, Oak Ridge, TN. The original failure symptoms were reported to be process variable (PV) drift, controller reset with loss of controller function, or create nuisance alarm conditions after a relatively short period (<1 year) following installation. These controllers passed all Method 1 Testing including an extended burn-in to monitor for early life failure. Initial investigation isolated the failure to the controller MPU [Micro-Processing Unit] Board and identified the cause as 'Indeterminate.' "Completion of a rigorous analysis by the OEM [Original Equipment Manufacturer] and ATC Nuclear has identified the failures are the result of the introduction of a 3 vDC SRAM Chip P/N CY62256VNLL-70SNXI on the MPU by Moore Industries International in 2010 which is not compatible with the 5vDC circuit. Operation of the 3V part at 5V reduces reliability of the part and could lead to failures in the field. The part change bypassed Moore's Engineering Change Process and therefore was not evaluated as their program requires. An Extent of Condition review performed by the OEM verified no additional part changes at Moore went unevaluated." The orders were delivered to the following facilities: Clinton, LaSalle, Byron, Callaway, Fermi 2. Notified R3DO (Daley), R4DO (Allen), and Part 21 Group via e-mail.. * * * UPDATE FROM RAY CHALIFOUX TO HOWIE CROUCH VIA FAX 1141 EDT ON 7/7/12 * * * "During the ATC root cause investigation, a technical error in the original qualification document S2000-RP-03, Revision 0, issued on February 7, 2000 was identified. The qualification test report identified the Moore 535 SLP controller's ability to withstand a total integrated dose (TID) of 1E5 Rad. This information is in error and is related to the original report creator's misunderstanding of the relationship between the presence of semiconductor materials and a citation from an EPRI report on the effects of radiation. The Moore 535 controllers have been tested for a TID of 1E3 Rad without failure. A report revision will be issued to clarify this item. No orders reviewed were provided for IEEE 323 harsh environment applications. "Because the end-use application of each specific item is not known by ATC Nuclear, the safety hazard evaluation has been deferred to customers. The licensees above have been formally notified of the defect." Notified R3DO (Daley), R4DO (Allen) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2011-10-06
47325 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-10-05 14:00 | 2011-10-06 13:16 | 2011-10-06 | ITEM RELIED ON FOR SAFETY NOT AS DESCRIBED IN THE INTEGRATED SAFETY ANALYSIS "During a review of the Integrated Safety Analysis (ISA) for a 3-gallon can elevator used in the Dry Scrap Recycle (DSR) area, it was determined that the ISA incorrectly describes the IROFS used to control movement of SNM. The system is composed of two sequential can elevators that are used to move SNM to different floors. A Fuel Business System (FBS) automated control and associated gate controls are designated as one of the Items Relied On For Safety (IROFS). In the ISA, this IROFS is incorrectly attributed to the 2nd can elevator instead of the 1st can elevator. Based on a review of this condition, determined at approximately 1400 on October 5, 2011, it was determined that the system was different than analyzed in the ISA and resulted in a failure to meet performance requirements. "The FBS and associated gate control were in place at all times on the 1st can elevator, was operating correctly, and supported by management measures. No unsafe condition existed. The ISA and associated documentation are being updated to designate the correct can elevator and associated controls. "Operation of the equipment has been suspended pending additional review and implementation of corrective actions. Additional corrective actions and extent of condition are being evaluated. "This event is being reported pursuant to the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery." The licensee will notify NRC Region 2 and State and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2011-10-06
47324 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2011-10-04 | 2011-10-06 12:05 | 2011-10-06 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON PROCESS GAUGE The following report was received from the Kansas Department of Health and Environment via facsimile: " The licensee attempted to close the shutter [on a process gauge] in preparation for a job. The shutter would not close. There were no personnel exposures [associated with this event]. Because of the location [of the gauge], there are no likely exposures due to this failure. The source is located approximately 12 feet above the ground on a tank. Access is by portable ladder. Operations and maintenance personnel were notified. "The shutter in question is on an Ohmart/VEGA model SHF1 B-45 source holder (S/N 7294CN) containing 100 milli-Curies of Cs-137 in a sealed source. "The manufacturer, [Ohmart] VEGA, has been contacted and is working to schedule their service technician to [make repairs]. "Sealed Source and Device Registry OH-0522-D-01 02-B states 'Commonly reported device failures associated with this device series includes stuck shutters, shutter handles breaking off, and broken screws. A review of these failures indicate common root cause issues are associated with: operating the devices outside the normal conditions of use; failure to seek appropriate device service when shutters start becoming difficult to operate; shutter binding due to environmental contaminant intrusion into the shutter; and, forcing operation of shutter instead of seeking corrective action. The most commonly involved series is the SH-F2 which is the model typically installed in harsh environmental conditions'." Kansas Report Number: KS110011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2011-10-11
47323 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-10-05 15:53 | 2011-10-05 19:17 | 2011-10-05 | OFFSITE NOTIFICATION DUE TO POTENTIAL CHEMICAL SPILL IN THE DELAWARE RIVER "At 0930 on 10/5/11, a fuse failure in a 1E to non - 1E interface failed causing a false run signal to the water treatment system for a standby station service water pump. The water treatment system responded by opening the injection valve for the out of service pump. With the associated pump out of service, the sodium hypochlorite can communicate with the Delaware river. This was discovered at 1553 and immediately terminated. This resulted in the discharge of approximately 195 gallons of 15% sodium hypochlorite to SSW intake which communicates with the Delaware river. The associated service water pump was started thus withdrawing residual product from the intake. A portion of the discharged sodium hypochlorite may have entered the Delaware river. A sample was obtained from the Delaware river just outside the intake structure and there was no detectable chlorine in the sample and there were no abnormal conditions noted on the river. Based on Environmental Licensing review, this was reportable to the state of NJ within 15 minutes. The report to the state was initiated at 1608 on 10/5/11. "Subsequent calls were made to the Hope Creek Senior NRC Resident, the National Response Center and the US Coast Guard. Affected systems are limited to the Station Service Water (SSW) system and the sodium hypochlorite water treatment system. There was no impact on plant operations and these systems remain fully operable. Evaluation is underway to fully understand the impacts of the fuse failure to prevent reoccurrence. There was nothing unusual or not understood. All safety related equipment continues to function as required. There were no injuries or reported wildlife impact." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-05
47322 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-09-26 06:02 | 2011-10-05 18:00 | 2011-10-05 | UNANALYZED CONDITION - APPENDIX R EQUIPMENT MAY NOT HAVE BEEN AVAILABLE "An Appendix R non-compliance issue was identified. When the plant automatically tripped on September 25, 2011, an unexpected automatic trip was identified in DC shunt trip breakers 72-01 and 72-02. This automatic trip function was not considered in the Appendix R electrical coordination evaluation. Preliminary analysis has shown that if the shunt trip breaker would have automatically opened due to fire induced fault currents, then Appendix R credited equipment may have been lost unexpectedly. The operability evaluation performed, resulted in increasing the shunt trip settings to maximum, and implementing compensatory measures to isolate some non-safety related electrical loads, which restored compliance with 10 CFR 50 Appendix R. "The licensee notified the NRC Senior Resident Inspector." CR# PLP2011-04835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-10-05
47321 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-10-05 07:27 | 2011-10-05 15:50 | 2011-10-07 | TWO LOOPS OF REACTOR COOLANT SYSTEM (RCS) WERE DECLARED INOPERABLE "Unit 2 was shut down at 1048 CDT on October 4, 2011 due to 22 Reactor Coolant Pump (RCP) low seal leak off flow. At 0727 CDT on October 5, 2011 with Unit 2 in Mode 4 and 22 RCP secured, 21 RCP was also secured due to low seal leak off flow. "It was determined that the station would not consider RHR [residual heat removal] available for decay heat removal per Technical Specification (TS) due to a procedural issue related to component cooling shutdown lineups. RCS temperature is being maintained stable in Mode 4 between 320 and 340 degrees Fahrenheit using natural circulation and the steam dump to the condenser. No operations were permitted that would have caused introduction into the RCS, coolant with boron concentration less than required to meet the Shutdown Margin. "At approximately 1329 CDT, 21 RCP was restarted after the flow transmitters were vented and 21 RCP seal leak off flow was determined to be acceptable. The RHR procedural issue has been resolved. "Per TS LCO 3.4.6, 'Two loops consisting of any combination of RCS loops and residual heat removal (RHR) loops shall be OPERABLE, and one loop shall be in operation.' This condition is reportable as an event or condition that could have prevented fulfillment of a safety function under 10CFR 50.72(b)(3)(v)(B)." During this event, RHR could not be credited because the utility was not able to valve in component cooling water to a SFP heat exchanger due to procedural issues. With the restart of 21 RCP and shutdown cooling water alignment, TS 3.6.4 A and B statements have been met and exited. 21 RCP loop in operation and 22 RHR is operable and can be aligned for shutdown cooling. Both Unit 2 EDG's are available and offsite power is normal electrical lineup. The licensee is no longer in any TS LCO statements. The NRC Resident Inspector has been notified. * * * RETRACTION ON 10/7/11 AT 1146 EDT FROM DAMMANN TO SNYDER * * * "An eight hour report (EN #47321) per 10CFR 50.72(b)(3)(v)(B) was conservatively reported because both trains of Residual Heat Removal (RHR) system and both trains of Reactor Coolant System (RCS) were thought to be unavailable. "Additional review indicated that 21 RCP and 22 RCP were undamaged, functional, and available for loop operation; therefore, there was no loss of safety function as RCPs were available. "The station evaluated 21 and 22 RCP seal leak off flow performance and subsequently restarted 21 RCP and restored forced cooling. The 21 RCP seal leak off flow has remained stable in the acceptable range. 21 RCP was available throughout this evolution. If needed in Mode 4, 22 RCP was also available. "The procedures that were in place and available to the operators prior to 1320 CDT on October 5, 2011, would have allowed RHR operation; however, to supply RHR to Unit 2, Unit 1 would have entered an LCO (for supplying Component Cooling (CC) water to the Spent Fuel Pool (SFP) heat exchangers) to maintain RHR's safety function. After 1320 CDT, procedure revisions allowed operation of RHR without an associated Unit 1 LCO entry. RHR remained operable throughout this evolution. "In summary, a loss of safety function for both trains of RHR and RCS did not exist and the 50.72(b)(3)(v)(B) report (EN # 47321) is retracted. "The NRC Resident Inspector has been informed." R3DO(Phillips) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-10-05
47320 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2011-10-05 08:21 | 2011-10-05 15:24 | 2011-10-05 | PAGING SYSTEM IS OUT OF SERVICE "At 0812 EDT on October 5, 2011, Millstone Power Station determined that a condition exists affecting Emergency Preparedness Capabilities due to a major loss of offsite communications capability. Specifically, Millstone Power Station was notified by an offsite vendor that the system relied upon for offsite communications in accordance with the Millstone Emergency Plan using a pager system is not functioning reliably. The Millstone Emergency Plan will be implemented by the approved, pre-existing alternate notification method. "Appropriate officials are being notified that the alternate method is being employed until the primary means is restored. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii)." The paging system is being repaired and the utility has an alternate communication method in place. The NRC Senior Resident Inspector has been notified as well as Waterford local government and the Connecticut Department of Environmental Protection. IRF Number: 2011066 | 0 | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-05
47319 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-10-04 16:35 | 2011-10-04 19:33 | 2011-10-04 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "At 1430 CDT, 10/4/11, the licensee Main Control room received an emergency phone call for medical assistance. The caller reported that he had a person down in the auxiliary building. On-site medical response team reported the person was not breathing and not responsive. The symptoms were non-occupational. The person was transported off site via ambulance to the local hospital. At 1635, 10/4/11, the licensee was informed that the individual was declared deceased. OSHA is being notified pursuant to the requirements of 29CFR1904.39. This ENS report is being made in accordance with 50.72 (b)(2)(xi) "There was no radioactive contamination involved in this event. The licensee does not plan any media or press release and have not notified any other government agencies besides OSHA. The NRC Resident Inspector will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-10-04
47318 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-09-27 09:00 | 2011-10-03 18:48 | 2011-10-03 | AGREEMENT STATE REPORT - LICENSEE FAILED TO TURN IN THEIR NUCLEAR GAUGE AFTER LICENSE WAS TERMINATED The following was received from the state via e-mail: "On September 27, 2011, RHB [Radiologic Health Branch] was informed by Pacific Nuclear Technology (PNT) that they collected a moisture density gauge that was left on the adjacent office porch of the BSK & Associate office. The gauge was discovered by BSK & Associate's employee, and according to PNT service records, the gauge belonged to J. Yang and Associates. The gauge was delivered to CDPH-RHB on 09/27/11 by PNT. RHB will investigate to determine how the gauge was lost. Mr. Yang terminated his CA License in 2008, but apparently did not relinquish all of his licensed materials." CA 5010 Number: 092711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-10-06
47317 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-10-04 04:00 | 2011-10-03 15:00 | 2011-10-04 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0400 EDT on Tuesday, October 4, 2011, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room, if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1500 EDT on Tuesday, October 4, 2011. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM BUD HINCKLEY TO JOE O'HARA ON 10/04/11 AT 1443 * * * "The TSC ventilation system maintenance began at 0504 EDT on 10/04/11 and the system was restored to service at 1430 EDT on 10/04/11." The NRC Resident Inspector has been notified. Notified R3DO(Phillips) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-03
47316 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-10-03 10:35 | 2011-10-03 14:45 | 2011-10-03 | TECHNICAL SPECIFICATION (TS) REQUIRED SHUTDOWN DUE TO BOTH 'A' TRAIN EDG'S INOPERABLE "Dual Unit Shutdown due to T.S. 3.0.3. Unit 1 and Unit 2 'A' Train Emergency Diesel Generators (EDGs) OOS [Out-of-Service]. '2A' DG OOS due to '21' Salt Water Header scheduled maintenance. '1A' DG OOS due to emergent loss of '16' Battery charger for the '1A' DG DC bus. Neither '11' nor '22' 125 VDC busses have an Operable charger. (Chargers have power, but do not have an Operable DG). " The licensee entered TS 3.0.3 at 1035 EDT and is expected to be in Mode 3 on both units at 1735 EDT unless the licensee exits T.S. 3.0.3 upon restoration of the battery charger. '0C' EDG is functional but not credited towards T.S. The salt water header is not expected to be restored until 10/4/11. There are no issues with offsite power. The NRC Resident Inspector has been notified. The licensee will notify the Calvert Control Center and plans to make a press release. CR No.: CR-2011-009860; Calvert Cliffs internal event notification number 4194. | 60 | 67 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2011-10-03
47315 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-10-03 08:50 | 2011-10-03 10:24 | 2011-10-03 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0850 [CDT] on Monday, October 03, the Callaway Plant Technical Support Center (TSC) is undergoing planned maintenance to repair MTSUB7001, Manual Transfer Switch between normal and emergency power. This maintenance is currently scheduled to last for 1 day, at which time the TSC will be restored to service. During this period, the TSC will be without either normal or emergency power, thus rendering it non-functional. "If an emergency is declared requiring TSC activation while the TSC is non-functional, TSC emergency response personnel will report to their backup locations in accordance with Callaway Plant emergency planning procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the planned unavailability of an emergency response facility. * * * UPDATE AT 1907 EDT ON 10/03/11 FROM GERRY RAUCH TO JOE O'HARA * * * "Callaway Plant Technical Support Center (TSC) normal power was restored at 1751 CDT. The TSC is functional and available as an emergency response facility." The NRC Resident Inspector has been notified. Notified R4DO (Whitten). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-03
47314 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-10-03 03:45 | 2011-10-03 05:25 | 2011-10-03 | UNIT 2 ENTERED TECH SPEC 3.0.3 AFTER DECLARING ALL THREE CONTAINMENT RECIRC FAN COOLERS INOPERABLE Indian Point Unit 2 entered TS 3.0.3 (TS Required Shutdown) at 0345 EDT on 10/3/11 after declaring all three Containment Recirc Fan Coolers inoperable due to insufficient Service Water (SW) flow through SW Headers 1, 2, and 3 during the quarterly surveillance test. At 0438 EDT, Unit 2 commenced a controlled shutdown. The licensee has shifted SW flow to Headers 4, 5 and 6 and is in the process of re-performing the test. If the test is successful, they will exit TS 3.0.3. Unit 2 is currently stable at 99% reactor power. The licensee informed state agencies and the NRC Resident Inspector. * * * UPDATE FROM JOHN TAYLOR TO CHARLES TEAL ON 10/3/11 AT 0625 EDT * * * "Three trains of Fan Cooler Units (FCU) are inoperable due to insufficient flows during the flow test 2-PT-Q016. Entered ITS 3.0.3 at time 0345 EDT. At time 0438 EDT Unit 2 commenced a plant shutdown. At time 0515 EDT the plant was at 99% and stable under operator control. Service water headers were swapped from the 1,2,3 header to the 4,5,6 header. The plant is in the process of re-performing the FCU flow tests with the 4,5,6 as the essential Service Water header." The licensee informed the NRC Resident Inspector. Notified R1DO (Doerflein). * * * UPDATE FROM STEVEN RADOMSKI TO CHARLES TEAL ON 10/3/11 AT 0752 EDT * * * "After swapping Essential Service Water headers from the 1,2,3 header to the 4,5,6 header, 2-PT-Q016 Containment Cooler Unit Cooling Water Flow Test was performed satisfactorily. At 0532 EDT LCO 3.0.3 was exited, and LCO 3.6.6 was met. All five Fan Cooler Units were declared operable." The licensee informed the NRC Resident Inspector. Notified R1DO (Doerflein). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-10-03
47313 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2011-10-02 02:48 | 2011-10-02 03:27 | 2011-10-02 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO ISFSI AREA MONITORING Safeguards system degradation related to the monitoring and detection of the ISFSI. Compensatory actions taken upon discovery. Call the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-10-02
47312 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-10-02 01:00 | 2011-10-02 01:06 | 2011-10-02 | SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO TRANSFORMER FAULT "This event is being reported in accordance with 10CFR50.72(b)(2)(i). On October 2, 2011, at approximately 0100 hours [EDT], the Perry Nuclear Power Plant commenced a controlled plant shutdown. The shutdown was due to the anticipated investigation and expected repair time of the Unit 1 startup transformer exceeding the Technical Specification (TS) Required Action completion time. "On September 29, 2011, at 0529 hours [EDT] the Unit 1 startup transformer failed due to an internal fault, which required entry into TS 3.8.1 Action A.2 for one required offsite circuit inoperable. The determination has been made that the required action, which is to restore the required offsite circuit to OPERABLE status, cannot be met by the required completion time and a plant shutdown is being initiated. "The NRC Resident Inspector has been notified." The licensee expects to have the Unit offline between 1300-1400 hours [EDT] and plans to issue a press release. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-10-02
47311 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-10-01 16:00 | 2011-10-01 23:10 | 2011-10-01 | LOSS OF ERDS CONNECTIVITY DUE TO A COMPUTER ISSUE "On 10/1/2011, for a period of approximately 4 hours between 1600 EDT to 2000 EDT, the capability of transferring Emergency Response Data System (ERDS) information to the NRC Operations Center was lost for Brunswick Units 1 and 2. The cause was attributed to a software issue affecting communication between plant process computing and the network server. This constituted a loss of emergency preparedness capabilities and is reportable under 10CFR50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-01
47310 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-09-30 08:54 | 2011-10-01 00:46 | 2011-10-01 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING A LOSS OF ONE LEG OF DOUBLE CONTINGENCY "Description: At 0854 CDT on 09-30-11, the Plant Shift Superintendent (PSS) was notified that water was observed in the #5 withdrawal position scale pit during the completion of the monthly test of the C-310 scale pit water detection system alarm module. The alarm module was being tested per procedure, when the module was found with the visual alarm (a red light) on at the local panel in the #5 withdrawal position room. In response to the alarm, the scale pit hatch was opened and the water detection sensor cable was observed to be at least partially submerged. Immediate investigation found the sump pump breaker to be tripped; when the breaker was reset the pump actuated and water was immediately removed. At the time of the occurrence, product withdrawal was in progress in the #3 and #4 withdrawal position room, and no cylinder was present in the #5 withdrawal position room. The source of the water was found to be a leaking steam condensate valve above the #5 withdrawal room ceiling. The water had drained to the concrete pad outside the building and then along the scale cart rails, eventually finding its way into the #5 scale cart pit where it gradually accumulated. Because the C-310 Scale Pit Water Detection Alarm did not function as credited, it is in violation of NCSE 032 (NCSA 310-004). Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "The NRC Senior Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-11-2610; PGDP Event "Report No. PAD-2011-17 "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low, even though the event made it possible for the level of pre-existing water to exceed the safe geometry limit. Although it is normal case for overall PGDP operations to have assay up to 5.5 wt.% 235U, the actual assay of product withdrawal operations during the period in question remained no higher than 2.0 wt. % 235U. At that actual assay, the depth of water necessary to support a criticality would have been more than 7.21 inches, which might have been credible but in itself would have remained a very unlikely possibility due to the slow ingress rate and high probability of detection and mitigation by personnel performing routine activities in that area. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): In order for a criticality to happen, a significant breach in the process system integrity would have to occur. After the breach, fissile UF6 and its reaction products would have to react with pre-existing water to form fissile solution. There would have to be a sufficient depth of water in the pit to support a criticality (e.g. more than 3.68 inches of water at 5.5 wt. % 235U). "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The two process conditions relied upon for double contingency are mass and geometry. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Product withdrawal assay at the time of the event was no higher than 2.0 wt% U235. However, no UF6 release occurred. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Geometry is controlled in the second leg of double contingency by limiting the level of pre-existing water that might be present in the scale pit. Water accumulation is considered normal case in the NCSE by acute or by chronic sources. The NCSE credits the Scale Pit Water Detection Alarm to provide detection of chronic water accumulation in the scale pit. The alarm is set to actuate before the water level exceeds 2.5 inches in the pit. The geometry parameter limit is 3.68 inches assuming the worst-case possible enrichment of 5.5 wt.% 235U. The alarm is credited to provide early indication, and result in prompt mitigation, of water ingress to the pit before the NCS parameter limit is exceeded. Since the alarm was not functional, and the ingress rate was sufficiently slow that ingress was not easily detectable, there was no reliable means in place to detect and mitigate the ingress of water into the pit. The sensor and local panel light performed their intended function; however, it is the ACR audible and visible alarms that are controlled as AQ-NCS equipment and not the local panel light and buzzer. With the alarm out of service, continued ingress of water to the pit could have resulted in exceeding the geometry parameter limit for water depth before detection and mitigation. NCS entered the scale pit for inspection shortly after notification of the discovery and after the water had been drained. NCS observed that the water level at the lowest point in the pit may have reached 2.5 inches. Based on those inspections, it is likely that the water level remained below the 3.68-inch level, but there was no definitive way to prove the maximum height that might have occurred throughout the period of time when the alarm was not functional. Therefore, for conservatism it is assumed credible that the geometry parameter limit was violated during the lime the alarm was not functional. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The sump pump was immediately activated by resetting its breaker, which restored the water level in the pit below the 2.5 inch administrative limit, thus removing the hazard of this incident. The #5 withdrawal position scale pit will be checked twice per shift beginning on 9-30-11 in accordance with procedure due to the ACR alarm being out-of-service." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2011-10-01
47309 | 0 | UNITED STATES AIR FORCE |  |  |  |  | 2011-09-30 14:20 | 2011-09-30 15:46 | 2011-09-30 | LOST AMERICIUM-241 SOURCE During a visual inspection of a source storage area at the Wright-Patterson AFB, 88th Medical Group, the licensee was unable to locate a 12 mCi Am-241 source. A rad survey was conducted but the source was not located. A search of the nuclear medicine area was performed with negative results. The source was last leak tested in July, 2002, then placed in storage. The last visual inspection where the source was identified was performed in September, 2009. The source was slated for disposal. The licensee is searching through their records to determine if the source, in fact, was sent to a disposal facility. The licensee notified Jackie Cook, R4DNMS. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-09-30
47308 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-09-29 11:20 | 2011-09-30 11:00 | 2011-09-30 | EQUIPMENT CONFIGURATION DIFFERENT THAN ANALYZED IN THE ISA "During a review of Integrated Safety Analysis (ISA) and criticality evaluation assumptions for a floor cleaning scrubber used in the Dry Conversion Process facility, it was determined that an equipment configuration was different than that analyzed in the ISA. Field verification of the floor cleaning scrubber recovery tank determined that its capacity was greater than the safe volume limit referenced in the analysis. The tank volume is credited as an IROFS [Items Relied On For Safety] in the ISA summary. Based on a review of this as-found condition, discovered at approximately 1120 EDT on September 29, 2011, it was determined that the system was different than analyzed in the ISA and resulted in a failure to meet performance requirements. "The tanks for the floor cleaning scrubbers were inspected and no unsafe condition existed. Operation of the equipment has been suspended pending additional review and implementation of corrective actions. Additional corrective actions and extent of condition are being evaluated. "This event is being reported pursuant to the reporting requirements of 10CFR70 Appendix A (b)(1) within 24 hours of discovery." The licensee will notify the NRC Region 2, North Carolina Radiation Protection Agency and New Hanover County Emergency Management. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | DEV FROM ISA | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(5) |  |  |  | 0 | 2011-09-30
47307 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-09-30 08:10 | 2011-09-30 10:50 | 2011-09-30 | HYDRAULIC LEAK CONTAINED ON SITE- STATE OFFICIALS NOTIFIED "On 9/30/11 at 0730 [CDT], the main hydraulic hose ruptured on a coal truck making a routine delivery to the CÀ600 coal pile. The PSS [Plant Shift Superintendent] was notified and it was determined that approximately 30 to 35 gallons of hydraulic fluid was released on the coal pile delivery area which is greater than the reportable quantity for petroleum products. At 0810 [CDT], the PSS made notification to the Kentucky Environmental Response Team (KERT) and a courtesy notification to the Kentucky Department for Environmental Protection (KDEP.) "This event is reportable under Criteria P in Appendix D of USEC procedure UE2-RA-RE1030 as any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. "The NRC Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRCÀ11À2607; PGDP Event Report No. PADÀ2011À16; NRC Worksheet No.; Responsible Division: Operations" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2011-09-30
47306 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-09-29 17:00 | 2011-09-30 00:18 | 2011-09-30 | INADEQUATE SURVEILLANCE TESTING OF EMERGENCY DIESEL GENERATORS "Monticello has discovered that it has not met Technical Specification Surveillance Requirement (SR) 3.8.1.7 relating to the largest single post-accident load reject for the Emergency Diesel Generators (EDG). Although the current test designated post-accident load is successfully load rejected during the surveillance, the test load rejection must be higher to bound all post-accident load scenarios. The capability of an EDG subsystem to recover from a reject of the largest single post-accident load testing has not met the requirements of SR 3.8.1.7. Therefore, both EDGs have been declared inoperable. Both EDGs are considered Functional and Available for use at this time. "There were no automatic EDG initiation signals associated with this event." The licensee notified the NRC Resident Inspector and will notify the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2011-09-30
47305 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-09-29 17:10 | 2011-09-29 17:40 | 2011-09-29 | GEORGIA DEPARTMENT OF NATURAL RESOURCES NOTIFIED DUE TO TRITIUM LEVELS ABOVE BACKGROUND DETECTED AT SAMPLE POINTS ONSITE "On Sept. 28, 2011, results from routine monitoring of groundwater at Plant Hatch indicated tritium was detected above historical background levels at two sample points on site. Additional samples were taken from the same points and analysis confirmed that tritium was present at elevated levels in both samples and that tritium had not migrated out of the general area of initial discovery. Tritium concentrations up to 5.34 million picocuries per liter were observed. Immediate actions were taken to locate the source of the leak and actions are in progress to stop the leak. The tritium is confined to a small area on the plant site in the vicinity of the Unit 1 condensate storage tank, and there is no significant potential for off-site impact. Additionally, there is no impact to on-site personnel. No tritium levels above background have been detected or migrated outside the area where the two sample points are located. "Southern Nuclear will continue to sample strategic locations in the ground water monitoring network to determine if there are changes in the impacted area and beyond. SNC is confident that these levels are of low safety significance and do not pose any issues to the public health and safety. "In accordance with Southern Nuclear's groundwater protection procedures and the Nuclear Energy Institute (NEI)/Industry Groundwater Protection Initiative, Southern Nuclear contacted the Nuclear Regulatory Commission (NRC) Region II Resident Inspector and the Georgia Department of Natural Resources to inform them of this matter." | 100 | 91 | 0 | 100 | 91 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-09-29
47304 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-09-28 09:30 | 2011-09-29 14:17 | 2011-09-29 | PENNSYLVANIA AGREEMENT STATE REPORT - INDUSTRIAL GAUGE SHUTTER FAILURE The following information was obtained from the Commonwealth of Pennsylvania via fax: "Event type: Shutter Failure "Notifications: On September 28, 2011, the Department's [Pennsylvania Department of Environmental Protection] Southwest Regional Office received notification via phone from the licensee at approximately 1530 hrs. of a reportable event listed under 10CFR 30(b)(2). (Note, this is similar but a different event from PA 110022 [EN#47226]). "Event Description: The shutter failure was identified while performing a routine preventative maintenance and standardization. The shutter became stuck in the closed position and could not be opened. No radiation exposure to personnel ensued during this event. The device is identified as: Manufacturer (IRMS), Model (TG-2), Serial# (00M0397-I5), Isotope (Americium- 241), and Activity (3 Ci). "Cause of the Event: Spring Default Piston "Actions: Service provider repairs were completed the same day by replacing the source holder which was then surveyed, wipe tested, and put back into operation." PA Report No.: PA110026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-10-04
47303 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-09-29 11:35 | 2011-09-29 12:19 | 2011-09-29 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO CHEMICAL SPILL "EAL HU7 was declared at 1135 hrs. [EDT] for a toxic of flammable gas which has been released onsite which could affect plant operations. Current plant conditions do not threaten public safety. "Less than 1 gallon of 15% sodium hypochlorite sprayed onto the floor during securing of a completed delivery to the water treatment plant, located within the Protected Area boundary. There have been no injuries to personnel." The licensee has notified the local and state authorities and will be notifying the NRC Resident Inspector. * * * UPDATE FROM VINCE BONELLI TO HOWIE CROUCH AT 1457 EDT ON 9/29/11 * * * "Limerick is terminating from the Unusual Event (HU7) due to the threat of toxic gas having been terminated. The sodium hypochlorite leak in the water treatment plant has been stopped and clean up activities are in progress. U1 and U2 remain at 100% power. There were no injuries." The licensee has notified state and local authorities and will be notifying the NRC Resident Inspector. Notified R1DO (Doerflein), IRD (Gott), NRR (Thomas), FEMA (O'Connell) and DHS (Flinter). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-09-29
47302 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-09-29 06:02 | 2011-09-29 06:56 | 2011-09-29 | UNUSUAL EVENT DECLARED DUE TO FIRE ALARM IN THE CONTAINMENT During plant startup, a single train fire alarm was received in containment at 0540 EDT on 9/29/2011. An Unusual Event was declared at 0602 EDT based on the containment not being accessible within 15 minutes. An inspection in containment revealed no fire or smoke or the cause for receipt of the alarm. The licensee has notified the State, Counties and the NRC Resident Inspector. * * *UPDATE FROM JOE PENNINGTON TO VINCE KLCO ON 9/29/2011 AT 0744* * * The Unusual Event was terminated at 0714 EDT on 9/29/2011. The licensee has notified the State, Counties and the NRC Resident Inspector. Notified the R2DO (Nease), NRR (Thomas), IRD (Gott), FEMA (Casto) and DHS (Rickerson). | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Startup; FMode1: Startup | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-09-29
47301 | 0 | AMETEK |  |  |  |  | 2011-09-28 07:00 | 2011-09-28 17:23 | 2011-09-28 | PART 21 REPORT - DIODE FAILURES DUE TO DETERIORATION The following was received via fax: "Component Description: International Rectifier (IR) and Vishay 150 amp clamp diodes with either forward or reverse bias These are Ametek Solid-state Controls part numbers 07-600150-00 and 07-600151-00. Diodes can be either installed in Ametek Solid-state Controls UPS equipment or provided as a spare part. "The diode failures due to this suspected defect have occurred generally at around the third or fourth year of operating life of the device. There are no warning signs that a failure is imminent, or detection method for predicting an approaching failure. "The investigation has revealed that the diode failures were due to voltage transients or punch through. A failure analysis by Southwest Research concluded that the device having an 'alloy junction' can deteriorate after three to four years of operation resulting in a 'punch through' condition within the device causing the diode to short. "The actual cause has not been determined; however it is suspected that the alloy junction type device may have sensitivity to age or voltages causing the device to more rapidly degrade. "The failures described above, could result in loss of output voltage and transfer of the static switch to the bypass source which could result in a potential damage to the load. "We have only two known failures in systems at this voltage level. We feel the failure rate has been extremely low and the risk is minimal. Each operating facility will need to evaluate the potential risk to their operation." The licensee did not indicate which NRC licensees, if any, are affected by this notice. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2011-09-28
47300 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-09-28 10:41 | 2011-09-28 12:02 | 2011-09-28 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "Due to unsatisfactory performance of TSC HVAC operation per Condition Report 355263, the TSC HVAC is considered non-functional until performance of the corrective work activity is performed. If an emergency condition occurs during the time these work activities are being performed, which requires activation of the TSC, the contingency plan calls for utilization of the TSC, as long as radiological conditions allow for habitability of the facility. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this activity affects the functionality of the TSC emergency response facility for the duration of the evolution." The licensee corrected an issue with the electrical power fuse block and returned the unit to service at 1210. The licensee cleared the associated action statement for this issue at 1350. The NRC Resident Inspector has been notified. | 100 | 91 | 0 | 100 | 91 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-28
47299 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-09-28 04:14 | 2011-09-28 08:26 | 2011-09-28 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP "At 0414 [CDT] on 9/28/2011, the Unit 3 reactor automatically scrammed due to actuation of the Reactor Protection System [RPS] from a turbine trip. Preliminary indications show the turbine tripped on a generator trip with generator neutral overvoltage (359GN) relay actuation. Cause of relay actuation is under investigation. Seven Safely Relief Valves (SRVs) cycled due to the reactor pressure transient with reactor pressure automatically controlled by the Main Turbine Bypass Valves. All systems responded as expected to the turbine trip. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary containment isolation and initiation signals for groups 2, 3, 6 & 8 were received as expected. Reactor water level is being automatically controlled by the feedwater system. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." All control rods fully inserted. The plant is being supplied from offsite power and is in a normal shutdown configuration. The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. There was no impact on Units 1 or 2. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-09-28
47298 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-26 | 2011-09-27 10:06 | 2011-11-17 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED PROCESS GAUGE The following information was received from the Texas Department of State Health Services via e-mail: "On September 26, 2011, the licensee reported that while preparing to enter a vessel, the shutter on a Ronan model SA-1 nuclear gauge containing 2000 millicuries of Cesium (Cs) -137 failed to shut and is stuck in the normally open position. The source serial number is 2943GK. No significant exposure has occurred due to this event. The gauge is located at a height of 150 feet on the tank. The licensee contacted a technical representative and expects to repair or replace the gauge at the end of the week. The cause for the event is under investigation. Additional information will be provided as it is received IAW SA 300." * * * RETRACTION FROM ART TUCKER TO JOHN KNOKE AT 1016 EST ON 11/17/11 * * * The following information was received from the Texas Department of State Health Services via e-mail: "The manufacturer inspected the gauge at the licensee's location and determined that the gauge was functioning properly. They also determined that the radiation measurements taken by the licensee to determine if the shutter was closed where taken at a distance that was closer than the reference reading causing the elevated readings. There was no reportable event." Notified the R4DO (Blair Spitzberg) and FSME (Angela McIntosh) Texas Incident #: I-8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-30
47297 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-09-26 23:40 | 2011-09-27 03:11 | 2011-10-10 | SAFEGUARDS REPORT INVOLVING DETECTION SYSTEM DEGRADATION The licensee reported a safeguards detection system degradation. Compensatory actions taken. Call the Headquarters Operations Officer for details. The NRC Resident Inspector will be notified. * * * RETRACTION FROM KEITH ROBINSON TO JOE O'HARA AT 1549 ON 10/10/11 * * * Upon further review, the licensee retracted the event. Call the Headquarters Operations Officer for details. The NRC Resident Inspector has been notified. Notified the R2DO(Vias) and the 73.71 group via e-mail. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-09-27
47296 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-06-28 | 2011-09-26 15:33 | 2011-09-26 | AGREEMENT STATE REPORT - LEAKING 8 MILLICURIE NICKEL 63 SOURCE The following report was received via facsimile: "The Radiation Safety Officer (RSO) for Virginia Tech notified the Virginia Radioactive Materials Program on September 23, 2011 that a leaking source had been identified on June 28, 2011. The source was an 8 millicurie (April 1989) nickel-63 source used in a Varian gas chromatograph. The source was contained in a detector kit model 02-001972-00, serial number A7074. The gas chromatograph was no longer used. While preparing the unit to be surplussed, the RSO identified contamination of 0.07 microcurie in the area where the ECD (electron capture detector) had been installed. The RSO reported that he did not report the leaking source in June because leak tests of the ECD itself showed no continuing leakage. The RSO indicated that the gas chromatograph would be decontaminated and that procedures would be modified to specify the required five-day reporting requirement for a leaking source to prevent recurrence of late reporting." Event Report No: VA - 11 - 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-09-29
47295 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-09-23 | 2011-09-26 15:00 | 2011-09-26 | AGREEMENT STATE REPORT - DAMAGED PORTABLE MOISTURE DENSITY GAUGE The following report was received via facsimile: "On Friday, September 23, 2011 the Radioactive Materials Program (RMP) received notification from the Virginia Department of Emergency Management (VDEM) regarding a transportation accident on I-64 at mile marker 167 in Goochland County. The accident involved a moisture density gauge. The RMP contacted the on-scene Incident Commander (IC) to receive details. The IC stated that a truck carrying the gauge had lost control and the gauge was breached on the road. The driver of the vehicle was available and a conversation was held during which he stated he had lost control and the transport case handle was broken off allowing it to become free from the back of his truck. He stated the case opened and the gauge was destroyed. The driver contacted the RSO who then drove to the incident. The RSO brought a survey meter and another transportation case. The RSO stated the source rod had been sheared off at the shielding base but that radiation readings were within tolerance. The RSO packaged the shield and other gauge parts into the new transport case and returned the transport case to their office location. An RMP employee was dispatched to the licensee's office to investigate the incident and perform surveys of the transport case. The investigation is ongoing including interviews of the RSO and driver. The manufacturer (lnstroTek) was contacted and instructions were discussed. A leak test wipe was taken and is being sent to lnstro Tek for analysis." Event Report No: VA - 11 - 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-09-29
47294 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-09-26 15:00 | 2011-09-26 15:09 | 2011-09-26 | NEW RIVER HYDRAULIC ANALYSIS RAISES MAXIMUM FLOOD LEVEL "TMI new river analysis indicates level above existing UFSAR [Updated Final Safety Analysis Report] flood analysis. At about 15:00 [EDT] on September 26, 2011, a revised River Stage Discharge Analysis was completed and concluded that the Probable Maximum Flood (PMF) water level is higher than previously described in the safety analysis report. This unanalyzed condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B). "Actions to protect the plant for the higher PMF river level have been implemented. The flood barrier gates that protect safety related equipment have been modified to accommodate the revised river levels. No onsite flood water levels have occurred that could potentially challenge the existing flood barrier system. "The licensee notified the NRC Resident Inspector." The licensee will be making a courtesy media notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-09-26
47293 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-09-26 11:45 | 2011-09-26 14:48 | 2011-09-26 | AUTOMATIC REACTOR TRIP DUE TO ONE LOOP LOW FLOW SIGNAL "At 1145 hours EDT on September 26, 2011, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the One Loop Low Flow reactor protection function. All Reactor Coolant Pumps (RCP) remained running. "The Auxiliary Feedwater System automatically actuated, as expected due to low steam generator water level, and provided feedwater to the steam generators. The steam generator and pressurizer Power Operated Relief Valves (PORVs) and the Main Steam Safety Valves did not open during the event. All control rods indicated fully inserted following the reactor trip. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable. Decay heat is being removed via the condenser. The reactor is currently stable in Mode 3. "The cause of the reactor trip is under investigation." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-09-26
47292 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-09-26 14:00 | 2011-09-26 14:27 | 2011-09-26 | 800 MHZ RADIO SYSTEM TEMPORARILY REMOVED FROM SERVICE DUE TO DEGRADED ANTENNA "The site's 800 MHz radio system was removed from service for approximately one (1) hour to support pre-planned maintenance to repair a degraded antenna. While the 800 MHz radio system is out of service, it will not be possible to activate any of the site's emergency sirens from any of the risk county Emergency Operations Centers nor from the plant. For the period of time that the sirens are non-functional, the three risk counties will be prepared to utilize the back-up method of route alerting to alert residents." The licensee has notified the NRC Resident Inspector. | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-10-02
47291 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-09-25 18:04 | 2011-09-25 19:48 | 2011-09-30 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "At 1804 on Sunday, September 25, the Callaway Plant Technical Support Center (TSC) will undergo planned maintenance to replace the building's heating, ventilation, and air conditioning (HVAC) system. This maintenance is currently scheduled to last for approximately five days, at which time the TSC will be restored to service. During this period, the TSC's HVAC system will not be able to provide positive pressure to the TSC, thus rendering it non-functional. "If an emergency is declared requiring TSC activation while the TSC is non-functional, TSC emergency response personnel will report to their backup locations in accordance with Callaway Plant emergency planning procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the planned unavailability of an emergency response facility. "The NRC Resident Inspector has been notified." * * * UPDATE FROM TIM HOLLAND TO HOWIE CROUCH AT 2027 EDT ON 9/30/1 * * * "At 1804 CDT on September 25, 2011, the Callaway Plant Technical Support Center (TSC) underwent planned maintenance to replace the building's heating, ventilation, and air conditioning (HVAC) system. While this maintenance was being performed, the TSC was unable to maintain positive pressure within the building, thus rendering it non-functional. "This ENS update is to document that, at 1800 on September 30, 2011, the Callaway Plant TSC was returned to service following successful completion of planned maintenance on the building HVAC system. "The NRC Senior Resident Inspector has been notified." Notified R4DO (Werner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-25
47290 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-09-25 15:06 | 2011-09-25 18:21 | 2011-09-25 | REACTOR TRIP DUE TO LOSS OF TWO 120 VOLT AC INSTRUMENT BUSSES "At 1506 EDT, while the electricians were working on the left train DC bus, a bus bar slipped causing an arc and a loss of the left train DC busses D-10 L and D-10 R. This resulted in the loss of two preferred AC [120 Volt Instrument] busses Y-10 and Y-30. The loss of both preferred AC busses caused a reactor trip, a safety injection signal, auxiliary feedwater actuation signal, containment high radiation isolation signal, and main steam isolation signal. "All systems responded as expected. Electric power has been restored to the affected DC busses and preferred AC busses. The plant is stable in Mode 3 at NOT and NOP, and controlling temperature using Atmospheric Dump Valves. Pressurizer level is high due to the loss of letdown (result of containment isolation signal), however, it is recovering slowly." All rods fully inserted and the electrical lineup is back to normal. The licensee has notified the NRC Resident Inspector, and will be notifying local agencies. The licensee will also be issuing a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-09-25
47289 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-09-22 17:30 | 2011-09-23 00:27 | 2011-09-26 | OFFSITE NOTIFICATION TO COUNTY AGENCY DUE TO INADVERTENT WASTEWATER DISCHARGE "This notification is for San Onofre Units 2 and 3, and is being made in accordance with 10CFR50.72(b)(2)(xi) to report a notification to another government agency regarding a spill of approximately 26000 gallons of untreated waste water (sewage). "A pending report will be made to the San Diego County Dept. of Environmental Health regarding a untreated (sewage) waste water spill that occurred as San Onofre. The details that were communicated to the DEH are that at 1730 PDT a sewage spill was identified at SONGS in the North Industrial yard area. The leak was being collected in the yard drains and being discharged to the ocean. The sump discharge system has been secured stopping the release." The licensee will inform the NRC Resident Inspector. * * * UPDATE FROM LEE KELLY TO JOHN KNOKE AT 1325 EDT ON 9/26/11 * * * "On September 22, 2011, an untreated (sewage) waste water spill was discovered in the San Onofre North Industrial Area. Southern California Edison (SCE) notified the NRC at 1730 PDT on September 22, 2011, (Event No. 47289) in accordance with 10CFR50.72(b)(2)(xi). The California Emergency Management Agency was notified (Control #11-5652) at 2223 PDT and San Diego County Department of Environmental Health (DEH) was notified at 2239 PDT. The initial report to the NRC indicated the spill was approximately 26,000 gallons. The estimated size of the spill has subsequently been revised to approximately 7,000 gallons. "At the time of the event, Units 2 and 3 were at 100 percent power. SCE notified the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." Notified the R4DO (Greg Werner). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-09-23
47288 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-09-22 14:52 | 2011-09-22 22:20 | 2011-11-20 | SALT SERVICE WATER PUMP INOPERABILITY DURING POSTULATED DEGRADED VOLTAGE CONDITIONS "On Thursday, September 22, 2011 at 1452 [EDT], with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) conservatively declared both Salt Service Water (SSW) subsystems inoperable when engineering analysis determined that inrush current on pump restart may exceed the thermal overload trip relay settings during certain degraded voltage conditions. A 24-hour Limiting Condition for Operation action statement was entered. "Entergy/Pilgrim is in the process of implementing temporary modifications to correct this issue. This potential concern has no impact on public health and safety. This 8-hour notification is being conservatively reported in accordance with 10 CFR50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." The licensee will notify the Massachusetts Emergency Management Center. * * * RETRACTION FROM DAVID NOYES TO VINCE KLCO ON 11/20/2011 AT 0733 EST* * * "Event Notification 47288 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were satisfied pending further evaluation of Salt Service Water (SSW) subsystem operability during certain degraded voltage conditions. "Pilgrim Station has subsequently evaluated the impact of the Salt Service Water (SSW) pump motor operating load; potential degraded voltage conditions on thermal overload settings; and pump motor restart requirements; and determined that reasonable assurance of SSW subsystem operability existed. Both SSW subsystems were evaluated to be capable of satisfying the system safety function of providing cooling water to the Reactor Building Closed Cooling Water System heat exchangers during accident and transient conditions. Pilgrim 's evaluation considered manufacturer's data for the thermal overload relays, site specific shop testing, and reliable grid conditions which minimize the potential for extended operation with 4 kV buses operating at just above degraded voltage relay trip settings. This past operability evaluation concluded that the SSW pumps would support continuous operation of the SSW subsystems. "Therefore, the initial 50.72 report is being retracted." The licensee will notify the NRC Resident Inspector. Notified the R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-09-22
47287 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-22 05:27 | 2011-09-22 10:29 | 2011-09-22 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO THE LOSS OF THE TSC CHILLER SYSTEM "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The Functionality of the Technical Support Center (TSC) has been lost due to a trip of the TSC Chiller System supply breaker. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BILL DUNN TO CHARLES TEAL ON 9/22/11 AT 2039 EDT * * * The TSC has been returned to service at 2000 EDT. Notified R2DO (Lesser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-22
47286 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2011-09-21 10:20 | 2011-09-21 22:48 | 2011-09-21 | RELAY MALFUNCTION RESULTED IN A VALID UNDERVOLTAGE SIGNAL "On 9/21/11 at 10:20 a.m. during the performance of a simulated loss of offsite power testing off the E33 4KV emergency bus, an unplanned start of the E3 Emergency Diesel Generator (EDG) occurred due to a valid bus under voltage signal caused by a relay malfunction. The bus being tested was inoperable in support of the test and was not carrying any required safety system loads at the time of the event. The EDG was secured and troubleshooting initiated. The initial determination was the EDG actuation was from an invalid signal but following further review it was determined that the relay malfunction had caused an untimely bus transfer that resulted in a valid 4KV bus under voltage condition." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-09-21
47285 | 0 | N/A |  |  |  |  | 2011-09-21 | 2011-09-21 09:15 | 2011-09-21 | ABANDONED DENSITY GAUGE A property owner called the Nuclear Regulatory Commission to report that he had found a CPN MC3 Porta- Probe gauge containing 10 mCi of Cs-137 abandoned at his property at Sand Point, ID. The gauge belongs to Inland Code Inspection & Consultation Services of Ponderay, ID. Another NRC licensee licensed to possess this type of equipment has retrieved the gauge and stored it at their site. * * * UPDATE FROM JAMES THOMPSON TO VINCE KLCO ON 9/21/2100 AT 1451 EDT* * * The serial number for the gauge is M370103535. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-09-21
47284 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2011-09-20 14:30 | 2011-09-20 18:02 | 2011-09-22 | AGREEMENT STATE REPORT - LEAKING SHIPMENT CONTAINING 53.2 CURIES TRITIUM The following was received by e-mail: "On 9/13/2001 Widetronix, Inc. (NY RAM License C5379) shipped a package containing tritium treated beta voltaic foils to Radiation Safety Engineering (RSE). The package was received and wiped for surface contamination by RSE on 9/14/2011. The results of the smears were below action levels. The packaging containing the foils was then transferred to Medtronic Microelectronics Center. "On 9/15/2011 the package was opened in a restricted laboratory area of the Medtronic's chip manufacturing in Tempe, AZ. Wipe samples were taken at each level as the package was opened by Medtronic's RSO. There were several layers of packaging, exterior shipping box, interior shipping box, large sealed metal canister, and a sealed bag containing smaller sealed metal canister containing the tritium treated chips. The licensee left each wipe and package layer on a lab work bench as he continued to open the next layer of packaging. The licensee finished taking wipe samples at approximately 10:30 a.m. and sent the sample to RSE for analysis. The results for the initial wipes were received back by the licensee at approximately 12:30 p.m. on 9/15/2011; the results indicated a leaking source. The licensee's estimated total quantity for the shipment is 53.2 Curies (1.4 Ci x 38 chips). "Bioassays were given to individuals present in the lab during the opening of the shipping containers and the results showed the highest Committed Effective Dose Equivalent was 0.26 mrem. "The investigation into this event is ongoing. "The U.S. NRC, AZ governor's office, and New York have been notified." Arizona First Notice: 11-010 * * * UPDATE FROM AUBREY GODWIN TO CHARLES TEAL AT 1630 EDT ON 9/22/11 * * * The following update was provided via email: "Based upon new information provided by the manufacturer, the total activity of shipment was 1.33 Curies." "An additional individual was assayed later and his results were 0.12 mrem." Notified R4DO (Walker), R1DO (Newport), and FSME EO (O'Sullivan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2011-09-23
47283 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-19 19:43 | 2011-09-20 16:39 | 2013-01-09 | POTENTIAL OVEREXPOSURE DUE TO FAULTY RADIOGRAPHY DEVICE The following was received via e-mail: "On September 19, 2011, at 1943 hours, the Agency [state] received an email stating that a radiography trainee may have received an over exposure to his right hand and was seeking medical attention. The email stated that the overexposure occurred because the radiography device used on the job was faulty, but did not provide any information on when or how the possible overexposure occurred. "On September 20, 2011, the Agency received an email from a licensee Radiation Safety Officer (RSO) stating that an overexposure may have occurred to an employee's hands. The email stated that the licensee had not received any information from the individual who was reported to have received the exposure. The RSO was in route to a hospital in Houston, Texas where the radiographer trainee was reported to have gone for treatment. The employee's film badge has been sent for processing, but no results are available at this time. The licensee is reviewing records to determine where and when the trainee worked during the two months he has been employed. Individuals that worked with the trainee are being interviewed. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-8886 * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 9/21/2011 AT 1820 EDT* * * The following information was received by facsimile: "The licensee has reported that the trainee stated that on September 12, 2011, while conducting radiography operations in the field, he removed the guide tube from an Amersham 660 D radiography camera containing [an Iridium - 192 source] and saw that the source was protruding out of the camera. The licensee stated that they did not know how far the source was protruding or how it was returned to the fully shielded position. The Agency [state] has contacted the trainee and conducted an interviewed with him over the phone. "The licensee stated that the results of the trainee's film badge indicated that he received 1,410 millirem on the film badge he was wearing at the time of the event. The trainee is in a Houston, Texas hospital. His doctors are conferring with [the] Radiation Emergency Assistance Center/Training Site (REAC/TS) regarding his medical treatment. An on-site investigation will be performed by the Agency at the licensee's location on September 22, 2011." Notified the R4DO (Walker) and FSME (O'Sullivan). * * * UPDATE AT 1806 EST ON 1/9/13 FROM ART TUCKER TO HUFFMAN * * * The following update was received from the State of Texas Radiation Branch Investigation Unit via e-mail: "This Agency has closed the investigation into this event, but due to the unique nature of this event this update is being provided. "On January 2, 2013, the Agency was contacted by the mother of the individual injured in this event. She stated that his right hand was worse than before and they were concerned. She stated they had sought medical help from two health care providers in the Houston, Texas, area, but neither could provide assistance. She asked if the Agency had any recommendations. The Agency suggested that she contact a physician who works at REAC/TS and provided the contact information. She stated that she would contact him. She provided the Agency with pictures of the individual's hand which have been sent to the NRC Region IV Headquarters. "On January 2, 2013, the Agency contacted the physician. He stated he had received copies of the radiographer trainee's medical records and a few recent pictures of his hand. The physician expressed concerns over the condition of the radiographer trainee's hand based on the pictures he had seen. He stated he would like to see the individual, but could provide the contact information for a physician he had trained and who practiced medicine in the Houston area. On January 8, 2013, the mother notified the Agency that she had been in contact with the REAC/TS physician and were working to get in contact with the physician in the Houston area recommended by REAC/TS. She stated that her son was in a lot of pain and his hand was getting worse each day. "Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Gaddy) and e-mailed a copy to FSME Events Resource. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-26
47282 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-19 07:00 | 2011-09-20 10:58 | 2011-09-20 | AGREEMENT STATE REPORT - INDUSTRIAL GAUGE SHUTTER FAILED OPEN The following was received from the State of Texas via e-mail: "On September 19, 2011, the licensee reported that while conducting routine inspections and maintenance, the shutter on a Ohmart Corporation model SH-F2 nuclear gauge containing 100 millicuries of Cesium (Cs) - 137 was found to be stuck in the normally opened position. No significant exposure has occurred due to this event. The licensee will contact the manufacture for repairs or replacement of the gauge. The cause for the event is under investigation. Additional information will be provided as it is received IAW SA 300." Texas Incident Number # I-8885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-23
47281 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-09-16 14:14 | 2011-09-20 10:27 | 2011-09-20 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING Y-90 THERASPHERE UNDERDOSE The following information was received from the Commonwealth of Pennsylvania via facsimile: "Event Type: A medical event (ME) involving Y-90 Theraspheres where the patient received 51% of the intended dose, which is reportable under 10CFR35.3045(a)(1)(ii). 'Notifications: On September 16, 2011, at 1414 [EDT], the Department's Southeast Regional Office received notification via phone message about the ME. "Event Description. The patient was being treated with MDS Nordion Y-90 glass Theraspheres for transarterial radioembolization. A suspected defective catheter caused 49% of the intended dose to clog up in the catheter. No harm to the patient is expected. The referring physician and patient have been notified. No more information is available at this time. "Cause of the event: The cause of the event is suspected to be a defective catheter. "Actions: After decay, the catheter will be returned to Nordion for inspection and may also be returned to the manufacturer, Terumo Medical, for a defect analysis. The licensee will be submitting a written report within 15 days. The [Pennsylvania] Department [of Environmental Protection] plans to do a reactive inspection." PA Report ID: PA110025 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-09-26
47280 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-09-19 | 2011-09-20 08:12 | 2011-09-20 | AGREEMENT STATE REPORT - MISSING CO-57 FLOOD SOURCE The following information was received from the State of Florida via email: "During a routine inspection, a Co-57 flood source was determined to be missing. Source was accounted for on 18 Aug 11. [A state] inspector surveyed the area and could not locate the source. Licensee believes the source may be at a doctor's office; they will continue to look for it and will notify us [Florida Bureau of Radiation Control] if found. Any further action is referred to [Florida Bureau of Radiation Control] Radioactive Materials [Branch]." The Co-57 source strength was reported as 414 microcuries. FL Incident Number: FL11-081 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-09-23
47279 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-09-13 07:00 | 2011-09-19 18:00 | 2011-09-19 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING THE MISADMINISTRATION OF I-125 SEEDS IN A PROSTATE CANCER TREATMENT The following was received from the state via e-mail: "On Thursday, September 15, the Radiation Safety Officer (RSO) for the licensee called [the state] to make a preliminary advisement that a medical event involving a prostate cancer treatment had occurred at their facility. The treatment called for the placement of seventy one I-125 seeds in the prostate. As advised by the RSO, post implant imaging revealed only 3 seeds located in the target, indicating a dose under 20 percent of the prescribed amount in the written directive was likely. Post operatively, seven seeds were discovered to be in the bladder and were immediately removed. Additional post operative imaging indicated that a number of seeds were placed in bowel wall, bladder wall, and the lumen of the bowel. "Subsequent to that initial notification, the licensee conducted additional imaging and reviews of the case in order to assess the dosimetry associated with the implant. The written directive called for 145 Gray to the target and allowed for up to 100% of the reference dose to the prostatic urethra and 150% of the dose to the rectum. Preliminary estimates are that the D90 to the prostate was 2.2 Gy. The dose to the prostatic urethra was 15.3 Gy and the dose to the rectum was 63.9 Gy. Due to the misplaced application of the seeds, doses to the large bowel (10 cc), small bowel (10 cc) and bladder are also believed likely to have occurred. Those doses are 49.19 Gy, 20.7 Gy and 23.8 Gy, respectively. All estimates provided were preliminary and subject to change. "The patient and referring physician were advised of the event on the day following surgery. The patient was cautioned that due to seed placement, the sources may be passed in the patient's stool and/or urine. Imaging on September 15 suggested the patient in fact passed 8 seeds since the initial implant on September 13. (Additional passages would affect dose estimates.) The patient intends to attempt a second placement procedure at the licensee's facility in order to treat the cancer. Additional corrective measures and risks were also discussed with the patient. "The licensee notes that two procedural items that have been consistent with other successful treatments at their facility were not in place during this event. Fluoroscopy was not used during needle placement and the benefit of the physical presence of a medical physicist was not used. The Agency [state] intends to conduct an on-site investigation to gather additional information related to the cause of this event and review the licensee's proposed corrective action as well as review additional cases conducted at the facility. The licensee was advised of the 15 day written reporting requirement. Pending submission of that report and the Agency's investigation, this item remains open." Illinois Item Number: IL11126 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-09-25
47278 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-19 08:00 | 2011-09-19 11:59 | 2011-09-19 | OFFSITE NOTIFICATION DUE TO ACID LEAK ONSITE "A report has been made to the Texas Commission on Environmental Quality concerning leakage of BULA 7016 (phosphoric acid) from a tank and berm at the Service Water Intake Structure. The berm is cracked, therefore the material is leaking into the soil surface. No chemicals have reached the reservoir." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-09-19
47277 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-19 10:07 | 2011-09-19 11:10 | 2011-10-08 | SPDS AND ERDS UNAVAILABLE DURING REPLACEMENT OF PLANT PROCESS COMPUTER SYSTEM "At 1007 CDT on September 19, 2011, the Unit 2 Plant Process Computer (PPC) was removed from service for a planned replacement in the current Unit 2 Refueling Outage. The Unit 2 PPC feeds the Safety Parameter Display System (SPDS) used in the Main Control Room (MCR) and the Technical Support Center (TSC). The Unit 2 PPC also feeds the Emergency Response Data System (ERDS). The Unit 1 and Unit 2 PPCs also feed the Plant Parameters Display System (PPDS) used in the MCR, TSC and Emergency Operations Facility (EOF). Meteorological data will remain available. The dose assessment program will remain functional as the Unit 1 PPC will be capable of providing the necessary data through PPDS to run the program. The dose assessment program is not affected by the Unit 2 PPC being out of service. As compensatory measures, a proceduralized backup method to fax or communicate via a phone circuit applicable data to the NRC, TSC, and EOF exists. There is no impact on the Emergency Notification System (ENS) or Health Physics Network (HPN) communication systems. "The new Unit 2 PPC is scheduled to be functional on September 25, 2011. However, based on the Mode Unit 2 will be in, this will limit the number of points that would provide usable data. The Unit 2 PPC will be tested as Mode changes occur. The Unit 2 PPC is planned to be declared functional by Mode 2. A follow-up ENS call will be made once the Unit 2 PPC is declared functional. "The loss of SPDS and ERDS is a 'major loss of assessment capability' and is reportable under 10CFR50.72(b)(3)(xiii). "The NRC Senior Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS call." * * * UPDATE ON 10/08/11 AT 2130 EDT FROM WELT TO HUFFMAN * * * "As of 1800 CDT on October 8, 2011, the Unit Two PPC is considered operational with respect to the Safety Parameter Display System (SPDS), Plant Parameter Display System (PPDS) and Emergency Response Data System (ERDS). Therefore, a major loss of assessment capability no longer exists on Unit 2. The Byron EP manager contacted the NRC ERDS Center yesterday on 10/7/11 to conduct an ERDS test for Unit 2 to ensure the data was being satisfactorily sent to the NRC. Unit-1 and Unit-2 ERDS data to NRC was tested satisfactory IAW EP-AA-124-F-01. "The NRC Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS update." R3DO (Phillips) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-19
47276 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-09-07 | 2011-09-18 13:42 | 2011-09-18 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY CAMERA LOCKING MECHANISM The following information was received via e-mail: "On September 7, 2011, the licensee discovered a failure of the locking mechanism of a QSA 880-Delta radiography exposure device. This is a 30-day notification event. Device: 880 Delta. S/N: D7822. "During the installation of the 880 camera, it was discovered that the locking mechanism would not return to the 'Stored / Locked' position. While investigating the malfunction, it was determined that possibly one of the springs in the locking mechanism was bad. The manufacturer (QSA Global / Sentinel) was called and the malfunction was explained and it was requested that the camera be sent back for further investigation and correction of the malfunction. "This camera did not have a radioactive source in it or attached to the drive cable at the time of the malfunction discovery. This is a brand new 880 Delta camera and has not had a radioactive source in it. The source to be installed in the camera is being stored in a 650L changer, serial number 2168 and secured in [the licensee's] radiography booth. "The RSO was the only person in the radiography booth when the malfunction was discovered and no potential exposure occurred. "Updates will be provided through NMED. North Carolina Incident Number: NC 11-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-09-21
47275 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-09-18 10:56 | 2011-09-18 12:41 | 2011-09-18 | ALERT DECLARED DUE TO A FREON GAS RELEASE INTO A SAFE SHUTDOWN EQUIPMENT AREA "An Alert was declared at Callaway Nuclear Plant at 1056 [CDT] due to EAL HA3.1. Access to an Auxiliary Building area which is prohibited due to release of toxic gas which jeopardizes operation of systems required to maintain safe operations or safely shutdown the reactor. EAL HU3.1 (Unusual Event) is also applicable at the same time. "The cause of the toxic gas release was a Freon gas leak from the 'A' Control Room air conditioner unit." The licensee has notified the NRC Resident Inspector and state and local government. Also notified USDA (Pitt) and HHS (Emerson). * * * UPDATE FROM DAVID LANTZ TO JOHN KNOKE AT 1847 EDT ON 9/18/11 * * * At 1737 CDT, Callaway Nuclear Plant exited from the Alert for EAL HA3.1, and exited from the Unusual Event for EAL HU3.1. The plant continues to operate at 100% power in Mode 1. There was no radiological release due to this event. Additionally, a press release will be performed after the event closeout. The licensee has notified the NRC Resident Inspector and state and local government. Notifications were also given to R4DO (Pick), NRR EO (Giitter), IRD-MOC (Morris), HQ PAO (Hayden), DHS (Gates), FEMA (Via), DOE (Foote), USDA (Sanders) and HHS (Hoskins). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 4 | MO | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-09-18
47274 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-09-18 08:30 | 2011-09-18 11:00 | 2011-09-18 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This report is being made under 10 CFR 50.72(b)(3)(xiii) for unavailability of the Palo Verde Technical Support Center (TSC). On September 18, 2011, from approximately 0830 to 1700 MST, a scheduled power outage will cause the TSC to be non-functional due to the loss of lighting, ventilation, Emergency Response Facilities Data Acquisition and Display System (ERFDADS), and the Plant Information (PI) System in the TSC. Temporary lighting will be installed prior to the power outage. In the event that the TSC is required to be activated, the Emergency Response Organization (ERO) will respond to the TSC and the electrical maintenance group will stop maintenance activities and restore power. The TSC will then be declared functional after power is restored. "In addition, due to the power outage to the TSC, PI and ERFDADS will be unavailable at the Emergency Operations Facility. "The NRC Resident Inspector has been notified of the planned power outage." * * * UPDATE FROM MIKE KOHART TO JOHN KNOKE AT 2200 EDT ON 9/18/11 * * * At 2200 EDT the Palo Verde Technical Support Center (TSC) has been restored to service This includes Emergency Response Facilities Data Acquisition and Display System (ERFDADS), and the Plant Information (PI) System. The licensee has notified the NRC Resident Inspector. Notified the R4DO (Pick). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-18
47273 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2011-09-18 04:44 | 2011-09-18 08:52 | 2011-09-18 | TRANSPORT OF POTENTIALLY CONTAMINATED INJURED WORKER "A worker was transported to an off-site medical facility due to a work-related hand injury. The individual was not contaminated. The individual's left hand work glove was found to be contaminated. The individual remains under the care of physicians and all contaminated material was safely collected and is being transported back to Peach Bottom Atomic Power Station as required." A licensee health physics employee accompanied the worker to the hospital. There was no spread of contamination in the ambulance or at the hospital. The licensee notified the NRC Resident Inspector and will be notifying the Pennsylvania Emergency Management Agency and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2011-09-18
47272 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2011-07-31 | 2011-09-16 18:01 | 2011-09-16 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE TO RADIOGRAPHER The following report was received from the State of Louisiana via facsimile. "On Monday, September 12, 2011, LA DEQ [ Louisiana Department of Environmental Quality] received a notification from Integrity [Inspection] Solution that a radiographer's personnel monitoring device received an excessive exposure of 10811mrem for the month of July 2011. The RSO [Radiation Safety Officer] has begun an investigation into the exposure. The individual left the monitor at the office while he was on a week off. The individual was referred to a physician for blood work and will have follow up check ups. Preliminary findings were no unusual activities. Updates will be provided when available." Event Report ID No: LA-1100XXX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2011-09-21
47271 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-09-16 14:50 | 2011-09-16 15:04 | 2011-09-16 | NOTIFICATION OF UNUSUAL EVENT DUE TO PRIMARY SYSTEM LEAKAGE GREATER THAN 10 GPM The Licensee declared an Unusual Event for Palisades Unit 1 on 09/16/2011 at 1450 EDT based on EAL SU 8.1, RCS (Reactor Coolant System) leakage exceeding 10 gallons per minute (gpm). The licensee was monitoring an increase in RCS leakage, and at a rate of 3.5 gpm entered their off normal procedure and began shutting down the plant. Technical Specification requires the plant to be in Mode 3 within 6 hours. Leakage increased to greater than 10 gpm, and at 1454 EDT the reactor was manually tripped from 79% power. All control rods fully inserted, and the shutdown was described by the licensee as uncomplicated. Unit 1 is stable in Mode 3. No safety injection was required since two charging pumps (B&C) were able to keep up with RCS leakage estimated to be between 14 and 15 gpm. Pressurizer level was restored to 43% and rising. RCS pressure was greater than 2000 psi and RCS temperature was being maintained at no load Tave of 535F on the turbine bypass valves. There is no indication of any primary-to-secondary leakage and all equipment is available except for charging pump 'A', which was tagged out of service for planned maintenance. An entry into containment had been made and the licensee had identified the source of the RCS leakage as being in the vicinity of the 'A' pressurizer spray control valve #1057. This was based on a steam plume seen from below the pressurizer looking up through grating towards this valve. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JAMES BYRD TO JOHN KNOKE AT 1952 EDT ON 09/16/11 * * * At 1934 EDT the licensee terminated from their Unusual Event due to EAL SU 8.1. The plant is still in Mode 3 with a leak rate of 0.324 gpm..The licensee has confirmed that the leak is a result of the packing gland backing out of pressurizer spray valve #1057. The licensee has notified the NRC Resident Inspector. The R3DO (Bloomer) was notified. Notified FEMA (Eiscoe) and DHS (Flinter). | 0 | 0 | 0 | 79 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-09-16
47270 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-09-14 | 2011-09-16 12:01 | 2011-09-16 | AGREEMENT STATE REPORT - SHUTTER ASSEMBLY FAILED IN OPEN POSITION This event was received via facsimile. "On September 15, 2011 at 1600, the Department's central office [PA Department of Environmental Protection] received notification of a shutter failure reportable under 10 CFR 30.50(b)(2), which was discovered on September 14, 2011 at 45 Aspers Road North, Aspers, PA 17304. "The device was manufactured by Heuft USA Inc., Model (45US), Serial # (7533LQ), Isotope (Am-241), Activity (44.2mCi). No radiation exposure to personnel ensued during this event. "The cause of the event is unknown at this time. "The gauge manufacturer, Heuft, has been notified and is scheduled to make repairs today, September 16, 2011. A Departmental [PA Department of Environmental Protection] reactive inspection is planned to investigate this event further. More details will be provided when known." Report No: PA 110024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-09-21
47269 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-09-14 15:30 | 2011-09-15 14:45 | 2011-09-23 | 24 HOUR REPORT DUE TO DOUBLE CONTINGENCY NOT MAINTAINED "During a GNF-A Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA) team walk-down of HVAC systems in the decontamination facility area, it was observed that a log entry for a waste-oil can mass was greater than the limit specified in procedural requirements. "Upon further investigation it was determined at 3:30PM on September 14, 2011 that an operator had incorrectly processed a waste oil can with a gross weight in excess of the limit specified by criticality safety requirements. This resulted in a condition where one of the two controls on mass documented as being necessary to meet double contingency had not been maintained. The second criticality control on mass was maintained at all times. "At no time was an unsafe condition present, however the decontamination oil processing area was shut down until necessary controls were available. "This event is being conservatively reported pursuant to GNF-A internal procedure reporting requirements within 24 hours of discovery." The licensee will inform the state and local agencies and the NRC Region II Office of this incident. * * * UPDATE FROM SCOTT MURRAY TO DONALD NORWOOD AT 1832 EDT ON 9/16/2011 * * * "The incorrect processing of the waste oil can as reported on 9/15/11 resulted in a failure to meet the performance requirement of 10CFR70.61 and as a result, met the reporting requirements of 10CFR70 Appendix A(b)(2) [and 10CFR70.74]. Notified R2DO (Guthrie) and NMSS EO (McCartin). * * * UPDATE AT 1100 EDT ON 09/23/11 FROM SCOTT MURRAY TO S. SANDIN * * * "An extent of condition review has identified two additional cans that were improperly processed with a gross weight over the 9.58 kg gross weight limit specified in procedural requirements. "March 2, 2011 9.66 kg "July 13, 2009 9.65 kg "At no time was an unsafe condition present. The decontamination oil processing area remains shutdown." Notified R2DO (Lesser) and NMSS (Benner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | ADDITIONAL REPORTING REQUIREMENTS | [8 empty] | NON EMERGENCY | 2 | NC | FUE |  |  | 70.74 APP. A |  |  | 0 | 2011-09-15
47268 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-09-14 10:23 | 2011-09-14 18:15 | 2011-09-14 | LOSS OF TWO PUBLIC WARNING SYSTEM SIRENS "On September 12, 2011, the Palo Verde Emergency Preparedness Department discovered that public warning system siren 1 was not responding and was out of service. The loss of this siren did not constitute a loss of capability to alert a large segment of the population for greater than one hour and was therefore, not reported. Troubleshooting had commenced but was not completed. On September 14, 2011, at 1023 Mountain Standard Time, the Palo Verde Emergency Preparedness Department was notified by Maricopa County Sheriff's Office (MCSO) that siren 6 had failed. Since siren 1 remains out of service pending repairs, and siren 6 is now out of service, the loss of the two sirens constitutes a loss of capability to alert a large segment of the population for greater than one hour and is reportable. This is a reportable event as a loss of communication and assessment capability that could potentially impact a population of greater than 10 percent of the people in the 10-mile emergency planning zone (approximately 750 people affected). Therefore, this notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). "If an event occurs while the sirens are out of service, the Palo Verde Emergency Plan has a contingency for dispatching MCSO vehicles with loudspeakers to alert persons within the affected area. The MCSO is prepared to implement this contingency should it become necessary. "Troubleshooting to determine the cause of the failure of siren 6 has also commenced. "The NRC Resident Inspector has been notified of the out of service sirens and this ENS call." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-14
47267 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-12 | 2011-09-14 15:26 | 2011-09-14 | AGREEMENT STATE REPORT - RADIOGRAPHER EXCEEDS FIVE REM TEDE FOR YEAR The following information was received via E-mail: "On September 14, 2011, the Agency was notified by the licensee that a radiographer had exceeded 5 REM TEDE for the year. On September 12, 2011, while operating an INC IR102 camera, serial number 4843, containing a 67 Curie Iridium (IR) 192 source, the radiographer failed to fully retract the source into the camera after completing three shots on a weld. This was discovered when the trainee discovered that safety lock was already in the open/unlock position when he was going to unlock the source for the first exposure on the second weld. The radiation survey meter was turned off and no radiation pagers alarmed. Both radiographers noted that their 0-200 mR pocket dosimeters were off scale. They stopped work, fully retracted the source in the camera, and reported the incident to the RSO. Their Landauer badges were sent off for emergency processing and the results were received on September 14, 2011. The trainer received 3.361 Rem deep dose equivalent whole body dose. The trainee received 2.787 Rem. The total exposure for the year of the trainer is at 5.152 Rem and the RSO is still awaiting his August 2011 dose report to add to his total dose for the year. The trainer has been removed from duty. Additional information will be provided as it is received in accordance with SA300." This event occurred at Total Refinery, Highway 366 and 32nd St., Port Arthur, Texas, 77642. Texas Incident Number: I-8884. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-19
47266 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-09 18:00 | 2011-09-14 15:03 | 2011-09-14 | AGREEMENT STATE REPORT INVOLVING A LESS THAN PRESCRIBED DOSE ADMINISTRATION The following information was received from the State of Texas via email: "On September 13, 2011, the Agency was notified by the licensee that it had determined that a medical event had occurred at its facility. The licensee reported that on Friday, September 9, 2011, a patient had undergone a therapy procedure at approximately 3:00 p.m. which involved insertion of Yttrium-90 TheraSpheres into the liver. The patient's prescribed dose was to be 80 gray. Following the procedure, the technician took measurements, as part of the standard operating procedures, of the vial and other items associated with the treatment. The technician found that the dose rate was higher than would be expected if all of the contents of the vial had been delivered. The technician notified the medical physicist and they discussed the measurements. At approximately 6:00 p.m. they determined that an underdose had most likely occurred, but they were not yet sure it was a medical event. On Monday, September 12th, evaluation and measurements were conducted on the vial and dose calculations were completed. On Monday afternoon, it was determined that the patient had received a dose of 49 gray (22.3 millicuries administered), which is 39% less than the prescribed dose of 80 gray (37 millicuries). A meeting was arranged with the facility's Radiation Safety Officer on Tuesday, September 13th, at which time he was advised of the findings. Initial investigation by the licensee indicated some type of failure of the septum on the TheraSphere vial had occurred. The licensee will complete their investigation and submit a written report. An update to this report will be provided when new information is received." Texas Incident No.: I-8883 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-20
47265 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-09-13 14:45 | 2011-09-14 13:32 | 2011-09-14 | 24-HOUR REPORT INVOLVING POTENTIAL FAILURE TO MAINTAIN DOUBLE CONTINGENCY CRITERIA "As part of the ongoing GNF-A Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA) project, reviews of documentation for scrap accumulation hoods were performed that identified procedural actions that were different than described in the criticality safety analysis. It was determined at approximately 2:45 PM on September 13, 2011 that uranium mixed with small amounts of moderator were not prevented from movement into these hoods. This resulted in a condition where the moderation criticality control documented as being necessary to meet double contingency may not have been maintained. The other criticality control on geometry was maintained at all times. "At no time was an unsafe condition present, however the accumulation hoods were shut down until necessary controls were available. Additional corrective actions and extent of condition are being evaluated. "This event is being conservatively reported pursuant to GNF-A internal procedure reporting requirements within 24 hours of discovery." The licensee will inform state and local agencies and the NRC Region II Office of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2011-09-14
47264 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-08-12 | 2011-09-14 13:07 | 2011-09-14 | AGREEMENT STATE REPORT - MISSING CS-137 SOURCE The following information was received via facsimile: "[The State of Florida] received a report from licensee of a missing 144.6 microCurie Cs-137 sealed source used as a dose calibrator. Source was first discovered missing by inventory on Aug 12, 2011. Also reported by licensee that the Hot Lab was broken into 2 weeks ago and items were missing from a crash cart. Advised licensee to make a police report. Central Inspection Office assigned to investigate." Florida Incident Number: FL11-078. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-09-19
47263 | 0 | QUEEN'S MEDICAL CENTER |  |  |  |  | 2011-09-13 10:30 | 2011-09-13 22:01 | 2011-09-13 | MEDICAL EVENT INVOLVING THE ADMINISTRATION OF THE WRONG RADIOPHARMACEUTICAL At approximately 1000 HST a patient scheduled to receive an administration of 5 mCi In-111 for an imaging scan (Octreotide) received instead a 1.55 mCi Sr-89 injection. The Sr-89 dose, originally 4mCi, was expired (89 days) and administered unintentionally due to personnel error. The RSO calculates that the red bone marrow will receive a dose of 63 rem. The patient was informed and is being monitored for changes in blood chemistry. The attending and prescribing physician will be informed. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2011-09-19
47262 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2011-09-13 | 2011-09-13 16:52 | 2011-09-13 | AGREEMENT STATE REPORT INVOLVING A TRACTOR-TRAILER INCIDENT WHILE TRANSPORTING NUCLEAR GAUGES The following report was received from the State of Georgia via fax: "Location of Event: I-20 EB near Six Flags Road (near exit 46) "A tandem tractor trailer carrying 8 Troxler moisture-density gauges overturned at [about 2330 EDT] on 9/12/2011 after hitting the guardrail. Gauges were en route from Alexandria, LA to Cleveland, TN to be calibrated. "County HAZMAT arrived on the scene, assisted by GA Environmental Radiation Program personnel (paged by GEMA at [0047 EDT], 9/13/2011). All 8 shipping containers sustained damage. Seven (7) gauges were intact in the shipping containers. One (1) gauge sustained damage: electronic components were separated from the gauge body, survey and wipe smear indicated shielding was still intact, no release of radioactive material. "At [about 0445 EDT], 9/13/2011, a local Environmental Cleanup Company took temporary possession of the gauges and secured them at their facility. A representative from the calibration lab in Cleveland, TN will bring replacement shipping containers and repackage the gauges on 9/14/2011. "Isotope: Cs-137; Am-241 "Amount of Activity: 8 mCi; 40 mCi (per gauge) "Date of Event: 9/12-13/2011 (overnight) "Date of Report to RCP (Radioactive Control Program: 9/13/2011, [0047 EDT] "Describe clean-up actions taken by RCP: Performed area surveys and took wipes to confirm integrity of the gauges (no release of radioactive material) "List radiation measurements taken by RCP: "Background: 10 uR/hr "Highest reading, outside trailer: 120 uR/hr "Damaged gauge, contact: 50 mR/hr "Damaged gauge, @1m: 50 uR/hr" GA Incident No.: GA-2011-46i National Response Center Incident No.: 989403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2011-09-16
47261 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-13 10:40 | 2011-09-13 16:18 | 2011-09-13 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR EMPLOYEE A non-licensed employee supervisor had a confirmed positive drug test during random testing. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 75 | 0 | 100 | 75 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2011-09-13
47260 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-09-13 08:22 | 2011-09-13 13:00 | 2011-09-16 | LOSS OF TECHNICAL SUPPORT CENTER VENTILATION "VA-106, TSC HVAC Unit VA-107 Rooftop Condensing Unit, tripped off and attempts to restart were unsuccessful. The cause of VA-106 tripping is unknown at this time. Troubleshooting is in progress. "This condition renders the Technical Support Center unavailable for Emergency Planning Responses. Approved compensatory actions are to relocate personnel to alternate facilities if required. This condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for Loss of Emergency Preparedness Capabilities." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM ERICK MATZKE TO DONALD NORWOOD AT 1245 EDT ON 9/16/2011 * * * "TSC ventilation troubleshooting has been completed and the system was determined to be functional today, September 16, 2011 at 1115 CDT." The licensee notified the NRC Resident Inspector. Notified R4DO (Pick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-13
47259 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-09-13 07:30 | 2011-09-13 09:07 | 2011-09-13 | SAFEGUARDS REPORTS - DOCUMENT CONTROL VULNERABILITY DISCOVERED "Discovered vulnerability in a safeguards system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1540 EDT ON 09/13/11 FROM GENE DORMAN TO S. SANDIN * * * The licensee is retracting this report after further review concluded that it does not meet the criterion for a 1 hour report under 10 CFR 73. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. Notified R1DO (Burritt), ILTAB (Whitney) and 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-09-13
47258 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-12 17:45 | 2011-09-13 01:57 | 2011-10-19 | CONTROL ROOM ENVELOPE DECLARED INOPERABLE "On September 12, 2011, at 1745 PDT operators declared the control room envelope (CRE) inoperable and entered Technical Specification (TS) 3.7.10 Action B. This was due to discovery of inadequately documented CRE in-leakage test data. "On September 12, 2011, DCPP [Diablo Canyon Power Plant] personnel reviewing the CRE testing dated February 3, 2005 determined that the test report provided inadequate information to conclude that the most limiting alignment for control room pressurization would result in zero cubic feet per minute (CFM) in-leakage into the CRE, contrary to the Final Safety Analysis Report (FSAR) accident analysis for the most limiting design basis accident. Three of the four ventilation alignments tested had reported values of in-leakage greater than zero CFM. "Plant staff implemented compensatory measures by placing the control room ventilation system into its pressurization accident alignment at 1828 PDT using the alignment from the test which had a reported value of zero CFM in-leakage. Additionally, administrative controls are being established to maintain post-Loss of Coolant Accident Emergency Core Cooling System leakage at a rate that would ensure operator doses are maintained less than the FSAR accident analysis results for the highest in-leakage rate reported by the test. "Plant personnel notified the NRC Resident Inspector." * * * UPDATE FROM MICHAEL KENNEDY TO JOHN KNOKE AT 1816 EDT ON 09/16/2011 * * * "On 9/13/11 procedure revisions were approved with reduced limits for post-Loss of Coolant Accident Emergency Core Cooling System (ECCS) leakage. These reduced limits ensure operator doses are maintained less than the FSAR accident analysis results for the highest in-leakage rate reported by the CRE in-leakage test. Plant staff have since determined that the potential benefit of operating the control room ventilation system in its pressurization alignment was unnecessary with the ECCS leakage restriction and on 9/16/11 operators restored the control room ventilation system into its normal operating alignment." The licensee has notified the NRC Resident Inspector. Notified R4DO (Greg Pick) * * * UPDATE FROM SHANE GUESS TO DONALD NORWOOD AT 0042 EDT ON 10/19/2011 * * * "This is an update to EN #47258 reported on 9/13/11 where it was reported that operators had declared the Control Room Envelope inoperable. [This report was subsequently] updated on 9/16/2011. "On 10/18/11 at 16:45 PDT, plant staff determined that the CRE testing dated February 3, 2005 was not performed using a bounding configuration which would result in greatest consequence to the control room operators. The recorded in-leakage from the test was therefore considered to be non-bounding. "[As a result of this determination, plant staff have] implemented additional compensatory measures by issuing a shift order requiring the use of self-contained breathing apparatus and potassium iodide tablets under certain accident conditions in accordance with Regulatory Guide 1.196 and NEI 99-03. "Plant personnel notified the NRC Resident Inspector." Notified R4DO (Campbell). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-09-13
47257 | -1 | U.S. ARMY |  |  |  |  | 2011-09-12 09:00 | 2011-09-12 17:19 | 2011-09-22 | MISSING/UNACCOUNTED FOR AM-241 SPECIAL FORM SEALED SOURCE IN A M43A1 CHEMICAL AGENT DETECTOR A Michigan National Guard Unit in Lansing, MI while preparing for deployment identified that a 250 microcurie Am-241 special form sealed source (S/N Z03-C-36663) was missing from a M43A1 Chemical Agent Detector. The detector was last confirmed intact in 2008 prior to the Unit's last deployment to Iraq. The licensee has initiated a formal investigation and notified the State of Michigan of the incident. * * * UPDATE AT 1332 EDT ON 09/13/11 FROM THOMAS GIZICKI TO S. SANDIN VIA FAX * * * "Description of the event: On September 12, 2011 the Michigan Army National Guard, United States Property and Fiscal Office (USPFO) warehouse, Lansing, MI reported to the licensee of a missing Am-241 cell from a M43A1 chemical agent detector. The Am-241 cell is a sealed source, special form that contains 250 microcuries of Am-241. The Am-241 cell (s/n C-36663) belonged to detector s/n D-36025. Detector is NSN 6665-01-081-8140 and SSDR no. NR-1129-D-102-S (inactive). "The detector with Am-241 cell belongs to 'A' Co. 125th Infantry. A physical inventory was performed by 'A' Co. in January 2008 at which time the unit was deployed to Kuwait for 1 year. The unit was getting ready for redeployment to Kuwait in the next several weeks and performed an inspection of all equipment needing to be shipped. It was at this time that cell C-36663 was discovered missing from the detector. The USPFO warehouse was searched wall to wall and the missing cell was not found. The Michigan National Guard is conducting a formal investigation regarding the lost radioactive cell. Exposure to personnel is not likely to occur in an unrestricted area since the Am-241 source is contained in a cell module that is sealed source special form." Notified R3DO (Lipa) and FSME (McIntosh). Provided to ILTAB (Whitney) via e-mail. * * * RETRACTION AT 1148 EDT ON 09/22/11 FROM THOMAS GIZICKI TO PETE SNYDER * * * The item identified as lost was located on post therefore this report is retracted. Notified R3DO (Stone) and FSME (McIntosh). Provided to ILTAB (Allston) via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-09-12
47256 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-12 13:05 | 2011-09-12 13:54 | 2011-09-12 | OFFSITE NOTIFICATION TO THE TENNESSEE DEPARTMENT OF ENVIRONMENT AND CONSERVATION (TDEC) "On August 25, 2011, it was discovered that a hazardous waste drum containing x-ray fixer waste was not shipped to the permitted Hazardous Waste Storage Facility within the timeframe required by the Tennessee Department of Environment and Conservation (TDEC) regulations. The drum was shipped to the permitted Hazardous Waste Storage Facility on September 01, 2011. The written notification to TDEC was signed on September 12, 2011." The licensee informed the NRC Resident Inspector. | 100 | 75 | 0 | 100 | 75 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-09-12
47255 | 0 | DEEP GREEN WEST VIRGINIA INC |  |  |  |  | 2011-09-08 10:00 | 2011-09-09 17:03 | 2011-09-09 | FIXED GAUGE SHUTTER FAILURE "On 9/8/2011, during site cleanup activities, workers at the Greenfields coal processing facility near Pageton, WV unexpectedly discovered two generally licensed, fixed-type gauges in a remote, back lot area of the plant property. One of the gauges had a stuck open shutter. The gauges are currently clamped to pipes, roped off in an area restricted from personnel access, at about a 300 foot distance from personnel. No threat to health and safety exists at this time. "The gauges are designed to be affixed to piping for industrial process control, but were found among various discarded metal parts. "An inspector from the West Virginia Radiological Health Program took survey measurements and verified there was no spread of contamination. Dose rates outside of the gauge casing are about 0.4 mRem/hr. Dose rates inside of the pipes are about 40 mRem/hr, which indicates that the shutters are likely open. "Facility personnel will take photos of the gauges and send to NRC Region I. Additionally, they intend to place the gauges with the piping in a locked gang box that will be chained and locked to a fixed metal structure. "The facility owner, Deep Green, is taking steps to have the material removed from the site. "Gauge information: [2] Berthold Technologies gauges, Model No. LB 7440 D; 30 mCi, Cs-137 source (Sep. 21, 2001); Source serial # HE681 manufactured by AEA Technologies, model CDC.p4; SSD Safety Evaluation No. TN-1031-D-101-B." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-09-09
47254 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-09-07 12:00 | 2011-09-09 16:26 | 2011-09-09 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN UNDERDOSAGE "Wisconsin Department of Health Services (DHS) received notification by phone call from the licensee on September 8, 2011 about a medical event involving I-125 permanent prostate seed implants. During a standard review conducted September 7, 2011 of a post seed implant report the Authorized Medical Physicist determined that the dose delivered differed from the prescribed dose by 20% or more. Specifically it was found that only 76% (110 Gy) of the prescribed dose was delivered to 90% of the CTV for an implant completed on July 22, 2011. The licensee had established the dose based criteria that by post-operation CT, prostate D90 values are < 80% or >130% for classifying medical events. The licensee has notified the Authorized User, referring physician and will notify the patient during a scheduled examine the week of September 11, 2011. There is no expected immediate harm to the patient and the Authorized User and referring physician will discuss with the patient to determine if supplemental radiation (implant or external beam) will be done. DHS conducted an investigating of this medical event on September 9, 2011 by sending a special inspection team. The preliminarily conclusion after reviewing the licensee's procedures and discussion with the Authorized User and Authorized Medical Physicist is that the under dose was directly caused by edema of the prostate, i.e. post implant procedure swelling." Wisconsin Event Number: WI110014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-09-15
47253 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-09-09 | 2011-09-09 14:01 | 2011-09-09 | OFFSITE NOTIFICATION DUE TO LEAKING A SMALL QUANTITY OF DIESEL FUEL OIL "A temporary diesel generator has emitted droplets of oil to the ground which was washed to a storm drain. The exhaust droplets were contained in secondary containment. An oil-only absorbent boom was placed around the storm drain to capture residual oil and prevent oil to the storm drain." It is estimated that 0.05 gallons of diesel fuel entered a storm drain. The licensee notified the Maryland Department of Environment, National Response Center, U.S. Coast Guard and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-09-09
47252 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-09-08 15:38 | 2011-09-08 19:08 | 2011-09-08 | AUTOMATIC REACTOR TRIP DUE TO A GRID DISTURBANCE On September 8, 2011 at 1538 PDT, the San Onofre Units 2 and 3 reactors tripped due to a grid disturbance. All control rods fully inserted. The EFAS (Emergency Feed Actuation System) initiated as expected for a reactor trip. Steam generators are being fed by the main feedwater system and decay heat is being removed through the steam bypass system to the main condensers. There is no primary to secondary leakage and no safety relief valves lifted. Site electrical power sources are being fed from off-site power and both units are in a normal shutdown configuration. The emergency diesel-generators are in standby/operable status and were not required during the event. Both units are stable (NOT/NOP) and in Mode 3. The reactor trip response is considered uncomplicated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | N | A/R | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-09-08
47251 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-09-08 05:00 | 2011-09-08 16:54 | 2011-09-08 | AGREEMENT STATE REPORT- REPORTED STOLEN AND THEN FOUND MOISTURE/DENSITY GAUGE The following information was received by e-mail: "On September 8, 2011, Arrow Engineering contacted California Office of Emergency Services to report a stolen moisture/density gauge, Troxler model 3440 Plus, 8 mCi Cs-137 source and 40 mCi Am:Be-214 source, S/N 39529. The gauge was locked in the transport case, secured in the back of a vehicle, a 2001 Chevy Silverado. The gauge operator discovered the vehicle stolen at approximately [0500 PDT], when he was leaving his home, to proceed to the worksite. The operator then notified police and then the Radiation Safety Officer (RSO). The Los Angeles County Sheriffs Department arrived approximately [0545 PDT] and the operator made his report of the stolen vehicle and gauge. After the operator had made the report, he then proceeded to return to work. "After the RSO was notified of the incident, he proceeded to contact Los Angeles County Radiation Management and left a detailed message and then contacted the Office of Emergency Services to report the incident. Approximately [0940 PDT] a LA Co. inspector notified the ICE RAM South of the incident. An ICE inspector then contacted the RSO to obtain information on the incident. The RSO confirmed the incident took place at the residence of the operator sometime in the early morning of September 8, 2011, prior to [0500 PDT], when the operator discovered that the vehicle was missing. He stated that the operator had left the gauge in the locked transport case, locked in the bed of the pickup with two chains and three locks. He also stated that the operator had an alarm on the vehicle, but did not hear it since he was likely asleep at the time. He also stated that the vehicle was not able to be stored in the garage since it was a 4 wheel drive vehicle. The gauge was left in the vehicle since the operator had returned from a jobsite late the prior evening and had an early appointment the next morning. The RSO was informed to provide a written report within 30 days, to place an ad and a reward in the local newspaper and to notify ICE if the gauge is found. "At approximately 1100 [PDT], the RSO contacted RHB reporting that the vehicle was found with the gauge and transport case still locked in the bed of the truck and with a broken drivers side window. The RSO stated that the vehicle was left in the driveway of a neighbors house. It was found by the owner while returning home from the office at approximately 1030 [PDT]. The owner then contacted the LA Co. Sheriff and was told not to touch the vehicle before the Sheriff arrived. When they arrived, he was allowed to check the gauge case to confirm that the gauge was still inside and intact. The operator was able to confirm this and the Sheriff were able to inspect the vehicle and gather evidence. The licensee was informed to take a leak test immediately and keep the gauge out of service until the leak test results were returned and confirmed to be below the contamination limit. "While the investigation is still ongoing, pending licensee's findings in their 30 day report, the licensee is likely to be cited for storing the gauge in an unauthorized storage location, for improperly securing the gauge, or leaving the gauge unattended." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-09-13
47250 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-09-08 10:30 | 2011-09-08 14:21 | 2011-09-08 | POTENTIAL VULNERABILITY DISCOVERED A potential vulnerability was discovered in a safeguard system for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-09-08
47249 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-05 15:20 | 2011-09-08 10:34 | 2011-09-08 | INVALID SPECIFIED SYSTEM ACTUATION "This report is a 60-day telephone notification in lieu of a written licensee event report being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1). The event was an invalid actuation of a Unit 2 Containment Ventilation Isolation (CVI). At the time of the event Unit 1 was at 100% power and Unit 2 was at 85% power. "At 1520 EDT on 5/5/2011, an 'A' train CVI signal was inadvertently initiated during a surveillance test for containment purge air exhaust radiation monitor 2-RM-90-130. The inadvertent CVI signal was initiated due to incorrect connection of test equipment. The signal caused the 'A' train containment upper and lower compartment radiation monitor isolation valves to close. Unit 2 entered Technical Specification Limiting Condition for Operation (LCO) 3.3.3.1 Action 27 and LCO 3.4.6.1 Action b, due to the isolation of lower compartment radiation monitor 2-RM-90-106. The inadvertent CVI signal was also received by the containment vent system, but the containment vent system was not in service and no valves were actuated. "The radiation monitoring (system 90) and the containment vent (system 30) systems received a complete 'A' train CVI signal. The 'A' train radiation monitoring isolation valves closed as designed. The containment vent system was not in service, and since the valves were already closed, no valves were actuated. Actual plant conditions did not exist that required a CVI signal. Therefore, this actuation was invalid. "The delay in reporting this event was due to an initial interpretation that the event did not result in an actuation of the systems listed in paragraph 10CFR50.73(a)(2)(iv)(B), because only one system was in service which was affected by the actuation. Subsequent discussions noted that while only one system was in service, both systems received the CVI signal. The event is reported as a 60-day telephone notification in lieu of a written licensee event report being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1)." The date, when the final determination of the invalid system actuation was made, was not provided. The licensee notified the NRC Resident Inspector. | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-09-08
47248 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-09-07 | 2011-09-07 13:12 | 2011-09-07 | FITNESS FOR DUTY REPORT RELATED TO INTRODUCTION OF ALCOHOL INTO PROTECTED AREA The licensee reported a fitness-for-duty violation due to an employee who inadvertently brought alcohol into the protected area. The violation was self-reported by the individual involved. The employee is being tested under the FFD program and his access has been denied pending outcome of an investigation. Contact the HOO for additional details | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2011-09-15
47247 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-09-07 08:54 | 2011-09-07 12:14 | 2011-09-07 | AUTOMATIC REACTOR TRIP FOLLOWING MAIN TURBINE TRIP FROM 100% POWER "On Sept 7, 2011, at 0854, DC Cook Unit 1 reactor automatically tripped due to a trip of the main turbine. The cause of the main turbine trip is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "The DC Cook Sr. Resident NRC Inspector has been notified. "The electrical grid is stable and Unit 1 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 1 remains stable in Mode 3 while conducting the post trip review." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-09-07
47246 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS |  |  |  |  | 2011-08-30 | 2011-09-06 15:59 | 2011-09-06 | NOTIFICATION THAT CERTAIN ROSEMOUNT PRESSURE TRANSMITTERS MAY NOT PERFORM THEIR INTENDED SAFETY FUNCTION The following is a summary of a Part 21 notification was received from Rosemount via facsimile: "Re: Notification under 10 CFR Part 21 on certain Rosemount Model 1153 Series B, 1154 and 1154 Series H Pressure Transmitters "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform [the NRC] that one (1) Model 1153 Series B, fourteen (14) Model 1154, and twenty (20) Model 1154 Series H pressure transmitters may not perform their intended safety function. "Rosemount Nuclear Instruments, Inc. does not have complete information relating to specific plant applications and therefore cannot determine the potential effects of the condition on plant operation. "The thirty-five (35) potentially affected Model 1153 Series B, 1154, and 1154 Series H pressure transmitters were shipped from RNII between April 19, 2011 and August 12, 2011. [The list of Plant Sites that have received the affected transmitters is provided at the end of this report.] "If you have any questions, or require additional information related to this issue, please contact: Mike Dougherty (208) 865 -1112 or Tracy Kaluzniak (952) 949-7159. "Identification of items supplied: "One (1) Model 1153 Series B, fourteen (14) Model 1154, and twenty (20) Model 1154 Series H potentially affected units have been shipped. "Identification of firm supplying the item: "Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 "Nature of the failure and potential safety hazard: "On each Model 1153 Series B, 1154, and 1154 Series H transmitter, four diodes are used on a circuit card assembly which is installed within the welded sensor module subassembly. These diodes convert the AC oscillator signal to a DC current proportional to the pressure applied to the sensor. The diodes (P/N DZ911218A) are manufactured by Microsemi Corporation (MSC). "Recently an unexpected drop in yield was identified during electrical testing of the circuit card assembly. A hold was placed on production to further investigate the issue. It was determined that the drop in yield was caused by intermittent open diodes on the circuit card assembly. Failure of one diode will result in an off-scale failure of transmitter output. Failure of two or more diodes may result in an on-scale failure of transmitter output. "MSC determined that the intermittent open electrical failures were the result of a poor solder bond formation within the diode at the cathode lead. This was caused by either inadequate heat flow or surface contamination during the component manufacturing process. "Working with MSC, RNII used material traceability data to confirm the potential problem was limited to one manufacturer's lot code of the diode. RNII was then able to utilize material traceability data to further identify the specific shipped transmitters affected by this notification. "On August 30, 2011, it was concluded that a substantial safety hazard may exist. Rosemount Nuclear Instruments, Inc. does not have sufficient information to determine the safety impact related to the potentially anomalous output in plant applications. As a result, a notification about the potential substantial safety hazard is being made in accordance with 10 CFR Part 21 to customers who purchased one or more of the thirty-five (35) potentially affected Model 1153 Series B, 1154, or 1154 Series H pressure transmitters. "The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: "(a) RNII held shipments of completed Model 1153 Series B, 1154, and 1154 Series H transmitters and determined which specific units were assembled with diodes from the suspect lot code. "(b) RNII quarantined all Model 1153 Series B, 1154, and 1154 Series H transmitters and sub-assemblies in manufacturing while a determination was made as to which specific units were assembled with diodes from the suspect lot code. "(c) RNII worked with the diode supplier (MSC) to determine the root cause and identify the suspect lot code. Since this part is no longer being manufactured by MSC, no corrective actions were implemented at MSC. "(d) RNII is in the process of reworking all unshipped Model 1153 Series B, 1154, and 1154 Series H transmitters and subassemblies that were completed or in manufacturing that contained diodes from the suspect lot code. "(e) Potentially affected pressure transmitters can be returned and reworked at the factory at the end user's request. "(f) RNII is qualifying a substitute diode to replace the obsolete DZ911218A diode. The qualification is expected to be complete within the next six months. This qualification will be documented in an update to the Model 1153 Series B, 1154, and 1154 Series H qualification reports "Any advice related to the potential failure of the Item: "RNII recommends that users review the application where any of the thirty-five (35) potentially affected Model 1153 Series B, 1154 and 1154 Series H transmitters are used to determine any safety considerations in the operation of the plant. RNII recommends that potentially affected transmitters be returned to RNII for rework at the end user's earliest opportunity." List of Affected Sites: U.S Facilities Calvert Cliffs -5 Transmitters Oconee -2 Transmitters San Onofre -1 Transmitter River Bend -1 Transmitter Waterford -1 Transmitter Diablo Canyon -1 Transmitter Farley -4 Transmitters Foreign Facilities Shin Kori -1 Transmitter Ringhals -3 Transmitters Fuqing -4 Transmitters Fangjishan -4 Transmitters Yangjiang -4 Transmitters Tihange -1 Transmitter Asco II / Vandellos II -3 Transmitters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2011-09-06
47245 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-09-06 | 2011-09-06 17:42 | 2011-09-06 | AGREEMENT STATE - RADIOGRAPHY CAMERA SOURCE DISCONNECT FROM DRIVE CABLE The following event was provided by the State of Texas Health Services Radiation Branch via facsimile: "On September 6, 2011, the [State of Texas Radiation Branch] was notified by the licensee that while using a Spec 150 radiography camera (serial number 1154, containing a 47.2 Curie Iridium -192 source), the source disconnected from the drive cable. The licensee's Radiation Safety Officer stated the radiographer was starting to crank the source out for the eighth shoot of the day when he noted that the guide tube had come loose from the camera and that the drive cable had began to spool in front of the camera. The radiographer attempted to return the source to the locked position in the camera, but it would not lock. The radiographer went to investigate at the front of the camera and saw the source lying on the ground in front of the camera. The radiographer contacted the RSO and a source recovery team went to the location. Lead shot was placed over the source to reduce the area dose rates. The source recovery team was able to reconnect the source to the drive cable and return the source into the camera and lock it in place. The licensee has returned the camera to its storage location and will conduct a leak test of the source and inspect the guide tube and crank-outs. The RSO stated that it appears that the quick disconnect on the camera failed. No significant exposure was received by the source recovery team or any member of the general public. Additional information will be supplied as it is received in accordance with SA-300." Texas Report Number I-8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-09-09
47244 | 0 | ENVIRONMENTAL PROTECTION AGENCY |  |  |  |  | 2000-06-30 | 2011-09-06 14:36 | 2011-09-06 | STOLEN AND RECOVERED GENERALLY LICENSED X-RAY FLOURESCENCE ANALYZER A representative for the EPA reported that a Thermo Fisher Scientific Niton XLp 722W XRF metal analyzer was stolen and subsequently recovered. The analyzer was inside a car parked at a hotel in Anderson, South Carolina and was stolen sometime during the night of 6/30/11. The technician using the gauge discovered the theft in the morning and filed a police report. Shortly thereafter, on 6/30/11, the police recovered the gauge at a nearby dumpster. The gauge appear to be undamaged but was sent to the vendor for inspection. The gauge has been returned to the EPA and is currently back in service. The gauge contains a 40 milliCurie Cd-109 source and two Am-241 sources with a total activity of 14.005 milliCuries. The licensee did not originally recognize the reportability of this event. After discussions with NRC R1 (Welling) and NRC FSME HQ (McIntosh), the licensee is making this report. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-09-06
47243 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-09-02 | 2011-09-06 12:38 | 2011-09-06 | AGREEMENT STATE - FIXED PROCESS GAUGE FAILED SHUTTER CHECK The following report was received from the State of Illinois via e-mail. "While performing routine shutter checks of fixed gauges at the licensee's site, a device failed to perform as expected. As a result, the Radiation Safety Officer contacted the Agency and made the required report. The failed Ohmart/Vega Model SH-F2 gauge is used for level detection on a high temperature, high pressure vessel. The vessel is located on a roof 50 feet above grade with the nearest workstation approximately 300 feet away. The gauge was left in the 'on' position so as to allow continued routine operation of the process line. Shift supervisors and site personnel were advised of the situation and any entry into the vessel has been prohibited should the line become disabled or shut down. The manufacturer has been contacted and arrangements are pending for repair of the device at the first available opportunity. Should the gauge mounting fail and it become necessary, additional shielding material is available on-site to cover the open beam port and personnel have adequate training to perform that task. No threat to health and safety exist at this time and there are no associated exposures." The Ohmart Gauge Model SH-F2, Serial Number 7306GK contains an 0.3 Ci sealed Cs-137 source. Illinois Report Number IL11120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-09-09
47242 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2011-09-06 01:04 | 2011-09-06 05:54 | 2011-09-06 | CONTROL ROOM INDICATION OF HPCI MINIMUM FLOW VALVE POSITION LOST "On September 6, 2011 at approximately 0104 EDT during surveillance testing of the High Pressure Coolant Injection (HPCI) system, control room position indication was lost on the HPCI Minimum Flow Valve, E4150F012 as the valve was stroking closed following shutdown of HPCI. The Minimum Flow Valve main power fuses were checked (found blown) and replaced in accordance with plant procedures. During stroke time testing of E4150F012, control room position indication was again lost when the operator depressed the open pushbutton. "HPCI had been removed from service for quarterly surveillance testing at 2219 EDT September 5, 2011. The unplanned inoperability condition began at 0104 EDT when position indication was lost on the Minimum Flow Valve during system shutdown. The valve was locally verified closed to comply with the action of LCO 3.6.1.3 to isolate the penetration. A 14-day LCO was entered and back dated to the time that HPCI was removed from service for surveillance testing. This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on loss of a single train safety system. RCIC was and has remained operable. "The NRC Resident Inspector has been notified. The failure is currently under investigation." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-09-06
47241 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-09-05 04:03 | 2011-09-05 09:40 | 2011-09-05 | LOSS OF METEROLOGICAL TOWER VERTICAL TEMPERATURE DIFFERENCE INSTRUMENTATION DUE TO LIGHTNING STRIKE "On 9/5/11 at 0403 EDT, Vermont Yankee Nuclear Power Station experienced a lightning strike which resulted in a loss of all vertical temperature difference instrumentation. "This condition is being reported as a loss of emergency assessment capability in accordance with 10CFR50.72(b)(3)(xiii) "Procedure OPOP-PHEN-3127, Natural Phenomena, was entered and the lightning damage indicator walkdown checklist was performed with no additional damage found. Several other spurious alarms were received at the time of the lightning strike and are being investigated. None of these alarms indicate any other potentially reportable conditions. "The plant is continuing normal power operation at approximately 98 percent rated thermal power. "The NRC Resident Inspector has been informed." The licensee reports that repairs are currently underway. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-05
47240 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-09-04 10:20 | 2011-09-04 13:27 | 2011-09-09 | TECHNICAL SUPPORT CENTER LOST DUE TO FAILED BACKUP DIESEL GENERATOR SURVEILLANCE TEST "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The Functionality of the Technical Support Center (TSC) has been lost due to a failure to pass a required surveillance of the backup diesel generator for TSC Support Systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DANIEL MONAHON TO VINCE KLCO ON 9/9/2011 AT 1418 EDT* * * The licensee has declared the TSC Operable. The licensee notified the NRC Resident Inspector. Notified the R2DO (Rich). | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-04
47239 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2011-09-03 15:30 | 2011-09-03 15:35 | 2011-09-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO "A" TRAIN SERVICE WATER LEAK A leak in the "A" train of the service water system was identified on August 17, 2011. The leak is in the auxiliary building at the minus 5' elevation and the water is being collected in the waste drain tank. At 1530 on September 3, 2011, the leak was quantified as being less than 15 gpm and the service water system was declared inoperable in accordance with Technical Specification (TS) 3.7.4.1 for the Service Water System and the Technical Requirements Manual 3.4.10 for Structural Integrity. The leak is on a 10" flange between two bolt holes in a welded area of the flange. Maintenance has been able to reduce the leakage to approximately 3 gpm. The plant is in a 72 hour Tech Spec and is making preparations to shutdown to mode 5 for repairs. The licensee notified the NRC Resident Inspector and will notify state and local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-09-03
47238 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-09-03 02:35 | 2011-09-03 03:28 | 2011-09-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO RHR/CS ROOM COOLER BEING INOPERABLE "Technical specification required shutdown due to reactor recirculation unit #7 [RHR/CS Room Cooler] inoperable. This cooling unit impacts the operability of 'A' Low Pressure Coolant Injection (LPCI) and 'A' Core Spray (CS). "Entered TS 3.5.A.6. Commenced reducing power for 24 hour cold shutdown LCO." The licensee has initiated repairs to the cooling unit. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1432 EDT ON 09/03/11 FROM JAMES KRITZER TO S. SANDIN * * * The licensee exited TS 3.5.A.6 at 1000 EDT and declared CS operable after implementing compensatory measures. They are currently in a 7-day LCO Action Statement and expect to complete repairs within the time allowed. The Unit is currently holding power at 98%. The licensee informed the NRC Resident Inspector. | 96 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-09-03
47237 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-09-02 16:00 | 2011-09-02 22:15 | 2011-09-02 | INTAKE STRUCTURE FIRE SUPPRESSION SYSTEM FAILED SURVEILLANCE TEST "During intake structure fire suppression sprinkler system surveillance testing, Operations identified that a portion of the sprinkler system was not able to pass flow. A 14-day fire protection system impairment was entered and a continuous compensatory fire watch with backup suppression was stationed prior to removing the system from service for testing. Upon failure of the surveillance test, the impairment remained in effect and the continuous fire watch remained stationed pending investigation/repair by Maintenance. On 9/2/2011 at approximately 1600 [CDT], Mechanical Maintenance personnel informed Operations that the sprinkler suppression piping was found to be fouled and not capable of passing flow. The intake sprinkler system is relied upon in part to satisfy an exemption for the station to 10CFR50 Appendix R, Section III.G.2.B concerning separation of components in the intake structure. Based upon the intake sprinkler system being non-functional, this condition is being reported under 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition affecting plant safety systems." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-09-02
47236 | 0 | COVIDIEN-MALLINCKRODT, INC |  |  |  |  | 2011-09-02 | 2011-09-02 10:59 | 2011-09-02 | LOST PRODUCT CONTAINING 18 MILLICURIES INDIUM - 111 The licensee shipped the radioactive imaging product to a customer in Rochester, NY on 8/7/11. The courier, Medical Delivery Services, called the licensee that evening to report that they had three bills of lading for the customer but only two packages to deliver. The licensee has commenced an investigation to determine the root cause and develop corrective actions. Customers along the route have been contacted without success of finding the missing product. The calculated activity level now is 31 microcuries. The licensee notified R3DO (Bob Gattone). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-09-02
47235 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-09-01 10:50 | 2011-09-01 17:54 | 2011-09-02 | TECHNICAL SUPPORT CENTER DIESEL GENERATOR NON-FUNCTIONAL "At 1050 (CDT), on September 1, 2011, the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) Emergency Diesel Generator (EDG) was declared non-functional due its failure to start during routine testing. The plant is currently in the process of determining the cause of the failure. Normal power to the TSC is currently available. This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JEFFREY MIELL TO MARK ABRAMOVITZ AT 1313 EDT ON 9/2/11 * * * "The TSC Emergency Diesel Generator failure has been identified and corrected. The unit has been successfully tested, restoring the EDG and TSC to a functional status." The TSC was restored at 1145 CDT. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Kunowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-01
47234 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-09-01 16:00 | 2011-09-01 17:37 | 2011-09-01 | FITNESS FOR DUTY (FFD) REPORT INVOLVING A FFD PROGRAM DEFICIENCY "At 1600 on 9/1/11 the control room was notified that the 10CFR Part 26 requirement for the Medical Review Officer (MRO) and Substance Abuse Expert (SAE) to be subject to the FFD Rule has not been met. "10CFR 26.4 (g), 'FFD program applicability to categories of individuals', states that 'All FFD program personnel who are involved in the day-to-day operations of the program, as defined by the procedures of the licensees and other entities in 26.3(a) through (c), and, as applicable, (d), and whose duties require them to have the following types of access or perform the following activities shall be subject to an FFD program that meets all of the requirements of this part, except subparts I and K of this part, and, at the licensee's or other entity's discretion, subpart C of this part: (1) All persons who can link test results with the individual who was tested before an FFD policy violation determination is made, including, but not limited to the MRO; (2) All persons who make determinations of fitness;' "Contrary to the above, the SSES MRO (who is also an SSES SAE) is not included in the SSES random drug testing program as required by the regulation. This individual is also not included in the documented Behavior Observation Program. "This event is reportable under 10CFR26.719(b)4 requiring a 24 hour ENS notification." This deficiency has existed since December of last year and was identified during a routine on-going QA Audit. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2011-09-01
47233 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-08-31 | 2011-09-01 16:02 | 2011-09-01 | AGREEMENT STATE REPORT INVOLVING A FIXED NUCLEAR GAUGE SHUTTER THAT FAILED TO CLOSE The following information was received from the State of Illinois via email: "Late yesterday the Agency's [Illinois Emergency Management] W. Chicago office received a call from PDV Midwest Refining (IL-01603), 135th St and New Ave., Lemont, IL 60439. The caller reported that while his crew was performing routine shutter checks of fixed gauges in his area of the plant, a shutter failed to close. The vessel the gauge was on was in use as part of a sulfur unit and needed to remain in operation with the gauge 'on-line', so no other immediate action was taken other than to advise all shift supervisors of the gauge's status and to avoid performing any work in the area. "This morning, the radiation safety officer was contacted for additional information and instructions regarding necessary actions on their part. The RSO advised that the gauge was an Ohmart model SH-F1-45, containing 15 milliCi of Cs-137 as of April 2002. It was one of two gauges on that vessel. The other gauge which was lower on the vessel showed no difficulties in its operation. However, he noted that a similar problem had occurred in the past with the same model gauge on a parallel sulfur unit in the same physical position. At that time, field notes prepared by the manufacturer's representative who inspected the device indicated that some corrosion was present on the device. Both vessels and thus all four gauges are exposed to the full range of seasonal cycles of weather. All site staff have been made aware of the gauge condition and to ensure all 'lock out - tag out' practices are in effect in the area to preclude any work on the vessel until such time the manufacturer's rep has repaired the device or removed it from the vessel. "The radiation safety officer was advised of the need to file a written report within 30 days in keeping with Illinois regulations. "Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide: CS-137 "Manufacturer: OHMART CORP. Activity: 0.015 Ci [or] 0.555 GBq "Model Number: A-2102 "Serial Number: unk Illinois Item Number: IL11117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-09-06
47232 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-09-01 12:18 | 2011-09-01 14:36 | 2011-09-01 | FITNESS FOR DUTY REPORT INVOLVING AN EMPLOYEE SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2011-09-01
47231 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-09-01 11:20 | 2011-09-01 13:15 | 2011-09-09 | SAFEGUARDS REPORT INVOLVING SAFEGUARDS SYSTEM DEGRADATION The licensee reported a loss of control of a security guard's weapon. Compensatory measures were taken upon discovery. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. * * * RETRACTION FROM RICK LULLING TO PETE SNYDER ON 9/9/11 AT 1639 EDT * * * Upon further review the licensee determined that the weapon was not in the protected area while missing and was recovered in 20 minutes. Since the weapon was discovered within an hour a one hour report was not warranted. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R2DO (Rich) and 73.71 Distribution. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-09-01
47230 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2011-09-01 09:06 | 2011-09-01 12:30 | 2011-09-01 | LOSS OF ALL LAND LINE COMMUNICATIONS FOR GREATER THAN AN HOUR During local utility restoration from the recent hurricane, land line communications were lost for approximately two hours (0906 to 1106 EDT) on 9/1/2011. The licensee notified the State of Connecticut Department of Emergency Management and Homeland Security and the Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-09-01
47229 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2011-08-12 18:00 | 2011-09-01 11:30 | 2011-09-01 | POTENTIAL VIOLATION OF TECHNICAL SPECIFICATIONS Technical Specification 3.2.3 requires two (2) channels of reactor period and reactor level are functional during work involving reactivity being moved in the core. In this case an experiment was being moved into the core and performing some blade testing. The reactor was shutdown at the time with all prior required tests competed satisfactorily. Upon completion, it was discovered that one of the period channels alarm function required by TS was disconnected. The licensee implemented corrective actions to prevent recurrence. A conference call was established with the licensee and NRR (Adams, Quichocho and Sloan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MA | NPR | [5 empty] | 0 | 2011-09-01
47228 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-09-01 05:18 | 2011-09-01 05:40 | 2011-09-01 | UNUSUAL EVENT DECLARED DUE TO AN AFTERSHOCK EARTHQUAKE At 0518 EDT, North Anna Power Station declared an Unusual Event due to seismic activity onsite (EAL HU 1.1). Both units are currently shutdown and electrical power is being supplied from offsite. There were no personnel injuries. There was no radiological release. Site structure and system inspections are in progress. No damage has been identified. The NRC Resident Inspector and state and local authorities have been notified. * * * UPDATE AT 1232 EDT ON 9/01/11 FROM DIEDERICHS TO ABRAMOVITZ * * * The licensee has exited from its unusual event at 1223 EDT on 9/01/11 based on completion of plant walk downs and equipment checks, after the latest 3.4 magnitude earthquake, and no damage noted. The licensee has notified appropriate state and local authorities and will notify the NRC Resident Inspector. Notified R2DO (Sykes) , NRR (King) , IRD (Gott) , FEMA (Blankenship), DHS (Gates) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-09-01
47227 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-08-30 | 2011-08-31 16:15 | 2011-08-31 | AGREEMENT STATE REPORT - PATIENT RECEIVED WRONG ISOTOPE DURING A DIAGNOSTIC PROCEDURE The following information was obtained from the State of Wisconsin via facsimile: "The Wisconsin Department of Health Services (DHS) received a phone call from the Imaging Manager at Aurora Medical Center of Washington County on August 30, 2011, that a patient received a dose of 5 mCi of I-131 on February 2, 2011. The patient, according to the written directive, was to receive a dose of 5 mCi of I-123. This diagnostic procedure was ordered to evaluate whether any thyroid tissue remained following an iodine ablation dose one year earlier. "DHS conducted an investigation on August 31, 2011 and the licensee will submit a 15-day written report concerning the medical event. At this time, the licensee is evaluating their process and is developing a new written directive form. The authorized user will discuss this with the referring physician to determine if the patient will be notified." Wisconsin Report ID: WI110013 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-09-06
47226 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-08-02 | 2011-08-31 14:41 | 2011-08-31 | AGREEMENT STATE REPORT - SHUTTER MECHANISM FAILURE The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "EVENT DESCRIPTION: Failure of the shutter mechanism on one of its generally licensed thickness gauges was identified immediately to operators through a computer based warning message and visually by a red status light adjacent to the gauge location. Adjustment of the air supply allowed the shutter to close but still not operate properly. Routine maintenance activities were not successful in allowing the shutter to return to operational status and Applied Health Physics were notified to provide radiological support. No radiation exposure to personnel ensued during this event. The device is identified as: Manufacturer (IRMS), Model (TG-2), Serial# (00M0397-I5), Isotope (Americium-241), Activity (3 Ci), Location (Cold Reduction Mill). "CAUSE OF THE EVENT: A faulty actuator cylinder. "ACTIONS: The shutter mechanism was replaced, tested, and confirmed as operating properly. The actuator cylinder will be placed on a preventive maintenance schedule following this event." PA Report No.: PA110022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-09-05
47225 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-08-30 16:00 | 2011-08-31 13:01 | 2011-08-31 | COMPLETION OF ACTION PLAN (FABRICATION) MILESTONE "In response to a Notice of Violation (NOV), Global Nuclear Fuels - America (GNFA) committed to perform a review of the existing Integrated Safety Analysis (ISA). An ISA Action Plan and schedule for performing the ISA review was described in GNF-A's response to the NOV and the second milestone (fabrication) was scheduled for completion by July 31, 2011. This milestone was subsequently extended by approximately 30 days. On 8/30/11, GNF-A completed the ISA review for the fabrication area and has identified 125 existing safety controls that are now being designated as Items Relied On For Safety (IROFS). Implementation of the revised safety basis, IROFS and application of management measures to the new IROFS will be completed within 90 days per the ISA Action Plan. Because the revised ISA has designated existing safety controls as additional IROFS, GNF-A is making a report of this completion pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours." The NOV inspection report (70-1113/2010-013) was dated June 9, 2010 with an NOV response on July 23, 2010. Milestone #1 was reported in EN #46710 on March 30, 2011. This report concerns milestone #2 of 3. The licensee will notify the NRC Region 2 Project Manager, the State of North Carolina, and Hanover County. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.74 APP. A |  |  |  | 0 | 2011-08-31
47224 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-08-31 09:06 | 2011-08-31 12:02 | 2011-08-31 | TURBINE TRIP ON HI-HI STEAM GENERATOR LEVEL RESULTS IN AUTOMATIC REACTOR TRIP "While preparing Loop 2 Main Feed Reg Valve (MFRV) for maintenance, it was placed on its 'air gag' that maintained the MFRV in position, while any small changes in feed flow would be modulated by the associated Bypass Feed Reg Valve (BFRV). Approximately 5 minutes after the MFRV was placed on the air gag, with Steam Generator (S/G) level stable, control room operators observed S/G level start to increase. The operators observed for a short time to see if the associated BFRV would control the level change. When it became apparent that level was not being controlled automatically, the operators took manual control of the BFRV, eventually closing it all the way, and observed that S/G level was then increasing very slowly. While level was still slowly rising, two hi-hi level bistables actuated, generating a P-14 [hi-hi S/G level trip] signal which tripped the main turbine, which then caused an automatic reactor trip. As a result of the reactor trip, all systems functioned as required and there was nothing unusual or not understood." During the transient, no safeties, primary relief valves or secondary relief valves lifted. All control rods inserted into the core. Auxiliary Feed Water automatically initiated and is supplying the steam generators. Decay heat is being removed via the steam dumps to condenser. The grid is stable with all safety buses powered from offsite power via a normal shutdown electrical lineup. Unit 2 was unaffected by the trip. The licensee will be issuing a press release. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-08-31
47223 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-29 17:24 | 2011-08-30 17:04 | 2011-08-30 | MAINTENANCE INADVERTENTLY RENDERS CONTROL ROOM VENTILATION SYSTEM INOPERABLE "On August 29, 2011, at 1724 PDT, plant operators discovered that the Control Room Envelope (CRE) boundary required by Technical Specification (TS) 3.7.10, 'Control Room Ventilation System (CRVS),' lost its integrity. This was due to maintenance personnel removing a blank flange on the line to Unit 2 CRVS dampers MOD-2 and MOD-2A with the dampers inoperable. "On August 29, 2011, at approximately 1400 PDT, plant personnel completed maintenance on Unit 2 control room dampers MOD-2 and MOD-2A and planned to perform static testing of the CRE on the morning of August 30, 2011. Prior to reporting off the clearance, maintenance personnel removed a blank flange from the upstream side of the dampers. This blank flange was maintaining the integrity of the CRE boundary while dampers MOD-2 and MOD-2A were inoperable during the maintenance. Upon completion of maintenance on the dampers, the blank flange was removed with shift foreman authorization. Later, personnel recognized that the flange had been removed prematurely while dampers MOD-2 and MOD-2A were still inoperable. Personnel took required actions associated with TS 3.7.10 and re-installed the blank flange on August 30, 2011, at 0110 PDT. "The loss of the CRE boundary rendered the CRVS incapable of performing its specified safety function of mitigating the exposure of control room personnel to the consequences of an accident. "The cause of the event was inadequate coordination between maintenance personnel and plant operators to maintain the integrity of the CRE boundary. "Plant personnel notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-08-30
47222 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-20 10:00 | 2011-08-30 14:15 | 2011-08-30 | OFFSITE NOTIFICATION TO FEDERAL AGENCY REGARDING EXCAVATION ACTIVITIES "On April 16, 2011, a suspected buried pipe leak was identified in the plant yard. Subsequent investigation revealed that the source of the water was a leak in the Unit 1 Condenser Circulation Water (RC) intake pipe. In order to perform a repair, the ground in the vicinity of the pipe, including the toe of the dike berm, required excavation. McGuire Nuclear Station (MNS) site personnel recognized that excavating into the dike would require Federal Energy Regulatory Commission (FERC) involvement. Duke Hydro was contacted, and confirmed that the dike across the MNS intake is an extension of the Cowans Ford Dam and would require FERC authorization to dig into it. On the morning of April 20, 2011, Duke Hydro personnel contacted the FERC engineer assigned to Duke Energy's Cowans Ford Hydroelectric Development to seek FERC authorization for the excavation. Duke Hydro hosted a conference call later that same morning between FERC's Atlanta Regional Office and MNS site personnel to discuss the details of the situation and planned repairs. FERC later dispatched their personnel to the site to observe the repair effort. "10 CFR 50.72(b)(2)(xi) requires a 4-hour notification to be made for any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. º50.72(b)(2)(xi) further states that such an event may include an onsite fatality or inadvertent release of radioactively contaminated materials. "Although a phone call to an outside government agency (FERC) was made, Duke Energy made the decision at the time to not make a 4-hour notification to the NRC. This decision was based on the belief that 1) the RC leak and impact on the dike had no safety significance, 2) there were no concerns regarding protection of the environment, and 3) the situation did not involve an on-site fatality or an inadvertent release of radioactively contaminated materials. However, based upon how the matter was characterized in discussions between NRC and FERC, the NRC is not in agreement with the Duke Energy position. Therefore, the purpose of this phone call is to provide the necessary 10 CFR 50.72(b)(2)(xi) notification retroactively." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-30
47221 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-29 13:19 | 2011-08-30 12:34 | 2011-08-30 | PROGRAMMATIC DEFICIENCY IDENTIFIED IN FITNESS FOR DUTY PROGRAM "At 1319 [hrs. EDT on] 8/29/2011, a programmatic deficiency was reported involving the SSES [Susquehanna Steam Electric Station] Fitness For Duty (FFD) program and compliance with 10CFR26. Current contractual agreement with PPL vendor to perform Employee Assistance Program (EAP) counseling and treatment for self referrals does not require appropriate reporting to the utility as mandated by 10CFR26. "This event is reportable under 10CFR26.719(b)4, 'Any programmatic failure, degradation, or discovered vulnerability of the FFD program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program." The licensee has obtained an informal agreement by the vendor to report appropriate information until the contract can be amended. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2011-08-30
47220 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-08-29 13:00 | 2011-08-30 12:30 | 2011-08-30 | CRITICALITY ACCIDENT ALARM SYSTEM HORN DISCOVERED INOPERABLE "On 8/29/11, it was discovered during troubleshooting on an outdoor Criticality Accident Alarm System (CAAS) Data Acquisition Module (DAM #21), that the module had inadequate voltage to properly sound its local alarm horn. The module has been repaired and the system was returned to normal on 8/29/2011. "An investigation into the cause of the failure has been initiated. There are indications that the apparent cause of the failure is an AC to DC converter that had a component short circuit. "There were no active fissile material operations impacted by this failure. Consequently, no unsafe condition existed. "This event is being reported pursuant to the requirements of 10CFR70.50 (b)(2)." The licensee stated that the system had been tested satisfactorily within the last month. The licensee will notify state and local authorities. The licensee also plans to notify NRC Region 2 (Sykes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-08-30
47219 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2011-08-29 09:20 | 2011-08-30 12:01 | 2011-09-02 | 24-HOUR REPORT DUE TO FAILURE OF A GAMMA MONITORING SYSTEM "On 8/28/11 at 0920 hrs. PDT, electrical storms in the area caused power surges. The site backup power generators activated as designed. However, it was later discovered that a gamma monitor associated with the waste water treatment process was damaged. When the gamma monitoring system failed, the system interlocks shut the system down as designed. The system has remained down since that time and will remain down until repaired. "This report is being made per the requirements of 10 CFR 70, Appendix A(b)(4), (24-hr. report criteria), 'Any natural phenomenon that has affected the availability or reliability of one or more Items Relied On For Safety (IROFS)'. "An updated report with additional timeline information will be provided as the information becomes available. "SAFETY SIGNIFICANCE OF EVENTS: Low. The waste water treatment system was shut down as designed. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: The only potential pathway is gradual accumulation of uranium in the waste water treatment equipment over an extended period of time. "CONTROLLED PARAMETERS: Concentration is controlled. Maximum concentration in the equipment is estimated to be less than 1.5 grams of uranium per liter based on gamma monitor reading when the system shut down. "ESTIMATED AMOUNT/ENRICHMENT, FORM OF LICENSED MATERIAL: Facility is licensed for 5 wt% U-235. Normal system clean out results in about 120 grams of uranium. A minimum critical mass assuming spherical geometry is [much greater than normal system content]. "CORRECTIVE ACTIONS: System automatically shut down as designed and will remain down until the equipment is repaired and returned to service. * * * UPDATE AT 1214 EDT ON 09/02/11 FROM CALVIN MANNING TO S. SANDIN * * * The following information was received via email: "At approximately 0920 local time, 8/28/2011 and closely associated in time with both a thunderstorm and a test of various internal backup power generators, an operator at the Waste Water Treatment (WWT) facility noticed that the gamma monitors on two sand filters had ceased to function correctly. Apparently as an immediate result of this failure to function, the associated flows to the sand filters shut down automatically (normal fail-safe shutdown). The system has remained down since that time and will remain down until the gamma monitoring system is repaired. "This plant condition was brought to the attention of the HRR EHS&L staff on Tuesday 8/30/2011 at 0800 by an engineer responsible for the gamma monitoring system who was soliciting potential options to restore the system to service. "At 0901 local time AREVA's HRR EHS&L notified the NRC Operation's Center of this condition per the requirements of 10CFR70 Appendix A criterion (b) (4) (24 hour report) which requires reporting of any natural phenomenon that has or may have affected the intended safety function or availability or reliability of one or more items relied on for safety. "Safety Significance of Event: The safety significance of this event is low. The feed and discharge to and from the waste water treatment sand filters were shut down as designed when the gamma detectors failed. "Potential Nuclear Criticality Pathways Involved: The only potential pathway is for gradual build up / accumulation of uranium in the WWT equipment over an extended period of time (many years). "Controlled Parameters (Mass, Moderation, Geometry, Concentration, Etc.): Uranium concentration is controlled. The maximum concentration of uranium in the equipment is estimated to be less than 1.5 g U/L based on gamma monitor readings just prior to the system being shut down. "Estimated Amount, Enrichment, Form of License material (Includes process limit and % worst case critical mass): The facility is licensed for 5 wt.% U-235. Normal system clean out results in about 120 grams of uranium. A minimum critical mass of uranium at 5 wt.% U-235 assuming spherical geometry is about 38,000 grams. "Nuclear Criticality Safety Control(s) or Control System(s) and description of the failures or deficiencies: No control system failures occurred. "Corrective Actions to Restore Safety Systems and When Each Was Implemented: The system automatically shut down as designed and will remain down until the equipment is repaired, functionally tested, and returned to service." Notified R2DO (Sykes) and NMSS (Pstrak). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NAT PHENOM AFFECTING SAFETY | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(4) |  |  |  | 0 | 2011-08-30
47218 | 0 | NEW JERSEY DEPT OF ENVIRONMENT PROT |  |  |  |  | 2011-08-29 03:00 | 2011-08-30 11:09 | 2011-08-30 | AGREEMENT STATE - LOST GADOLINIUM CAMERA SOURCES The following report was received via facsimile. "The (New Jersey) (Bureau of Emergency Response) BER received a call from the (Radiation Safety Officer) RSO at Trinitas Hospital at 1500 (EDT) on Monday August 29, 2011. This past Friday, while performing an inventory of their sealed sources, it was discovered that two (Gadolinium) Gd-153 camera sources were missing. These sources were dated March 2002, with an initial activity of 250 mCi apiece. (The half-life of Gd-153 is 241 days, therefore each source had decayed to ~0.01 mCi). The RSO stated that these sources were never used on the camera, and had been in storage since 2002. During the last routine inventory (July 2011) the sources were accounted for. Friday's inventory was being conducted as a result of a recent cleanup of the storage area. The RSO indicated that hospital staff conducted thorough searches of the hospital on Friday, as well as over the weekend, but have not found the sources. It was also indicated that the chief nuclear medicine technologist, who was involved in the cleanup, is currently overseas until September 7. When he returns, the RSO will discuss with him to see if he has knowledge of the location of these sources." The search and investigation is still ongoing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-09-02
47217 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-08-06 08:20 | 2011-08-30 10:56 | 2011-08-30 | AGREEMENT STATE REPORT - GAUGE RUN OVER BY EXCAVATOR "Kentucky Radiation Health Branch was notified on 08/08/2011, by a representative from Patriot Engineering and Environmental, Inc. of a vehicle running over a portable gauge on Saturday morning, 08/06/2011. The gauge was run over by an excavator during backfill operation. The gauge is identified as Humboldt Model 5001 EZ, serial no. 3260, containing 11 mCi of Cs-137 and 44 mCi of Am-241/Be. Surveys of the damaged gauge taken by the licensee indicated that the source had not been breached and that there was no leakage." Kentucky Event Report ID No: KY110006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-09-02
47216 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2011-08-29 16:00 | 2011-08-29 19:05 | 2011-08-29 | AGREEMENT STATE - LOST IODINE-129 CALIBRATION SOURCE The following report was received from the Colorado Department of Public Health and Environment via facsimile: "The Colorado Department of Public Health and Environment received telephone notification of a lost Iodine-129 sealed source (~24.8 microCuries; Assay date: 6/1/1992) on 8/29/2011 at approximately 4:00 p.m. The University of Colorado, a research licensee, reported that a campus inspection conducted on 8/12/2011 identified a missing gamma counter calibration source. As of 8/29/2011, all efforts to locate the source have failed. It is suspected that the source was discarded with an entire sample rack that was removed from the counter for disposal at some time within the last six months. The source was used for reference in a gamma counter and was an epoxy sealed type source with a small vial geometry. "The licensee will submit a written report with more detail within the next few days. "No other details are available at this time." Colorado Report: CO11-I11-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2011-09-01
47215 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-29 12:00 | 2011-08-29 15:07 | 2011-08-29 | EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE FOR MAINTENANCE "At 1200 hours on 08/29/11, the ERDS (Emergency Response Data System) was removed from service for a planned maintenance outage on a site network server. The duration of work, which affects ERDS for Brunswick Unit 1 and Unit 2, is expected to be approximately four (4) hours. Since the ERDS will be unavailable during this maintenance activity, this is considered a Loss of Emergency Assessment Capability and reportable under 10 CFR 50.72(b)(3)(xiii). An update will be provided when the scheduled work has been completed and ERDS has been restored. "ERDS is a direct near real-time electronic data link between the licensee's onsite computer system and the NRC Operations Center that provides for the automated transmission of a limited data set of selected parameters. ERDS supplements the existing voice transmission over the Emergency Notification System (ENS) by providing the NRC Operations Center with timely and accurate updates of a limited set of parameters from the Brunswick Plant installed onsite computer system in the event of an emergency. During the time ERDS is unavailable, emergency plan contingency measures are in place to transmit data, if required. "The NRC Senior Resident Inspector will be notified of this evolution and the planned return to service of the system." * * * UPDATE AT 2152 EDT ON 8/29/11 FROM MILLER TO HUFFMAN * * * The licensee reports that the ERDS server replacement maintenance has been completed and ERDS capability was re-established at 2147 EDT on 8/29/11. The licensee will notify the NRC Resident Inspector. R2DO (Widmann) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-29
47214 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-08-28 10:00 | 2011-08-28 16:55 | 2011-08-28 | 24 HOUR NOTIFICATION OF POLLUTION DISCHARGE PERMIT NOTIFICATION "On August 28, 2011 at approximately 1000 EDT the Indian Point common discharge canal was reported to be overflowing. The overflow condition was caused by the elevated river water levels experienced during Hurricane Irene. The site SPDES (State Pollution Discharge Elimination System) permit requires the canal discharge to be subsurface. Since the overflow was not a subsurface discharge it constituted a SPDES permit violation. There was no failure or malfunction of the outfall structure, and by 1430 EDT river level had lowered enough that the discharge canal was again operating within normal limits. "The resident inspector has been notified. New York State Department of Environment Control has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2011-08-28
47213 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2011-08-28 08:58 | 2011-08-28 11:13 | 2011-08-28 | EMERGENCY SIRENS OUT OF SERVICE "Oyster Creek has lost 10 sirens in the Emergency Plan Zone. Communications with the Ocean County Office of Emergency Management has been conducted to inform them of the outage." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-28
47212 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-08-29 06:00 | 2011-08-28 10:05 | 2011-08-29 | TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE ACTIVITY "On 8/29/11, Monticello Nuclear Generating Plant's Technical Support Center (TSC) power supply will be isolated to perform a planned maintenance activity. The maintenance activity requires implementation of compensatory measures to maintain TSC functions during the activity. The compensatory measures include having the Emergency Director report to the Control Room and co-locating the remaining TSC staff at the EOF should an event be declared requiring ERO activation. The ERO has successfully previously demonstrated the ability to implement these compensatory measures. The maintenance activity is scheduled to be completed with the TSC returned to full functionality by the end of the dayshift on 8/29/11. The site Emergency Response Organization has been notified of the maintenance activity and instructed on the planned compensatory measures to be implemented during the activity. The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1735 EDT ON 8/29/11 FROM ANDERSON TO HUFFMAN * * * The licensee reports that TSC maintenance activities were completed at 1308 CDT and that the TSC was declared fully operational at 1545 CDT on 8/29/11. The licensee has notified the NRC Resident Inspector. R3DO (Kunowski) notified. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-28
47211 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2011-08-28 05:15 | 2011-08-28 06:35 | 2011-08-28 | EMERGENCY SIRENS OUT OF SERVICE "PBAPS [Peach Bottom Atomic Power Station] Control Room was notified of a loss of greater than 25% of sirens after severe storms in the area associated with Hurricane Irene. 51 of 97 Emergency Plan Zone (EPZ) sirens are unavailable in York County and Hartford County. Actions are currently being taken to restore unavailable sirens." The licensee notified Pennsylvania and Maryland Emergency Management and York and Harford Counties. The licensee notified the NRC Resident Inspector. | 100 | 91 | 0 | 100 | 91 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-28
47210 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-08-27 20:30 | 2011-08-28 03:38 | 2011-10-13 | INVALID AUTOMATIC ACTUATION OF AN EMERGENCY DIESEL GENERATOR "At 2130 [EDT] on August 27, 2011, an automatic actuation of the Unit 1 Train A emergency diesel generator occurred due to an actuation signal from the load sequencer. The Train A 4160 kV emergency bus transferred to the emergency diesel generator and all Train A emergency loads required for Mode 2 started and sequenced onto the Train A 4160 KV emergency bus except the 480 volt center breaker to the bus E1A2 that did not close. The load sequencer is designed upon the receipt of a safety injection actuation and/or loss of offsite power to provide a signal to strip loads from the 4160 kV emergency bus and then, in sequence, to re-energize the associated 480 volt buses and to load engineering safety feature components onto the 4160 kV and associated 480 volt emergency buses in a predetermined sequence. Per 10 CFR 50.72(b)(3)(iv)(B), additional emergency safety features loads that actuated were the Train A reactor containment fan coolers and auxiliary feedwater system. "Unit 1 remains critical at 100 percent power. No emergency core cooling system injection occurred into the reactor coolant system. "The event occurred during surveillance testing when the Train A sequencer was taken from the AUTO Test position to the local position. It is not understood why the actuation occurred. In addition, it is not understood why the 480 volt load center breaker to the bus E1A2 did not close. "The 480 volt bus E1A2 was re-energized at 2308 [EDT] on August 27, 2011. The Train A 4160 kV bus was restored to the offsite power source at 0150 [EDT] on August 28, 2011 and the Train A emergency diesel generator and engineering safety features loads were restored to their normal condition at 0201 [EDT] on August 28, 2011. "With the Train A sequencer non-functional, the following Train A components are inoperable: 1) High Head Safety Injection Pump 1A; 2) Low Head Safety Injection Pump 1A; 3) Containment Spray Pump 1A; 4) RCFC [Reactor Containment Fan Cooler] Fan 11A; 5) RCFC Fan 12A; 6) Component Cooling Water Pump 1A; 7) Essential Cooling Water Pump 1A; 8) Aux Feedwater Pump 11; 9) Control Room/Elect. Aux Bldg HVAC; 10) Ess [Essential] Chiller 12A; and 11) ESF Diesel Generator 11. "Although these components will not automatically start on a safety injection signal or loss of offsite power, these loads can be manually actuated. Engineered Safety Features Trains B and C remain operable." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 10/13/11 AT 1221 EDT FROM MORRIS TO HUFFMAN * * * The licensee is updating this event report to retract the originally reported valid specified system actuation and report it instead as a 60-day invalid specified system actuation report made by telephone: "This update is a 60-day telephone notification in lieu of a written licensee event report being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1). "This event was originally reported per 50.72(b)(3)(iv)(A) as a valid actuation of the Unit 1 Train A emergency diesel generator and sequencing of Mode II (Loss of Offsite Power) emergency loads. The actuation occurred during surveillance testing when the Train A load sequencer was taken from the AUTO test position to the local position. Subsequent investigation has determined that the actuation occurred due to a faulty integrated chip within the sequencer's load sequence auto test module, and was not due to sensed or simulated plant conditions that would require a Mode II actuation. Unit 1 was at 100% power and no loss of offsite power occurred. "The Train A equipment response to this invalid actuation is described in the original notification information provided on 08/28/2011. "Additionally, the 10CFR50.72 Notification originally reported under Event Number 47210 is being retracted, since the actuation has been determined to be not valid." The licensee will notify the NRC Resident Inspector. R4DO (Whitten) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-08-28
47209 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-08-27 20:21 | 2011-08-28 02:41 | 2011-08-28 | SHUTDOWN COOLING TEMPORARILY ISOLATED "In accordance with 10 CFR 50.72 (b)(3)(v)(B) this event notification is being made to report an event that could have prevented the fulfillment of the safety function to remove residual heat. On August 27, 2011, following refueling, the plant was shutdown in Mode 4 with reactor coolant temperature being maintained 100-120 degrees F. Reactor coolant temperature was being controlled with RHR B operating in the Shutdown Cooling mode. At 2021 [EDT], an equipment failure caused a loss of Reactor Protection System (RPS) B resulting in a closure of RHR-V-9 (RHR Shutdown Cooling Inboard Isolation Valve), interrupting shutdown cooling flow. Operators transferred RPS B to the alternate power supply and restored RHR B to shutdown cooling. Shutdown cooling was out of service for 34 minutes. "During the 34 minute interruption of shutdown cooling, reactor coolant temperature rose from 107 degrees F to 111 degrees F. Following restoration of shutdown cooling, reactor coolant temperature was restored. All containment isolations resulting from the loss of RPS B occurred as expected. Further investigation is ongoing to determine the cause of the equipment failure that caused the loss of RPS B." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-08-28
47208 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2011-08-27 23:02 | 2011-08-27 23:27 | 2011-08-28 | UNUSUAL EVENT - TRANSFORMER EXPLOSION NEAR TURBINE BUILDING "At 2248 on 8/27/2011, the Unit 1 Reactor experienced an automatic trip due to loss of load. This trip occurred due to a phase to phase short on the main generator output step-up transformer that resulted from a large section of turbine building siding breaking loose in high winds from Hurricane Irene and impacting the transformer. This impact resulted in an explosion (briefly until the trip removed power from the impact area) which met emergency action level declaration criteria A.U.6.2.2, 'Unanticipated explosion within Protected Area resulting in visible damage to permanent structures or equipment.' The Unusual Event was declared at 2302, 8/27/2011. Follow-up investigation determined no fire resulted from the explosion. "Following the trip, Emergency Procedure, EOP-0, 'Post Trip Immediate Actions' was implemented. All safety functions were met during EOP-0 indicating an uncomplicated reactor trip response, allowing transition to EOP-1, 'Reactor Trip,' at 2300, 8/27/2011. During implementation of EOP-1, it was noted that #14 Containment Air Cooler had stopped running, as had #21 and #24 Containment Air Coolers on Unit 2. This was investigated and it was determined they had stopped running due to an instantaneous voltage drop that had occurred on the site distribution system during the phase to phase short event. This short duration voltage drop caused the Containment Air Coolers' controller to drop out and secure them. They were restarted without issue. "At 2400, 8/27/2011, numerous alarms on the 1A DG started to be received. These were investigated and it was found that water was intruding down the DG exhaust piping resulting in a DC ground. Based on these indications the 1A DG was declared inoperable and appropriate technical specifications implemented. "Besides the above issues plant response was as expected and EOP-1 was exited at 0130, 8/28/2011. [Procedure] OP-4, 'Shutdown from Power Operation to Hot Standby,' was implemented at that time. All control rods fully inserted on the reactor trip. The plant is in a normal post-trip electrical lineup. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM GREGG BUCKMASTER TO PETE SNYDER AT 0811 EDT ON 8/28/11 * * * At 0755 EDT the licensee exited the Unusual Event condition based on the fact that they were able to inspect the area in the daylight and were satisfied that they knew the extent and nature of the damage. The licensee will notify the NRC Resident Inspector. Notified R1 IRC (Dentel), DHS (Hill), FEMA (Via). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | MD | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2011-08-27
47207 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-08-27 19:15 | 2011-08-27 21:06 | 2011-09-02 | EMERGENCY SIRENS OUT-OF-SERVICE "Sirens in St. Mary's and Calvert counties are out of service exceeding the minimum required of 19. Currently 44 sirens are out of service due to local power outages caused by the storm. Compensatory measures are in place for the affected counties. Route alerting will be used if necessary." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1730 EDT ON 09/02/11 FROM TOM JONES TO S. SANDIN * * * As of 1655 EDT on 9/2/11, all 72 emergency sirens have been returned to service. The licensee informed the NRC Resident Inspector. Notified R1DO (DiPaolo). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-27
47206 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-27 01:56 | 2011-08-27 03:25 | 2011-08-28 | ACTUAL UNAUTHORIZED ENTRY PAST VEHICLE ACCESS POINT Actual entry of unauthorized person past the controlled access point. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DANNY BRADFORD TO PETE SNYDER AT 0410 EDT ON 8/27/11 * * * The individual was identified with local law enforcement assistance and determined not to be a threat. | 61 | 100 | 0 | 61 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-08-28
47205 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-27 01:56 | 2011-08-27 03:25 | 2011-08-27 | UNUSUAL EVENT DECLARED DUE TO ENTRY INTO EAL HU 4-1 The licensee declared a Notice of Unusual Event per emergency plan condition HU 4-1 due to a security event. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DANNY BRADFORD TO PETE SNYDER AT 0410 EDT ON 8/27/11 * * * The Notice of Unusual Event has been terminated. Contact the Headquarters Operations Officer for details. Notified: R4DO (Haire), NRR (Bahadur), DHS (Knox), FEMA (Blankenship). | 61 | 100 | 0 | 61 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-28
47204 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-08-24 17:30 | 2011-08-26 17:00 | 2011-08-26 | AGREEMENT STATE - TROXLER GAUGE DAMAGED BY CONSTRUCTION EQUIPMENT The following report was received from the Kentucky Radiation Health Branch via facsimile: "A Troxler model 3430 belonging to Gregg Laboratories, Inc, containing a Cs-137 source and a Am-241:Be source was run over by a D6 bull dozer. The company was working at a job site on the campus of Asbury College in Wilmore, KY at the time of the accident. The technician using the gauge was calibrating the gauge on the source block, source rod not exposed, when the dozer ran over the device. The technician set a 50 foot boundary and called the RSO. The RSO called the Wilmore Fire Department (FD) who responded but did not have a survey meter. The Wilmore FD called the Nicholasville, KY FD who then responded. The Nicholasville FD surveyed the damaged gauge with a GM detector and detected radiation but no contamination. Nicholasville FD called CMC Environmental Remediation in Nicholasville, KY who sent a response team to recover the gauge. The gauge was double bagged, put in a 55 gallon drum, surrounded by dirt removed from the site of the accident and everything surveyed by the Nicholasville FD with a Ludlum survey instrument equipped with a GM pancake probe. All survey readings of the site, the dozer, the equipment used to remove the gauge, and surrounding vicinity read background readings of 8 micro-R/hr. Based on [these] findings, [it is] believed that no breach of either source occurred and that there is no radioactive contamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-08-31
47203 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-08-26 16:30 | 2011-08-26 16:56 | 2011-08-26 | HURRICANE NOTIFICATION PER TECHNICAL REQUIREMENTS MANUAL "A hurricane is within 500 nautical miles from Indian Point Energy Center with wind speed in excess of 87 knots. The National Weather Service has issued a hurricane warning for a hurricane with wind in excess of 87 knots (approximately 100 mph) within 500 nautical miles of the facility. Per the Technical Requirements Manual a prompt report shall be made to the NRC Incident Response Center within 1 hour of receipt of that hurricane warning." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2011-08-26
47202 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-08-26 12:36 | 2011-08-26 16:45 | 2011-08-26 | TECHNICAL SUPPORT CENTER UNAVAILABLE FOR EMERGENCY RESPONSE "During performance of IC-PM-VA-0200, Preventive Maintenance Air Flow Measurement of TSC Air Filter Unit VA-119, it was discovered that the required flow-rate of 2700 cfm and minimum overpressure of 0.1 inches of water in the TSC could not be achieved. Troubleshooting on VA-107, TSC Air Handling Unit, is in progress. "This condition renders the Technical Support Center unavailable for Emergency Planning Responses. Approved compensatory actions are to relocate personnel to alternate facilities if required. This condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for Loss of Emergency Preparedness Capabilities." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-26
47201 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-08-26 13:00 | 2011-08-26 16:23 | 2011-09-09 | UNANALYZED CONDITION BASED ON SEISMIC ACTIVITY THAT POTENTIALLY EXCEEDED DESIGN BASIS EARTHQUAKE MAGNITUDE "On August 23, 2011 at 1351 hours, North Anna Power Station experienced a seismic activity event which resulted in a loss of offsite power and automatic reactor trip of both units. At 1403 hours, an Alert was declared, based on Shift Manager judgment, due to significant seismic activity on the site. Subsequent to the earthquake, both units were stabilized and offsite power was restored. Following the event, seismic data was retrieved from the installed monitoring system and shipped to the vendor to determine the response spectrum for the event. On August 26, 2011 at 1340 hours, initial reviews of the data determined that the seismic activity potentially exceeded the Design Basis Earthquake magnitude value above 5 Hz. Therefore, this is reportable per 10CFR50.72(b)(3)(ii) (B) for the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "North Anna Unit 1 is currently in Cold Shutdown with the Residual Heat Removal System providing core cooling. North Anna Unit 2 is currently in Hot Shutdown and will be taken to Cold Shutdown with the Residual Heat Removal System providing core cooling. No significant equipment damage to Safety Related system (including Class 1 Structures) has been identified through site walk-downs nor has equipment degradation been detected through plant performance and surveillance testing following the earthquake. Therefore, there is reasonable assurance that the Safety Related systems are fully functional. "The Spent Fuel Pit cooling system also remains fully functional and the temperature of the Spent Fuel Pit remained unchanged during the event. "The vendor will complete the analysis of the seismic data and this information will be utilized to address the long term actions following the earthquake." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DON TAYLOR TO PETE SNYDER AT 1739 EDT ON 9/9/11 * * * "This is an update to EN 47201 reported on 8/26/2011 where It was reported that North Anna potentially exceeded the Design Basis Earthquake (DBE) magnitude value above 5 Hz. "The vibratory motion from the 5.8 magnitude earthquake were recorded in all three orientations at several locations in the plant using two types of instruments: the Engdahl scratch plates that record 12 discrete spectral accelerations between 2 and 25.4 Hz, and the Kinemetrics analog recorders that recorded time histories of the accelerations. Based on evaluation of recorded plant data, it is concluded that the Central Virginia earthquake of 8/23/2011 exceeded the spectral accelerations for the Operational Basis Earthquake (OBE) and DBE of North Anna Plant. "Extensive actions are underway to inspect. evaluate, test, and repair if necessary. systems and components to ensure they are capable of performing their required functions. To date, no significant damage to safety related structures, systems or components (SSC) has been identified." The licensee notified the NRC Resident Inspector. Notified R2DO (Rich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Cold Shutdown | Hot Shutdown |  | Cold Shutdown | Hot Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-08-26
47200 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-08-26 13:45 | 2011-08-26 16:22 | 2011-08-26 | PRESS RELEASE REGARDING LICENSEE HURRICANE PREPARATION ACTIVITIES "At approximately 1345 EDT, on 8/26/2011, Entergy Corporation issued a press release regarding ongoing preparations at Vermont Yankee Nuclear Power Station for hurricane Irene currently located approximately 300 miles SSW of Cape Hatteras, NC. "The purpose of the press release is to reassure the public regarding the safety and security of the facility and the extent of preparations that are in progress. Plant operation is not currently impacted, and the release of this information does not indicate a current threat to the facility or the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-26
47199 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-08-26 13:45 | 2011-08-26 15:02 | 2011-08-26 | PRESS RELEASE RELATED TO HURRICANE PREPARATIONS AT THE PILGRIM SITE "At approximately 1345 EDT, on August 26, 2011, Entergy Corporation issued a press release regarding ongoing preparations at Pilgrim Station for hurricane Irene currently located 300 miles SSW of Cape Hatteras, North Carolina traveling in a northerly direction at approximately 14 miles per hour. The purpose of the press release is to re-assure the public regarding the safety and security of the facility and the extent of preparations that are in progress. Current plant operation is not impacted and the release of this information does not indicate a current threat to the facility or the health and safety of the public. "The licensee has notified the NRC Resident Inspector. "This four (4) hour report is being made in accordance with 10 CFR 50.72(b)(2)(xi). "State and local notifications will be made coincident with the Issuance of this Event Report." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-26
47198 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-08-25 16:10 | 2011-08-25 17:14 | 2011-08-25 | NOTIFICATION TO OFFSITE AGENCY REGARDING AN ONSITE OIL SPILL "At 1610 EDT on August 25, 2011 the Virginia Department of Environmental Quality was notified of an oil spill that occurred at 1900 EDT on August 24, 2011. The spill was approximately 150 gallons to the gravel outside the North Anna Unit 2 Turbine Building. The event occurred while purging CO2 from the Unit 2 Main Generator with air. Standing oil from the gravel was pumped to barrels and oil soaks were applied to the remaining oil. Clean up of the gravel areas continued." The NRC Resident Inspector has been notified in addition to the state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-25
47197 | 0 | INTEGRITY TESTLAB |  |  |  |  | 2011-08-24 09:17 | 2011-08-25 11:50 | 2011-08-25 | RAD WORKER DOSIMETRY IN EXCESS OF EXPOSURE LIMITS "At 0917 EDT on 8/25/11, Integrity Testlab received a facsimile notification from Integrity Testlab's dosimeter processor, Landauer, that an assistant radiographer's July 2011 dosimeter had received/recorded 9.587 R. "According to the assistant radiographer, his dosimeter had come off his work clothes during radiographic operations on 7/29/11. When he discovered that his film badge was not on his work clothes, he looked for and found the dosimeter near the exposure device. He believes that his dosimeter had 4 or 5 exposures during the time the dosimeter was near the exposure device. "The exposure time for each exposure was about 40 seconds in length. On 8/2/11, the assistant radiographer informed the RSO what had occurred on 7/29/11. The RSO instructed the assistant to complete a statement on what transpired on that date. The RSO verified the assistant's statement with the radiographer. "The RSO verbally instructed the assistant how to best secure the dosimeter on the rate alarm meter pouch and to periodically check that all required dosimetry remains on his person during radiographic operations. "The RSO reviewed all daily pocket dosimeter readings recorded for the month of July. He determined that the assistant had performed radiography for a total of 9 days in July. The RSO also noticed that he had performed radiography with the same radiographer 8 of those 9 days. The radiographer's pocket dosimeter reading recorded 200 mR, while his assistant's daily readings totaled 201 Mr. The RSO contacted Landauer in order to get the radiographer's July recorded dosimeter results and Landauer verbally informed the RSO that the total was 87mR for the month of July for the radiographer. "After reviewing all documentation, the RSO believes that the assistant's dosimeter was accidently exposed to excessive radiation and that this was not an actual overexposure. Furthermore, the RSO intends to inform all personnel involved in Integrity Testlab's Radiation Safety Program about this event and to instruct the personnel on the importance of securing their dosimetry on their person. "An 880 Sigma device was involved during this occurrence and it had contained Ir -192, 55.5 Ci." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | DE | MAT | GEN | 20.2202(b)(1) |  |  |  | 0 | 2011-08-25
47196 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-08-25 01:18 | 2011-08-25 01:48 | 2011-08-28 | UNUSUAL EVENT DECLARED DUE TO AN AFTERSHOCK EARTHQUAKE On August 25th at 0118 EDT, North Anna Power Station declared an Unusual Event due to seismic activity onsite (EAL HU 1.1). Both units are currently shutdown and electrical power is being supplied from offsite. There were no personnel injuries. There was no radiological release. Site structure and system inspections are in progress. No damage has been identified. The NRC Resident Inspector and state and local authorities have been notified. * * * UPDATE FROM JOHN BALTOR TO ERIC SIMPSON AT 1215 EDT ON 8/25/11 * * * At 1149 EDT another minor tremor was felt at the station. No geological information is available at this time. There is no immediate indication of any equipment damage. Walkdowns are being performed at this time. North Anna Emergency Management indicated that there was currently no plan to secure from the Notification of Unusual Event until there is sufficient indication that the station will not experience any additional aftershocks to prevent having to re-enter an emergency status once exited. The current status of North Anna, Unit 1 is Mode 5. Unit 2 is in Mode 3 in preparation for cool down. The licensee will verify that the NRC Resident Inspector is notified. Notified IRD (Marshall), NRR (Thorp), and R2DO (Widmann). * * * UPDATE AT 1546 EDT ON 8/28/11 FROM LINDNER TO HUFFMAN * * * The licensee has exited from its unusual event at 1536 EDT on 8/28/11 based on the cessation of any further seismic activity. The licensee has notified appropriate state and local authorities and will notify the NRC Resident Inspector. Notified R2DO (Widmann), NRR (Bahadur), IRD (Marshall), FEMA (Vitale) and DHS (Hill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Hot Standby |  | Cold Shutdown | Hot Standby |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-25
47195 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2011-08-23 15:30 | 2011-08-23 23:10 | 2011-09-20 | CREFS WAS DECLARED INOPERABLE "This telephone report is being made in accordance with 10 CFR 50.72(b)(3)(v) as a loss of safety function for a single train safety system. On August 23, 2011 at 1530 CDT, the clevis pin that connects the valve with the air operator was found not fully inserted on the Control Room HVAC Emergency Bypass System Inlet Valve, HV-AO-271 AV. This valve is normally closed and opens in response to a Group 6 isolation signal to align the Control Room Emergency Filtration System) (CREFS) to outside air. A retaining clip at one end of the pin was found to be missing, allowing the pin to partially back out of the clevis. The pin was found engaged with half of the clevis. This condition resulted in declaring CREFS inoperable at 15:30 CDT, and CNS entered LCO 3.7.4 Condition A which requires the CREF system to be restored to OPERABLE status in 7 days. The cause of the displaced clevis pin is under investigation." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM RANDY KOUBA TO JOE O'HARA AT 1406 EDT ON 9/20/11 * * * "This notification is being made to retract Event Notification EN# 47195 which reported a loss of safety function for a single train safety system due to the unplanned inoperability of the Control Room Emergency Filtration System (CREFS). CREFS was declared inoperable on August 23, 2011 per LCO 3.7.4 due to finding a clevis pin not fully inserted on the valve operator for the Control Room HVAC Emergency Bypass System Inlet Valve IIV-AOV-271AV. This normally closed valve opens on a Primary Containment Group 6 Isolation signal to align CREFS to outside air. The retaining clip at one end of the pin was found missing which allowed the pin to partially back out of the clevis. "Cooper Nuclear Station (CNS) recently completed its trouble shooting of the as-found condition of the pin and a subsequent evaluation of its ability to withstand seismic loading. CNS determined that CREFS would have been able to fulfill its safety function. The clevis pin was shown via testing to remain engaged when the valve was stroked. The seismic evaluation showed that the maximum seismic force is less than one-tenth of the estimated force required to remove the pin, and consequently it is not credible that the pin would have become disengaged in a seismic event. CREFS did not lose the ability to perform its safety function." The NRC Resident Inspector has been notified. Notified the R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-08-23
47194 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-23 14:24 | 2011-08-23 14:33 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "At 1424 [hrs. EDT] on Tuesday, August 23, 2011, an Unusual Event was declared for Unit 1 and Unit 2 based on Emergency Plan criterion N-1, 'Natural of Destructive Phenomena Inside the Protected Area'. "The Unusual Event was declared following detection of ground motion by persons on site with confirmation based on United States Geological Survey information. Plant operation was not impacted by the event. Site structure and system inspections are in progress in accordance with the Abnormal Operating Procedure for earthquake. No damage has been identified. "In accordance with Emergency Plan procedures, notifications of Berrien County and State of Michigan were completed. The licensee has notified the NRC Senior Resident Inspector. A follow-up notification will be made after the Unusual Event is terminated. "This notification is being made in accordance with 10 CFR 50.72 (a)(1)(i) due to declaration of an emergency class. " * * * UPDATE FROM SCOTT BURNS TO HOWIE CROUCH AT 1543 EDT ON 8/23/11 * * * "A press release has been issued regarding the seismic event. This notification update is being made in accordance with 10 CFR 50.72 (b)(2)(xi) for news release or notification of other government agency. Notifications were made to the following local media: St. Joseph Herald Palladium, South Bend Tribune, Niles Daily Star, WSJM Radio, WNDU TV, WSBT TV, and WSJV TV. Notification was also made to the Platt News Service. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT BURNS TO ERIC SIMPSON AT 1859 EDT ON 8/23/11 * * * "The Unusual Event due to Seismic Event was terminated at 1723 EDT following an examination of plant systems which revealed no damage due to the seismic event. A press release has been issued regarding the termination of the Unusual Event. This notification update is being made to notify of the Unusual Event termination and also notify of the press release describing the Unusual Event termination in accordance with 10 CFR 50.72 (b)(2)(xi) for news release or notification of other government agency. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R3DO (Passehl), IRD (Gott), DHS (Flinter), FEMA (Via), USDA (Kraus), and DOE (Bailey). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-08-23
47193 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2011-08-23 14:06 | 2011-08-23 15:27 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT The licensee declared a Notification of Unusual Event (NOUE) under EAL HU1.1 based on an earthquake felt at the plant with confirmation by the National Earthquake Center. They have made state and local notifications and notified the NRC Resident Inspector. * * * UPDATE ON 08/23/11 AT 1810 EDT FROM AL BOSTIC TO HOWIE CROUCH * * * The licensee has terminated from the NOUE at 1757 EDT. The termination basis was that no safety equipment was impacted by the earthquake and walkdowns of plant safety equipment was complete. The licensee has notified the NRC Resident Inspector and state and local authorities Notified R2 IRC (Franke), IRD (Gott), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47192 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-08-23 14:00 | 2011-08-23 14:42 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "On 8/23/11 at 1400 hrs. EDT, Hope Creek and Salem generation stations declared a common site Unusual Event in accordance with EAL 9.5.1.a, due to an earthquake felt by onsite personnel within the protected area. The plant is operating at 100% power with no significant anomalies noted. Walkdowns of safety related areas are currently in progress. All ECCS systems are available and in standby alignment." The licensee has notified the NRC Resident Inspector and state and local authorities. (See also EN #47191). * * * UPDATE FROM MARK SCHWARTZ TO HOWIE CROUCH AT 1639 EDT ON 8/23/11 * * * "Initial walkdowns are complete with no anomalies noted. Detailed walkdowns of all rooms and areas are in progress with estimated completion time of 1900 hrs." The licensee has notified the NRC Resident Inspector. Notified R1 IRC (Dentil). * * * UPDATE FROM MARK SCHWARTZ TO HOWIE CROUCH AT 1941 EDT ON 8/23/11 * * * Hope Creek and Salem have terminated their Notification of Unusual Event. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1DO (Krohn), IRD (Morris), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47191 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-23 14:00 | 2011-08-23 14:42 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "On 8/23/11 at 1400 hrs. EDT, Hope Creek and Salem generation stations declared a common site Unusual Event in accordance with EAL 9.5.1.a due to an earthquake felt by onsite personnel within the protected area. The plants are [both] operating at 100% power with no significant anomalies noted. Walkdowns of safety related areas are currently in progress. All ECCS systems are available and in standby alignment." The licensee has notified the NRC Resident Inspector and state and local authorities. (See also EN #47192). * * * UPDATE FROM MARK SCHWARTZ TO HOWIE CROUCH AT 1639 EDT ON 8/23/11 * * * "Walkdowns are in progress and are approximately 40% complete with no anomalies noted. Estimated completion time of 1900 hrs." The licensee has notified the NRC Resident Inspector. Notified R1 IRC (Dentil). * * * UPDATE FROM MARK SCHWARTZ TO HOWIE CROUCH AT 1941 EDT ON 8/23/11 * * * Hope Creek and Salem have terminated their Notification of Unusual Event. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1DO (Krohn), IRD (Morris), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47190 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-08-23 14:01 | 2011-08-23 14:23 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "At 1401 hrs. EDT on 8/23/11, TMI (Three Mile Island) declared an Unusual Event due to a threshold seismic condition (HU5) earthquake. The earthquake was felt at the plant. No equipment damage has been identified." No personnel injuries were reported. The licensee has notified the NRC Resident Inspector and state and local authorities. * * * UPDATE FROM JOE SHUFFNER TO JOHN SHOEMAKER AT 1744 EDT ON 8/23/11 * * * "The Unusual Event declared at 1401 EDT due to the ground motion felt at the site has been terminated at 1730 EDT. Walkdowns have been performed and no equipment damage has been identified. The plant remains in a stable condition at 100% power. Offsite power and diesel generators were verified to be unaffected by the event." The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1 IRC (Dentil), IRD (Gott), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47189 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-08-23 14:04 | 2011-08-23 14:35 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT The licensee declared a Notification of Unusual Event under EAL HU1.1 for seismic activity felt by station personnel. Both units will remain at 100% power. No equipment failures have been identified. No Reactor Coolant System or Steam Generator leakage identified. The licensee will upgrade this event if damage to safety-related equipment is identified. The plant is accessible. Engineering walkdowns have been initiated in the station, switchyard and intake structures. The licensee has notified the NRC Resident Inspector and state and local authorities. * * * UPDATE AT 1752 ON 08/23/11 FROM DAVID BRIDGES TO JOHN SHOEMAKER * * * License terminated the Unusual Event. Notified R2 IRC (Franke), IRD (Gott), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47188 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2011-08-23 14:05 | 2011-08-23 14:35 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT License declared an Unusual Event based on seismic activity. * * * UPDATE AT 1801 EDT ON 08/23/11 FROM LISA SWEENEY TO JOHN SHOEMAKER * * * "Oyster Creek has terminated from the Unusual Event for seismic activity. "Engineering walk downs of reactor building, turbine building, switchyard, emergency diesel generators, intake structure, dilution structure, ISFSI (Independent Spent Fuel Storage Installation), and fire pond were completed and no problems noted. "All plant conditions remain stable." Licensee notified the NRC Resident Inspector and applicable state and local authorities. A press release is planned. Notified R1 IRC (Dentil), IRD (Gott), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47187 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-08-23 14:52 | 2011-08-23 15:07 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT The licensee declared a Notification of Unusual Event under EAL HU1.1 due to seismic activity. There were no reports of personnel injury or significant plant damage. The licensee has notified the NRC Resident Inspector and state and local authorities. * * * UPDATE FROM TODD MULFORD TO JOHN KNOKE AT 1842 EDT ON 8/23/11 * * * The licensee terminated the Notification of Unusual Event at 1825 EDT. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R3DO (Passehl), IRD (Morris), FEMA (Via) and DHS (Bean). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47186 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-23 14:05 | 2011-08-23 14:58 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "At 1355 hrs. EDT, an event was recorded by the seismic monitoring system. The seismic monitoring system classified the event as less than Operating Basis Earthquake (OBE) and less than Safe Shutdown Earthquake (SSE). The seismic monitoring system additionally classified the event as Seismic: NO "At 1405 hrs., SSES [Susquehanna Steam Electric Station] declared an Unusual Event [under EAL OU5] after confirmation by outside agencies that an actual seismic event had occurred and reports from numerous personnel that they had detected ground motion. "At time of transmittal there is no indication of equipment damage, personnel injuries and no automatic initiations of any ECCS or ESF systems or RPS actuations occurred. Assessment of any equipment damage is ongoing." The licensee has notified the NRC Resident Inspector and state and local authorities. * * * UPDATE FROM FRITZ OHLSEN TO JOHN KNOKE AT 2110 EDT ON 8/23/11 * * * The licensee has terminated the Notification of Unusual Event. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1DO (Krohn), IRD (Morris), DHS (Bean) and FEMA (Via). | 100 | 15 | 0 | 100 | 15 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47185 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-23 14:15 | 2011-08-23 14:56 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "Seismic event occurred resulting in a Notification of an Unusual Event. No plant impact to either unit. Both units are stable with safety systems functional." There were no personnel injuries and no reports of structural damage. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DAN WILLIAMSON TO HOWIE CROUCH AT 1819 EDT ON 8/23/11 * * * "Limerick is terminating from the Unusual Event (HU5) based on the conditions that originally presented entry to the Unusual Event (HU5) no longer exist and it is unlikely that plant conditions will deteriorate. No emergency conditions exist at this time for either unit. Both Unit 1 and Unit 2 are operating at 100% power and are stable. A walk down of the facility has been completed with no deficiencies identified. No indication of system degradation has been detected." The licensee has notified the NRC Resident Inspector and has notified state and local authorities. Notified R1 IRC (Dentil), IRD (Gott), DHS (Bean), FEMA (Via), USDA (Kraus), and DOE (Turner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47184 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2011-08-23 14:05 | 2011-08-23 14:53 | 2011-08-24 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT "At 1354, the Calvert Cliffs Nuclear Plant (CCNPP) felt seismic activity in the control room. "Both Unit 1 and Unit 2 maintained full power operations. At 1405 CCNPP declared an Unusual Event (UE) for Unit 1 and Unit 2. NRC Operations center was notified at 1453 via dedicated phone (CCNPP event 4189). "Both Units continued to operating safely with no actuations. There were no radiological releases. "An Issue Response Team (IRT) was formed and the site commenced walkdown and inspections of all systems, structures and components for possible seismic damage. All problems found will be entered into the site's Corrective Action Program (CAP) and evaluated for operability." The licensee notified the NRC Resident Inspector, State, and local government agencies. * * * UPDATE FROM JUSTIN INLOW TO CHARLES TEAL AT 0027 EDT ON 8/24/11 * * * They have terminated their Notification of Unusual Event as of 0005 EDT. The licensee has notified the NRC Resident Inspector. Notified R1DO (Krohn), IRD (Morris), DHS (Knox), FEMA (Via). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | MD | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47183 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2011-08-23 14:01 | 2011-08-23 14:50 | 2011-08-23 | NOTIFICATION OF UNUSUAL EVENT DUE TO SEISMIC EVENT "PBAPS [Peach Bottom Atomic Power Station] Units 2 and 3 experienced a seismic event which was felt in the control room in conjunction with a seismic trigger alarm set a 0.01G acceleration. The operating basis earthquake alarm of 0.05G was not received. 'Both units continue to operate at pre-event levels. "Currently there is no indication of damage at the site. Initial plant walkdowns indicate no plant damage and walkdowns are continuing." There were no personnel injuries. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BRAD KIRKMON TO HOWIE CROUCH AT 1800 EDT ON 8/23/11 * * * "At 1750 hrs. EDT, Peach Bottom terminated the Unusual Event that was declared at 1401 today due to a seismic event that occurred at the station. Both Unit 2 and 3 operational walk downs of the site have been completed. There are no issues related to the seismic event which would impact continued safe operation of either unit." The licensee has made state and local notifications as well as notifying the NRC Resident Inspector. Notified R1 IRC (Dentil), IRD (Gott), DHS, FEMA, HHS, USDA. | 100 | 93 | 0 | 100 | 93 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47182 | 0 | NORTH CAROLINA STATE UNIVERSITY |  |  |  | 1000 KW PULSTAR POOL TYPE | 2011-08-23 14:30 | 2011-08-23 14:30 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT The licensee declared a Notification of Unusual Event due to seismic activity. Equipment walkdowns performed. The licensee also terminated the event at the time of notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | OTHER UNSPEC REQMNT | [9 empty] | UNUSUAL EVENT | 2 | NC | NPR | [5 empty] | 0 | 2011-08-23
47181 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-08-23 14:03 | 2011-08-23 14:24 | 2011-08-26 | ALERT DECLARED DUE TO AN EARTHQUAKE IN THE AREA AND A LOSS OF OFFSITE POWER At 1403 hrs. EDT, North Anna Power Station declared an Alert due to significant seismic activity onsite. The Alert was declared under EAL HA6.1. Both units experienced automatic reactor trips from 100% power and are currently stable in Mode 3. All offsite electrical power to the site was lost. All four emergency diesel generators (EDG) automatically started and loaded and provided power to the emergency buses. While operating, the 2H EDG developed a coolant leak and was shutdown. As a result, the licensee added EAL SA1.1 to their declaration. All control rods inserted into the core. Decay heat is being removed via the steam dumps to atmosphere. No personnel injuries were reported. * * * UPDATE FROM ROBERT RINK TO HOWIE CROUCH AT 1116 EDT ON 8/24/11 * * * The licensee has downgraded the Alert to a Notification of Unusual Event based on equipment alignments and inspection results. The licensee notified R2 IRC. Notified IRD (Marshall), NRR (Thorp), FEMA (Hollis), DHS (Inzer), USDA (Ferezan), HHS (Willis) and DOE (Parsons). * * * UPDATE FROM ROBERT RINK TO HOWIE CROUCH AT 1317 EDT ON 8/24/11 * * * The licensee has exited the Notification of Unusual Event at 1315 EDT. The exit criteria was that all inspections and walkdowns were completed and plant conditions no longer meet the criteria for a NOUE. Notified R2DO (Widmann), IRD (Marshall), NRR (Thorp), FEMA (Hollis), DHS (Inzer), USDA (Ferezan), HHS (Willis) and DOE (Jackson). * * * UPDATE FROM DON TAYLOR TO DONALD NORWOOD AT 1405 EDT ON 8/26/11 * * * "This notification is to report new information identified post event that a condition existed which met the emergency plan criteria but was not declared. On August 23 at 1403 EDT, North Anna Power Station declared an Alert due to seismic activity onsite. The Alert was declared under Emergency Action Level (EAL) HA6.1 "Other conditions existing which in the judgment of the SM warrant declaration of an alert. Initial review of seismic response data from the earthquake on 8/23/11 (1348 hours) indicates that design spectrum input assumptions (i.e. Design Basis Earthquake [DBE] limits) may have been exceeded above 5 HZ. This would have resulted in classification of an Alert under EAL HA1.1. "No significant equipment damage to safety related systems (including class I structures) has been identified through site walk-downs nor has equipment degradation been detected through plant performance and surveillance testing following the earthquake." The licensee notified the NRC Resident Inspector. The licensee also plans on notifying the State Emergency Operations Center and the Louisa County County Administrator. Notified R2DO (Widmann) and NRR EO (Bahadur). | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | ALERT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-08-23
47180 | 0 | UNIV OF MARYLAND |  |  |  | 250 KW TRIGA (CONVERSION) | 2011-08-23 14:05 | 2011-08-23 14:05 | 2011-08-23 | NOTIFICATION OF AN UNUSUAL EVENT DUE TO A SEISMIC EVENT The licensee declared a Notification of Unusual Event due to seismic activity. The reactor was not operating at the time of the earthquake. Facility walkdown is in progress. * * * UPDATE FROM MOHAMMED AL-SHEIKILY TO HOWIE CROUCH AT 1415 EDT ON 8/23/11 * * * The licensee exited the NOUE. Notified R1DO (Krohn) and NRR (Thorp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | OTHER UNSPEC REQMNT | [9 empty] | UNUSUAL EVENT | 1 | MD | NPR | [5 empty] | 0 | 2011-08-23
47178 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2011-08-22 15:13 | 2011-08-22 17:48 | 2011-08-22 | MANUAL REACTOR TRIP DUE TO RISING CONDENSER BACKPRESSURE "On August 22, 2011 at 1513 [hrs. EDT], Unit 1 was manually tripped due to rising condenser backpressure. All CEAs fully inserted into the core. Decay heat removal was initially from main feedwater and steam bypass to the main condenser. The cause of the rising back pressure was an influx of jellyfish into the intake structure, degrading the circulating water system performance. "Subsequent to the manual trip, the 1B Main Feedwater Pump was manually secured due to a leak on the pump casing. The 1A Main Feedwater Pump subsequently tripped due to low suction pressure after manually securing the 1B Condensate Pump, per procedure. Decay heat removal was transitioned to atmospheric dump valves and auxiliary feedwater. "Unit 2 is in Mode 1, currently at 70 % power. Unit 2 power is being reduced from 100% in response to the influx of jellyfish. "This event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip." During the transient, no primary or secondary relief valves lifted. Offsite power is stable and the plant is in its normal shutdown electrical line-up with power being supplied from offsite. There is no known primary-to-secondary leakage. The cause of the 1A Main Feedwater Pump trip is under investigation. Unit 2 remained at 70% reactor power before and after the event. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1856 EDT ON 08/22/11 FROM CARLOS SANTOS TO JOE O'HARA * * * "On August 22, 2011 an abnormal fish kill of at least 1000 lbs was observed in the combined unit's intake canal. The cause of the fish kill was related to an unusually large sustained influx of jellyfish into the intake canal. "Per the plant's environmental permit, the Florida Fish and Wildlife Conservation Commission (FWCC) was notified at 1627 EDT. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the notification of the FWCC." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  |  | 0 | 2011-08-22
47177 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-08-19 18:05 | 2011-08-19 23:54 | 2011-08-20 | PARTIAL LOSS OF OFFSITE POWER RESULTING IN EDG AUTOSTART "At 1805 Indian Point Unit 3 experienced a loss of normal 138 KV Offsite Power (LOOP) during a thunderstorm in the area. The Station Auxiliary Transformer (SAT) protection circuitry actuated and de-energized 6.9 KV buses 5 and 6. Thirty two and 33 Emergency Diesel Generators (EDGs) auto-started and loaded onto Safeguards buses 5A and 6A per plant design. The corresponding blackout logic resulted in an auto start of 32 and 33 Auxiliary Feed Water pumps (AFW). The plant remained in Mode 1; however, due to the loss of two 6.9 KV buses, three Circulating Water pumps (CW) tripped as designed, which caused main condenser backpressure to rise (i.e., vacuum degraded). As a result of rising condenser backpressure, a manual turbine load reduction to 75% power was performed. The reactor remains stable at 75% power and buses 5 and 6 have been manually re-energized from the alternate 13.8 KV offsite power source and the Emergency Diesel Generators have been unloaded, shutdown, and realigned for auto start capability. "The only unusual system response was 32 Component Cooling Water (CCW) pump did not auto-start on a low pressure signal when the remaining pumps were stripped and re-loaded by the EDG sequencing logic due to a problem with the closing spring on the supply breaker. CCW system pressure was observed to be at normal levels when 31 and 33 CCW pumps were loaded on the EDGs. 32 CCW pump remains inoperable due to the breaker issue. "There was no impact to the operation of Unit 2 during this event." The licensee has notified the NRC Resident Inspector and the New York State Public Service Commission. | 0 | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-08-20
47176 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-08-19 08:15 | 2011-08-19 16:26 | 2011-08-19 | 24-HR LOSS OF CRITICALITY CONTROL REPORT REQUIRED UNDER BULLETIN 91-01, SUPPLEMENT 1 "At 0815 CDT on 08-19-11, a Chemical Operations First Line Manager discovered that during disassembly of a single Seal Exhaust/Wet Air (SX/WA) pump, pump housing subcomponents (i.e. two piston slides and a cam) were placed within 2 feet of the internal oil separators. Nuclear Criticality Safety Approval (NCSA) GEN-011 requires a minimum 2-foot edge-to-edge spacing between pump housing subcomponents and internal oil separators. The purpose of this control is to ensure interaction between grossly contaminated fissile items is minimized during movement and storage. The Plant Shift Superintendent and the NCS group were notified and access to the area was controlled. "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01, Supplement 1. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-11-2161 "PGDP Event Report No. PAD-2011-13 "POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for a criticality to be possible, the components would have to be grossly contaminated and brought together in a geometry capable of supporting a criticality and an additional spacing violation would have to occur before a criticality is possible. "CONTROLLED PARAMETERS: Double contingency is maintained by implementing controls on geometry and interaction. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL : Uranium contaminated oil. Product withdrawal assay at the time of the event was less than 4.95 wt% U235. The pump components were not grossly contaminated. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on the geometry of the seal exhaust/wet air pump components. The pump components are controlled as safety related items. This control was not violated. Therefore, this leg of double contingency was maintained. The second leg of double contingency relies on minimizing interaction between internal oil separators and pump housing subcomponents. Interaction is controlled by maintaining a minimum 2-foot edge-to-edge spacing between pump internal oil separators and pump housing subcomponents. The pump housing subcomponents were placed within 2 feet of the internal oil separators in violation of this control. The interaction parameter was not maintained; therefore this leg of double contingency was not maintained. Double contingency was not maintained because the interaction parameter was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Control Access to the area. This was completed at 0845 CDT on 08/19/11. 2. Move one item at a time such that the spacing between the pump housing subcomponents and the internal oil separators is always increasing until a minimum 2-foot edge-to-edge spacing has been established. This was completed at 1445 CDT on 08/19/11. 3. Upon establishing the proper spacing between the pump housing subcomponents and the internal oil separators, the exclusion zone may be removed. This was accomplished at 1450 CDT on 08/19/11." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2011-08-19
47175 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-07-15 12:15 | 2011-08-19 15:39 | 2011-08-19 | AGREEMENT STATE REPORT - IMPROPER THERAPEUTIC HYPERTHYROID DOSE Kentucky provided the following information via e-mail: "On July 15, 2011, an 82 year old male patient was scheduled for a therapeutic dose of I-131, 15 mCi for the treatment of subclinical hyperthyroidism with [the prescribing physician]. The therapeutic dose received from the radiopharmacy was assayed prior to administration and indicated an amount of 19.9 mCi. "The technologist assaying the dose contacted [the physician] concerning the difference in the amount ordered and the amount received. [The physician] chose to accept the dose and administer it to the patient based on the patient's age and symptomatic subclinical hyperthyroidism and enlarged lobe. "[The physician] accepted the dose clinically but did not document this on the written directive prior to administration. The change in dose is documented in [the physician's] dictation, completed on July 15, 2011 at 1:44 p.m., acknowledges the change in the dose administered and it is documented that the technologist informed him of the difference in dose and his acceptance and why this amount was acceptable. "The failure to change the written directive prior to administration was not identified until August 8, 2011 during OLBH's [Our Lady of Bellefonte Hospital] annual audit conducted by a Medical Physicist. [The] RSO and the Director of Radiology contacted the RHB [Radiation Health Branch] on August 9, 2011 for notification of the medical event. "Contributing Factor: Failure to change the written directive prior to administration of the I-131. "Corrective Actions by Licensee: A policy and procedure review was conducted. The Quality Management form and Written Directive used with administration of I-131 therapies was reviewed and updated to include an area that requires explanation of any dose that differs from the prescribed dose being administered and the signature of the AU [authorized user] confirming the change in dose prior to administration." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-08-25
47174 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-08-07 | 2011-08-19 15:42 | 2011-09-02 | VIRGINIA AGREEMENT STATE REPORT - DOSE RECEIVED BY PATIENT GREATER THAN PRESCRIBED The following information was obtained from the State of Virginia via fax: "On August 7, 2011, the licensee's RSO received notification of an incident. A patient was treated for bronchial/trachea carcinoma using temporary brachytherapy employing a HDR delivery system. Subsequent to treatment, it was realized that dwell positions were misrepresented on the approved treatment plan. Reconstruction of the applicator position led to the conclusion that dose to organs or tissue other than the treatment site received more than 50 Rem and more than 50% of the expected dose. Licensee notified Virginia Department of Health on August 17, 2011. Referring physician was notified on August 17, 2011. Physician is meeting with patient on August 19, 2011. Licensee indicated organs at risk and health effects to patient are under development." Virginia Report ID: VA-11-08 * * * UPDATE AT 1458 EDT ON 09/02/11 FROM MIKE WELLING TO S. SANDIN * * * The following update was received from the State of Virginia via email: "On August 31st the licensee report was received. The report indicated the cause was human error during data loading into the delivery system. An error was received and in order to clear the error the source position spacing was changed. The report detailed the licensee's dose calculations to the surrounding organs and tissue. The estimated maximum amount received by the larynx was 2.332 Gy which was 581% over the expected dose of 0.42 Gy. "A subsequent licensee response on September 1st detailed the dose to the lungs. The dose to the lungs did not differ between expected and delivered. "The patient has had two follow up visits and shows no adverse effects. A positive tumor effect was observed by the referring physician." Notified R1DO (DiPaolo) and FSME (Hsueh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-08-25
47173 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-08-16 14:44 | 2011-08-19 14:52 | 2011-08-19 | CALIFORNIA AGREEMENT STATE REPORT - LEAKING IODINE-125 BRACHYTHERAPY SEEDS The following information was obtained from the State of California via email: "UCLA contacted the Brea office of RHB [Radiologic Health Branch] to report a leaking source of I-125 brachytherapy seeds. Initial survey of the packaging, upon receipt, did not show any contamination. Subsequent testing showed 1.8 microCuries of contamination. The order was for 19 seeds, 16 for treatment, one for calibration and 2 for spares. A physician was preparing an eye plaque using the 16 seeds. A dish of acetone was used to remove glue from the seeds. A radiation survey discovered that the dish had become contaminated with I-125. The patient's procedure was cancelled and EH&S [Environmental Health and Safety] personnel were notified about the issue. EH&S collected all 19 seeds and performed a leak test on the 16 treatment seeds by soaking them in isopropyl alcohol. The fluid was analyzed on a liquid scintillation counter which found 1.8 microCuries of removable contamination. "Per 10 CFR 35.3067, a licensee shall file a report within 5 days if a leak test required by 35.67 reveals the presence of 185 Bq (0.005 uCi) or more of removable contamination. "RHB is requesting UCLA to obtain copies of the leak tests performed by the manufacturer to determine if the seeds were leaking prior to being shipped to UCLA. These copies will be in the final report. If the seeds were discovered to be shipped in a compromised condition, the Virginia Division of Radiological Health will be notified since the manufacturer (Best Medical International, Inc. of Springfield, Virginia) is located within their jurisdiction." California Report Number: 5010-081611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-08-24
47172 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-19 10:46 | 2011-08-19 14:06 | 2011-08-19 | REACTOR SCRAM DURING QUARTERLY SURVEILLANCE TEST "At 1046 hours on August 19, 2011, Susquehanna Steam Electric Station Unit 2 reactor scrammed while [operators were] performing a quarterly functional test of reactor water high level trip channels for feedwater / main turbine. The main turbine tripped when a single channel high reactor water level signal was inserted, which was unexpected. Actual water level was within the normal band when the main turbine tripped. The main turbine trip resulted in a reactor scram. Reactor recirculation pump trips as designed and all control rods inserted. Reactor water level lowered to +2 inches causing Level 3 (+ 13 inches) isolations. Reactor water level was restored to the normal operating band using the feedwater system. Six main steam relief valves opened for a short duration, as expected, due to the turbine trip transient. Subsequently, reactor pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. No ECCS or RCIC initiations occurred or were required. "The reactor recirculation pumps were subsequently restarted to re-establish forced core circulation. "The reactor is currently stable in Mode 3. An investigation into the cause of the scram is underway. "Unit 1 was unaffected and continued power operation. "The NRC Resident Inspector was notified. A press release will occur." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-08-19
47171 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2011-06-21 13:08 | 2011-08-19 13:43 | 2011-08-19 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "Invalid Actuation of Turbine Driven Auxiliary Feedwater (TDAFW) pump. "This telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1). "On 6/21/11 at 1308 EDT, during maintenance activities for replacement of relay UVTXSB/1732, associated with 6.9kv Emergency Bus 1B-SB undervoltage trip circuitry, an automatic start of the Turbine Driven Auxiliary Feedwater (TDAFW) pump occurred while using a new procedure, CM-E0032. At the time of the event, all steam generator levels were normal. The TDAFW pump was secured by Operations on 6/21/11 at 1311 EDT. "No actual condition existed that would require an automatic start of the TDAFW pump and therefore this event has been classified as an invalid actuation. "The start of the TDAFW is considered a complete train actuation. The system started and functioned successfully." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-08-19
47170 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-08-19 10:30 | 2011-08-19 12:32 | 2011-08-19 | INADVERTENT SOUNDING OF EMERGENCY PREPAREDNESS ZONE SIREN "Limerick Generating Station Site EP [Emergency Preparedness] Manager was informed by Chester County 911 Dispatch Center that Limerick Emergency Preparedness Zone (EPZ) Siren #132, located at Pothouse Road West of Ridgeview Road in Chester County, was sounding. Notification occurred at 1030 hrs. [EDT] 8/19/11. "The siren maintenance contractor was contacted, and the sounding was terminated at 1120 hrs. 8/19/11. "No actual plant emergency exists. The siren activation was caused by equipment malfunction. "[The] remaining 164 of 165 Limerick EPZ Sirens remain functional, no other reportability threshold(s) have been met or exceeded. "An 'Event of Potential Public Interest' will be issued to the state and local agencies." The maintenance contractor is currently troubleshooting the cause. The licensee will be notifying the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-19
47169 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-08-18 22:50 | 2011-08-19 01:10 | 2011-08-19 | AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP BUS UNDERVOLTAGE "At 2250 EDT on 8/18/2011, Unit 1 Reactor/Turbine automatically tripped on RCP [Reactor Coolant Pump] Busses UV [Under-Voltage] trip. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected from the Feedwater Isolation Signal. No primary PORVs and/or Safety Valves opened during or after this trip. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F [degrees] and 2233 psig, with Auxiliary Feedwater supplying the Steam Generators. "At the time of the trip, a 50G (instantaneous overcurrent ground) relay flag was found dropped on the '1A' 6.9 KV unit board. Subsequently, the '1A' 6.9 KV start bus was found to have transferred to its alternate supply, 'B' CSST [Common Station Service Transformer]. 1A condenser circulating water pump motor trip out was also received in the MCR [Main Control Room]. "The method of decay heat removal is via steam dumps to the condenser with MSIVs open. The current temperature and pressure is stable. There is no indications of any primary/secondary leakage. All control rods inserted. The electrical alignment is normal with the exception of the above mentioned items, supplied from off-site power. There is no impact to Unit 2. Unit 2 is operating at 100% power/ Mode 1." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-08-19
47168 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2011-08-17 13:00 | 2011-08-18 17:18 | 2011-08-18 | GEORGIA AGREEMENT STATE REPORT - LOST INDUSTRIAL NUCLEAR GAUGE On 8/17/11, the licensee discovered that a nuclear process gauge was missing. The gauge was suspected to have been placed in the trash and transported to a local landfill. The landfill operators have been notified. Workers at the facility were interviewed but the licensee could not determine the disposition of the gauge. The gauge, a BSI Instruments model NW201, serial number 1041, was last seen on or about August 4, 2011. The missing gauge, plus two others, were verified to be in temporary storage awaiting transfer to an outside organization. The gauge contained 0.5 mCi of Cs-137. The two other gauges are accounted for and stored properly. Georgia Report #: GA2011-40I THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2011-08-23
47167 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-08-18 10:00 | 2011-08-18 16:11 | 2011-08-18 | UNANALYZED CONDITION THAT COULD POTENTIALLY IMPACT BOTH TRAINS OF 480V SAFEGUARDS BUSES "During NFPA-805 Fire PRA [Probabilistic Risk Assessment] model development, Ginna Station identified a non-compliance with the Appendix R requirement to maintain one train of systems that are necessary to achieve and maintain hot shutdown and remain free from fire damage. A fire in the Turbine Building could cause a loss of 4160V power to the 480V safeguards buses while disabling control power to the 480V bus normal supply breakers and preventing both diesel generator output breakers from closing. Since the non-safety related 4160V buses are located in the same area of the turbine building, this could potentially impact both trains of AC power. This was determined to be an unanalyzed condition reportable in accordance with 10CFR50.72(b)(3)(ii)(B). Compensatory measures have been established to provide interim guidance to identify the condition and locally trip the bus supply breaker prior to closing the diesel generator output breaker." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-08-18
47166 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2011-08-17 18:45 | 2011-08-18 15:26 | 2011-08-18 | FITNESS FOR DUTY - PRESENCE OF ALCOHOL IN THE PROTECTED AREA A non-licensed contract employee was determined to have alcohol in his possession while in the Protected Area. The contractor's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2011-08-18
47165 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-08-17 08:30 | 2011-08-18 11:35 | 2011-08-18 | AGREEMENT STATE REPORT INVOLVING A DAMAGED MOISTURE DENSITY GAUGE The following information was obtained from the State of Texas via email: "On August 18, 2011, the Agency [Texas Department of State Health Services] was notified that a Humboldt model 5001 EZ, serial number 4220, containing a 44 milliCurie Americium-241/Beryllium source and an 11 milliCurie Cesium-137 source was run over by a dirt compactor. The user placed the device on the ground 12 feet from his truck to perform prior to use checks on the gauge. The sources were in the fully shielded position. When the technician went to the cab of their truck to record readings, a dirt compactor came up out of a pit near the truck. The technician could not get the attention of the compactor driver in time to prevent them from driving over the gauge. The technician contacted the fire department and [informed] his manager of the event. The licensee's Radiation Safety Officer (RSO) and fire department both responded to the scene. The RSO conducted a radiation survey of the device and determined that the sources were fully shielded. A service company was contacted and they took the device to their facility. The service company performed leak tests on both sources. The results were below the regulatory limit. Additional information will be provided as it is received." Texas Report # I-8879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-08-23
47164 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-08-18 10:24 | 2011-08-18 11:07 | 2011-08-18 | SECURITY REPORT INVOLVING A DEGRADATION IN A SAFEGUARDS SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not be taken. The licensee informed the NRC Resident Inspector and will inform the States of New Jersey and Delaware including the New Jersey State Police. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-08-18
47163 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-08-16 | 2011-08-17 16:50 | 2011-08-17 | AGREEMENT STATE REPORT - STUCK SHUTTER IDENTIFIED FOLLOWING MAINTENANCE The following was received via email: "On August 17, 2011, the Agency [Texas Department of Health] was notified that they were unable to open the shutter on a Ronan Engineering model GS 400 nuclear gauge. The gauge contains 20 milliCuries of cesium 137. "The gauge had been taken out of service by the licensee to conduct maintenance in the area around the gauge. Once the work was completed, they were unable to get the gauge shutter to open. The licensee has taken the gauge out of service until it can be replaced. "The gauge does not present an exposure hazard to anyone. The manufacturer has been contacted and is making arrangements to replace the gauge. The gauge was installed in 2010. The Radiation Safety Officer stated that the gauge has been cycled several times since it was installed. The licensee was not able to determine the cause for the failure. Additional information will be provided as it is received." Texas Incident No. I-8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-08-22
47162 | 0 | HYDROAIRE |  |  |  |  | 2011-08-10 | 2011-08-17 16:52 | 2011-08-17 | PART 21 - PUMP SHAFT COUPLING FAILURE During operation a service water pump coupling failed on 8/10/2011 at Entergy Palisades. The failure occurred in a threaded line shaft coupling. At this point, the failure cause is not known. The root cause analysis is currently underway. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2011-08-17
47161 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-08-16 12:00 | 2011-08-17 11:16 | 2011-08-17 | IMPROPER CRITICALITY SAFETY EVALUATION "As part of the ongoing GNF-A review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), facility walk downs of the UO2 sinter furnace area were performed that identified a configuration that had not been properly analyzed. Based on a review of this as-found condition, it was determined at approximately 12 p.m. on August 16, 2011 that a floor trench in the furnace area was improperly analyzed in a criticality safety evaluation. This resulted in a condition in which criticality controls that were documented as being necessary to meet double contingency were not maintained or available because the geometry of the trench was not properly modeled. There was not an actual loss of double contingency. "The floor trench does not normally contain uranium, and has removable covers in place to prevent material accumulation and per procedure, is routinely inspected. It was inspected during the spring maintenance shut down and was inspected again today. These inspections confirmed that no visible uranium accumulation was present. At no time was an unsafe condition present. Additional corrective actions and extent of condition are being evaluated. "This event is being conservatively reported pursuant to GNF-A internal procedure reporting requirements within 24 hours of discovery." The licensee will notify North Carolina State Radiation Protection agency and the New Hanover County Emergency Coordinator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2011-08-17
47160 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-08-16 20:10 | 2011-08-16 22:40 | 2011-08-16 | OFFSITE NOTIFICATION DUE TO CHLORINE SPILL A potential spill of 1 to 2 gallons of Chlorine was discharged to the Delaware River through a storm drain that had a piping leak. This discharge was reported to New Jersey Department of Environmental Protection (case #: 11-08-16-2024-28). Chlorination was isolated and the storm drain plugged. Clean up is in progress. The licensee has notified the NRC Resident Inspector and will notify Lower Alloways Creek Township. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-16
47159 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-08-16 13:17 | 2011-08-16 15:01 | 2011-08-16 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received via fax: The state reported that their licensee has a gauge with a shutter is in the stuck position. The device contains 300 mCi of Cs-137. The device is secured and no one was exposed during this event. The licensee has contacted the vendor for repairs and will notify the department (Pennsylvania Department of Radiation Protection) when repairs have been made. The department (Pennsylvania Department of Radiation Protection) plans to do a reactive inspection." PA Report #: PA110021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-08-19
47158 | -1 | CHRISTIANA CARE |  |  |  |  | 2011-08-09 | 2011-08-16 14:47 | 2011-11-01 | DOSE DIFFERENT THAN PRESCRIBED A patient was scheduled to receive three separate treatments for pancreatic cancer containing Yttrium-90. Each dose was to contain 10.5 milliCuries of Yttrium-90 for a total of 31.5 milliCuries. Cardinal Health (the producer of the treatment) provided the entire dose of 31.5 milliCurie in a single syringe. The physician verified the receipt of the syringe and administered it to the patient. When the patient was scheduled to return on 8/16/11 for the second treatment Cardinal Health realized that they had provided the entire dose instead of three separate doses of 10.5 milliCuries. Cardinal Health notified Christiana Care of the error. The treating physician and patient have been notified. No adverse health effects are expected. * * * RETRACTION FROM JOESPH SOLGE TO JOHN SHOEMAKER AT 1009 EDT ON 11/01/11 * * * The original directive was correct in regard to the dose administered, therefore this event is being retracted. Notified the R1DO (Perry) and FSME (McIntosh). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2011-08-22
47157 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2011-08-06 10:55 | 2011-08-16 11:50 | 2011-08-16 | INVALID ACTUATION OF MOTOR DRIVEN AUXILIARY FEEDWATER PUMP "This telephone notification is being made in lieu of submitting a written LER for an invalid actuation of the 1A Motor Driven Auxiliary Feedwater (MDAFW) pump under 10 CFR 50.73(a)(2)(iv)(A). "On August 6, 2011 at 1055 CDT, during the performance of surveillance testing on the 1A Containment Spray (CS) pump, an unexpected automatic start of the 1A MDAFW pump occurred. While installing jumpers in the B1F sequencer to cause an automatic start for the 1A CS pump per the test procedure, the jumpers were inadvertently connected to the wrong relay which started the 1A MDAFW pump instead. This automatic start was considered invalid since the start signal was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. The 1A MDAFW pump was restored to a normal standby alignment at 1131 CDT. "The following required information is being submitted per NUREG-1022, Rev. 2. "(a) The 1A MDAFW pump is an 'A' train component. "(b) The 1A MDAFW pump automatic start is considered a complete train actuation. "(c) Once the 1A MDAFW pump inadvertently started, the system functioned per design." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-08-16
47156 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-08-16 06:00 | 2011-08-16 09:36 | 2011-08-16 | OFFSITE NOTIFICATION DUE TO AN ON-SITE, NON-WORK RELATED, FATALITY "The purpose of this report is to notify the NRC of a fatality involving a contract worker from Duke Energy's Oconee Nuclear Station. At approximately 0600 EDT, the control room was notified of an unconscious individual, located in a non-radiological area outside the protected area. The Medical Emergency Response Team was activated and dispatched to the scene. At 0640, the worker left the site in an ambulance. The individual was pronounced dead at the local hospital. This fatality was the result of a medical emergency and was not occupationally related. "Duke Energy is making a notification to the South Carolina Department of Occupational Safety and Health Administration. This ENS notification is in response to a notification to another government agency in accordance with 10CFR50.72(b)(2)(xi). "The licensee notified the NRC Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-16
47155 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2011-08-12 | 2011-08-15 19:10 | 2011-10-19 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received via email: "On Friday August 12, 2011, the gauge owned by the licensee had been run over by a roller. The licensee reported that the gauge was in the shielded position and there were no elevated readings on the gauge. The gauge was placed into the shipping case and returned to the office for disposal." The device was a CPN MC moisture density gauge serial number M390104801 containing 10 milliCuries Cs-137, Am-241/Be 50 milliCuries. Incident #: 11-0028 * * * UPDATE FROM DARYL LEON TO PETE SNYDER AT 1253 ON 10/19/11 * * * On August 17, 2011, the above source was received by Qal-Tek of Idaho Falls, ID who possesses NRC license 11-27610-01, for disposal. Both sources passed a leak test performed by Qal-Tek. Notified R4DO (Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2011-08-18
47154 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-08-15 10:55 | 2011-08-15 13:10 | 2011-08-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - CONTAMINATED OIL SAMPLE "On 8/11/2011 at 1145 CDT the Turbine Driven Auxiliary Feedwater pump was declared inoperable due to oil sample results indicating high particulate (ISO Solid Contamination Code above the Action Limit IAW I-ENG-004) in the turbine lube oil. The action limit is 19/16 and the sample result was 23/21. The ISO Solid Contamination Code is a measure of particle count and size. The same sample was analyzed for metal particulate concentration and results were satisfactory. Efforts have been underway to determine the source of the contaminate and to restore the turbine lube oil to within specifications. "On 8/14/2011 at 0945 CDT NRC Region IV granted a Notice of Enforcement Discretion NOED beginning at 1145 CDT on 8/14/2011 to expire at 1145 CDT on 8/15/2011. "Cleaning efforts have been completed. Current sample results indicate acceptable levels. A Basic Engineering Disposition has been issued supporting the sample results and basis for operability. Technical Specification required shutdown per TS 3.7.5 condition C.1 and C.2 was initiated at 1055 CDT on 8/15/2011. The Turbine Driven Auxiliary Feedwater Pump was declared operable at 1203 CDT on 8/15/2011 and the power reduction was halted at 82% Rated Thermal Power (RTP). Power ascension to 100% RTP was commenced at 1209 CDT on 8/15/2011." The licensee has notified the NRC Resident Inspector. | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-08-15
47153 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-08-12 | 2011-08-15 10:51 | 2011-08-15 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK IN OPEN POSITION The following report was received from the Virginia Department of Health via facsimile: "On August 12, 2011, the Radiation Safety Officer of American Electric Power, Clinch River Plant, reported a fixed gauge shutter stuck in the open position. The gauge is a Thermo MeasureTech Model 5197 containing 100 millicuries of cesium-137. It is a general license device used to measure levels in a fly ash precipitator hopper. Based on the licensee's lock-out procedures for entry into the hopper, the licensee has been authorized to continue operations. The licensee has contracted a licensed service provider to repair or replace the gauge. The malfunction does not pose a risk of additional radiation exposure to personnel. VA report ID: VA-11-0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-08-18
47152 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-08-12 12:00 | 2011-08-13 11:00 | 2011-08-24 | INTEGRATED SAFETY ANALYSIS (ISA) - UNANALYZED CONDITION "As part of the ongoing GNF-A review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis, accident sequences associated with hydrogen piping are being evaluated. As part of this evaluation, facility walk downs of the piping were performed that identified a configuration that had not previously been analyzed. Based on a review of this as found condition, it was determined at approximately 12 p.m. on August 12, 2011 that the system was improperly analyzed in the ISA and resulted in a failure to meet performance requirements. "Hydrogen supply to the affected piping system inside the building has been isolated. Additional corrective actions and extent of condition are being evaluated. "This event is being reported pursuant to the reporting requirements of 10 CFR 70 Appendix A (b)(1) within 24 hours of discovery." The licensee will notify NRC Region 2 and appropriate state and local authorities. * * * UPDATE FROM PHILLIP OLLIS TO ERIC SIMPSON AT 1228 EDT ON 8/24/11 * * * "Unnecessary piping branches have been removed and caps welded in place. The new piping configuration has been analyzed for ISA accident sequences. "Based upon this, hydrogen supplies to affected equipment will resume and normal operations will commence." The licensee will notify NRC Region 2. Notified R2DO (Widmann) and NMSS EO (Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | DEV FROM ISA | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(5) |  |  |  | 0 | 2011-08-13
47151 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-08-12 14:29 | 2011-08-12 20:20 | 2011-08-12 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO VALVE BODY LEAK "On Friday August 12, 2011 at 1429 CDT, a through-wall leak was discovered on the body of the High Pressure Coolant Injection (HPCI) Inlet Drain Pot Inboard Drain valve to the Main Condenser, AOV 2-2301-29. This is a safety-related, ASME Code Class 2 valve. Dresden Technical Requirements Manual 3.4.a, Condition B requires the leak to be isolated which renders the HPCI System Inoperable. The Unit 2 HPCI system was isolated and declared inoperable at 1646 CDT, and Technical Specification 3.5.1 Condition G has been entered. The HPCI system is a single train system. "The event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' T.S. 3.5.1 condition G is a 14 day LCO and the utility can make the repair at power. The unit is in a normal electrical lineup with offsite power available and all EDG's are operable. There was a slight increase in plant risk to "yellow" as a result of this issue. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-08-12
47150 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2011-07-22 15:00 | 2011-08-12 16:31 | 2011-08-12 | AGREEMENT STATE REPORT - ATTEMPTED BREAK-IN ON TRUCK CONTAINING A RADIOGRAPHY CAMERA The following report was received via e-mail: "On July 22, 2011 at 3:00 p.m., [the Louisiana Department of Environmental Quality] received a call from Team Industrial, that there was an attempted break in on a radiography crew's truck, while staying at a hotel in Belle Chasse, LA. It was around 9:30 p.m. on July 21, 2011, when the crew heard the alarm on the truck go off. They came out to see what happened and saw two men take off. There was nothing taken and they called the local law enforcement. However, there was no video surveillance footage available. The crew moved to another hotel with video surveillance in the area of the IR [Industrial Radiography] truck." The crew came from the Team office in Gonzales, LA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2011-08-17
47149 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2011-08-11 15:00 | 2011-08-12 13:25 | 2011-08-12 | AGREEMENT STATE REPORT - LOSS OF MATERIAL The following report was received from the state of Maryland via fax: "The RSO of UMCP [University of Maryland - College Park] telephoned 8/11/11 at 3:00 p.m. to report the loss of a vial of 5 ÁCi [microCuries] C-14. [The RSO] indicated that they were in the process of cleaning out a lab and discovered the vial frozen inside of the lab freezer. The vial was removed and placed in a styrofoam cup and put on the counter for removal by the Radiation Safety Office. [At some time subsequent to placing the vial on the counter, the vial disappeared and is now presumed lost.] From the time of discovery of the vial to the response of the Radiation Safety Office was less than 3 hours. It is believed that the facility management personnel cleaning the office, picked up the cup, and disposed of it as regular trash. They looked through the trash and monitored, but couldn't find the vial." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2011-08-17
47148 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2009-01-20 08:00 | 2011-08-12 13:27 | 2011-08-12 | AGREEMENT STATE REPORT - STUCK SOURCE The following report was received via fax: "The field service engineer was conducting the quarterly source exchange at the facility. While unloading the source into the transport container, the engineer received an error code indicating there were issues with the source side drive mechanism. The problem with the drive mechanism prohibited the source from fully deploying into the transport container or retracting back into the safe. The emergency motor was not able to retract the source. Following emergency procedures, the engineer tried to manually retract the source, however, the cable drum was locked-up and would not wind the source cable, He removed the unload transfer tube from the indexer, cut the exposed source cable and manually inserted the source in to the emergency container. The engineer disassembled the drive mechanism and collected the damaged parts. The unit was then cleaned and the cable drum and gear wheel were replaced. The system was tested repeatedly and found to be functioning properly. "Initial calculations of 241 mR whole body dose were 'worst case scenario'. The dosimeter badge report indicated a whole body dose of 40 mR which does not exceed the regulatory limit for occupational exposure. "The Root Cause Investigation was completed on 06-15-2009 by Nucletron B.V. in the Netherlands. "For the investigation and analysis of the incident, the collected damaged parts were sent to Nucletron B.V. in the Netherlands where they were photographed and inspected. Additionally, the engineer was asked for his findings and the system logbook was scrutinized. "According to the damage on the source cable drum, the drum had made at least 2.2 rotations before it got stuck (293 mm to move out of the indexer; 242 mm from where the source cable was cut off; source cable drum diameter is 80 mm). After examining the damaged parts, there was no visible cause as to why the drum became damaged. An obstruction at this position during the source exchange into the transport container is not expected since at this point it is a single straight tube; however, this cannot be ruled out as a possibility. "The message logbook of the system was investigated and showed that during the source exchange, the engineer received seven error code 3's at 176 mm all within a six minute time frame. Error code 3 is a source obstruction which can happen when the bushing between the rigid and flexible part of the source cable cannot pass through the indexer clamp of the unload tube due to a misalignment of the clamping mechanism or damage to the source cable. The transfer tube was removed and a normal 'treatment' was performed without problem. The transfer tube was then reattached to exchange the source and four more error code 3's were received within two minutes at the same distance, thus indicating it was purely a container problem. "There were no errors in the logbook that indicated the source remained outside the system. After the multiple tries with the error code 3, the system was switched off. Upon restart an hour later, two more attempts were made. However, the engineer now received error code 2 indicating the source would no longer come out of the safe. The system was turned back off again. Upon restart thirty minutes later, the unit had a dummy source in it; the source had apparently been unloaded by hand and replaced with a dummy. Later, the source exchange procedure was performed and a dummy source loaded properly; after which, the system worked normally again. "According to the engineer, the system did not show any error or radiation/out-of-safe message when it was switched off following the problem with the container. When he entered the treatment room, he unexpectedly found the source to be outside the system, at which point he followed the emergency procedures in order to secure the source. Once the source was secure, the engineer forcibly pulled the remaining cable from the cable drum. He then proceeded to clean the system and assess the damaged parts. "There is no logical explanation as to how the source got stuck outside the system. The logbook does not have any indication to this fact. The damage to the drum and cable may have occurred during the emergency procedure that was carried out to secure the source. Since operator error by the service engineer cannot be ruled out, a retraining on source exchange and handling is required. In addition, the transport container has been returned to Nucletron B.V. in the Netherlands for further investigation." The source exchange was being conducted on a MicroSelectron HDR-V2, S/N 31526, TCS software version 1.50C, located at the Grant/Riverside Methodist Hospital in Columbus Ohio. The field problem report number is FPR 252753. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2011-08-17
47147 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2011-08-11 16:31 | 2011-08-11 21:07 | 2011-08-11 | LOSS OF INTAKE COOLING WATER FOR 20 MINUTES "At 1631 hours on Thursday, August 11, 2011, Turkey Point Unit 3 lost the function of the Intake Cooling Water (ICW) System for approximately 20 minutes. This is reportable in accordance with 10 CFR 50.72(b)(3)(v)(B) and (D). Loss of function occurred when manual valve 3-50-406, ICW/Component Cooling Water (CCW) Heat Exchanger Outlet Valve, failed closed. Valve 3-50-406 is located in the common discharge line preventing flow through both ICW headers to the CCW heat exchangers. Operations Department personnel opened the bypass valves associated with the failed valve and restored ICW flow to the CCW heat exchangers at approximately 1651 hours. "Presently, Unit 3 is in Mode 1 at 100% power with all systems stable." The failed valve is a manual 24" butterfly valve. The bypass valve can maintain full flow. During this event, Operations personnel monitored CCW temperature. Unit 3 briefly entered T.S. 3.0.3 before restoring flow using the bypass. A high RCP temperature alarm was received following the momentary loss of ICW flow. The valve failure was accompanied with a loud bang. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-08-11
47146 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2011-08-11 19:28 | 2011-08-11 20:30 | 2011-09-16 | SAFEGUARDS REPORT - DEGRADATION OF DETECTION SYSTEM Safeguards system degradation related to monitoring and detection of PA boundary. Compensatory actions taken. Call the Headquarters Operations Officer for details. The NRC Resident Inspector has been notified. * * * UPDATE FROM MARK EGHIGIAN TO JOHN KNOKE AT 1339 EDT ON 09/16/11 * * * This event has been reevaluated by the licensee using the guidance provided in NRC Generic Letter 91-03 and Regulatory Guide 5.62, Rev 1, and is being retracted. Call the Headquarters Operations Officer for details. The NRC Resident Inspector has been notified. Notifications provided to R3DO (Tamara Bloomer) and 73.71 Group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-08-11
47144 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-08-06 04:30 | 2011-08-11 15:06 | 2011-08-17 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was received from the state of California via e-mail: "On August 8, 2011, Mr. Todd Rucker, RSO from Pavement Engineering, Inc., notified RHB [Radiation Health Branch] Sacramento that one of their moisture-density gauge operators lost a gauge at their job site on August 6, 2011 at approximately 4:30 am. The gauge had been borrowed from A. Teicher & Son, Inc., License No 4030-34. The gauge was used on a job site on HWY 70 in Yuba County, near the town of Olivehurst, CA." The lost gauge is a Troxler, Model 4640-B, Serial number T464 1793. This model moisture density gauge has an 8 mCi Cs-137 source. California event number: 080611 * * * UPDATE FROM EPHRIME MEKURIA TO CHARLES TEAL ON 8/17/11 AT 1731 EDT * * * Pavement Engineering has found the lost gauge. Notified R4DO (Hay), FSME EO (Watson), ILTAB (Johnson), and Mexico via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-08-16
47143 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-08-11 11:38 | 2011-08-11 15:29 | 2011-08-11 | UNPLANNED PRIMARY CONTAINMENT ISOLATIONS "At 1138 CDT, while in the process of shutting down as required by Technical Specifications (Reference EN# 47142), with the reactor at approximately 15 percent power, a manual scram was inserted in order to complete the TS Required Action of being in Mode 3 within 12 hours. Upon inserting the manual scram, reactor water level dropped below 170 inches resulting in Primary Containment Isolation System (PCIS) Groups 2, 3 and 4 being received. This reactor water level response is considered normal following a reactor scram from power due to void collapse in the reactor vessel. Reactor water level is currently being controlled in the normal band. All PCIS group isolations went to completion and were subsequently reset. The PCIS isolations all functioned properly. This event is being reported pursuant to 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-08-11
47142 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-08-11 03:27 | 2011-08-11 07:02 | 2011-08-11 | INITIATION OF TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 0327 [CDT] on August 11, 2011, NextEra Energy Duane Arnold commenced a reactor shutdown as required by TS 3.7.2.B for both River Water Supply subsystems inoperable. At 0008 [CDT], both River Water Supply subsystems were declared inoperable as a result of high differential pressure across the intake travelling screens. TS 3.7.2.B requires that one River Water Supply subsystem be restored or commence reactor shutdown. While the River Water Supply system is currently supplying rated flow, high differential pressure across the travelling screens indicates the potential for eventual degraded flow. This event is being reported pursuant to the requirements of 10 CFR 50.72(b)(2)(i), as a TS required shutdown. "Additionally, the current condition of both trains of River Water Supply inoperable also potentially affects the plant capability to remove residual heat. Therefore, this event is also being reported under 10 CFR 50.72(b )(3)(v)(B), as an event that could prevent fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 68 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(B) |  |  | 0 | 2011-08-11
47141 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-08-11 00:16 | 2011-08-11 01:05 | 2011-08-11 | MANUAL REACTOR SCRAM INSERTED DUE TO A FEEDWATER LEAK ON A MIN FLOW LINE "NMP2 inserted a manual reactor scram due to a through wall leak on feedwater pump 2FWS-P1A minimum flow line. 2FWS-P1A has been removed from service to minimize the leak. All control rods inserted and all systems functioned as designed. The unit will remain in hot shutdown until plant startup." All systems functioned as required and the scram was uncomplicated. The licensee plans to issue a press release and has informed the NRC Resident Inspector and the New York State Public Service Commission. * * * UPDATE AT 1035 EDT ON 8/11/11 FROM MANLEY TO HUFFMAN * * * The licensee will not be issuing a press release regarding this manual scram. R1DO (Powell) notified. | 0 | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-08-11
47140 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-07-22 | 2011-08-10 16:23 | 2011-08-10 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The following information was received by e-mail: "On August 8, 2011 the licensee's radiation safety officer called to advise the Agency [Illinois Emergency Management Agency] of a gauge shutter failure. During the performance of routine operability checks and area surveys on July 22, 2011 it was found that the shutter lever on a Kay- Ray/Sensall 7062P could not be completely closed. The gauge is permanently mounted to a 12 inch pipeline in a remote area of the refinery. The line runs overhead at a height of approximately 10 to 12 feet. Arrangements were made to have personnel with duties in the area to be notified of the shutter failure and to prohibit any work in the immediate area. The nearest work station was determined to be over 200 feet away. Radiation levels at one foot from the gauge were measured at less than 1 milliR/h. "After contacting the manufacturer on August 8 to determine the best course of action, the licensee applied a lubricant to the shutter area. Subsequently, after waiting a day, attempts to close the shutter were successful. The shutter is now operating as expected. Arrangements have been made to have a service licensee visit the site to ensure operation is as expected. As the failure was noted during performance of routine tests designed to detect such failures, no changes to the licensee's procedures or protocols are anticipated. The licensee was reminded of the importance of promptly reporting such events in the future." The sealed source gauge is a Kay-Ray/Sensall model 7700-Y containing 0.14 Ci of CS-137. The fixed gauge is a Kay-Ray/Sensall, Model number 7063P; Serial number S96G1816. Illinois Event Number IL11105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-08-15
47139 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2011-08-10 07:30 | 2011-08-10 14:42 | 2011-08-10 | EMERGENCY SIRENS OUT OF SERVICE DUE TO A COMMUNICATION PROBLEM "At approximately 0730 [EDT] on 8/9/11 a siren system communication problem was discovered by Emergency Preparedness personnel at the Harris Nuclear Plant (HNP). Telecommunications was contacted to troubleshoot the problem and at approximately 0820 [EDT] the communications system was restored. A previously scheduled quarterly growl test was conducted with 83 sirens performing satisfactorily. Upon further investigation, it was determined that there were communication failures recorded during the 0600 [EDT] report. "20 of the 83 sirens were impacted by the communications errors. The previous 0000 [EDT] report indicated no communications errors. Investigation is continuing as to the ability of the sirens to be activated during the period the errors were received. It is likely that the ability to activate the sirens had been lost, therefore, this event is reportable per 10 CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The cause of the communication errors are believed to be due to radiofrequency disturbances however the investigation is ongoing. "In the event that the sirens had been needed, the State of North Carolina and all four counties within the 10-mile emergency planning zone would have implemented mobile route alerting, as detailed in the Emergency Plan." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-10
47138 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-08-10 01:00 | 2011-08-10 02:06 | 2011-08-12 | POTENTIAL LOSS OF TSC OPERABILITY WHILE PERFORMING PLANNED MAINTENANCE "A planned maintenance evolution at the Duane Arnold Energy Center (DAEC) will have the potential to remove the plant computer systems (Plant Process Computer, Intranet, and Internet) from service. The TSC would be rendered non-functional with the loss of all computer systems. The replacement and testing of the automatic power transfer relay is expected to de-energize the computer systems for less than 20 minutes at any time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Maintenance will be terminated and power will be restored to the plant computer systems. The restoration of power to all computer systems is estimated to take less than one hour. "This notification is being made in accordance with 10CFR50.72 (b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF). An update will be provided once the plant computer systems power supplies have been restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM STEVE BREWER TO CHARLES TEAL ON 08/10/11 AT 1305 EDT * * * The TSC has been restored to operational status. The licensee has notified the NRC Resident Inspector. Notified R3DO (Dickson). * * * UPDATE FROM ROBERT SPADING TO JOE O'HARA ON 08/12/11 AT 2205 EDT * * * The licensee is performing planned maintenance on the TSC automatic power transfer relay which could render the TSC inoperable if power to the TSC computers is lost. Maintenance is expected to commence at 2130 CDT. The licensee has notified the NRC Resident Inspector. Notified R3DO (Peterson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-10
47137 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-08-09 12:30 | 2011-08-09 16:25 | 2011-08-09 | INADVERTENT ACTUATION OF AN EMERGENCY SIREN "[There was an] inadvertent actuation of siren 46 due to water intrusion into the control box. The door was knocked open by a falling tree branch. Power to the siren has been isolated to prevent re-occurrence. Repair is scheduled for August 10, 2011" The licensee notified both Wayne and Monroe counties and the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-09
47136 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-08-08 16:45 | 2011-08-09 15:41 | 2011-08-09 | POTENTIALLY CONTAMINATED PERSON TRANSPORTED OFFSITE FOR MEDICAL TREATMENT "A person working at the sampling plant driving a forklift to move drums began having chest pains. The individual was taken to the site dispensary for evaluation. An ambulance was requested to take the employee to the hospital for further evaluation. The employee had contamination on his coveralls and boots. Before leaving for the hospital the employee's plant clothing was removed and surveyed. There was no detectable contamination on the employee when he was transferred to the hospital." The NRC Region II Senior Fuel Cycle Inspector (Gibson) has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-08-09
47135 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-08-07 | 2011-08-09 12:26 | 2011-08-09 | AGREEMENT STATE REPORT - THERASPHERE TREATMENT TO WRONG LOBE OF LIVER The following was received via fax: "The Wisconsin Department of Health Services (DHS) received a phone call from the Radiation Safety Officer (RSO) on August 8, 2011 that a patient received a dose of 1.05 GBq of Y-90 Theraspheres on July 7, 2011 to the wrong side of the liver as documented on the written directive. The patient was scheduled for treatment of 1.04 GBq Y-90 Theraspheres for multinodular hepatocellular cancer (HCC) to the left lobe of the liver. The dosimetry for Y-90 Theraspheres was based on volume (mass) of the lobe bearing the tumors (the patient has tumors on both lobes, right and left). A treatment plan was created for the left lobe (using the volume of the left lobe) but during the procedure the right lobe was treated with the prescribed dose for the left lobe. "DHS will be conducting an investigation on August 12, 2011 and the licensee will be submitting a 15 day written report concerning the medical event." WI Event Number: 110012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-08-15
47134 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-08-05 19:44 | 2011-08-06 22:25 | 2011-10-25 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The licensee notified the state of California that on 8/5/2011 they had discovered one of its tritium exit signs missing. The licensee is investigating. The sign contained approximately 20 curies of H-3. * * * RETRACTION BY GENE FORRER TO VINCE KLCO ON 10/25/11 AT 1801 EDT * * * Following a licensee review of inventory, the missing tritium exit sign was discovered. Therefore, the event is being retracted. Notified the R4DO (Haire), FSME EO(Chang), ILTAB via email and Mexico via fax. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-08-10
47133 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2011-08-06 11:19 | 2011-08-06 17:41 | 2011-08-06 | AUTOMATIC REACTOR TRIP DUE TO DROPPED CONTROL ELEMENT ASSEMBLY "On August 6, 2011, at approximately 1119 MST, the Palo Verde Unit 1 reactor tripped from approximately 100% rated thermal power due to a valid Reactor Protection System (RPS) actuation. The actuation was caused by a dropped Shutdown Group Control Element Assembly (CEA) during surveillance testing to exercise the CEAs. Following the reactor trip, one Regulating Group CEA indicated a failure to insert, however the CEA subsequently indicated fully inserted with no additional operator actions approximately 2 minutes after the trip. All CEAs are currently inserted fully into the reactor core. With the exception of the delayed indication of one CEA to fully insert, this was an uncomplicated reactor trip. No emergency classification was required per the Palo Verde Emergency Plan. No automatic or manual ESF actuations occurred and none were required. Safety related electrical buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3." Decay heat is being removed via the steam generators to the main condenser using the turbine bypass valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-08-06
47132 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-08-06 05:30 | 2011-08-06 17:44 | 2011-08-06 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following information was obtained from the State of California via email: "At 0530 PDT on 8/6/2011, a Model 4640 Troxler material density gauge belonging to Pavement Engineering of Redding, CA was lost at a construction site between McAllen Road and Olivehurst on Highway 70 south of Yuba City, CA. The operator set the gauge down by the side of the road and returned to find it missing. It was reported missing at 1105 PDT on 8/6/2011 to the California Emergency Management Agency who contacted the California Department of Public Health, Radiological Health Branch (RHB) at 1126 PDT. Sutter County Sheriff's office has responded and is investigating. Also contacted was Sutter County Fire Dept. A health physicist has been deployed from RHB to assist in the search with a variety of radiation survey instruments in case the gauge was misplaced by the side of the road. "The gauge contains 9 mCi of Cs-137. " * * * UPDATE ON 08/06/2011 AT 1936 PDT FROM JOHN FASSELL (VIA EMAIL) TO ERIC SIMPSON * * * "A survey by RHB staff over 0.6 miles of highway margin assisted by licensee personnel failed to recover the gauge. A reward will be posted by the licensee." Notified R4DO (Hagar) and FSME EO (McKenney) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-08-10
47131 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2011-08-05 16:30 | 2011-08-06 13:22 | 2011-08-06 | MATERIAL DISCOVERED IN AN UNANALYZED CONTAINER "Condition Description: During the morning of 8/05/2011, Radiation Protection personnel discovered potentially contaminated waste being stored in an unmarked container in the mass spec room. Radiation Protection Management and Criticality Safety personnel were notified. Upon learning at 4:30 pm [that] the unmarked container was not a Safe By Design [SBD] container, a criticality anomalous condition was declared at approximately 4:30 pm, in accordance with CR-3-1000-04, based on a violation of Nuclear Criticality Safety (NCS) guidelines and procedural requirements. Thus, at 4:30 pm, a cognizant individual was notified of the potential safety significant condition and, therefore, understood the condition could adversely impact safety. This report is being submitted as a conservative measure as the volume of waste, mostly gloves and wipes, was much less than 12 liters and could easily fit into a SBD container. The material that could be surveyed was cleared as non-radioactive material, and placed in a clean waste container. The material that could not be surveyed was transferred to a SBD container pending further analysis. The initial analysis of the material placed in the SBD container did not indicate the presence of any trace uranic material. At no time was there ever a concern of imminent criticality or for the health and safety of workers at URENCO USA. "(1) Radiological or chemical hazards involved, including isotopes, quantities, and chemical and physical form of any material released: Potential Uranium 235 contaminated PFPE oil ampules in a solid state. "(2) Actual or potential health and safety consequences to the workers, the public, and the environment, including relevant chemical and radiation data for actual personnel exposures to radiation or radioactive materials or hazardous chemicals produced from licensed materials (e.g., level of radiation exposure, concentration of chemicals, and duration of exposure): None. Radiological surveys were taken on the material in the container. No radiation levels or contamination levels were noted above background. All of the material, except for 4 ampules, were released as non-radioactive. Although the ampules did not have radiation levels above background, there was a slight potential for a trace level or uranic contamination. "(3) The sequence of occurrences leading to the Condition, including degradation or failure of structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences: One 24 liter container was placed in the mass spec room. Instead of a 24 liter container, a 12 liter SBD container should have been utilized. Chemistry personnel used the 24 liter container to store potentially radioactive material. The actual quantity of material in the 24 liter container was less than 12 liters. Personnel should not have used the 24 liter container to store potentially radioactivity contaminated material. This was a violation of site procedure RW-1003-09, Rev. 5. "(4) Whether the remaining structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function: The structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function. "(5) External conditions affecting the Condition: None. "(6) Additional actions taken by the licensee in response to the Condition: Radiation Protection Technician notified her supervisor who notified criticality safety, who then notified the shift manager. The 24 liter container was removed from the mass spec room. Radiological surveys were taken and all material released as clean except for 4 potentially contaminated ampules. Initial surveys did not find radiation levels above background on the 4 ampules. The 4 potentially contaminated ampules were placed into a 12 liter SBD container until they undergo a final analysis to determine if they contained trace uranic material or not. Actions have been initiated to establish a waste accumulation area in the mass spec room in accordance with RW-3-1000-09. Meetings have been set up with Chemistry personnel to review control of potentially contaminated material. The Criticality Safety Officer generated Condition Report 2011-2560 -- Use of non-SBD Container to collect potentially uranic contaminated waste. "(7) Status of the condition (e.g., whether the condition is on-going or was terminated): The condition is not ongoing as the material has been placed in a SBD container. "(8) Current and planned site status, including any declared emergency class: Plant is operational; condition is non-emergency. "(9) Notifications, related to the condition that were made or are planned to any local, State, or other Federal agencies: None "(10) Status of any press releases, related to the Condition that were made or are planned: None." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2011-08-06
47130 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-08-06 06:17 | 2011-08-06 10:45 | 2011-08-06 | INITIATION OF TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On August 6, 2011, Reactor Protection System (RPS) power supply 1B failed resulting in a partial loss of power to Primary Containment Isolation System (PCIS) groups and an invalid actuation of those PCIS groups. PCIS groups 1 and 2 received partial isolation signals with no subsequent system isolations, as designed. PCIS group 3, 6, and 8 received partial isolation signals with resulting system isolations, also as designed. The combination of loss of RPS 1B and PCIS group 6 isolation resulted in the isolation of the Drywell Floor Drain Sump and the Drywell Continuous Atmospheric Monitor for both particulate and gaseous activity. Thus, both means of automatic monitoring of Reactor Coolant System leakage became inoperable. Unit 1 entered Technical Specification Limiting Condition for Operation (LCO) 3.4.5.D (all required leakage detection systems inoperable) and immediately entered LCO 3.0.3 as required. "At the time of occurrence, RPS 1A was being supplied from its alternate source for scheduled maintenance. Thus, the alternate source was not available to RPS 1B. "Unit 1 entered LCO 3.0.3 at 0524 [CDT], 'Initiate actions within one hour to place the unit in MODE 2 within 10 hours; MODE 3 within 13 hours; and MODE 4 within 37 hours.' At 0617, Unit 1 began reducing reactor power to comply with LCO 3.0.3. "This event requires a 4 hour report IAW 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The PCIS isolations which occurred at 0524 CDT are also reportable within 8 hours per 10CFR 50.72(b)(3)(iv)(A) 'Any event or condition that results in a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B)(2), 'General Containment Isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs)], except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' This event also requires an LER within 60 days per 10CFR 50.73(a)(2)(iv)(A). The event time for the PCIS isolations is 0524 CDT. "The NRC resident inspector has been notified. "Service Request 412927 was initiated in the Corrective Action Program." * * * UPDATE ON 08/06/2011 AT 1350 EDT FROM WILLIAM BAKER TO ERIC SIMPSON * * * Browns Ferry restored power to the 1B Reactor Protection System power supply at 1208 CDT, reset all isolations and exited LCO 3.0.3. The licensee plans to return the unit to full power. The licensee notified the NRC Resident Inspector. Notified R2DO (Binoy Desai). | 97 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-08-06
47129 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-08-06 03:22 | 2011-08-06 03:53 | 2011-08-06 | UNUSUAL EVENT AND PLANT SHUTDOWN DUE TO DRYWELL UNIDENTIFIED LEAKAGE GREATER THAN 10 GPM "At 0152 [EDT], Nine Mile Point Unit 2 received red alarms for containment monitoring cabinets 10A and 10B along with a rise in drywell floor drain leakage and drywell pressure. "At 0205 [EDT], Nine Mile Point Unit 2 entered technical specification action statement (TS 3.4.5 B) due to unidentified leakage rise of greater than 2 gpm within 24 hours. "At 0217 EDT, the control room commenced power reduction to mitigate the rise in drywell leakage and drywell pressure. "At 0322 EDT, Nine Mile Point Unit 2 declared an Unusual Event (EAL 2.1.1) due to unidentified drywell leakage greater than 10 gpm. Actual drywell floor drain leakage reached 11.3 gpm. "The cause of the rise in unidentified leakage is unknown at this time. "At 0345 EDT, Nine Mile Point Unit 2 has commenced a plant shutdown." The licensee has notified State and local authorities. The NRC Resident Inspector has been notified. * * * UPDATE ON 08/06/2011 AT 1140 EDT FROM JULIAN THOMPSON TO DAN LIVERMORE * * * The licensee terminated Notice of Unusual Event at 1127 EDT because leakage rates, drywell level, drywell pressure, rad levels, and all other parameters on the licensee checklist were normal and stable. The licensee is continuing to power down in order to perform inspections in the drywell area. The licensee notified State and local authorities and the NRC Resident Inspector. Notified: IRD MOC (Gott), R1RA (Dean), R1DO (Bellamy), NRR (Leeds), NRR EO (Cheok), DHS (Inzer) and FEMA (O'Connel) . | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2011-08-06
47128 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-08-05 19:32 | 2011-08-05 21:14 | 2011-08-05 | OFFSITE NOTIFICATION DUE TO INADVERTENT EMERGENCY NOTIFICATION SIREN ACTUATION "The purpose of this report is to provide a telephone notification under 10CFR50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of one Oswego County Emergency notification siren at approximately 1932 EDT on 8/5/2011. Initial notification to the James A Fitzpatrick control room of the siren activation was via the RECS [Radiation Emergency Communication System] Notification System. Power was removed to the affected siren by off-site repair personnel at 1948 EDT. "The affected siren provides coverage to Oswego County. The sirens are utility owned and shared with the Nine Mile Point site. "In the event the sirens are needed, the county has its Hyper-Reach (911 call back system) on standby. "This issue has been entered into the station corrective action program. "The NRC Sr. Resident Inspector has been notified." The licensee notified the State of New York and Oswego County. See similar EN #47127. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-05
47127 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-08-05 19:32 | 2011-08-05 21:04 | 2011-08-05 | OFFSITE NOTIFICATION DUE TO INADVERTENT EMERGENCY NOTIFICATION SIREN ACTUATION "One of the 37 prompt notification sirens surrounding the James A. Fitzpatrick (JAF) and Nine Mile Point (NMP) sites spuriously activated at time 1932 EDT. "The Oswego County 911 Center notified the NMP emergency preparedness department of the inadvertent siren activation. "Repair technicians have deactivated and silenced the faulty siren as of time 1948 EDT. "The cause of the inadvertent siren activation is not yet known. This issue has been entered into the site's corrective action program." The NRC Resident Inspector has been informed. See similar EN #47128. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-08-05
47126 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-08-05 08:54 | 2011-08-05 16:53 | 2011-08-05 | 24-HOUR FITNESS-FOR-DUTY REPORT A non-licensed contract supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2011-08-05
47125 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-08-03 17:00 | 2011-08-04 14:21 | 2011-08-04 | 24-HOUR FITNESS-FOR-DUTY REPORT A non-licensed, non-supervisory employee was in possession of and had used a prescription drug for which the employee did not have a valid prescription. The employee's access to the facility has been suspended. Contact the Headquarters Operations Officer for further details. The licensee notified the NRC Resident. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2011-08-04
47124 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-08-04 08:35 | 2011-08-04 14:18 | 2011-08-04 | LOSS OF POWER TO EMERGENCY SIRENS DUE TO WEATHER "At 0945 CDT on August 4, 2011, the TVA Corporate Operations Duty Specialist notified the Browns Ferry Shift Manager that 35 of the emergency sirens (33 in Limestone County and 2 in Morgan County) had been inoperable since 0835 CDT due to loss of power from thunderstorm activity. This constitutes a significant degradation (greater than or equal to 30%, i.e. 35 out of 100 sirens) in the BFN Alert and Notification System and is therefore reportable. "At 1002 CDT 14 sirens were restored resulting in 21 sirens being out of service (19 in Limestone County and 2 in Morgan County), and a significant degradation of the BFN Alert and Notification System no longer exists. "The following notifications have been made: State of Alabama at 0950 CDT Local government of Limestone County at 0954 CDT Local government of Morgan County at 0959 CDT NRC Resident at 1005 CDT "This 8 hour notification is being made per the reporting requirements specified by 10 CFR 50.72(b)(3)(xiii), 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability.'" The licensee has notified the NRC Resident Inspector. | 50 | 50 | 50 | 50 | 50 | 50 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-04
47123 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2011-08-04 | 2011-08-04 12:18 | 2011-09-07 | PART 21 - POSSIBLE WELD ROD CERTIFICATION ISSUES "On March 3, 2011, an audit of one of Fisher Control's suppliers determined that weld rod certified by an ISO process (instead of ASME) might have been used for weld repair of castings intended for nuclear service. Fisher and the supplier are in the process of reviewing all orders affected by this issue and have yet to find any that used the subject non-confirming material "Fisher expects to complete this evaluation by August 26, 2011. At this time, if the review determines that a failure to comply condition exits, Fisher will issue notification per the requirements of 10 CFR 21.21(b)." * * * UPDATE AT 1300 EDT ON 9/7/11 FROM FITZGERALD TO HUFFMAN VIA FACSIMILE * * * "Fisher Controls is providing this final notification per the requirements of 10CFR21.21(a). "On August 3, 2011, Fisher provided an interim report concerning an audit of one of Fisher Control's suppliers and the determination that weld rod certified by an ISO process (instead of ASME) might have been used for weld repair of castings intended for nuclear service. "Fisher and the supplier have completed the process of reviewing all orders affected by this issue and did not find any orders that used the subject non-conforming material. "Therefore, Fisher will not issue a notification per the requirements of 10CFR21.21(b), because the review determined that a failure to comply condition does not exist." Notified the NRC Part 21 Group and all NRC Regional RDOs via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-08-04
47122 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-08-03 10:11 | 2011-08-03 16:58 | 2011-08-03 | 24-HOUR FITNESS-FOR-DUTY REPORT "A non-licensed supervisor tested positive for alcohol during a random fitness-for-duty test. The employee's access to the facility has been suspended. Contact the Headquarters Operations Officer for further details. "NRC Resident has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2011-08-03
47121 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-06-08 | 2011-08-03 14:44 | 2011-08-03 | AGREEMENT STATE REPORT INVOLVING AN UNDER-DOSE The following report was received from the State of Virginia via fax: On June 8, 2011, a prostate implant procedure was performed utilizing 57 seeds of 0.406 mCi/seed to a gland size of 33.7 cc. The intended dose was 145 Gy. On August 2nd during a post-plan evaluation, a CT was performed where it was discovered the base of the prostate was under-dosed. It is estimated that all 57 seeds are 1 cm short of the far superior position. The prescribed minimum D-90 dose was 80 Gy, a calculation was performed estimating that the actual dose delivered was 51 Gy. The physician and patient have been notified. A follow-up visit has been scheduled. Virginia Event Report ID No.: VA-11-06 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-08-09
47120 | -1 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2011-08-02 13:46 | 2011-08-02 21:27 | 2011-08-18 | VULNERABILITY FROM A POTENTIAL HIGH ENERGY LINE BREAK "The following condition is being reported by Arkansas Nuclear One, Unit 2 (ANO-2) in accordance with 10CFR 50.72(b)(3)(ii)(B), 'Unanalyzed Condition' and in accordance with 10CFR 50.72(b)(3)(v)(D), 'A Condition That Could Have Prevented Fulfillment of a Safety Function.' On 08/02/2011 at 1346 CDT, the ANO Unit 2 Control Room was notified by Engineering that a postulated High Energy Line Break (HELB) could potentially cause both the Red and Green Train Emergency Safeguard Features (ESF) Rooms to exceed their environmentally qualified temperature limits. This postulated condition would be possible due to normally open room purge dampers exposing ESF equipment in these rooms to a common area impacted by HELB conditions. The ESF Rooms contain the Red and Green Trains of High Pressure Safely Injection Pumps, Low Pressure Safety Injection Pumps, Containment Spray Pumps, and Shutdown Cooling Heat Exchangers. Until further Engineering evaluation can be performed to validate this postulated scenario, ANO-2 has closed ESF room purge dampers to provide Red and Green ESF train separation during a potential HELB event. "Refer to [ANO-2] Condition Report CR-ANO-2-2011-02772 for further information. The NRC Resident has been notified." * * * RETRACTION FROM STEVE COFFMAN TO HOWIE CROUCH AT 1514 EDT ON 8/18/11 * * * "The purpose of this notification is to retract a previous report made by Arkansas Nuclear One, Unit 2 (ANO-2) on 08/02/2011 at 2127 [EDT] (EN# 47120). The initial report documented that a postulated High Energy Line Break (HELB) could potentially cause rooms containing both trains of Emergency Safeguard Features (ESF) equipment to exceed their environmentally qualified temperature limits. The ESF rooms contain the High Pressure Safely Injection Pumps, Low Pressure Safety Injection Pumps, Containment Spray Pumps, and Shutdown Cooling Heat Exchangers. Specifically, normally open ESF room purge dampers exposing both trains of ESF equipment to a common area impacted by postulated HELB conditions were not modeled in the ANO-2 HELB analysis. This condition was reported in accordance with 10CFR 50.72(b)(3)(ii)(B), 'Unanalyzed Condition' and 10CFR 50.72(b)(3)(v)(D), 'A Condition That Could Have Prevented Fulfillment of a Safety Function'. "Since the initial report, Engineering has revised the ANO-2 HELB model to include the effects of the open ESF room purge dampers. The resulting analysis shows that a HELB event will not cause the required ESF equipment to exceed analyzed temperature limits with the room purge dampers in the open configuration. Therefore, the condition did not result in 'a condition that could have prevented the fulfillment of a safety function' and did not result in an 'unanalyzed condition that significantly degrades plant safety'. Based on the revised HELB analysis, the previous report (EN#47120) describes a condition that does not meet the reporting requirements of 10CFR 50.72(b)(3)(v)(D) or 10CFR 50.72(b)(3)(ii)(B) and is therefore retracted. "The NRC Resident Inspector has been informed of the retraction." Notified R4DO (Hay). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-08-02
47119 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-08-03 04:00 | 2011-08-02 19:52 | 2011-08-04 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 0400 [CDT] on Wednesday, August 3, 2011, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system will be removed from service for planned preventative maintenance activities on the TSC ventilation radiation monitoring system (PING). The TSC air handing and filtration units will be nonfunctional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 48 hours. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning procedures and checklists. If radiological conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with, EP-AA-112-200-F-01. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM JASON SOLBERG TO CHARLES TEAL ON 8/4/11 AT 2040 EDT * * * "At 1905 CDT on August 4, 2011, Dresden TSC ventilation was restored. The emergency response facility is fully functional at this time. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Skokowski). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-02
47118 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-06-04 22:43 | 2011-08-02 19:52 | 2011-08-02 | INVALID SIGNAL CAUSED A PARTIAL CONTAINMENT SYSTEM ISOLATION "While preparing to restore AOV 3-1601-22, Drywell /Torus Vent Valve, to operable status following solenoid replacement, operations personnel attempted to open AOV 3-1601-22 in accordance with plant procedures. When the control switch was taken to the open position, the U3 control room received a partial U3 Containment System Isolation. Light indication was lost for several Containment Isolation valves. "Troubleshooting revealed that a control power fuse had blown during the attempt to open AOV 3-1601-22. Operations personnel entered the appropriate Technical Specification and Technical Requirement Manual Required Actions. "Operations personnel replaced the blown fuse and indication was restored to the affected valves. "Following the fuse replacement, the following containment air sample valves were observed to have repositioned during the event: 3-8501-3B, 3-8501-1B, 3-8501-5B, 3-9205B, 3-9206B, 3-9207B, and 3-9208B. "Subsequent troubleshooting revealed that during the AOV solenoid replacement, the conduit cover screw penetrated the tape of an electrical splice and caused a short to ground. "The solenoid was repaired and systems were restored as required. "During this event, all valves repositioned to their intended safety position. There was no loss of function as a result of this condition. Therefore, the health and safety of the public were not compromised. "Since this ESF actuation was caused by an invalid signal, it is being reported pursuant to 10 CFR 50.73(a) (2) (iv) (A) as specified by 10 CFR 50.73(a) (1), which allows a telephone notification in lieu of a written licensee event report within 60 days." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-08-02
47117 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2011-07-20 | 2011-08-02 16:43 | 2012-07-12 | AGREEMENT STATE REPORT OF LOST GENERAL LICENSED DEVICES The following report was received from the State of Alabama via fax: "On the afternoon of July 20, 2011, a representative of the Alabama Office of Radiation Control [the Agency] discovered that five general license devices containing radioactive material were unaccounted for at the closed Quantegy, Inc. facility located in Opelika, AL. The Agency representative was there to perform a routine inspection of general licensed activities and discovered that the facility was being demolished and the metal was being sold for scrap. Records indicate that the company did possess at one time fifteen general license devices. The Agency representative was able to account for ten of the fifteen devices. Five devices are unaccounted for at this time. The demolition crew, the scrap company and the Georgia Department of Natural Resources have been made aware of the missing devices. Also, the Agency is working with the manufacturer to determine if these devices were returned to the manufacturer in the past. The devices missing include four NDC Model 105 devices containing 250 millicuries (original assay) each of Cm-244. The serial numbers on record for these devices are 6075, 6025, 6102 and 6024. The fifth device missing is an NDC Model 103 device containing 150 millicuries (original assay) of Am-241. The serial number on record for this device is 2063. "This is all the information that this Agency has at this time and is current as of 1530 CDT, August 2, 2011." Alabama Incident No.: 11-30 * * * UPDATE FROM THE ALABAMA OFFICE OF RADIATION CONTROL TO HUFFMAN VIA FAX ON 7/12/12 AT 1605 EDT * * * "On August 2, 2011, the NRC Operations Center was informed of an incident when five general devices containing radioactive material were determined to be unaccounted for at the closed Quantegy, Inc. facility located in Opelika, AL. At that time, an Agency representative was able to account for ten general license devices. These ten devices were secured in a building on site. On July 12, 2012, the Agency was advised that five of the ten in storage were now missing and are considered stolen. All five devices are NDC model 105 gauges each containing Curium-244. The serial number and activity of each are noted below: NDC 105 SN 6025 Cm-244 250 mCi on 11/84 NDC 105 SN 6062 Cm-244 250 mCi on 8/87 NDC 105 SN 6064 Cm-244 250 mCi on 10/87 NDC 105 SN 6027 Cm-244 100 mCi on 5/98 NDC 105 SN 6001 Cm-244 250 mCi on 10/83 "The owner of the property indicated that the devices were stolen with other property in the recent past and the local law enforcement was notified. The time and date of the theft has not yet been made available to the Agency. A copy of the police report has been requested. The five remaining devices were impounded by Agency personnel for security on the morning of July 12, 2012." R1DO (Burritt) has been notified. FSME Resources ILTAB notified via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2011-08-05
47116 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-08-02 09:48 | 2011-08-02 15:30 | 2011-08-02 | FITNESS-FOR-DUTY REPORT INVOLVING AN EMPLOYEE SUPERVISOR A utility non-licensed supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The individual's access to the site has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2011-08-02
47115 | -1 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-07-28 12:00 | 2011-08-02 10:54 | 2011-08-03 | FIRE AT RADIATION THERAPY PRACTICE The following was received from the state via e-mail: "N.C. Radiation Protection Section was notified on 1 August 2011 by the Regional Medical Physicist for NC Radiation Therapy Management Services, Inc. d/b/a 21st Century Oncology of a major fire on the fifth floor of the building in which the licensee operates a radiation therapy practice on the ground floor. The ground floor did not receive direct fire/smoke damage, but did realize significant water damage to portions of its facility. One fireman was killed and 10 injured while fighting the fire. The entire building has been closed and is currently under the command of the Bureau of Alcohol, Tobacco, Firearms and Explosives (ATF) National Response Team (NRT) along with special agents from their Charlotte Field Division. Other agencies involved in this investigation are the North Carolina State Bureau of Investigation and the Asheville Fire Department. The licensee has been permitted to enter its facility once to retrieve critical computer servers that are utilized in patient care at their clinics throughout western North Carolina. The licensee examined its HDR remote afterloader containing one Ir-192 sealed source (<12 Ci) and found the afterloader to be undamaged and securely locked in a treatment vault. The licensee also has a small number of Cs-137 brachytherapy sealed sources (<450 mCi total) in a locked lead source safe within a locked source storage room. The licensee determined that there was no damage to the source storage room and that the room is secure. The licensee is in the process of contracting Nucletron to remove and dispose of the Ir-192 sealed source and is investigating the disposal of all Cs-137 brachytherapy sealed sources. "The Radiation Protection Section has assigned an inspector to contact the ATF to determine the earliest possible time for a site visit. "N.C. Radiation Protection has not received any media attention as of this report. No press release has been issued." NC Event Report ID No. NC-11-42 * * * UPDATED AT 1515 EDT ON 08/03/11 FROM CLIFF HARRIS TO S. SANDIN * * * The State of North Carolina is retracting this report based upon further review and discussions with NRC Region I Office staff in that the sealed sources were not impacted by the fire. Notified R1DO (Bellamy) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-08-05
47114 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-08-02 07:00 | 2011-08-01 19:43 | 2011-08-02 | PLANNED MAINTENANCE THAT WILL RESULT IN TECHNICAL SUPPORT CENTER UNAVAILABILITY "On August 02, 2011, at 0700 EDT, the Technical Support Center will be unavailable due to pre-planned maintenance to maintain the Technical Support Center and Emergency Response Data Acquisition and Display System ventilation system. The TSC is expected to be restored to available status in approximately 12 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures, and the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM TIM MILLER TO VINCE KLCO ON 8/2/2011 AT 1726 EDT* * * On August 2, 2011 at 1645 EDT the TSC was restored and is now fully functional. The licensee notified the NRC Resident Inspector. Notified the R2DO (Desai). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-08-01
47113 | 0 | LIBERTY HOSPITAL |  |  |  |  | 2011-07-29 | 2011-08-01 12:27 | 2011-08-01 | RADIATION ALARM AT WASTE FACILITY DUE TO IMPROPER DISPOSAL OF RADIOACTIVE MATERIAL On 7/28/11 a patient received a 28.3 mCi dose of I-131 as treatment for a hyperthyroid condition. The patient was incontinent and not discharged from the hospital as originally planned. On 7/29/11 a landfill company informed the State of Missouri that a load of waste received from Liberty Hospital caused an alarm on their radioactive portal detector. Investigation identified two (2) soiled diapers which were bagged and returned to the hospital for proper disposal. Liberty Hospital discussed this incident with the NRC Region III staff who recommended that the hospital report the incident. Also, the RSO for the facility has corrective actions to preclude future incidents under review. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-08-01
47112 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2011-06-16 12:00 | 2011-08-01 12:03 | 2011-08-01 | PART 21 - EMERGENCY DIESEL GENERATOR FAILED AIR START MOTOR The following information was received by facsimile: "COMPONENT: Air start motors with friction-clutch inertia drives (not pre-engagement type) "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 06/16/11 upon receipt of a failed air start motor from Exelon - Clinton. According to information provided by Clinton Nuclear Plant, they experienced a slow start of an EDG during one of their surveillance runs. Subsequent troubleshooting revealed that one of the air start motors had failed. Specifically, it was found that the starter drive had failed which prevented the air start motor from applying full starting torque to the engine. The inspections performed by Clinton indicated the failed motor had what appeared to be excessive preload applied to the springs of the drive clutch which led to spring roll and fragmentation. Clinton had also supplied six remaining air start motors from their inventory to ESI for evaluation of the drive clutch torque setting. The air starters are Pow-R-Quik type LS-60-RH1 and LS-60-LH1 (where RH and LH designate right hand and left hand rotation respectively). "The evaluation was concluded on 08/01/11 and determined the air motor failure to be a reportable defect as defined by 10CFR21. The starter drive failure was attributed to excessive torque adjustment of the clutch assembly. This overstressed the clutch disc plates which lead to eventual failure of the friction-clutch inertia drive assembly. Failure of the clutch drive renders the air start motor inoperative. Depending upon the configuration of the engine's starting system, an inoperative air start motor could cause excessive starting times or a start failure. Either scenario has the potential to prevent the emergency diesel generator from performing its safety related function. "Clutch torque testing was performed on the six (6) starters returned from Clinton's inventory. [Results indicate inconsistent clutch settings]. The specified torque setting for the clutch drive is 275-300 ft-Ibs. Of the six starters tested, only one was within specification. "Based on the test data obtained from the six (6) Clinton starters, all previous shipments of air motors with the friction-clutch inertia drive are suspect for having inconsistent clutch drive torque settings." Affected users of the air start motors that contain friction-clutch inertia drives include the following: Exelon-Clinton, Entergy-Indian Point 3 and PSE&G-Salem. Engine Systems, Inc Report Number: 10CFR21-0102, Rev. 0. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-08-01
47111 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-07-31 10:30 | 2011-08-01 11:27 | 2011-08-11 | UNPLANNED CONTAMINATION AREA "On 07/31/11 a water leak was found coming through the C-310 North NaF (Sodium Fluoride) trap room ceiling. The leak was coming from a steam condensate header located over the trap room. The leak had created a puddle, approximately 8' by 6', in the trap room. The area was checked by Health Physics and the spill area in the trap room was upgraded to a Contamination Areas at 1030 [CDT]. The condensate water is not contaminated but is spreading contamination from a contamination area above the ceiling. Decontamination of the trap room has been performed; however, due to a small amount of water that continues to leak into the area the area is being recontaminated. Access to the area has been restricted with the contamination area requirements for more than 24 hours. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(1)(i) 'An unplanned contamination event that: Requires access to the contaminated area, by workers or the public, to be restricted for more than 24 hours by imposing additional radiological controls or by prohibiting entry into the area.' "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRCÀ11-1944: PGDP Event Report No. PAD-2011-12." * * * RETRACTION ON 08/11/2011 AT 1356 EDT FROM CALVIN PITTMAN TO DAN LIVERMORE * * * "Once the floor was decontaminated and down posted, which was within the 24-hour limit, a Nuclear Criticality Safety (NCS) approved 5.5 gallon container was placed on the floor to contain the continuing leak. Due to the fact that the water dripping into the container was contaminated, the container was posted as a contamination area. The above statement that the area was being recontaminated by a small amount of water that continued to leak is referring to the water dripping into the bucket. A review of the sequence of actions to contain the water leak and decontaminate the area resulted in the conclusion that the contaminated area was down posted within the 24-hour limit. The fact that the NCS approved 5.5 gallon container placed on the floor to contain the leak was posted as a contamination area is not considered a continuation of the spread of contamination event. The spread of contamination onto the floor had been stopped and the floor decontaminated. With the leak contained, the floor decontaminated, and returned to the radiological control level that existed prior to the leak within the 24-hour limit, the event notification was not required. Thus, the notification is being retracted." The licensee has notified the NRC Resident Inspector. Notified R2DO (Hopper) and NMSS EO (Hiltz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2011-08-01
47110 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-07-30 10:55 | 2011-07-30 11:05 | 2011-07-30 | TECHNICAL SUPPORT CENTER HVAC OUT OF SERVICE "Due to unsatisfactory performance of TSC HVAC operation, the system is removed from service for corrective maintenance under Operating Permit 1ÀOP-11-1X75-00211. "The TSC HVAC is considered non-functional during the performance of this corrective work activity. If an emergency condition occurs during the time these work activities are being performed, which requires activation of the TSC, the contingency plan calls for utilization of the TSC, as long as radiological conditions allow for habitability of the facility. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this activity affects the functionality of the TSC emergency response facility for the duration of the evolution." The NRC Resident Inspector has been notified. * * * UPDATE FROM FRANK GORLEY TO PETE SNYDER AT 2041 EDT ON 7/31/11 * * * The TSC HVAC system is back in service as of 1700 EDT on 7/31/11 following compressor replacement. The licensee notified the NRC Resident Inspector. Notified R2DO (Blamey). | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-30
47109 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-29 16:15 | 2011-07-29 17:35 | 2011-07-29 | NOTIFICATION OF NORTH CAROLINA WILDLIFE RESOURCES DUE TO STRIPED BASS MORTALITY "Duke Energy Scientific Services group notified the NC [North Carolina] Wildlife Resources Commission that we (Duke Energy) had identified some striper fish mortalities in and around Cowan's Ford Dam on Lake Norman. We also notified North Carolina Department of Environmental and Natural Resources in Mooresville, N.C. about the Striper mortalities. "[Duke Energy personnel] collected 49 stripers in various stages of decay today (Friday, 7-29-2011). The fish collected were around the Cowan's Ford Dam and up to 1 mile North of Darn on Lake Norman. "The Duke Energy Scientific Services group representative also notified the NC Wildlife Resources Commission that the McGuire Nuclear Station had been operating their Low Level Intake [LLI] Pumps to support compliance with our NPDES Permit average monthly temperature limit of 99 degrees Fahrenheit. "July has been unusually hot and plant management has felt the need to run the LLI approximately 5 days to achieve compliance with our temperature limit. The LLI Pumps were secured July 25th at 2015. During the operation of the LLI pumps, Duke Energy's Scientific Services group was monitoring water quality and fish in the lake via the following activities. "1) Around-the-clock monitoring of fish behavior in the immediate vicinity of the LLI via a Didson Camera. The Didson Camera sits atop the LLI (25 meters deep) and records hourly video of areas both above the LLI and in front of the LLI. These videos are monitored remotely by [personnel] throughout the day and night. "2) Periodic water quality monitoring including dissolved oxygen and temperature profiles at every meter to the bottom of the lake. These profiles occur in the fore bay and at multiple locations up the lake channel. "3) Surveys for dead striped bass by boat up the major tributaries of the lake. Lengths, weights and condition of both dead and dying stripers are recorded before disposing of them. "4) Hourly MNS discharge temperature monitoring. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-29
47108 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-07-29 | 2011-07-29 13:43 | 2011-07-29 | AGREEMENT STATE REPORT - DOSE TO EMBRYO/FETUS The following information was provided by the Commonwealth of Massachusetts via fax: "On July 15, 2011, a female patient received a diagnostic scan and was administered 22 mCi of Tc-MDP. Before the CT scan and contrast administration, the patient signed a declaration that she was not pregnant. The RSO informed [the Commonwealth of Massachusetts representative] that it is Lahey's policy to have the patient sign an attestation to knowledge of pregnancy before the diagnostic scans, and they only do pregnancy tests before therapeutic administrations. "On July 28, 2011, the patient notified the Lahey Clinic that she was pregnant at the time of the scan. The RSO, following the ANSI standard, calculated the dose to the fetus due to the radioactive materials was .506 rads. The total body burden from the CT scan was 2.1 rads. They used the conservative estimate that the embryo/fetus received all 2.1 rads making the total dose to the embryo/fetus 2.6 rads." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-08-04
47107 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2011-07-28 21:15 | 2011-07-29 01:02 | 2011-07-29 | OFFSITE NOTIFICATION DUE TO FISH KILL EVENT "At 2115 on 7/28/2011, Oyster Creek experienced a fish kill of greater than 100 fish caused by a loss of the thermal dilution plant power. The loss of thermal dilution plant power was based on a faulted breaker in the Oyster Creek/JCP&L substation. "The reported failure was a relay failure inside a 34.5KV substation breaker. Oyster Creek is holding at 53% power until thermal dilution is restored for environmental limitations." The New Jersey Department of Environmental Protection has been notified. The NRC Resident Inspector will be notified. | 53 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-29
47106 | 0 | MALLINCKRODT, INC. |  |  |  |  | 2011-07-28 12:00 | 2011-07-28 13:03 | 2011-07-28 | DEPLETED URANIUM-238 SHIELDS ARE MISSING Between April and June of 2010, the licensee shipped shielded Tc-99m generators to customers in Ohio and Hawaii. Each generator was shipped with a 8.1mCi depleted U-238 shield. Ohio State University (OSU) Medical Center received 2 generators and Tripler Army Medical Center in Hawaii received 1 generator. Once the generators are depleted, they are returned to Mallinckrodt in the depleted uranium shields. OSU Medical Center shipped one depleted generator in April 2010 (shield s/n 004631) and one in May 2010 (shield s/n 004042). Tripler Army Medical Center in Hawaii shipped their depleted generator in June 2010 (shield s/n 002426). Records confirm that all three shields were picked up by the carriers at the respective facilities but Mallinckrodt has no records of the shields being returned to their facility. The shields are returned to a courier contracted by Mallinckrodt who in turn delivers the shields to the Mallinckrodt facility. The carriers used for the return shipments were contacted about the missing shields and are presently investigating there whereabouts. The licensee, as well as the customers, are also searching their facilities. This matter is under investigation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-07-28
47105 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2011-07-28 01:15 | 2011-07-28 09:57 | 2011-07-28 | CONTROL ROOM TEMPERATURE RECORDER INOPERABLE "On July 28, 2011, at 0115 hours, a main control room recorder failed. The recorder functions to remotely monitor plant area temperatures, including eight areas used in accident classification (specifically, Emergency Action Level classifications when predetermined temperature levels are exceeded). "Troubleshooting efforts have been initiated to determine the cause of the recorder failure; the eight affected areas are being monitored locally twice per shift during operator rounds. "Given this recorder is used for accident classification, this event is reportable under 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-28
47104 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-07-27 23:20 | 2011-07-28 02:53 | 2011-07-28 | NON-FUNCTIONAL TECHNICAL SUPPORT CENTER (TSC) CLIMATE CONTROL SYSTEM "The Technical Support Center climate control system was found to be non-functional on 7/27/11 at 2320. System repair is in progress at this time. The time period that the Technical Support Center climate control system was non-functional has exceeded the 30 minute limit that is delineated in the Technical Requirements Manual section T3.10.1. This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG 1022, Rev. 1 since this issue affected an emergency response facility. Also, this 8 hour notification is being made in accordance with the Technical Requirements Manual section T3.10.1.B.2. "The alternate Technical Support Center facility remains functional." The NRC Resident Inspector has been notified. * * * UPDATE FROM FRANK GORLEY TO PETE SNYDER AT 2149 ON 7/28/11 * * * At 2100 EDT on 7/28/11 the TSC climate control system has been restored and the TRM action statements have been exited. The licensee notified the NRC Resident Inspector. Notified R2DO (Blamey). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-28
47103 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2011-07-27 20:59 | 2011-07-28 01:00 | 2011-08-01 | LOSS OF BOTH TRAINS OF EMERGENCY RESPONSE DATA SYSTEM DUE TO LOSS OF PLANT PROCESS COMPUTERS "At 2059 [hrs. EDT] on 7/27/11, St. Lucie Unit 1 lost both the 'A' and 'B' computer trains associated with Emergency Response Data Acquisition and Display System (ERDADS). Attempts to restore either train have been unsuccessful. The cause of the failure is not known and continues to be investigated. "This is reportable in accordance with 10CFR 50.72(b)(3)(xiii) due to a major loss of emergency assessment capability for greater than one hour." The loss of the plant process computers also resulted in the loss of the Safety Parameter Display System. Redundant indicators are available to operators. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 8/1/2011 @1140 EDT FROM JOE HESSLING TO MARK ABRAMOVITZ * * * "On 8/1/11 at 1052, Unit 1 ERDADS has been restored to an available status." The licensee notified the NRC Resident Inspector. Notified the R2DO (Blamey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-28
47102 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-07-27 12:29 | 2011-07-27 14:46 | 2011-07-27 | OFFSITE NOTIFICATION OF A SMALL OIL SPILL "Unit 2 control room was notified of a small hydraulic oil spill (less than 1 quart) from a construction truck to a gravel parking lot. [The licensee] made notifications to the New York Department of Environment Conservation [DEC] and the Westchester Department of Health. The spill was cleaned up by 1400 [EDT] on 7/27/11. The spill report number to the DEC is #1104806." The licensee has notified State and local authorities and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-27
47101 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2011-07-19 | 2011-07-27 12:27 | 2011-07-27 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following report was received from the Alabama Department of Public Health via facsimile: "On July 19, 2011, [the] Radiation Safety Officer for Building and Earth Sciences of Birmingham, Alabama notified the Alabama Office of Radiation Control that their 2004 Toyota Tacoma truck with a Troxler model 3430 moisture density gauge was stolen at the Kroger's Grocery Store parking lot at 300 North Dean Road in Auburn, Alabama. Building and Earth Sciences is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 1266. The Auburn Police Department was advised of the incident. The stolen gauge was identified as a Troxler model 3430, serial number 22300, with 0.3 gigabecquerels of Cs-137 and 1.48 gigabecquerels of Am-241:Be. [The RSO] indicated that the gauge transport case was properly secured within the bed of the pickup. "As of July, 27, 2011, 11:00 AM CDT, the truck and the device containing radioactive material remain missing. This is all the information that this Agency [Alabama DPH] has at this time." Alabama Event 11-28 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2011-08-01
47100 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-07-27 09:04 | 2011-07-27 11:54 | 2011-07-27 | OFFSITE NOTIFICATION OF SIREN ACTIVATION BY LIGHTNING STRIKE "At approximately 0904 CDT on July 27, 2011, the licensee was notified of an inadvertent activation of emergency siren (G-03) in the township of Welch, MN. The site contacted the siren vendor. It was determined that the siren was damaged by a lightning strike and has since been deactivated after sounding for approximately 35 minutes. The Goodhue County Sheriff's department received calls from some area residents. The siren remains out of service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ)." The licensee stated that the vendor is working on repair of the siren. The licensee has notified local authorities and the NRC Resident has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-27
47099 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-07-27 04:15 | 2011-07-27 05:43 | 2011-07-27 | ALERT DECLARED DUE TO ONSITE RELEASE OF FLUORINE/CHLORINATED FLUORINE GAS MIXTURE At 0415 CDT while changing out a cylinder of Fluorine/CL3 gas mixture in the C350 building, apparently a gasket failure occurred and an uncontrolled release of the gas mixture began. The licensee estimates that at the time the release began, there was approximately 160 lbs. of material in the cylinder. The release continues at this time. The C350 building was evacuated. There were no personnel injuries as a result of this event. No offsite assistance is being requested by the licensee. The local emergency squad is responding. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MIKE BOREN AND GREG BARNA TO DONALD NORWOOD AT 0631 EDT ON 7/27/2011 * * * The licensee believes, but has not verified at this time, that the gas leak has been stopped. A 'shelter in place' order has been issued for the following buildings: C337, C337a, C360, C335, C635 and C631. Samples exterior to building C350 are negative. Samples interior to building C350 still show residue and fog in the building. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MIKE BOREN TO DONALD NORWOOD AT 0714 EDT ON 7/27/2011 * * * The licensee has verified that the leak has been stopped. * * * UPDATE FROM GREG BARNA TO DONALD NORWOOD AT 0726 EDT ON 7/27/2011 * * * At 0615 CDT, an employee that was involved with the cylinder change-out and response to the event was transported to the onsite medical facility. He was complaining of a burning sensation to his right arm. At 0625 CDT, samples obtained both inside and outside of building C350 were negative. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM GREG BARNA TO DONALD NORWOOD AT 0736 EDT ON 7/27/2011 * * * At 0631 CDT, the licensee has terminated the Alert. The licensee is controlling access to building C350 for investigation. The licensee has setup a recovery team. As a precautionary measure, a second individual that was involved in the cylinder change-out was also transported to the onsite medical facility. The licensee notified the NRC Resident Inspector. Notified R2DO (Blamey), NMSS EO (Habighorst), IRD MOC (Marshall), DHS (Arnold), FEMA (Hollis), DOE (Connally), EPA (Brett), USDA, and HHS (Jones). * * * UPDATE FROM DEREK WARFORD TO HOWIE CROUCH AT 0916 EDT ON 7/27/2011 * * * "On 7/27/11 at 0710 [CDT], the Paducah Gaseous Diffusion Plant decided to issue a press release describing the Alert issued by the plant earlier in the morning. The Alert issued on a chlorine trifluoride (CIF3) release in the C-350 facility was declared on 07/27/11 at 0415 [CDT] and terminated on 07/27/11 at 0631 [CDT]. . "This event is reportable under Criteria P in Appendix D of USEC procedure UE2-RA-RE1030 as any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. "The NRC Senior Resident Inspector has been notified of this event." Notified R2DO (Blamey), NMSS EO (Habighorst) and PAO (Harrington). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | OTHER UNSPEC REQMNT | [8 empty] | ALERT | 2 | KY | FUE |  | 76.120(a)(4) |  |  |  | 0 | 2011-07-27
47098 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-07-03 | 2011-07-26 18:03 | 2011-09-07 | ENTRY OF UNAUTHORIZED PERSON INTO PROTECTED AREA An actual entry of an unauthorized person into a protected area. The licensee informed the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. See related event EN #40797. * * * UPDATE FROM STANLEY STONE TO HOWIE CROUCH AT 0032 EDT ON 9/7/11 * * * The licensee has retracted this event based on the fact that at the time of entry into the protected area, the person was authorized. The licensee will inform the NRC Resident Inspector. Notified R2DO (Rich) and ILTAB (Whitney). Contact the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-07-26
47097 | -1 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-26 17:05 | 2011-07-26 17:47 | 2011-09-07 | ENTRY OF UNAUTHORIZED PERSON INTO PROTECTED AREA An actual entry of an unauthorized person into a protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. See related event EN #40798. * * * RETRACTION AT 1515 EDT ON 9/7/11 FROM DORMAN TO HUFFMAN * * * The licensee has retracted this event based on the fact that at the time of entry into the protected area, the person was authorized. The licensee will inform the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. Notified R2DO (Rich) and 73.71 group (via e-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-07-26
47096 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2011-07-26 16:00 | 2011-07-26 16:47 | 2011-07-26 | UNANALYZED CONDITIONS INVOLVING THE SAFETY RELATED DIRECT CURRENT (DC) SYSTEM "Information was received in regards to an old design issue identified in a Component Design Basis Inspection Unresolved Item. Two issues were identified with the Safety-Related Direct Current (DC) System: "1. The plant's licensing basis states that non-safety-related electrical equipment, whose failure under postulated environmental conditions could prevent satisfactory accomplishment of the specified safety-related electrical equipment required safety functions, is qualified as required. However, the Reactor Coolant Pump (RCP) backup lift oil pump motors and the Containment Emergency Lighting Panel L49E1 are located inside containment and are not environmentally qualified. This could challenge the adequacy of electrical separation between the potentially grounded non-safety related equipment and the safety related batteries. "2. Automatic transfer switches are installed to automatically transfer non-safety related loads such as non-nuclear instrumentation, station annunciators, plant computer, and integrated control system between two non-safety related inverters, which receive power from the safety-related DC power system. If a ground fault existed on one of these switches, the fault could be transferred from one power source to the redundant source, potentially impacting the ability of both safety-related DC power sources to perform their required functions. This type of transfer is not permitted by the plant's licensing basis. "The breakers for the 4 RCP backup lift oil pump motors and for the Containment Emergency Lighting were opened. One train of instrumentation power was placed on its alternate power source from the Alternating Current (AC) system, eliminating the potential to impact both trains of the DC power system. "This condition is being reported per 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(A-D) as an event or condition that could have prevented fulfillment of a safety function." The licensee has notified state and local authorities and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2011-07-26
47095 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-07-26 12:00 | 2011-07-26 16:44 | 2011-07-26 | AGREEMENT STATE REPORT INVOLVING A STOLEN HUMBOLDT NUCLEAR GAUGE The following report was received from the State of Texas via email: "On July 26, 2011, the Agency was notified by the licensee that a Humboldt model 5001 EZ moisture/density gauge serial number 3567 was stolen out of one of their trucks in Houston, Texas. The gauge contains a 40 milliCurie Americium-241 source and a 10 milliCurie Cesium-137 source. The gauge was locked in the back of a pickup parked at a training center where the user was attending safety training. When the user returned to the truck, he found the lock and chain securing the gauge had been cut and the transport case with the gauge was missing. The user contacted his employer who then contacted local law enforcement who responded to the scene. The licensee's Radiation Safety Officer also responded to the scene. The licensee believes that the gauge operating trigger was locked, but could not state that with all certainty. Additional information will be provided as it is received." Texas Incident No.: I-8875 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-29
47094 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-06-03 00:39 | 2011-07-26 12:14 | 2011-07-26 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of Emergency Diesel Generator 'A' on June 3rd, 2011 while performing service water valve isolation signal testing. Emergency AC Electrical power system, including emergency diesel generators, is a system named in 50.73(a)(2)(iv)(B). "During a refueling outage, testing was in progress to verify that service water isolation valves received the proper close signal during a safety injection. The test configuration required pulling control power fuses for the Bus 14 normal supply breaker to prevent operation and allow for manual relay actuation. Within seconds of pulling these fuses, the control room received a Bus 14 undervoltage annunciator, Emergency Diesel Generator 'A' started, and the generator output breaker closed onto Bus 14. Upon further investigation, the cause of this signal was identified as a degraded control relay that failed to mechanically latch and unexpectedly changed state when control power was removed. This resulted in an invalid undervoltage signal. Bus voltage remained within normal operating range. Given that the diesel generator was in unit mode of operation and was not fully synchronized with the normal bus supply, the diesel generator tripped shortly after starting due to a valid reverse power signal. A field verification and technical review was performed to ensure that this condition did not cause significant stress on the generator or engine. "This start signal is considered an INVALID signal with respect to 50.73(a)(2)(iv)(A), however the system was not fully removed from service. The 'B' train was not affected by this event. The actuation was considered complete since all necessary components responded to the undervoltage signal as expected under the actual field conditions. The control relay would have remained in the desired position and performed its required function under design conditions with normal control power available. Therefore the degradation was not determined to have an impact on the safety function." The NRC Resident Inspector was notified. See related EN #46917. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-07-26
47093 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-07-21 12:00 | 2011-07-25 14:05 | 2011-07-25 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING EXPOSURE LESS THAN PRESCRIBED The following information was received from the State of Pennsylvania Department of Environmental Protection Bureau of Radiation Protection via e-mail: "Event Type: A medical event (ME) where the patient was being treated via [Yttrium - 90] TheraSphere for disease of the liver and received 64% of the intended dose, which is reportable under 10CFR35.3045. "Notifications: On July 22, 2011, at 1541 [EDT] the department's [PA Bureau of Radiation Protection] Southeast Regional Office received notification via email about a ME that was identified during a routine internal audit. "Event Description: As noted, the event was identified on July 21, 2011, during a routine internal audit by U Penn. The patient was being treated for disease of the liver and received 64% of the intended dose. No harm to the patient is expected. The treating physician notified the patient. No more information is available at this time. "Cause of the Event: The cause of the event is currently under investigation by the licensee. "Actions: The licensee will be submitting a written report within 15 days. The department [PA Bureau of Radiation Protection] plans to do a reactive inspection." The actual event date is unknown based on the state's report. PA Event Report: PA110019 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-07-31
47092 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-07-24 13:05 | 2011-07-24 16:38 | 2011-07-24 | EXTENDED EMERGENCY SIREN ACTIVATION DURING TESTING "At approximately 1305 Central Time, a Grundy County Illinois representative notified Exelon of an extended Emergency Preparedness Zone (EPZ) siren activation. EPZ siren DR-13 was tested as part of normal routines this date at 1200 Central Time. During the test the siren lost AC power which shifted the power supply to the back up battery. The alarm continued to sound following the test until the back up battery depleted. "The siren is declared inoperable. The siren contractor (Fulton Technologies, Inc) is in route for troubleshooting and repairs. 45 of 46 sirens remain operable for the Dresden Emergency Preparedness Zone. "This condition is reportable under 10 CFR 50.72(b)(2)(xi). News release or notification of other governmental agency." The licensee informed the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-24
47091 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-07-23 19:00 | 2011-07-23 23:20 | 2011-08-26 | OFFSITE NOTIFICATION DUE TO UNMONITORED RELEASE OF TRITIUM TO SEPTIC SYSTEM "It was discovered that water containing tritium from a secondary system steam leak has been periodically disposed of via the septic system versus the normally monitored turbine building sump effluent path. The tritium amount was 8.00 E-5 microcuries per milliliter. The tritium sample is consistent with normal secondary plant samples. Since November, 2010, there have been no abnormal tritium results from the septic system. There was also MPA (29.7 parts per million) which is a pH additive. "The septic system is monitored on a monthly basis but is not a normal path for discharge of equipment related fluid leakage. The steam has been condensed and collected in a 5 gallon pail that is periodically emptied by crew personnel. Management just became aware that there were instances where disposal of the water was to the septic system. This practice has been halted. The steam leak has been active since November of 2010. "This is being reported due to the potential for being an unusual or abnormal release of radioactive effluent. "The NRC resident has been informed." The licensee will also inform state and local agencies of this event. * * * UPDATE FROM BILL SCHALLER TO DONALD NORWOOD AT 1505 EDT ON 8/26/11 * * * "This is an update to EN 47091 (Water containing tritium from secondary system leak disposed of via septic system) submitted at 2320 EDT on 7/23/2011. "The fluid in the septic system at Prairie Island Nuclear Generating Plant is removed from site by a vendor, who transports the fluid to the Red Wing, MN Wastewater Treatment Plant where it is processed prior to being discharged. "The NRC Resident Inspector has been informed. Notified R3DO (Passehl). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-23
47090 | -1 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-07-21 | 2011-07-22 16:29 | 2011-07-26 | AGREEMENT STATE REPORT INVOLVING A PATIENT RECEIVING AN INCORRECT DOSAGE OF I-131 The following report was received from the State of Wisconsin via fax: "The Wisconsin Department of Health Services (DHS) received a phone call from the Radiation Safety Officer (RSO) on July 22, 2011 that a patient received the wrong dose of I-131 on July 21, 2011. The patient was scheduled for a diagnostic procedure involving 8 mCi of I-131, but instead received a 150 mCi therapeutic dose of I-131. "DHS will be conducting an investigation on July 26, 2011 and the licensee will be submitting a 15 day written report concerning the medical event." Wisconsin Event Report ID No.: WI10010 * * * RETRACTION ON 7/26/11 AT 1405 EDT VIA FAX TO HUFFMAN FROM TIMMERMAN * * * "This is an update to [the State of Wisconsin] Event Notification WI-10010. On July 26, 2011, the licensee informed [the Wisconsin Department of Health Services] that the reported medical event on July 22, 2011 involving a patient that received 150 mCi dose of I-131 on July 21, 2011, was an internal miscommunication. Upon review of the written directive and speaking with UW-Madison staff, DHS has verified that the patient received an I-131 therapeutic dose as prescribed on the written directive. "This medical event is retracted." R3DO (Giessner) and FSME EO (McIntosh) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-07-28
47089 | 0 | ABB, INC. |  |  |  |  | 2011-07-22 | 2011-07-22 13:55 | 2011-07-22 | PART 21 REGARDING KF PROTECTIVE RELAY - DEFECTIVE CAPACITOR The following information was received via fax and email: "Subject: 10 C.F.R. Part 21 Notification of Deviation regarding KF Protective Relay - Defective Capacitor "On June 2, 2011, Constellation Energy reported that two relays caused unnecessary breaker trips three weeks after the relays were placed in service. Their investigation found that the Under-frequency Trip setpoint had drifted from the pre-set value of 57.77 Hz to 60.316 and 61.2 Hz. "Our investigation determined that both relays contained a defective capacitor (ABB Part Number #606B340H07). The capacitor should have measured 0.225 Áf (micro-farads) ? 3%. Actual measured value of the capacitors was 0.195 Áf and 0.208 Áf. A failure analysis conducted by Arizona Capacitor Corporation identified the capacitors were incorrectly constructed with metalized film, instead of oil impregnated paper/film/oil, as required by ABB design specifications. These capacitors were manufactured by Aldon Corporation, with a date code of April 4, 2008. "Per 10 C.F.R. 21.21 (b), we do not have the capability to perform the evaluation to determine if a defect exists, and will notify the purchasers or affected licensees within five working days. Currently, we believe there are a total of six suspect relays, provided to three customers." The three customers are: WESCO located in Murrysville, PA, KF Relay Style 1328D72A02A, S/N 12027, 12028A, Qty 2, ABB Inc located in Florence, SC, KF Relay Style 1328D72A02A, S/N 12253, Qty 1 and, ABB Ltd located in Cheonan, South Korea, KF Relay Style 1328D72A01, S/N 12025, 12026, 12366, Qty 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2011-07-22
47088 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-07-22 08:30 | 2011-07-22 13:23 | 2011-08-30 | FIRE SUPRESSION PUMPS INOPERABLE "Both Fire Suppression Pumps are not operable because the required monthly surveillance tests will not be completed for June and July. The surveillance tests will be completed when flood waters recede to below 1004 feet MSL. The current river level is 1006.3 feet. Both fire pumps, FP-1A and FP-1B, are available and lined up for use. Other options are also available to provide a means of backup fire water supply that include: - Water Plant Pumps DW-8A and DW-8B aligned to the Fire Protection (FP) system. - Temporary connection to the fire protection water distribution system by the Fort Calhoun Fire Truck that is staged on site or any other fire pumper truck via fire hydrant FP-3G. - Admin Building/Training Center fire hydrant via fire hoses or water truck. This supply is from Blair water system and FP storage tank west of Highway 75. - Drafting from the Missouri River via temporary pumps." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ERICK MATZKE TO HOWIE CROUCH AT 1714 EDT ON 8/30/11 * * * "Further review of the plant design and licensing basis determined that the plant is adequately analyzed for the reported situation and that it does not constitute an unanalyzed condition significantly degrading plant safety as originally reported. Therefore, this event is being retracted." The licensee has notified the NRC Resident Inspector. Notified R4DO (Proulx). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-07-22
47087 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2011-07-22 11:00 | 2011-07-22 12:18 | 2011-07-22 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR A contractor supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The individual's access to the site has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2011-07-22
47086 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-21 11:53 | 2011-07-21 20:39 | 2011-09-08 | VULNERABILITY FROM A POTENTIAL CONTROL ROOM FIRE ON "A" SAFEGUARDS BUS "A potential scenario has been identified that has not been analyzed in the Comanche Peak Nuclear Power Plant Fire Safe Shutdown Analysis (FSSA). This situation is described below for Unit 1, but also applies to Unit 2. Listed below is the configuration for 1EA1. The basic configuration is typical for 1EA2, 2EA1 and 2EA2 as well (ref. E1-0001) - Safeguard Bus 1EA1 is a 6.9 kV switchgear with a Main-Tie-Main configuration. - The normal lineup has one feeder breaker closed, the other feeder breaker open and the tie breaker closed. - 1EA1 receives normal power from the secondary side of Startup Transformer XST2 through breaker 1EA1-1. - 1EA1 receives alternate power from the secondary side of Startup Transformer XST1 through breaker 1EA1-2. - 1EA1 receives emergency power from diesel generator 1EG1 through breaker 1EG1. - An alternate source of power for 1EA1 is also available from Train C through breaker 1EA1-3. "The control wiring for the 1EA1-1 circuit breaker contains the following attributes that are important to understand the issue: - Switch 43/1EA1-1, located in the Shutdown Transfer Panel (STP) is used to transfer control of 1EA1-1 from the Control Room (1-CB-11 switch CS-1 EA1-1) to the Hot Shutdown Panel (HSP) switch CS-1 EA-1 L. (Ref. E1-0031-01&02) - There is a trip circuit fuse located in the 6.9 kV switchgear compartment for 1EA1-1 for control of the trip circuit when the breaker is controlled at 1CB-11 and a separate fuse for the trip circuit when the breaker is controlled by the HSP. - The trip circuit for 1EA1-1 has a contact routed through the Control Room to the Solid State Protection System (SSPS) Cabinet. This contact is in the trip circuit when control is from the Control Room or when control is from the HSP. (Ref. E1-0031-01) "The scenario is based on a fire in the Control Room. If the fire in the Control Room causes a ground in the wiring routed in the Control Room to the SSPS cabinet, the fuse for the 1E1-1 trip circuit would open. In the event of a fire in the Control Room, control of the plant is transferred to the HSP. When the control of breaker 1EA1-1 is transferred to the HSP and the ground condition in the SSPS wiring still exists, the second 1EA1-1 trip circuit would open. At this time there would be no way to remotely trip open 1EA1-1. The breaker could still be tripped mechanically at the breaker. Therefore, if 1EA1-1 is closed, 1EA1 could remain energized if off-site power is available. If off-site power is not available, but 1EA1-1 remains closed, bus 1EA1 would remain electrically connected to XST2. As part of the transfer of control from the Control Room to the HSP, operators start up the diesel generator and close 1EG1 to place 1EA1 loads on the generator. If 1EG1 is closed and 1EA1-1 breaker is still closed with off-site power available, the generator will be immediately connected to grid power through XST2 without synchronizing. If 1EG1 is closed and 1EA1-1 breaker is still closed with off-site power not available, the generator will be immediately connected to XST2 and attempt to energize XST2. This large current draw associated with energizing XST2 would likely stall and damage diesel generator 1EG1. "Compensatory Action is being implemented through procedure revisions to preclude damage to the diesel generator during this scenario." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM TOM RUCKER TO PETE SNYDER AT 1713 ON 9/8/11 * * * "At 1939 central daylight time on July 21, 2011, Luminant Power notified the NRC (Event No. 47086) of a Unanalyzed Condition per 50.72(b)(3)(ii)(B) regarding the vulnerability from a potential control room fire on 'A' Safeguards bus. The event report described a portion of a cable running from the Hot Shutdown Panel (HSP) to the Solid State Protection System (SSPS) cabinet in the Control Room (CR) that was not protected from a CR fire scenario for which a worst case Control Room/Cable Spreading Room fire induced short could result in the 1EA1-1 circuit breaker, connecting the 345 kV Startup Transformer to the grid, not tripping and damaging the EDG. "Upon further review it has been determined that the Fire Safe Shutdown Analysis (FSSA) modeled that cable in the analysis since CPNPP began commercial operation. Additionally, the FSSA accounted for the fire-induced circuit ground on this cable and one of the specified manual actions is to trip the 1EA1-1 circuit breaker to assure the EDG would load the 'A' Safeguard bus to support the required fire scenario. The EDG output breaker is designed to auto close once the 1EA1-1 circuit breaker is tripped open. The previous version (prior to compensatory actions) of ABN-803A/B, the procedure used should a fire occur in the Control Room, directed the Reactor Operator to trip 1EA1-1 circuit breaker once the diesel was verified running, then ensure the EDG breaker closed. There is no procedural step directing personnel to manually close the EDG breaker. Since, in this scenario, indication for the 1EA1-1 circuit breaker at the Hot Shutdown Panel would be lost, it would be expected that the RO would direct the RRO to verify 1EA1-1 circuit breaker position. "Based on the above, Luminant Power has concluded that the FSSA adequately modeled the plant and procedures were written which would not direct any action that would have caused the condition stated in the CR description. Based on the above, the conclusion is that CPNPP did not have an unanalyzed condition that significantly degraded plant safety per 50.72 (b)(3)(ii)(B) regarding the vulnerability from a potential control room fire on 'A' Safeguards bus. Therefore, this event is retracted." The licensee will notify the NRC Resident Inspector. Notified R4DO (Lantz). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-07-21
47085 | 0 | WEATHERFORD INTERNATIONAL |  |  |  |  | 2011-04-20 | 2011-07-21 17:45 | 2011-07-21 | POTENTIAL OVEREXPOSURE OF WELL LOGGING SUPERVISOR The RSO for Weatherford International located in Benbrook, TX was provided the 2nd quarter dosimetry readings of 7545 mRem for a well logging supervisory in their Weston, WV office. The supervisor has been removed from activities involving radioactive sources pending results of an investigation. Preliminary findings are that the individual involved was returning a 1.5 Ci Cs-137 source to storage and had placed his dosimetry, a Luxel, about 1 foot from the source at which time he had to use the restroom. When he returned he discovered that the storage area door had automatically locked requiring him to contact the custodian to reopen the area to recover his dosimetry. He estimated that the time involved was between 1-1.5 hours. The licensee investigation is on-going. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2011-07-21
47084 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-07-21 11:00 | 2011-07-21 16:45 | 2011-07-21 | POTENTIAL ADVERSE EFFECT ON ESW TRAIN DURING A POSTULATED CONTROL ROOM FIRE "On July 21, 2011 at 1100 [CDT] Callaway Plant staff determined that a design deficiency could adversely affect the 'B' Train of Essential Service Water (ESW) in the event of a Control Room fire. 'B' Train is the credited train for completion of a post-fire safe shutdown as a result of a Control Room evacuation. "As a result of this deficiency, normally closed valve EFHV0060 could spuriously open during a postulated control room fire. EFHV0060 is located on the ESW return line from the 'B' Component Cooling Water (CCW) heat exchanger. If EFHV0060 spuriously opened as a result of this postulated fire, the flow balance in the 'B' Train of the ESW system would be affected. In this scenario, cooling water flow to other essential components could be reduced to below the minimum requirements. "A fire watch has been imposed as a compensatory measure for this condition. Additionally, EFHV0060 has been closed and de-energized to preclude spurious opening in the event of a postulated control room fire. "This condition is reported in accordance with 10 CFR 50.72 (b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-07-21
47083 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-07-20 | 2011-07-21 12:42 | 2011-07-21 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISURE DENSITY GAUGE The following report was received via email from the State of Florida: "An accident caused damage to a moisture density gauge at a work site on the Kissimmee River Restoration/CSX Bridge project. The operator of a large earthmoving vehicle lost control and ran over a parked truck with the gauge sitting on the tailgate. The truck & contents were mangled and buried under the earthmoving vehicle. The tech was not injured. A 15 foot area was roped off around the accident site. When the gauge was recovered it appeared to have some damage to the top housing. Survey readings were elevated to around 40-50 mR/hr at one foot. Using shielding, the gauge was transported to the Troxler office in Orlando for repair. Licensee sent a written report to this office. This office will take no further action on this incident." The device is a Troxler Model No. 3440 S/N 37720 with two sources; 9.0 mCi Cs-137 and 44 mCi Am-241/Be. Florida Incident No.: FL-11-062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-07-26
47082 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-07-20 | 2011-07-21 08:38 | 2011-07-21 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY CAMERA LOCKING MECHANISM The following information was received via facsimile: "On July 20, 2011, the Agency [Texas Department of Health] was notified by the licensee that they had completed radiography operations at a field site using a INC IR-100 radiography camera containing an 82 curie iridium-192 source and retracted the source to its fully shielded position. The radiographer surveyed the camera and found the readings to be normal. When he disconnected the drive cable from the source pigtail, he found that the pigtail was no longer protruding from the back of the camera, it was now flush with the rear of the device. The shipping plug and the front dust cover were placed on the camera. The camera is being returned to the manufacturer for repair. Additional information will be provided as it is received. The licensee believes that the locking device that holds the pigtail in place inside the camera has failed. The serial number for the camera is 4590." Texas Incident Report Number: I-8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-26
47081 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-07-20 21:29 | 2011-07-21 00:53 | 2011-07-21 | AUTOMATIC REACTOR TRIP DUE TO NEGATIVE RATE TRIP FOLLOWING RAPID TURBINE LOAD REDUCTION "At 2129 EST on 7/20/2011, Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected from the Feedwater Isolation Signal. Primary PORVs and/or safety valves lifted and reseated as indicated by tailpipe temperatures and PRT pressure. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F and 2235 psig, with Auxiliary Feedwater supplying the steam generators. "At the time of the trip, maintenance was in progress on Preferred Inverter #1. AOP-P.09 'Loss of 120VAC Preferred Power' was used to restore power to #1 Preferred board after the trip. "Method of decay heat removal is via steam dumps to the condenser with MSIVs open. "Current temperature and pressure: Temperature - 548 degrees Fahrenheit and stable, Pressure 2235 - psig and stable "No indication of any primary/secondary leakage. "All rods are inserted. "Electrical alignment is normal, supplied from off-site power. "No impact on Unit 2. Unit 2 is operating at 100% power/Mode 1" The NRC Resident Inspector has been informed. The licensee notified the State of Tennessee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-07-21
47080 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-07-20 11:47 | 2011-07-20 20:45 | 2011-07-20 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR A contractor supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The contractor's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2011-07-20
47079 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-07-20 13:18 | 2011-07-20 20:10 | 2011-07-20 | OFFSITE NOTIFICATION - PRESS RELEASE AFTER FIRE ON SITE "On July 20, 2011 at 1318 PDT, during performance of STP M-9A, 'Diesel Engine Generator Routine Surveillance Test,' personnel reported a fire on the Unit 1 Emergency Diesel Generator (EDG) 1-1. No abnormal indications were observed in the control room and no annunciator for 'Fire Detected' was received. Operators shutdown the EDG and the onsite fire department responded immediately. "On July 20, 2011 at 1322 PDT, personnel reported that the fire, which was centered around the exhaust insulation material, had been extinguished. "EDG 1-1 is in a scheduled Maintenance Outage Window (MOW) and is not being relied on for emergency onsite power. The two sources of offsite power (the 230 kV startup system and the 500 kV system) along with the remaining two EDGs, are available and operable. "Unit 2 was not affected by the event. "The NRC Resident Inspector has been notified." A press release will be issued by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-20
47078 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-20 15:55 | 2011-07-20 17:30 | 2011-07-20 | OFFSITE NOTIFICATION TO THE NORTH CAROLINA WILDLIFE RESOURCES COMMISSION "Duke Energy Scientific Services group representative notified the NC Wildlife Resources Commission at 1555 hours that MNS was operating their LLI Pumps to maintain discharge temperatures within the NPDES permit average monthly temperature limit. "Based on the elevated lake temperatures, action to align circulating water to the LLI (cooler water) is necessary to prevent exceeding discharge temperature limits. Operation of the LLI pumps is sometimes needed during this time of year to comply with the water permit. Substantial effort is taken to avoid this alignment due to the potential to accelerate the natural phenomenon of oxygen depletion in the lower depths of Lake Norman that occurs as water temperature increases. The normal seasonal oxygen level changes can stress the fish population in that depth of the lake. "During the operation of the LLI pumps, Duke Energy's Scientific Services group monitors water quality and fish in the lake via the following activities, 1) Hydro acoustic surveys of the Cowan's Ford Dam fore-bay both immediate to the dam and also an approximate 2 mile run up the Catawba River channel. 2) Monitoring of fish behavior in the immediate vicinity of the LLI. A DIDSON camera sits atop the LLI (25 meter deep). 3) Water quality monitoring including dissolved oxygen and temperature profiles at every meter to the bottom of the lake. These profiles occur in the fore-bay and at multiple locations up the channel. 4) Hourly MNS discharge temperature monitoring. "These activities will continue to be exercised until the LLI pumps are turned off or the natural cycle of oxygen depletion has ended. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-20
47077 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-06-05 05:01 | 2011-07-20 16:50 | 2011-07-20 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - UNUSUAL EVENT "At 1650 [EDT] on 7/20/2011 it was determined that a Notification of Unusual Event (NOUE) was not declared for an event on 6/5/2011. The event occurred at 0501 [EDT] on 6/5/2011 when a low oxygen atmosphere condition was measured in the Unit 2 reactor containment building. The NOUE should have been declared in accordance with Surry Power Station Emergency Action Level HU3.1 (Report or detection of toxic, corrosive, asphyxiant, or flammable gases that have or could enter the Owner Controlled Area in amounts that can affect normal plant operations). This condition occurred during a refueling outage with maintenance being performed using a liquid nitrogen supplied freeze seal. The freeze seal activity released nitrogen, which slowly caused the low oxygen atmosphere (<19.5%). "In accordance with guidance provided in NUREG-1022, a one hour ENS notification is being made due to discovery of an undeclared condition that exceeded an Emergency Action Level." The licensee will inform Surry County, the State of Virginia and has informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2011-07-20
47076 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-07-20 13:15 | 2011-07-20 16:06 | 2011-07-20 | FIRE PROTECTION PROGRAM CONCERN "On July 20, 2011 at 1315 hours it was determined that a design deficiency at the Wolf Creek Nuclear Operating Corporation (WCNOC) constituted a fire protection program concern which could adversely affect the ability to achieve and maintain safe shutdown in the event of a control room fire. In the event of a postulated control room fire, a normally closed valve (EFHV0060) on the Essential Service Water (ESW) system return from the Component Cooling Water (CCW) heat exchanger could spuriously open. If this occurs, the flow balance in the ESW system would be affected and cooling flow to other essential components could be reduced to below the minimum required flow. "Present system operability is not affected as there has been no occurrence of a fire in the Control Room and compensatory actions are in place to detect and mitigate the effects of a fire in the Control Room. An hourly fire watch is currently in place in the control room and will remain in place until this issue is resolved. In addition to the hourly fire watch, alternate shutdown procedure OFN RP-017 is being revised to include interim compensatory actions to deenergize, and verify closed, valve EFHV0060. "This event is being reported in accordance with 10 CFR 50.72 (b)(3)(ii)(B) and 10 CFR 50.72 (b)(3)(v)(A) as an unanalyzed condition that significantly degrades plant safety. A follow-up licensee event report will be made in 60 days. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2011-07-20
47075 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-07-16 06:12 | 2011-07-16 09:12 | 2011-07-20 | SAFEGUARDS REPORT Safeguards System degradation related to monitoring and detection of PA boundary and Vital Areas. Compensatory actions taken. Call the Headquarters Operations Officer for details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-07-20
47074 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-07 | 2011-07-20 13:12 | 2011-07-20 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The following report was received from the State of Texas via email: "On July 19, 2011, the Agency [Texas Department of Health] received a call from the licensee's Radiation Safety Officer reporting that during a routine inspection on April 7, 2011, the shutter handle on an Ohmart/Vega Gauge model SHLG-1 broke off. The gauge serial number is 0678GK and contains 300 mCi of Cs-137. The gauge failed in the normally open position. The gauge was subject to condensation from a steam leak from above which caused the handle to rust. A vendor shut the gauge shutter on June 30, 2011. The gauge will be removed for disposal since the tank is no longer used. The failure did not create any additional exposure to any individual. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-25
47073 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2011-07-10 12:00 | 2011-07-19 13:30 | 2011-07-19 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR CONTAINING A 40 MILLICURIE PO-210 SOURCE The following event report was received from the Washington Office of Radiation Protection via e-mail: "On or about 10 July 2011, upon taking inventory of the static eliminators, a device was found to be missing. The device was leased from NRD, LLC on 10 November 2009. The last time the device was used was 2 June 2011. Upon discovering the device was missing, a thorough search of the facility was conducted to include personal lockers, the boat, the boat parts, the boat house, as well as other facilities around the company. At this time no one knows the location of the device, whether it was stolen, misplaced or thrown away. The company will inform the department if the device is found. Since this incident, Westport Shipyard 50 Meter Facility has changed its protocols for issuing and receiving these types of devices. They will be placed in the safety department in a locked cabinet. The will be logged out by safety on the day of use and logged back in the same day. Only leads and Supervisor will have the ability to sign for these devices and will be held accountable for their safe return at the end of the operation." The static eliminator was manufactured by NRD, LLC; Model # P-2030-0010 / Serial # A2GY503. The device contains a Po-210, 40 milliCurie sealed source. Washington State Report: WA110035 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2011-07-22
47072 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-07-19 11:13 | 2011-07-19 14:40 | 2011-07-19 | INADVERTENT ACTUATION OF EMERGENCY SIRENS DURING EXERCISE "At 1113 (EDT) on 7/19/2011, the emergency sirens surrounding the Surry Power Station actuated during an annual exercise being conducted at the local and state levels. The state was planning to simulate the actuation, but the sirens were inadvertently activated. The Virginia Department of Emergency Management made a news release regarding the actuation, notifying the public that there is no emergency at Surry Power Station. "This report is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of Surry Power Station by state agencies of an inadvertent activation of the public notification system. The site NRC resident inspectors have been notified." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-19
47071 | -1 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-07-12 11:00 | 2011-07-19 10:05 | 2011-07-19 | AGREEMENT STATE REPORT - PATIENT RECEIVED TREATMENT TO INCORRECT ORGAN "Approximately four (4) weeks prior to the therapy, patient was scanned for extrahepatic shunting through injection of 99mTc MAA into the hepatic artery per protocol. No shunting to the duodenum was identified. "On Tuesday July 12, 2011, at 11:00 AM the patient was treated with 0.977 GBq of 90Y TheraSphere per protocol. Interventional Radiologist properly placed catheter. A second interventional Radiologist confirmed the catheter placement. "On Tuesday July 12, 2011 at 6 PM, post procedure scan identified significant activity in the duodenum. Initial estimate indicates 0.117 GBq had shunted into the duodenum approximately 12% of the administered activity. An initial estimate indicates dose to duodenum is approximately 110 Gy. "The asymptomatic patient was discharged with follow up contacts for possible intervention as a result of the dose to the duodenum. Patient has been notified. Referring physician has been notified. "Literature search indicates patient may have developed vascularization post-scan, pretreatment. "An inspector from the Department [Ohio Bureau of Radiation Protection] will conduct an inspection the week of July 25, 2011." Ohio Event Report Number: 2011-014 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM MARK LIGHT TO VINCE KLCO ON 7/19/11 AT 1326 EDT * * * Based on further review by the licensee, the patient's organ in question did not receive the above referenced dose. Notified the R3DO(Duncan) and FSME (Zelac). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2011-07-25
47070 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-07-19 07:00 | 2011-07-19 09:04 | 2011-07-19 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY CAMERA "On July 19, 2011, the Agency [Texas Department of Health] was notified by the licensee that one of their radiography crews had discovered that the dark room on their truck had been broken into some time during the night. The radiographers stated the radiography camera transportation container containing a QSA Global model 880 D camera with a 33.7 curie iridium (Ir) 192 source and a portable electric generator had been stolen. "Local law enforcement was contacted and responded to the scene. The agency [Texas Department of Health] notified the Texas association of Pawnbrokers of the event and provided information on the device. Additional information will be provided as it is received." Texas Incident # I-8871 * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 7/19/2011 AT 1659 EDT * * * The following information was received by email: "Local law enforcement has reviewed the security tape at the hotel and was able to identify the vehicle type and manufacturer. They do not believe they can get a license plate number from the video. The time of the theft was set at between 0400 [CDT] and 0409 [CDT]. An Agency investigator went to the location and interviewed the radiographers. He found that the guide tube and crank cables were also stolen. The radiographer stated that the tailgate of the truck was not locked, but that the dark room door was locked. He stated that they did not test the alarm that day, but it had been tested on July 17, 2011. Because of the investigation by local law enforcement, they have not been able to test the alarm system today. The radiographer stated that a cable was used to secure the transport box to the truck and that one of the pad eyes used to secure the cable to the truck had been ripped through the dark room wall freeing the transportation container. The radiographer stated that the transport box has a new Yellow II label. "The alarm system was tested at 1141 [CDT] and found to be functioning properly. The radiographers stated that they had set the alarm when they got to the hotel, but failed to set it after returning from getting their dinner. "The agency [Texas Department of Health] has contacted the Federal Bureau of Investigation and informed them of the event. "The agency [Texas Department of Health] and the licensee are currently driving around the city of Austin, Texas with portable radiation detection instrumentation in an attempt to locate the camera." Notified the R4DO (Campbell), FSME (White), IRD (Gott), ILTAB (Allston), R4IAT(Howell) and Mexico (via email and fax). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-22
47069 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-07-15 12:00 | 2011-07-18 16:38 | 2011-07-18 | AGREEMENT STATE REPORT - DELIVERED DOSE POTENTIALLY DIFFERENT THAN PRESCRIBED DOSE The following information was received by e-mail: "A routine inspection was performed of the licensee on July 11 and 12, 2011. Based on records reviewed at the time of inspection and additional documentation provided to the Kentucky Radiation Health Branch on July 15, 2011. Three unreported Medical Event(ME)s appeared to have occurred during the past three years. " 1. On June 16, 2008 a Written Directive(WD) signed by an Authorized User [AU] for the administration for a total activity of 192.00 U (148.492 mCi) and a Prescription Dose of 125.0 Gy of Pd-103 seeds to the prostate. Manufacturer: Theragenics Model Number: Not Available Seed Lot No: NOT AVAILABLE Source Activity: 2.000 U (1.547 mCi )per seed Number of Seeds (Sources): 96 Based on the licensees use of the nationally recognized Report of AAPM [American Association of Physicists in Medicine] Task Group Report No. 64 for determining the dose received by the prostate a ME was identified. The post operative CT indicated the prostate received: D90 of 81.17 Gy (64.94%) of the prescribed dose. D100 of 43.71 Gy (34.97%) of the prescribed dose. " 2. On March 23, 2009 a Written Directive(WD) signed by an Authorized User for the administration for a Total Activity of 133.560 U (103.295 mCi) and a Prescription dose of 90. Gy of PD-103 seeds to the prostate. Manufacturer: Theragenics Model Number: 200 Seed Lot No: 0910E Source Activity: 1.590 U (1.230 mCi) per seed Number of Seeds (Sources): 84 Based on the licensees use of the nationally recognized Report of AAPM Task Group Report No. 64 for determining the dose received by the prostate a ME was identified. The post operative CT indicated the prostate received: D90 of 55.41 Gy (61.57% ) of the prescribed dose. D100 of 28.03 Gy (31.15% of the prescribed dose). "3. On April 12, 2010 a Written Directive (WD) signed by an Authorized User for the administration for a Total Activity of 140.736 U (108.848 mCi) and a Prescription Dose of 125.0 Gy of PD-103 seeds to the prostate. Manufacturer: Theragenics Model Number: 200 Seed Lot No: 0910E Source Activity: 2.199 U (1.701 mCi ) per seed Number of Seeds (Sources): 64 Based on the licensees use of the nationally recognized Report of AAPM Task Group Report No. 64 for determining the dose received by the prostate a ME was identified. The post operative CT indicated the prostate received: D90 of 70.71 Gy (56.57% )of the prescribed dose. D100 of 34.21 Gy (27.36% of the prescribed dose). "The licensee and the RSO [Radiation Safety Officer] were unaware the three procedures were reportable ME's. The RSO and the AU reviewed the Pre and Post implant plan and the AU was satisfied to follow the patients progress with repeated PSA testing. "The licensee is currently reviewing the findings and implementing preventive measures agreed to by the licensee and the [Agreement State]." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-07-24
47068 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-07-14 12:00 | 2011-07-18 16:30 | 2011-07-18 | AGREEMENT STATE - SOURCE DISCOVERED IN SCRAP SHIPMENT - TWO OTHERS STILL MISSING "On Thursday July 14 a scrap dealer contacted the Virginia Radioactive Materials Program (VRMP) indicating a load of steel had set off their alarm. The scrap yard was able to identify the material that set off the alarm and isolate. On Friday July 15 VRMP staff went to the scrap yard to perform surveys and identify the material in question. The investigation determined that the material had come from the demolishing site of Dan River, Inc, a former textile business that closed in 2008. The gauge was determined to contain Kr-85 utilizing a radionuclide identifier and the GL database, which lists three Mahlo Controls Kr-85 gauges being possessed by Dan River, Inc. The VRMP continues to work with the scrap yard and demolishing company looking for the other two gauges. VRMP is also working with Mahlo Controls in researching the three gauges in question." The sources in these generally licensed devices were originally 100 milliCuries each. It is estimated that they have decayed three half-lives and the current strength is estimated at approximately 13 milliCuries each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 0 |  | OTH | AGR |  |  |  |  | 0 | 2011-07-21
47067 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-07-18 12:15 | 2011-07-18 13:23 | 2011-07-18 | OFFSITE NOTIFICATION OF A RAW SEWAGE DISCHARGE "At approximately 1215 CDT FCS began discharging raw sewage to the Missouri River via the Raw Water Header. Portable toilets staged inside the plant for plant flooding are being pumped for disposal. Per discussions with the State of Nebraska, this is an additional bypass of the sewage system and requires state notification. This condition is being reported pursuant to 10 CFR 50.72(b)(2)(xi) for News Release or Notification of Other Government Agency. Applicable governmental agencies have been notified per plant procedures. NRC Resident informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-18
47066 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-05-01 12:00 | 2011-07-17 18:26 | 2011-07-17 | PREVIOUS INOPERABILITY OF CRITICALITY ACCIDENT ALARM SYSTEM WARNING CIRCUIT NOT IDENTIFIED "As part of the corrective actions for the Criticality Accident Alarm System (CAAS) events reported on 7/13/11 (EN #47047) and 7/15/11 (EN #47061), GNF-A is performing an investigation into the cause of the delayed audible alarm actuation. The investigation has determined that this delay existed at the time of the May and June 2011 functional tests and was not adequately identified and thus not reported. The response time to activate the horns did not meet the design requirement for CAAS. These events are being reported pursuant to the requirements of 10CFR70.50 (b)(2)." The licensee states that the delay in the alarm actuation existed during surveillance testing in May and June of 2011 but the delay was not recognized at the time. This condition rendered the system inoperable since May 2011. The licensee has notified R2 (Sykes) and will notify state and local authorities. R2DO (Freeman) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-07-17
47065 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-07-16 18:30 | 2011-07-16 22:40 | 2011-07-16 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM NON-FUNCTIONAL "The Technical Support Center ventilation system was found to be non-functional on 7/16/2011 at 1830 EDT. The time period that the Technical Support Center ventilation system was non-functional exceeded the 30 minute time limit that is delineated in the Technical Requirements Manual T3.10.1. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, rev. 2 since this adversely affects an emergency response facility. Also, this 8 hour notification is made in accordance with Technical Requirements Manual T3.10.1.B.2 "The alternate Technical Support Center facility was functional immediately and remains functional." Per the licensee, the Technical Support Center ventilation system remains out-of-service. The cause was due to a loss of refrigerant in the system. Repairs are currently underway. The licensee notified the NRC Resident Inspector. | 95 | 95 | 0 | 95 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-16
47064 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-07-16 06:12 | 2011-07-16 09:12 | 2011-08-03 | UNUSUAL EVENT DECLARED DUE TO ENTRY INTO EAL HU4.1 The licensee declared an Unusual Event at 0612 PDT due to entry into EAL HU4.1 for a security-related event. Contact the Headquarters Operations Officer for details. The licensee notified State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM DANIEL CRUZ TO DONALD NORWOOD AT 1255 EDT ON 7/16/11 * * * The licensee exited the Unusual Event at 0950 PDT after verifying that the exit criteria for EAL HU4.1 had been met. Contact the Headquarters Operations Officer for details. The licensee notified State and local authorities and the NRC Resident Inspector. Notified NRR EO (Giitter), R4DO (Cain), IRD MOC (Morris), ILTAB (Allston), DHS SWO (Gates), and FEMA (Via). * * * RETRACTION FROM LEE KELLY TO DONALD NORWOOD AT 1356 EDT ON 8/3/11 * * * After further investigation, the licensee determined that the declaration of the Unusual Event had been a conservative action not required by site procedures. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. Notified R4DO (Hagar), NRR EO (Thorp), and IRD MOC (Gott). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-07-16
47063 | 0 | QUALTECH NP |  |  |  |  | 2011-07-15 | 2011-07-15 20:43 | 2011-08-05 | POTENTIAL DEFECT IN QUALTECH NP SAFETY RELATED MOTOR CONTROL CENTER BUCKETS The following information was received via facsimile from QualTech NP: "This letter is issued to provide initial notification of a potential defect in QualTech NP safety related MCC [Motor Control Center] buckets, which were commercial grade dedicated at our Cincinnati facility. On June 9, 2011, TVA Watts Bar Unit 2 notified QualTech NP of a failure on a transformer module associated with an indicator light on the MCC bucket. Based on our investigations, QualTech NP has identified quality and performance issues relating to the 480 VAC input (primary side) portion of the subject indicating light. The light in question has shown the potential to flash/arc internally on the primary winding side of the built in transformer and create a substantial fault current. This fault current not only disables the light but can be large enough to trip the upstream circuit breaker, thus disabling all associated safety related circuitry. "The issues appear to revolve around inconsistent and poor quality fabrication methods employed during manufacturing, primarily with how the wires were wrapped in critical areas of the primary and how they were routed and attached to the termination points. "The recommended corrective action for existing safety related MCC buckets is to replace the indicator light and transformer module with a newly qualified acceptable substitute. The new indicator light and transformer module will go through a series of dedication inspections and tests to ensure that a similar failure does not occur. "Based on review of our records, Tennessee Valley Authority is the only customer to have these defective modules." * * * UPDATE ON 8/05/11 AT 1131 EDT TO HUFFMAN VIA FAX FROM QUALTECH NP * * * "QualTech NP conducted failure analyses to determine the root cause. Based on the results of our investigations, QualTech NP has determined that this failure represents a defect in a basic component as defined by 10CFR21. "The failure analyses concluded that all of the failure modes encountered were due to manufacturing defects associated with the soldering and handling of the wire strands in the vicinity of the line terminals. "QualTech NP has established a corrective action plan to replace all of these components known to be installed in safety-related applications. We are currently in the process of evaluating a suitable replacement. "Based on review of our records, Tennessee Valley Authority is the only customer to have these defective modules. We have been in close communications with TVA on this issue. "The specific component is Model Number 9001KP5R31, manufactured by Square D." R2DO (Desai) and the Part 21 Group notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2011-07-15
47062 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-07-13 | 2011-07-15 15:22 | 2011-07-15 | AGREEMENT STATE REPORT - THEFT OF AN X-RAY FLUORESCENCE ANALYZER The following report was received from the Radioactive Materials Section of the Illinois Emergency Management Agency: "[Arcos Environmental] a General Licensee, called the agency [Illinois Emergency Management Agency (IEMA)] to advise that a x-ray fluorescence analyzer [containing a 5 millicurie Cd-109 source] for measuring lead content of paint was stolen from a locked vehicle while at a temporary jobsite. The device along with several other items was removed from the car's trunk while it was parked at 6020 S. Langley Ave., Chicago, IL. At the time of the theft, the responsible user was in a building performing other duties. The theft was promptly reported to the Chicago Police Department. The general licensee is considering a news paper ad to encourage return of the device to its Tinley Park offices. "Use of the device requires a 'pass code' to activate the device's features and allow exposure of the radioactive source by the opening of an internal shutter. The pass code is maintained separate from the device. In addition, 6 years after the source has been installed, the device will no longer operate and a display message directs that the device be returned to the manufacturer. This device was initially sourced in Sept of 2007. "The maximum surface dose rate from the device is less than 100 microR/h when the shutter is closed. Based on the SSDR safety evaluation the maximum exposure rate, should the safety and security features be defeated and the shutter opened, would be 3 milliR/h. As a result, the potential radiation exposure to the thief or any member of the public is projected to be extremely low. "The general licensee has been advised of the requirement to file a written report within 30 days of the theft. The agency [IEMA] does not intend to conduct an on-site investigation unless additional information or circumstances change which warrant a visit." Illinois Report Number: IL11086 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-07-20
47061 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-07-14 16:55 | 2011-07-15 16:15 | 2011-07-17 | INOPERABLE CRITICALITY ACCIDENT ALARM SYSTEM WARNING HORNS "As part of the corrective actions for the event reported on 7/13/11 [EN #47047], GNF-A performed a Criticality Accident Alarm System (CAAS) audibility test covering the Controlled Access Area (CAA) at approximately 1655 on 7/14/11. The subsequent test revealed that the installed CAAS system failed to immediately activate the horn signal generators as expected. Activation of the associated warning horns was delayed approximately 3 minutes. This response time to activate horns did not meet the design requirement. Additionally, a review determined an approximately 3 minute horn signal delay was noted in a previous test on 7/12/11. An investigation into these matters is ongoing. "The FMO [Fuel Manufacturing Operations] complex fissile material process operations were suspended on 7/14/11 and personnel evacuated. The emergency organization was activated and efforts to troubleshoot the root cause in the horn signal activation circuit delay initiated. All production activities involving Special Nuclear Material are shut down. "The installed CAAS is a safety-significant system and is maintained through routine response checks and scheduled functional tests conducted in accordance with internal procedures. These events are being reported pursuant to the requirements of 10CFR70.50(b)(2)." The licensee notified NRC Region 2 personnel (Sykes), State of North Carolina Radiation Protection, and New Hanover County EMA. * * * UPDATE ON 7/17/11 AT 1826 EDT FROM OLLIS TO HUFFMAN * * * The cause of the inoperable Criticality Accident Alarm System (CAAS) has been identified as a hardware failure - specifically a capacitor on a circuit board. The CAAS has been repaired and a comprehensive testing plan is under development. The licensee continues to withhold personnel from the Controlled Access Area and all production activities remain shut down. A root cause analysis and recovery plan are underway. The licensee has contacted R2 (Sykes) and will be notifying state and local authorities. R2DO (Freeman notified). See related Events #47047 and #47066. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-07-15
47060 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-07-14 17:04 | 2011-07-15 16:01 | 2011-07-15 | INITIATION OF MATERIAL CONTROL AND ACCOUNTING RESOLUTION PROCEDURE "10CFR74.57(f)(2) requires notification within 24 hours that an MC&A [Material Control and Accounting] alarm resolution procedure has been initiated. In the solvent extraction area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure has been initiated, this notification is being made. There is no indication that a material loss has occurred. "MC&A process monitoring tests for material balance were run as specified by applicable procedures and requirements. Based on the test results for the Building 333 solvent extraction area, the test limit was exceeded. An investigation is currently underway to resolve the issue. "There were no actual or potential safety consequences to workers, the public, or the environment. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2011-07-19
47059 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-07-15 08:00 | 2011-07-15 14:22 | 2011-07-15 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER STUCK OPEN The following information was received from the State of Texas Health Services Radiation Branch: On July 15, 2011, the agency [Texas Department of Health] received an e-mail from the licensee's Radiation Safety Officer stating that during a routine inspection, the shutter of a Texas Nuclear model 5176 nuclear gauge containing 500 millicuries cesium - 137 (serial # B2623) was stuck in the open position. The RSO stated that open is the normal operating condition for the gauge and that it did not create any additional radiation exposure risk to any individual. The RSO stated that he was going to contact a vendor for repairs or replacement of the gauges. Additional information will be provided as it is received in accordance with SA-300. Texas Incident # I-8870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-20
47058 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-07-15 | 2011-07-15 14:28 | 2011-07-15 | AGREEMENT STATE REPORT - LOOSE SHUTTER ON PROCESS GAUGE The following information was received via email from the State of Texas Health Services Radiation Branch: "On July 15, 2011, the agency [Texas Department of Health] received an e-mail from the licensee's Radiation Safety Officer stating that during a routine inspection, the shutter on a Kay-Ray model 7062P nuclear gauge containing 100 millicuries of cesium - 137 (serial # KR 22151V) was loose and did not completely shield the source. The RSO stated that open is the normal operating condition for the gauge and that it did not create any additional exposure risk to any individual. The RSO stated that he was going to contact a vendor for repairs or replacement of the gauges. Additional information will be provided as it is received in accordance with SA-300." Texas Report ID: I-8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-20
47057 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-07-12 | 2011-07-15 11:33 | 2011-08-02 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING TREATMENT DOSE ADMINISTERED TO WRONG SITE The following event report was received from the Pennsylvania Bureau of Radiation Protection: "The licensee called the PA Department of Environment Protection (PaDEP) Southeast Regional Office at 1050 EDT on July 14, 2011 to provide a 24-hour verbal notice of a Medical Event (ME). A total treatment dose was administered to the wrong site, consequently requiring a 24-hour report per 10 CFR 35.3045(a)(3). This event also meets the criteria for Abnormal Occurrence (AO) reporting. "On July 12, 2011 a Yttrium-90 (Y-90) SIR-Sphere treatment was performed. The written directive was for treatment of the liver's right lobe, but the total treatment was delivered to the left lobe. The prescribed dose was 31.5 millicurie (mCi) of Y-90. "There are several open questions regarding root cause, potential health impact on the patient and communications to the patient and their physician. PaDEP/BRP will be performing a reactive inspection, which is scheduled for Monday July 18, 2011. Updates to this NRC report will be made once we investigate the ME at Lehigh Valley Health Network and obtain the follow-up written report from the licensee." PA report Number: PA110016 * * * UPDATE AT 1500 EDT ON 08/02/11 FROM D. ALLARD TO S. SANDIN VIA FAX * * * The State of Pennsylvania is retracting this report based on the following: "After a PaDEP reactive inspection on July 28, 2011 and discussion with the licensee regarding the circumstances of a SirSphere infusion performed on July 12, 2011, it was determined a Medical Event [and Abnormal Occurrence) did not occur. "The licensee's report concludes that there was no medical event because the authorized user intended to treat a lesion in the right lobe of the liver and that was what happened. The interventional radiologist who performed the procedure elected to use the left hepatic artery because a prior treatment through the right hepatic artery was unsuccessful in treating this lesion. The interventional radiologist and the authorized user discussed this at the time of the treatment and were in full agreement on the procedure. "Medical Event should be retracted; no further action to be taken at this time." Notified R1DO (Bellamy) and FSME (McKenney). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-07-21
47056 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2011-07-16 05:00 | 2011-07-15 13:15 | 2011-07-23 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO PLANNED MAINTENANCE "At 0500 on Saturday, July 16th and 0700 on Saturday, July 23rd, a sequence of activities are planned that will render the Technical Support Center (TSC) non-functional by removing all normal and emergency power. These activities are being performed in support of planned TSC facility upgrades. In preparation for this power outage(s), the TSC emergency responders were notified that use of the alternate TSC will be required in accordance with station procedures. Each TSC emergency response function has performed a walkdown and verification that required functions can be established in the alternate location. The duration for each of these TSC power outages is expected to be less than 24 hours. The NRC Operations Center will be provided an update to this notification when power has been removed and restored during this time period." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM RICK VIRGIN TO CHARLES TEAL @ 0730 ON 7/16/11 * * * On 7/16/2011 at 0707 power was removed from the TSC. If necessary, the alternate TSC is ready for use. * * * UPDATE FROM WARREN DEAGLE TO BILL HUFFMAN AT 1800 ON 7/16/11 * * * On 7/16/11 at 1729 EDT, power was restored to the TSC. The TSC has been restored to a normal operational status and can be utilized for emergency response. The licensee has notified the NRC Resident Inspector. R2DO (Freeman) notified. * * * UPDATE FROM CHRISTINE McKIM TO CHARLES TEAL AT 0647 EDT ON 7/23/11 * * * On 7/23/11 at 0645 power was removed from the TSC. If necessary, the alternate TSC is ready for use. The licensee has notified the NRC Resident Inspector. R2DO (Sykes) notified. * * * UPDATE AT 1650 ON 7/23/2011 FROM DAVID McAGY TO MARK ABRAMOVITZ * * * [At 1613], "power has been restored to the TSC. The normal TSC can be utilized for ERO response. There are no further planned TSC outages at this time." Notified the R2DO (Sykes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-15
47055 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-06-22 16:34 | 2011-07-15 12:06 | 2011-07-15 | AGREEMENT STATE REPORT - CONTAMINATED PATIENT / PATIENT ROOM The following information was received via facsimile: "On Wednesday, June 22, 2011 at 1634 EDT, an admitted patient was given a 182 mCi I-131 capsule for a thyroid ablation study. At approximately 0330 EDT on Thursday, June 23, 2011, the patient vomited onto herself and the floor. The nursing staff cleaned up the patient and the floor and then notified the Nuclear Medicine Department (NMD). NMD staff began to perform surveys of the patient and the room and found contamination. Further cleaning of the patient and room was performed. The patient was released on Saturday, June 26, 2011. The room was sealed off to allow the I-131 contamination to decay below regulatory limits. The room remains restricted. NMD staff are performing contamination surveys." Virginian Report Number: VA-11-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-07-21
47054 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-07-15 10:16 | 2011-07-15 11:54 | 2011-07-15 | ALERT DECLARED DUE TO TOXIC GAS RELEASE RESTRICTING ACCESS TO A VITAL AREA "An alert was declared due to a leak of sodium hypochlorite at the unit 2/3 cribhouse. Access to the unit 2/3 cribhouse, which is a vital area, was restricted. The leak has been isolated." The licensee has notified State authorities and the NRC Resident Inspector. The licensee stated that the sodium hypochlorite leak was actually outside the cribhouse and went into a sump. The fumes from the sodium hypochlorite restricted access to the cribhouse which contains safety related ultimate heat sink equipment (containment cooling service water pumps, emergency diesel generator cooling water pumps). Other than restricting access to the cribhouse, the leak has had no other impact on plant operation. The alert was declared under EAL H.A.7 - release of toxic gas within or restricting access to a vital area. * * * UPDATE AT 1626 EDT ON 7/15/11 FROM MIROCHNA TO HUFFMAN * * * "The alert has been terminated on 7/15/11 at 1520 CDT. The conditions which caused the alert no longer exist. A press release was made for the event. Two employees were sent for offsite medical attention as a precautionary measure; neither employee was contaminated." The licensee stated that the sodium hypochlorite had leaked from a pipe into a sump under the storage trailer near the cribhouse. The sodium hypochlorite that leaked into the sump has been pumped out. Access to the cribhouse has been restored and there are no other access restrictions at the site. Both units continue to operate at full power. The licensee will notify appropriate state and local authorities. The NRC Resident Inspector has been notified. The licensee has also issued press releases concerning this event. R3DO (Bloomer), NRR EO (Giitter), IRD (Morris), DHS(Knox), and FEMA (Burckhart) have been notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-07-15
47053 | 0 | UNIV OF WISCONSIN |  |  |  | 1000 KW TRIGA (CONVERSION) | 2011-07-14 11:52 | 2011-07-15 10:35 | 2011-07-18 | TEST REACTOR VIOLATED TECHNICAL SPECIFICATION STAFFING REQUIREMENTS "The following special report is being made in accordance with the requirements of Technical Specification (TS) 6.7.2(1)(c) which states in part: There shall be a report not later than the following day by telephone or similar conveyance to the NRC Headquarters Operation Center of any reportable occurrence as defined in TS 1.3. TS 1.3 defines an observed inadequacy in the implementation of administrative or procedural controls, such that the inadequacy caused the existence of a condition which results in a violation of technical specifications as a reportable occurrence. "Specifically, on Thursday July 14, 2011, while performing routine surveillance checks, an operator left the control room while the console key remained in the console key switch and the switch was in the TEST position. This is in direct violation of the staffing requirements defined in TS 6.1.3(1)(a) which states a licensed reactor operator must be in the control room when the reactor is not secured. The reactor was not secured by the fact that the console key switch was not in the OFF position and the key remained in the console key switch. However, all control elements were fully inserted, the reactor was shut down, no work was in progress involving core fuel, core structure, control elements or drives and no experiments were being moved. This condition remained for a period of approximately 7 minutes until the cognizant senior reactor operator entered the control room and secured the reactor." * * * UPDATE FROM ROBERT AGASIE TO PETE SNYDER ON 7/18/11 AT 0846 EDT * * * After a records review the licensee determined that: the actual event time was 1055 AM CDT and the actual duration of time that the operator was not in the control room was 85 seconds. Notified R3DO (Duncan) and NRR (Tran). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 3 | WI | NPR | [5 empty] | 0 | 2011-07-15
47052 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-14 20:53 | 2011-07-14 21:50 | 2011-07-15 | UNUSUAL EVENT DECLARED BASED ON REACTOR COOLANT LEAK GREATER THAN 10 GPM "At 2053 on July 14, 2011 Salem unit 2 declared an Unusual Event due to reactor coolant system leakage greater than 10 gallons per minute. While performing a monthly Emergency Core Cooling System vent of the high head safety injection piping a motor operated valve was opened and a leak developed on the high head piping greater than 10 gallons per minute. The leak rate was approximately 11-15 gallon per minute. The leak was terminated when the motor operated valve was closed. The time of the leak was about 6 minutes." At this time the leak is believed to be from a crack on the Boron Injection Tank (BIT) relief valve line which is connected to the high head piping. A total of approximately 90 gallon of reactor coolant leaked into the BIT room. The licensee has declared the high head safety injection inoperable and is proceeding to shutdown under Tech Spec 3.0.3. The license has notified appropriate State and local authorities. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM KARL HANPHO TO VINCE KLCO ON 7/15/11 AT 0025 EDT* * * "Salem Unit 2 declared an Unusual Event due to Reactor Coolant System (RCS) leakage being greater than 10 gpm and pressurizer level decreasing. Leakage was estimated to be approximately 15 gpm. The leakage was determined to be from a weld on the high head charging injection relief valve connection. This leaking weld impacts both trains of high head charging/safety injection. Both trains of high head charging/safety injection were declared inoperable at 2038 [EDT] on July 14, 2011, entering TS 3.0.3. Salem Unit 2 began the Technical Specification shutdown in accordance with TS 3.0.3 at 2136 [EDT]. The technical specification shutdown is being reported in accordance with 10CFR50.72(b)(2)(i) and RAL 11.1.1.a. "In addition since the leakage from the weld on the high head charging/safety injection piping exceeded the analyzed limit for ESF leakage outside containment, this event is also being reported in accordance with 10CFR50.72(b)(3)(v) and RAL 11.2.2.b as a condition that prevents the ability to mitigate the consequences of an accident. "Salem unit 2 is currently at 27% and reducing power." The licensee notified the states of New Jersey and Delaware, Lower Alloways Creek Township and the NRC Resident Inspector. Notified the R1DO (Dwyer), NRR-EO (Giiter) and IRD (Morris). * * * UPDATE FROM KARL HANPHO TO CHARLES TEAL ON 7/15/11 AT 0345 EDT* * * Salem Unit 2 has exited the Unusual Event as of 0339 EDT. The criteria for exit was the leakage rate was below the 10 gpm rate. The plant is in Mode 3 and is preparing to cooldown. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Dwyer), NRR EO (Giitter), IRD (Morris), DHS(Hill), and FEMA (Blankenship). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS | POT UNCNTRL RAD REL |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) | 50.72(b)(3)(v)(C) |  | 0 | 2011-07-14
47051 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-07-14 19:13 | 2011-07-14 20:24 | 2011-07-14 | UNUSUAL EVENT DECLARED DUE TO SUSPECTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA The licensee declared an Unusual Event due to indications that potentially dangerous contraband had been introduced into the protected area. After further investigation, the licensee determined that the indication of contraband was due to incorrect interpretation of screening equipment imaging. The licensee exited its Unusual Event declaration at 1942 CDT. The licensee continues to investigate the circumstances leading to this event declaration. The licensee notified State and local authorities and will notify the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-07-14
47050 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-07-14 14:11 | 2011-07-14 20:09 | 2011-07-14 | NEWS RELEASE REGARDING ARREST OF ILLEGAL IMMIGRANT WORKING AT PALO VERDE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This event is being reported as a newsworthy concern to the public under 10 CFR 50.72(b)(2)(xi). "Palo Verde Nuclear Generating Station (PVNGS) was notified that the Maricopa County Sheriff's Office (MCSO) issued a news release at 1411 on July 14, 2011, regarding entrance to the PVNGS site property by an individual who MCSO alleged to be an undocumented immigrant. "The individual had entered Palo Verde's Security Owner Controlled Area on July 13, 2011, but was not granted access to the site's Protected Areas surrounding the three units and Independent Spent Fuel Storage Installation. PVNGS Security contacted MCSO to validate the identification card furnished by the individual at the Security Owner Controlled Area. MCSO determined the identification card to be suspicious, responded to the site, detained the individual, and transported him off-site for questioning. "The station notified NRC Resident Inspectors and Region IV staff of the condition on July 13, 2011. "Arizona Public Service is planning to issue a news release and is responding to media inquiries regarding the matter." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-14
47049 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-07-14 | 2011-07-14 19:54 | 2011-07-15 | AUDIBILITY OF CRITICALITY EVACUATION ALARM DEGRADED "Early in the morning of 7/14/2011, intermittent trouble alarms associated with production area speakers were observed by security and Plant Superintendent personnel. Testing of the Public Address (PA) system confirmed that the speakers could not be heard in the production areas. The speakers associated with the PA system are also used for the criticality evacuation alarm. When in trouble alarm, the speakers do not function. Safety personnel were notified of the problem and a stop movement order was issued for the affected areas. Operations personnel were briefed on the situation and were provided with compensatory measures (e.g., radios). Nonessential personnel were also removed from the affected areas. Troubleshooting of the system was performed (e.g., re-termination of control module and panel reset) and the system was retested and restored to service. Operations have resumed in the affected areas. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM RANDY SHACKELFORD TO DONALD NORWOOD AT 1315 EDT ON 7/15/2011 * * * "Further testing of the speakers associated with the criticality evacuation alarm has indicated that the system was not compromised as originally thought when the telephone notification was made on 7/14/2011. The test performed on 7/14/2011 did not properly test the criticality evacuation alarm circuit. The criticality evacuation alarm was retested on 7/15/2011; and, the alarm was heard throughout the affected areas. Therefore, NFS is retracting the Event Report #47049. The NRC Resident Inspector has been notified." Notified R2DO (Freemen) and NMSS EO (Rahimi). Notified Fuels Group via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-07-18
47048 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-07-14 13:19 | 2011-07-14 16:19 | 2011-07-14 | OFFSITE NOTIFICATION DUE TO INADVERTANT SIREN ACTUATION "At about 1319 on July 14, 2011, Dauphin County 911 (Pennsylvania) was advised by a local resident that siren number 121 sounded for 3 minutes. Dauphin County (Pennsylvania) contacted the TMI main control room to inform Exelon of an inadvertent siren actuation at about 1350 on July 14, 2011. "Pennsylvania Emergency Management Agency (PEMA) later notified (about 1430 on July 14, 2011) the TMI main control room of the same issue. "This notification is being made in accordance with 10CFR50.72(b)(2)(xi) because offsite agencies were notified regarding the inadvertent actuation of part of the public notification system. "Siren Maintenance was notified and is troubleshooting the issue." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-14
47047 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-07-12 17:30 | 2011-07-13 17:12 | 2011-07-13 | INAUDIBLE CRITICALITY WARNING SIREN "At approximately 1730 on 7/12/2011, a regularly scheduled test of the inside Criticality Warning System (CWS) covering the Fuel Manufacturing Operation (FMO) was conducted. It was discovered that a CWS warning horn in the ChemMet lab was determined to be inaudible. Compensatory measures were immediately implemented. All other horns of the inside CWS in all other areas were functional and clearly audible. The affected area will remain shut down pending an investigation and implementation of additional corrective actions. The event is being reported within 24Àhours pursuant to 10CFR70.50(b)(2) as a safety equipment failure. A CWS warning horn in the ChemMet lab was determined to be inaudible. All other CWS warning horns operating correctly. Investigation results pending. Affected area access was restricted. The faulty CWS horn has been replaced and tested." The licensee notified Region 2(Coovert) and will notify the state radiation protection agency and New Hanover Emergency Management. See related Events #47061 and #47066. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-07-13
47046 | 0 | PARADISE FOSSIL PLANT |  |  |  |  | 2011-07-12 13:30 | 2011-07-13 14:25 | 2011-07-13 | MOISTURE DENSITY GAUGE SHUTTER STUCK IN THE CLOSED POSITION Tennessee Valley Authority Paradise Fossil Plant uses an Ohmart Model SR1-A density gauge with a sealed source containing up to 1,562 milliCuries of Cesium 137. The gauge is used to monitor the density of the limestone slurry at the Unit 2 scrubber. On July 12, 2011 at 1330 (CDT) the shutter on the density gauge was determined to be not operable. It was determined that the shutter failed in the closed position when the operator received a slurry density high alarm. The shutter failure is in the closed and safe position. The gauge has been entered into the corrective action program and will be repaired by the manufacturer at a later time. There were no personnel exposures, no damages to other equipment, and no additional compensatory actions necessary since the shutter is failed closed/safe position. The licensee notified the R2DO (Freeman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | KY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-07-13
47045 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-13 00:23 | 2011-07-13 01:08 | 2011-07-13 | OVERFLOW OF CONDENSER CIRCULATING WATER "At 0023 on 07/13/2011, a notification to an outside state agency, Tennessee Department of Environment and Conservation (TDEC), was made due to an overflow of Condenser Circulating Water from the northwest corner of the diffuser pond through a heavily vegetated area into a slough adjacent to the Sequoyah Training Center. Condenser Circulating Water is also discharging to the river via storm water outfall 14 near the cooling towers as well as the normal diffuser pond discharge at outfall 101. "At approximately 1545 on 07/12/2011, one of the two diffuser gates at Sequoyah failed and shut off the west diffuser pipe. The other diffuser remained open throughout the event. Plant personnel made several attempts to raise the diffuser gate utilizing divers and cranes. When it was determined the crane could not lift the diffuser gate, both units reduced power to 85% and one (1) Condenser Circulating Water pump for each unit, two (2) pumps total, were removed from service. Diffuser pond level is currently lowering." The NRC Resident Inspector has been informed. | 85 | 85 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-13
47044 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2011-07-11 09:00 | 2011-07-12 14:11 | 2011-07-12 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO WHOLE BODY (WB) AND HANDS The following was received via fax: "The Department of Health and Environmental Control was notified on July 12, 2011 at 10:25 AM by the licensee that it had received notification from Landauer that one of the employees WB and Ring badges exceeded the limits. The licensee stated that the WB badge had a reading of 77480 mR and the Ring badge had a reading of 65468 mR. The employee in question only administered doses to patients 6 out of the 10 days worked during the reporting period. The licensee is authorized for diagnostic administration of radioactive material (Tc-99m and TI-201 ). "The licensee was advised by [the state] to submit a written report detailing this event to the Department of Health and Environmental Control within 30 days. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2011-07-18
47043 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2011-07-08 07:30 | 2011-07-11 16:50 | 2011-07-11 | AGREEMENT STATE REPORT - MEDICAL EVENT OVEREXPOSURE TO THYROID GLAND The following was received from the state via fax: "The Colorado Department of Public Health and Environment received notification this date from The University of Colorado Hospital, Colorado License # 828-01, that a patient received the wrong dose of I-131 on July 8, 2011 resulting in a dose that exceeded prescribed by 50 rem and 50% of the dose expected from the administration defined in the written directive. The patient was prescribed 20 mCi of l-131 for Graves disease, but instead received 100 mCi of I-l31, which was intended for another patient. The patient was discharged before the error was discovered. The patient's physician and the patient have been contacted and made aware of the situation. The patient has been given additional instructions regarding contact with family members and members of the public. No other details are available at this time. "The Colorado Department of Public Health and Environment has initiated an investigation." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2011-07-17
47042 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-07-11 10:22 | 2011-07-11 10:58 | 2011-07-11 | TEMPORARY LOSS OF ERDS AND SPDS DUE TO PLANNED MAINTENANCE "The Emergency Plant Information Computer (EPIC) has been shutdown for planned maintenance. The maintenance is expected to last less than six (6) hours. The shutdown of EPIC has caused a loss of the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS). This is determined to be a partial, but significant Loss of Emergency Assessment Capability, and is an 8-hr. Non-Emergency 10 CFR 50.72(b)(3)(xiii) required notification. "There are no plant transients or power maneuvers in progress or planned. "Actions taken include: performance of the site specific Computer Out-of-service Surveillance (ST-40C) which provides for enhanced Control Room parameter monitoring, additional operating rounds in-plant on a recurring basis, and restriction of scheduled activities that could cause a plant transient. Members of the JAF [James A Fitzpatrick] Emergency Response Organization (ERO) have been briefed on contingencies required during an E-Plan [Emergency Plan] activation. A contingency plan for around the clock maintenance coverage to recover the EPIC if it is not restored as scheduled does exists." The licensee has notified the State, the County, and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-11
47041 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-07-11 01:25 | 2011-07-11 04:00 | 2011-07-11 | INADVERTENT EMERGENCY SIREN ACTIVATION COINCIDENT WITH ADVERSE WEATHER "At approximately 0125 CDT on July 11, 2011 licensee was notified by Goodhue County Sheriff's Department of an inadvertent emergency siren activation (R17) in the city of Red Wing, MN. The Sheriff's Department deactivated the siren and notified the siren vendor. Siren initiation was coincident with severe storm activity in the area, including lighting strikes. Siren remains out of service and is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ)." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-11
47040 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-11 04:00 | 2011-07-11 03:00 | 2011-07-11 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0400 EDT on Monday, July 11, 2011, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 2000 EDT on Monday, July 11, 2011. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM DAN KURTH TO JOE O'HARA AT 2151 ON 7/11/11 * * * "TSC ventilation system maintenance was completed satisfactorily and the system restored to service at 1800 EDT on 7/11/11. The NRC Resident Inspector will be notified." Notified R3DO(Bloomer) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-11
47039 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-07-07 11:00 | 2011-07-08 16:00 | 2011-07-08 | OFFSITE NOTIFICATION DUE TO A CONTAINED ON-SITE LIQUID RADWASTE LEAK "This notification is being made under 10 CFR 50.72(b)(2)(xi) of a situation related to the protection of the environment for which a notification to a state agency has been made. On July 8, 2011, South Carolina Electric & Gas Company (SCE&G) made a voluntary notification to the South Carolina Department of Health and Environmental Control (SCDHEC) in accordance with the Nuclear Energy Institute (NEI) Groundwater Protection Initiative for an on-site leak that may exceed 100 gallons. The leak was entirely contained within the V. C. Summer Nuclear Station site boundary. "On July 7, 2011 during a routine inspection, a leak was discovered in a liquid radwaste line upstream from its final discharge point and downstream of the release radiation monitors. This line contains processed liquid radwaste that has been sampled and permitted for release. The leak occurred inside a containment enclosure which overflowed. The enclosure was drained and the liquid was returned to the plant for disposal. The leak has been isolated and all radwaste release via this pathway has been suspended. The last inspection of this equipment was conducted on February 14, 2011, and revealed no external leakage." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-08
47038 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-05-01 | 2011-07-08 15:45 | 2011-07-08 | AGREEMENT STATE REPORT- UNDEREXPOSURE The following information was received from the Commonwealth by facsimile: "The RSO reported that a patient was 60% underexposed by an Ir-192 remote after-loader. The prescribed dose is not known. The error occurred because the physicist did not calculate the effect of the tube used to deliver the after-loader source. The target organ was the skin." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-07-14
47037 | 0 | WILCOX ASSOCIATES |  |  |  |  | 2011-07-08 11:30 | 2011-07-08 13:34 | 2011-07-08 | DAMAGED MOISTURE DENSITY GAUGE A gauge handle on a portable Troxler Gauge Model 3440 (S/N #16851) was run over by a truck in the Hastings, Michigan area. The measurement and source handle rod was bent. The licensee performed an area survey and no leakage was detected. The density gauge source was not exposed. The licensee plans to ship the damaged gauge to the Troxler Company for repair or replacement. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-07-08
47036 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2011-05-13 | 2011-07-08 14:24 | 2011-07-08 | VALVE FAILED LEAK TEST DUE TO A DISC/SHAFT ASSEMBLY MACHINING ISSUE The following information was received by facsimile: "After a valve failed a leak test, it was determined that a fixture to machine the valve disc was missing one of the locating pins that maintained the integrity of the shaft bore centerline when machining. It was determined that the pin was missing from the fixture from January 8, 2011, to April 7, 2011 . "Fisher has conducted a review and determined that the only ASME Section III code and commercial grade dedicated parts machined during this time that would use this fixture were the parts used for the orders referenced [below]. "Fisher Controls has implemented a corrective action program to address this issue. "Although this notice is dated July 5, 2011 , Palo Verde was officially notified May 13, 2011, when Fisher first became aware of this issue. In the mean time, all affected discs have been returned to Fisher Controls for evaluation. "Subject: NPS 16 Type A11 Disc/Shaft Assemblies for Palo Verde Orders 500541604 and 500548617 (Fisher Orders 019-F514977 and 019-F515346)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-07-08
47035 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-05-10 04:30 | 2011-07-08 13:48 | 2011-07-08 | 60 DAY REPORT - EMERGENCY DIESEL GENERATOR STARTED DUE TO INVALID SIGNAL "This 10CFR50.73(a)(1) report is a 60-day telephone notification in lieu of a written licensee event report being made under 10CFR50.73(a)(2)(iv)(A). On May 10, 2011 at 0430 CDT, during installation of the new loss of offsite power relay, Emergency Diesel Generator 2, started (a complete start) due to an invalid signal but remained operable while running as a backup power supply to its bus. The unit was in a refueling outage at the time. Offsite power was not lost and the diesel bus remained energized from offsite power and was operable. The diesel was subsequently secured." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-07-08
47034 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-07-07 15:40 | 2011-07-08 12:03 | 2011-07-08 | AGREEMENT STATE REPORT- DAMAGED SOIL MOISTURE NUCLEAR DENSITY GAUGE The following information was received from the State by facsimile: "Notifications: Licensee called the Pennsylvania Emergency Management Agency (PEMA), who then contacted Department of Environmental Protection (DEP) via phone on July 7, 2011 @ 1540. This event is 24 hour reportable under 10CFR 30.50(b) (2). "Event Description: A CPN Model MC3 soil moisture Nuclear Density Gauge with cesium-137 and americium-241 sources was damaged while in use. Specifically, the rod with the Cs-137 source was damaged during a field measurement. However, the licensee was able to pull the rod back enough to get the nuclear gauge in the DOT ship container. Per CPN specs, the source is an industrial type 10 millicurie Cs-137 source with double encapsulation. "Cause of the Event: A truck owned and operated by GA Covey Engineering drifted back over a CPN moisture density gauge bending one of the probe rods, leaving the Cs-137 source extended. "Actions: The gauge was inspected by the company's regional RSO. It was determined that the source was still contained within the probe rod and managed to fit it back into the shipping container and secure it in the company truck. The licensee secured the area around the truck until a confirmatory survey was performed by PA DEP Emergency Response staff. The gauge was then brought to a secure site in PA for storage. The licensee will work with CPN to have the nuclear gauge repaired." PA Event: PA110015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-07-13
47033 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-07-07 13:40 | 2011-07-07 14:50 | 2011-07-07 | LOSS OF POWER TO 10 EMERGENCY SIRENS "Power has been removed from 10 (out of 101) sirens due to flooding conditions. [Three] out of 5 sirens in Pottawattamie county, 4 of 18 in Harrison county and 3 of 78 in Washington county. There are compensatory measures in place to ensure notification to any members of the public that may still be in these areas. The station is also suspending testing and reporting (performance indicator) data for these sirens in accordance with NEI 99-02. All of these sirens serve areas for which there are no residents requiring evacuation. This is being reported per 10CFR50.72(b)(3)(xiii)) for 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or communications capability'." The licensee notified the States of Nebraska and Iowa, the Counties of Harrison, Washington and Pottawattamie and the NRC Resident Inspector of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-07
47032 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-07 09:00 | 2011-07-07 11:11 | 2011-07-07 | EMERGENCY SIREN OUTAGE "At 0900 EDT, the Shift Manager was notified that all off site notification sirens were discovered inoperable during the daily maintenance checks due to a loss of power supply. Upon discovery by the technicians of the loss of power supply, the backup power supply was energized and all sirens were tested and returned to operable status. "The time of power loss is unknown at this time and the reason for the failure of the transfer to the backup power supply appears to be a bad solder joint. "The backup power supply has been verified SAT." The sirens were last tested satisfactorily on Tuesday, 7/5/11. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-07
47031 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-07-06 14:40 | 2011-07-06 21:47 | 2011-07-06 | TECHNICAL SUPPORT CENTER (TSC) HVAC OUT OF SERVICE DUE TO LOSS OF POWER "At about 1440 EDT on July 6, 2011, the Technical Support Center (TSC) HVAC lost power during motor control switch testing. The transfer switch did not fully engage resulting in loss of power to the TSC HVAC fan motor. Troubleshooting was performed and power was restored to the TSC HVAC system at approximately 1625 EDT. "This involved an emergent loss of the TSC capability that could not be readily remediated in less than the TSC staffing time of one hour. "Unrelated to the first event, 13.2 KV power to the TMI station office buildings was lost at approximately 1740 EDT on July 6, 2011 due to a broken electric service pole. This resulted in another loss of the TSC HVAC that could not be readily remediated. At 2115 EDT power was restored and the ventilation was started. This event resulted in another reportable condition. "These events affected the ability of the TSC ventilation to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities were unaffected by this emergent condition. Existing procedures provide direction to relocate TSC personnel in the event of a TSC habitability concern, however the backup facility does not have standby electrical power or a filtered ventilation system." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-06
47030 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2011-07-06 14:10 | 2011-07-06 19:23 | 2011-07-06 | CONTROL ROOM EMERGENCY VENTILATION AC SYSTEM INOPERABLE "On July 6, 2011 at 1410, the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable due to unsatisfactory performance, high vibration condition of the air conditioning compressor. As a result, Technical Specification 3.7.5 condition A was entered. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-07-06
47029 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-06-27 | 2011-07-06 17:18 | 2011-07-06 | AGREEMENT STATE REPORT - IRIDIUM SOURCE DISCONNECTED FROM RADIOGRAPHY CAMERA The following information was received from the State of Texas via e-mail: "On July 6, 2011, the Agency [Texas Department of Health] received a written report from the licensee's Radiation Safety Officer (RSO) that on June 27, 2011, there was a source disconnection at a temporary field site [Dralco, Inc] in Weatherford, Texas. Upon discovering the disconnection, the radiographers roped off the area at the 2 millirem/hour boundary and notified the RSO. "The RSO arrived on site and confirmed that the source was disconnected. The RSO performed the retrieval by removing the source tube from the camera, shaking the source out of the source tube and placing a lead shield and shot bag(s) over the source with the pigtail exposed. He reconnected the drive cable and the source was cranked back into the camera. The camera was disconnected so that the drive cable and the pigtail connectors could be inspected. No damage was noted and the camera was immediately returned to service. "The RSO stayed on site approximately one hour to make sure there were no more issues. The RSO stated that the radiographers had failed to connect the pigtail to the drive cable before cranking out the source. The RSO received a dose of 52 mrem. Corrective action includes the event being discussed at the next safety meeting, the radiographers (who were trainers) were instructed to pay attention to safety and the process of connecting the drive cable to the source." Camera: Amersham Model 660B, SN: 4894 Source: QSA Global Model A424-9, SN: 69176B, Iridium-192, 22 curies Texas Incident #: I-8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-07-11
47028 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-06-30 | 2011-07-06 16:47 | 2011-07-06 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED DOSE The following information was received from the State of Wisconsin via fax: "Wisconsin Department of Health Service (DHS) received notification by voicemail from the licensee on July 5, 2011 about an incident that occurred on June 30, 2011. A patient was to receive 25.6 mCi of Samarium-153 (Sm-153) for bone pain; but the patient received 14.8 mCi (58%) of the planned dose. During administration of the Sm-153 to the patient, the staff used a three-way stopcock connected to the IV line. The syringe containing the radioactive material was connected to the stopcock. During the procedure the syringe was mistakenly removed from the stopcock and a few drops of the radioactive materials dripped on the absorbent pad before a member of the staff reconnected the syringe. The event was reported to the RSO within minutes, and a voicemail was left with DHS the following day (July 1, 2011). The patient was notified the same day. "On July 6, 2011, DHS inspectors conducted a reactive inspection. The licensee is instituting corrective actions. The corrective actions are as follows: 1) Conduct a dry run before administration of doses. 2) Use syringe shields previously used by the hospital, which fits syringes better. 3) Inform the nuclear pharmacy to add saline to the radioactive materials, which serves two purposes; first, decrease the radioactive material per volume of total material in the syringe so that administrations to the patient contain small amounts of radioactive materials, and second, if there is a spill, there will be only a small quantity of radioactive material in the spill. The licensee will send DHS an official report of the incident within 15 working days." WI Event #: WI110008 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-07-12
47027 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-07-06 09:03 | 2011-07-06 09:42 | 2011-07-06 | OPERATIONS SUPPORT CENTER OUT OF SERVICE DUE TO HVAC MAINTENANCE "Planned preventive maintenance activities are being performed today (July 6, 2011) on the Hatch Nuclear Plant's HP [Health Physics] / Chemistry area emergency air handling unit. The HP / Chemistry area emergency HVAC is required for functionality of the Operations Support Center (OSC), as this area may be utilized during declared emergencies. These planned work activities are to be completed today within (6) hours. During the time these activities are being performed, the HP office emergency HVAC will not be available for operation and will be rendered non-functional during the performance of the work activities. "If an emergency condition requiring activation of the OSC occurs during the time these work activities are being performed, then contingency plans call for continued utilization of the HP / Chemistry areas as long as radiological conditions allow. Habitability surveys will be performed more frequently in the areas while they are being utilized. If required, respiratory protection equipment will be utilized, as appropriate, for emergency responders utilizing this area until such time as the HP / Chemistry emergency HVAC to be returned to service. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 2, since this work activity affects an emergency response facility for the duration of the evolutions." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-06
47026 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2011-07-05 17:14 | 2011-07-06 09:10 | 2011-07-06 | SUPERVISORY EMPLOYEE TESTED POSITIVE FOR ALCOHOL A non-licensed employee supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's unescorted access has been terminated. Contact the NRC Headquarters Operations Officer for additional details. The plant is currently defueled and not in refueling mode. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2011-07-06
47025 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-07-06 04:00 | 2011-07-06 03:14 | 2011-07-07 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0400 EDT on Wednesday, July 6, 2011, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1600 EDT on Wednesday, July 6, 2011. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM DEAN BRUCK TO PETE SNYDER ON 7/7/11 AT 1056 EDT * * * "The TSC ventilation system maintenance was completed satisfactorily and the system restored to service at 1500 EDT on 7/6/11." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-07-06
47024 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-07-05 18:15 | 2011-07-05 20:35 | 2011-07-05 | TWO APPENDIX R WIRING ISSUES THAT COULD POTENTIALLY AFFECT THE ABILITY TO SHUTDOWN "On July 5, 2011, at 1815 hours, it was determined that a design deficiency at the Perry Nuclear Power Plant (PNPP) constituted a fire protection program concern which could adversely affect the ability to achieve and maintain safe shutdown of the plant in the event of a control room fire. (Reference event notification numbers 46811 and 46997). In the event of a postulated control room fire, the potential exists that two 4160 VAC breakers could trip open under a hot-short condition. "PNPP's Appendix R design vulnerability only affects Breakers EH1106, which supplies the Emergency Service Water Pump A and EH1107, which supplies the Control Complex Chiller A. Specifically, the current transformers used in these breakers for the 50/51 instantaneous and time over current protective relays are in line with the component control room ammeters. Therefore, a hot-short-to-ground in the associated control room ammeters could actuate the 50/51 relays and trip the component breaker. "Actions are in progress to isolate the control room ammeters for the Emergency Service Water Pump A in breaker EH1106 and the Control Complex Chiller A in breaker EH1107. Isolating these ammeters would isolate the affected circuitry from the described Appendix R failure mechanism. Control room amperage indication for the pump and chiller would be lost while this Temporary Modification is installed. PNPP will pursue a permanent resolution to the hot-short-to-ground fault for the EH1106 and EH1107 breakers. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B), as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. A follow-up licensee event report will be made in 60 days. The resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-07-05
47023 | 0 | NAVAL UNDERSEAS WARFARE CENTER |  |  |  |  | 2011-06-30 15:00 | 2011-07-05 12:12 | 2011-07-05 | IONIZING AIR NOZZLES LOST DURING TRANSPORTATION ACCIDENT On May 26, 2011 a transportation truck was involved in an accident in Ashland, NE. The truck was carrying 62 Ionizing Air Nozzles to NRD LLC in Grand Island, NY. The nozzles contained 10 mCi/each of Po-210 at the time of manufacture. At the time of shipment, a total activity of 74.9 mCi aggregate remained. After the accident, a contractor separated out the debris to damaged and undamaged packages. The damaged packages were sent to the landfill in Lancaster County, NE. After the remaining undamaged shipping containers were resorted, however, the shipping company could not locate the static eliminators. The licensee believes that the package containing the air nozzles were sent to the landfill. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-07-05
47022 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-06-04 15:17 | 2011-07-05 09:28 | 2011-07-05 | INVALID SPECIFIED SYSTEM ACTUATION CAUSED ALL 4 EMERGENCY DIESEL GENERATORS TO START "This report is a 60-day telephone notification in lieu of a written licensee event report being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1). The event was an invalid actuation of all four Emergency Diesel Generators (EDGs). At the time of the event Unit 1 was at 100% power and Unit 2 was in a refueling outage with the core offloaded. "At 1517 EDT on 6/4/2011, breaker 212 on Vital Battery Board III was opened under a work order in preparation for breaker maintenance. The opening of this breaker started the 2A-A EDG by removing the control power to the 2A-A EDG emergency start relays. In addition, the loss of control power to 2A-A EDG remote control circuit actuated a relay in the common emergency start circuit, which caused the other three EDGs to start. The 2A-A EDG was declared inoperable until it's control power was restored approximately 30 minutes after starting, requiring an unplanned entry for Unit 1 into Technical Specification Limiting Condition for Operation 3.8.1.1 action b. The impact on EDG control power was not foreseen when planning the breaker maintenance, so it was not expected that any EDGs would start. "Both trains of the Unit 1 and 2 EDGs received a complete train actuation, started and functioned successfully. The EDGs ran unloaded. Actual plant conditions did not exist that required an automatic start of the EDGs. Therefore, this actuation was invalid." The 4 EDGs were not loaded and were returned to normal stand-by alignment. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-07-05
47021 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-07-04 13:36 | 2011-07-04 17:21 | 2011-07-04 | OFFSITE NOTIFICATION DUE TO SPURIOUS SIREN ACTIVATION "TVA received notification from Tennessee Emergency Management Agency (TEMA) at 1336 Eastern Daylight Saving Time (EDT) that Rhea County 911 operators had received several calls (approximately 6) regarding a siren sounding in north Rhea County. "An electronic poll of the siren closest to the location of the reporting parties (Siren 43) indicated no response, although that siren did successfully respond to the 0700 daily poll on 7/4/2011. This may indicate that this siren is not operable. "A severe thunderstorm warning had been issued by the National Weather Service for the time period this potential activation was reported. During this period there were several spurious acoustic monitor alarms from three additional sirens, although there were no other indications of siren activations (e.g., rotate or timer signals). "A field investigation has been initiated, and the siren will be repaired as needed in accordance with TVA's corrective action program. "There was no plant event that required siren actuation, and all plant systems are operating as required." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-07-04
47020 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2008-12-01 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - MISPLACEMENT OF THREE POLONIUM-210 SOURCES The following information was received via fax: "On 12/9/2008, the RSO reported that a recent source inventory showed three [Po-210 Static Eliminators] missing from their last known use location. Calculations estimate that they contain less than 10 micro Curies of Po-210 each. Efforts to locate the missing units are continuing. Training is being conducted to prevent recurrence. "On 3/22/2010 the RSO reported that the three missing Po-210 static eliminators were located in July 2009. No reward offered. No press release issued. Incident Closed" New York Event: NY-11-21 New York Incident: 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47019 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2006-05-01 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - LOSS OF TRITIUM AND CARBON-14 SOURCES The following report was received via fax: "The licensee submitted a written report June 11, 2008 documenting the loss of 31 mCi of tritium and 0.6 mCi of carbon-14 which had been discovered missing in May 2008. "In September 2004, an incoming scientist brought the materials with him to Wadsworth. Since he was not an authorized. user, the RSO placed the material in a freezer in the chemical storage room. In May 2008 the RSO discovered the materials missing and initiated a thorough investigation. Unfortunately the disposition of the materials remains unknown. "The RSO has implemented corrective actions which include; better inventory practices, increased vigilance over materials in long term storage with an eye towards proper disposal, and no 'general' storage of materials. No reward offered. No press release issued. Incident Closed" New York Event: NY-11-20 New York Incident: 619 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47018 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2008-06-03 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - DISCARDED SOURCE The following report was received via fax: "06/11/08 the RSO [Radiation Safety Officer] called to report the inadvertent disposal of a Beckman Liquid Scintillation Counter instrument with the 30 micro-curie source still in place. He was not consulted in March 2008 when the Beckman was removed by a commercial waste hauler. The waste hauler was called to determine the disposition of this instrument. "On 07/07/08 the report was received from the RSO. The RSO reported that at this time (several months after pick-up) the waste contractor was unable to provide any information on the whereabouts of this instrument. No reward was offered. No press release was issued. Incident Closed." New York Event: NY-11-19 New York Incident: 617 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47017 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2011-07-01 15:52 | 2011-07-01 18:07 | 2011-07-01 | UNIT 1 MANUAL TRIP DUE TO ELECTRO-HYDRAULIC CONTROL FLUID LEAK ON TURBINE STOP VALVE "With Unit 1 at 100% power Unit 1 was manually tripped at 1552. The manual reactor trip was in response to the right main turbine stop valve failing closed as the result of an electro-hydraulic oil leak located at the stop valve. Procedure 1E-0 'Reactor Trip or Safety Injection' was completed at 1600. No SI [safety injection] required. 1ES-0.l 'Reactor Trip Recovery' is in progress. Offsite power remains on all safeguards buses for both units. 11 and 12 AFW pumps auto started on SG [steam generator] low level and are supplying Unit 1 Steam Generators. After the trip, power was lost to non-safety related 4160 VAC buses 11 and 14 as expected due to the electrical lineup. The loss of power to 4160 VAC bus 11 upon the reactor trip resulted in a loss of power to 11 RCP. 12 RCP continues to operate on offsite power. Unit 2 remains at 100% power/Mode 1. Reportable actuations are: Unit 1 reactor protection (scram), and Unit 1 AFW pumps auto start. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-07-01
47016 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2008-01-01 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - TWO STATIC ELIMINATORS DISCARDED The following report was received via fax: "Two static eliminators were thrown out during relocation of the process line to another building. NRD [The static eliminator vendor] has been notified in case units are recovered at the landfill. No press release issued. No reward offered." New York Event: NY-11-18 New York Incident: 579 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47015 | 0 | AUTOMATIC VALVE CORPORATION |  |  |  |  | 2011-06-28 07:00 | 2011-07-01 15:56 | 2011-07-01 | SEAL FAILURE AND LEAKAGE ASSOCIATED WITH MODEL B5497-301 VALVES The following was received via fax: Automatic Valve Corporation made this report based upon its investigation and engineering evaluation of valve serial number 57056 which was leaking following an outage stroke test at McGuire Station. Automatic Valve Corporation determined that the cause of the leakage was seal failure as a result of the seal being displaced from its retaining groove. The displaced seal became trapped between the poppet face and valve seat inside the valve body. Automatic Valve Corporation reported that seal replacement combined with inspection and testing would prevent additional failures. Shearon Harris and McGuire utilize these types of valves. Automatic Valve Corporation has no reported failures of these valves at Shearon Harris. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | OTH | PAR | 21.21 |  |  |  | 0 | 2011-07-01
47014 | 0 | PORTSMOUTH LEAD CASCADE |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-06-11 | 2011-07-01 16:34 | 2011-07-01 | POWER OUTAGE CAUSING LOSS OF BATTERY ROOM VENTILLATION AND HYDROGEN MONITOR "At approximately 1451 hours EDT on 07/1/2011, the Nuclear Regulatory Affairs Manager completed his review of the initial (draft) engineering report [related to an event that occurred on June 11, 2011].. [The review determined] the impact the June 11, 2011 power outage may have had on the Battery Room 3/4 forced air ventilation and hydrogen monitoring systems. [The review also] determined the incident should be reported to the NRC because he could find no evidence that either system would have met their respective IROFS [Item Relied On for Safety] surveillance requirements during the power outage. "This incident is being reported to the Nuclear Regulatory Commission (NRC) as a 24-hour event in accordance with American Centrifuge Administrative Procedure ACD2-RG-044 (Nuclear Regulatory Event Reporting), Appendix B, Section I, which states: 'An event in which equipment is disabled or fails to function as designed as described by any of the following: (Paragraph) 2. The equipment is required to be available and operable when it is disabled or fails to function: AND no redundant equipment is available and operable to perform the required safety function .'" The licensee will notify the NRC Region II office and site Department of Energy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2011-07-01
47013 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-11-09 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - P-32 SOURCE LOST The following information was received via fax: "351 microcuries of P-32 was lost (on 11/9/07). The isotope was checked in, delivered and signed for at the research lab on 11/9/07. When lab personnel went to use the isotope, they could not locate it. Radiation safety staff searched dumpsters, garbage cans, and the lab, but could not locate the vial of P-32. It is possible it was put out as garbage by mistake. The RSO contacted the garbage removal contractor. "Written report received on 11/16/07. Although the licensee could not determine the precise circumstances that caused the source to be lost, the corrective action appears to be adequate. No press release was issued. No reward offered. The incident will be reviewed during the next routine inspection. Incident closed." New York Event: NY-11-17 New York Incident: 575 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47012 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-10-29 | 2011-07-01 13:15 | 2011-07-01 | AGREEMENT STATE REPORT - RADIUM-226 FOUND IN DEMOLITION DEBRIS The following information was received via fax: "On 10/29/07, the portal monitor at Nucor Steel alarmed from a load originating at Eastman Kodak. The load contained structural demolition debris. An Exploranium GR-135 identified the source as Radium-226 with a max reading of 210 uR/hr. Eastman Kodak has been notified for follow-up." New York Event: NY-11-16 New York Incident: 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47011 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2008-02-18 | 2011-07-01 14:13 | 2011-07-01 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION DURING PROSTATE THERAPY The state found three cases of prostate seed (Pd-103) medical misadministration during an inspection on 1/14/2011. These cases are related to one doctor. 2/18/2008: 100 Gy prescribed, 70.24 Gy administered 4/8/2008: 125 Gy prescribed, 71.6 Gy administered 3/17/2009: 100 Gy prescribed, 160.8 Gy administered The physician was notified of the misadministration however the patients were not notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-07-07
47010 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-06-27 13:44 | 2011-07-01 15:06 | 2011-07-01 | OFFSITE POWER SOURCES DECLARED INOPERABLE "At 1344 CDT on June 27, 2011, off-site A.C. power sources to Unit 2 were declared inoperable as a result of Transformer 2RY lockout and less than the required minimum voltage on the transmission system. "At 1310 CDT on June 27, 2011, Transformer 2RY was locked out. The Transformer 2RY lockout resulted in entering Technical Specification 3.8.1, Condition A and a single path to the transmission system. At 1344 CDT, the site was notified by transmission systems operations that the 345 KV grid voltage could not be maintained at the minimum voltage required per procedure C20.3. The path to the transmission system was declared inoperable and Unit 2 entered Technical Specification 3.8.1, Condition C. Although inoperable, transmission system sources remained connected to Unit 2; emergency diesel generators were available but not required to run. "By securing a cooling tower pump and fans, the required minimum transmission system voltage was met and determined to be sustainable. Technical Specification 3.8.1, Condition C, was exited on June 28, 2011 at 0038 CDT. "After additional analysis, it was determined that this condition was a safety system function failure for Unit 2 and reportable under 10 CFR 50.72(b)(3(v)(D). This condition should have been reported on June 27, 2011 under the eight-hour reporting criteria. "The NRC Resident Inspector has been informed." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-07-01
47009 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2006-11-30 | 2011-07-01 13:19 | 2011-07-01 | AGREEMENT STATE REPORT - ELECTRON CAPTURE DEVICE DISCARDED The following report was received via fax: "On February 07, 2007 the RSO called to report a missing ECD [Electron Capture Device] detector. Apparently the entire GC [Gas Chromatograph] was discarded as obsolete equipment in the November / December 2006 timeframe. The RSO is looking into the disposition which he believes was a dumpster / roll-off that went to the Port of Albany. Fortunately Ni-63 has a low health and safety risk compared to other common isotopes. The date of occurrence has been estimated as 11/30/2006. The date of discovery is 01/31/2007. "No press release issued. No reward offered. Better training and inventory instituted as corrective action. Actions evaluated during next routine inspection. Incident closed." New York Event: NY-11-12 New York Incident: 504 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47008 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-10-25 | 2011-07-01 11:19 | 2011-07-01 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION DURING GAMMA KNIFE THERAPY The following report was received via fax: "On 10/25/2007, [the New York State Department of Health] received a call from a radiation oncology manager to report a therapy misadministration involving a gamma knife due to a machine malfunction, couch failure. The physicist and the neurosurgeon had to go in and manually pull the couch out. The physicist's badge was read on an emergency basis and showed DDE of 1 mRem and SDE of 2 mRem. The neurosurgeon did not have his badge on when he went in. The facility has treated about 125 patients in 4 years with the gamma knife unit, according to field notes from the inspection done in February 2007 and is close to the 5 year service requirement. The facility had planned to treat 10 lesions in the brain but stopped after 3 lesions were treated due to couch failure. The rest of the lesions were not treated with radiation. The patient had already received whole brain irradiation and received additional chemotherapy after the gamma knife procedure. "Service performed: couch repaired. Policy & Procedure regarding film badge use reviewed during next routine inspection. This event is closed." New York Event: NY-11-15 New York Incident: 570 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-07
47007 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-06-02 09:00 | 2011-07-01 13:32 | 2011-07-01 | AGREEMENT STATE REPORT - FAILED HANDLE ON BERTHOLD PROCESS GAUGE The following information was received from the state via e-mail: "Newmont Mining Corporation had a Berthold source, Model LB-7440, SN: 298, CS-137, 20mCi, with a handle that was found broken when doing the six month checks on 6/2/11. Currently arrangements have been made for the manufacturer, Berthold, to come onto the property to remove the old shield and put a new shield onto the source listed above. The date for repair [was scheduled for] 6/22/11. The manufacturer is scheduled to visit the facility and carry out the repair." Item Number: NV110018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47006 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-06-05 | 2011-07-01 11:19 | 2011-07-01 | AGREEMENT STATE REPORT - RECOVERY OF STOLEN MOISTURE DENSITY GAUGE The following report was received from the state via fax: "On 6/5/07, the NRC [Nuclear Regulatory Commission] called to report a Troxler gauge for sale on E-Bay. The gauge was listed as a Troxler 4640-B which contains a source of up to 9 mCi Cs-137. The seller listed the item as being in NY so the NRC contacted NYS DOH [New York State Department of Health]. After reviewing the item description it appeared to match an item that had been reported as stolen. E-Bay was notified as well as the NYPD. The item was delisted from the auction site and the seller was contacted by the NYPD to recover the device. "The gauge for sale was determined to be one reported stolen from a licensee on 6/9/03. The gauge was recovered on 6/5/07 from a garage in Valley Stream, NY by NYPD with assistance from Nassau Co. PD and FBI. The licensee took possession of gauge on 6/6/07 from NYPD. The gauge [was] sent for maintenance and inspection prior to [being] returning to service. The NRC was notified." New York Report: NY-11-14 New York Incident: 544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47005 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2009-12-09 | 2011-07-01 12:57 | 2011-07-01 | AGREEMENT STATE REPORT - MEDICAL EVENT - RADIOPHARAMACEUTICAL ADMINISTERED TO WRONG PATIENT The following information was received via e-mail: "On Wednesday, December 9, 2009, an 8 mCi dose of Tc-99m Sestamibi was administered via IV injection to an incorrect patient. The patient receiving the misinjection did not have a written order for the procedure in their medical chart. The event was reported to the RCP (Radiation Control Program) by telephone on Thursday December 10, 2009, as required in NRC 35.3045, 'Report and Notification of a Medical Event.' "The misinjection was a result of the technologist failing to follow established written policy and procedure of verifying the patient I.D. with three identifiers: Name (patient spelling last name), DOB (verbalized by patient) and UMC Account Number and not using an interpreter as directed by policy. This procedure of patient identification has been established as a barrier to prevent such a situation from occurring. Failure to follow procedure is in direct violation of hospital policy and resulted in disciplinary action. "The patient was immediately notified of the event. No adverse effect of the injection has been foreseen considering the activity of the radiopharmaceutical administered. The physician of the patient was also notified of the misinjection by telephone. "The RSO has been notified of the misinjection and the details of the incident have been entered into the minutes of the radiation safety committee meeting for this quarter on December 10, 2009. "This event is closed. "Item Number: NV090001." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2011-07-07
47004 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2001-08-03 | 2011-07-01 11:19 | 2011-07-01 | AGREEMENT STATE REPORT - LOST POLONIUM-210 STATIC ELIMINATORS The following information was received from the State of NY Bureau of Environmental Radiation Protection via fax: "The state received notification 03/06/2007 that static eliminators were lost sometime around 8/3/2001. SMSC [Standard Microsystems] suspects that they were inadvertently shipped to Delta Design because they were placed inside Delta Flex Handlers and were not visible from the outside. Delta Design presumes that the sources were scrapped sometime after 2001. The activity of the Polonium-210 at that time was less than 45 microcuries. "The written report from SMSC indicates that 5 NRD static eliminators, model P-2042, s/n SP101713 thru SP101717, each containing 5 milliCuries on 3/9/1998 were disposed. Decay corrected activity of each foil is less than 1 nanocurie. No further action is warranted." New York Incident: 519 New York Event: NY-11-13 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-07-06
47003 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-01 02:44 | 2011-06-30 21:03 | 2011-06-30 | INVALID RPS (SCRAM) ACTUATION "This 60-day telephone notification is being made under the reporting requirements specified by 10 CFR 50.13(a)(2)(iv) and 10 CFR 50.73(a)(I) to describe an invalid RPS (Scram) actuation. "On May 1, 2011, at 0244 hours Central Daylight Time (CDT), during a non-refueling outage, Browns Ferry Unit 2 was at 000 percent power in Mode 4 with all control rods already inserted into the core when an invalid full scram signal was received. "The reactor scram signal was determined to be the result of a failure of the Unit 2 Unit Preferred Motor-Motor-Generator Set, which caused an electrical transient and resulted in noise In adjacent nuclear instrumentation cables. "The scram signal was Initiated due to Invalid Indications (spikes) associated with the C and D Intermediate Range Monitors (IRMs). The spikes did not render the IRMs inoperable as these were momentary spikes. Therefore, the actuation was invalid. "The scram was reset at 0312 CDT. "This event was entered In the Corrective Action Program as Service Request (SR) 362127, which generated Problem Evaluation Report (PER) 362897. "There were no safety consequences or impact on the health and safety of the public as a result of these events. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-06-30
47002 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-06-30 14:25 | 2011-06-30 19:49 | 2011-06-30 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTUATION "On June 30th, 2011 at 1425 PDT, a public evacuation siren was inadvertently activated for ~ 40 seconds. Preventative maintenance was being performed on the siren at the time of actuation. "The licensee has notified Benton County, Franklin County, and the Department of Energy. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-30
47001 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-30 14:23 | 2011-06-30 16:37 | 2011-06-30 | OFFSITE NOTIFICATION DUE TO PERSON BEING EVACUATED "At 1423 CDT, the Control Room was notified of a fire inside the protected area isolated to a portable water evacuation pump. At 1425 CDT, the Control Room was notified the fire was extinguished and the presence of an injured person; the Control Room immediately notified Washington County 911 to request emergency medical assistance. At 1511 CDT, injured person was transferred off-site by medical helicopter. "This four-hour notification is being made pursuant to 10 CFR 50.72(b)(2)(xi), event or situation related to health and safety of on-site personnel for which notification to other government agencies has been made. NRC Resident informed. "Due to this event, 1/2 gallon of gasoline was discharged to the Missouri River. The spill was reported to the State of Nebraska on 6/30/2011. "This condition is also being reported pursuant to 10 CFR 50.72(b)(2)(xi) for News Release or Notification of Other Government Agency. Applicable state agencies have been notified per plant procedures." The injured person is a plant employee and was injured while refueling a portable generator. The injured person suffered burns to the forearms and neck. The licensee intends to issue a press release. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-30
47000 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-06-30 12:40 | 2011-06-30 13:39 | 2011-06-30 | TROXLER MODEL 3400 MOISTURE DENSITY GAUGE WAS DAMAGED AT A CONSTRUCTION SITE The following was provided by the State of North Carolina via e-mail: "A Troxler portable nuclear gauge belonging to Kam Engineering Services was run over by a smooth drum roller and has been damaged. "The event occurred near the intersection of Normandy Street and Half Street in Fort Bragg, NC. Fort Bragg is under a NRC license and the licensee should be working under reciprocity. "The licensee does not possess any survey instruments but they have an agreement to borrow one from Troxler (RTP, NC.) Someone has been dispatched to Troxler to get a meter and to take it back to the accident site. "The RSO is on-site and has cordoned off a 20 foot circle around the gauge." The licensee will notify the State of North Carolina when additional survey results are available. The gauge contained 9 milliCuries Cs-137 and 44 milliCuries of Am-241. ** * * UPDATE FROM HENRY BARNES TO JOE O'HARA VIA E-MAIL AT 1703 ON 6/30/11 * * * "The RSO called [the state]. The area was surveyed and the dose rate at the 20 ft boundary was 0.02 - 0.04 mR/hr. The RSO worked his way toward the damaged gauge and the readings remained constant. At 1 meter, the reading was still 0.2 mR/hr (Transport Index) On contact, the gauge was about 7 mR/hr. The RSO repositioned the gauge and sent pictures to Troxler. Troxler said it appeared that the tungsten blocks were still in place and there was no damage to the source shielding. The RSO (per Troxler instructions) then placed the gauge in the transport box and locked it. "The damaged gauge is being transported to the company office tonight and will be transported to Troxler tomorrow." Notified R1DO(Welling) and FSME(Jackson) Incident NC 11-35. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-07-05
46999 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-06-30 05:16 | 2011-06-30 12:08 | 2011-06-30 | POWER RANGE MONITOR CHANNELS OUT OF ALIGNMENT "At 0516 [CDT] on 6/30/11 after control rod movements to support rod pattern adjustment, 3 of 4 APRMs were out of required Technical Specification deviations of +/-2% power in relation to calculated Core Thermal Power. APRM #1 was at -3.6% deviation, APRM #3 was at +2.5% and APRM #4 was at +3.1 %. APRMs 1, 3, and 4 were declared inoperable. With 3 of the 4 APRM channels affected, the functions of the APRM were inoperable and that RPS trip capability had not been maintained. Technical Specification Conditions 3.3.1.1.A and 3.3.1.1.C were entered at 0516. All three (3) APRM gains were adjusted and the Tech Spec Conditions were exited at 0540 [CDT]. "Thermal Limits were evaluated and no limits were challenged. "This event is reportable under 10CFR50.72 (b)(3)(v) as an event that could have prevented the fulfillment of the safety function of a system needed to: 50.72(b)(3)(A) shutdown the reactor and 50.72(b)(3)(D) mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 80 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-06-30
46998 | 0 | WESTERN SD COMMUNITY ACTION AGENCY |  |  |  |  | 2011-06-30 07:55 | 2011-06-30 11:44 | 2011-06-30 | STOLEN NUCLEAR GAUGE CONTAINING 40 MILLICURIES CADMIUM 109 The gauge was stolen from a locked company truck along with other tools parked at the place of business sometime between 1800 on 6/29/11 and 0755 on 6/30/11. The device is a Niton machine built by Thermo-Fisher Scientific XRF Model 300 S/N U2349 used for measuring the quantity of lead in lead based paint. The source serial number is NR-1176 and contains 40 milliCuries of Cd-109. This is generally licensed material. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-06-30
46997 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-06-27 16:11 | 2011-06-29 09:49 | 2011-06-30 | APPENDIX R ANALYSES FAILS TO RECOGNIZE HOT-SHORT FAILURE RESULTING IN THE LOSS OF AN ESSENTIAL ELECTRICAL BUS The following Part 21 report was received via fax: "10 CFR 21: Appendix R analyses conducted for Virgil C. Summer Nuclear Station (VCSNS) failed to identify that a fire-induced hot-short failure in an ammeter circuit would result in a loss of the B-train 7.2KV essential electrical bus (XSW1DB). "Appendix R analyses performed by Gilbert/Commonwealth (now Worley Parsons) in the early 1980s failed to recognize the possibility of a fire-induced hot-short condition in a circuit that was identified as being required for safe shutdown. This circuit connects a set of sensing current transformers (CTs) to an ammeter on the Main Control Board, and provides over-current sensing for an over-current relay. Gilbert/Commonwealth recognized that a fire-induced open circuit in this ammeter circuit would result in damage to, or a fire in, the B-train 7.2kV essential switchgear. Thyrite protectors were added to the circuit to protect the CTs from this open circuit condition as part of the Appendix R analysis. "However, this analysis and resolution failed to consider the hot-short-to-ground failure mode. Current from a hot-short could flow through the ammeters, or neutral conductor, and then through the bus neutral over-current relay to ground. This could actuate the over-current relay, which in turn would actuate a lock-out relay and trip all incoming breakers to bus XSW1DB. This bus provides credited B-train power to safe-shutdown components credited for this scenario. The Appendix R analyses conducted for VCSNS by Gilbert/Commonwealth did not address the hot-short scenario and is considered to be a defect, or omission. reportable under 10 CFR 21. "This condition was identified during the circuit analysis review for transitioning the Appendix R Fire Protection Program to NFPA 805 and was reported to the NRC as an unanalyzed condition on 05/03/2011 (see Event Notification No. 46811). Corrective actions have been taken to address this issue." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM JOE MARSDEN TO MARK ABRAMOVITZ ON 6/30/2011 AT 1643 * * * "Worley Parsons Investigation Results: "Although this design was not a generic or standard design, Worley Parsons performed further evaluation, including extent of condition, for other Nuclear Power Plants that Worley Parsons performed the original design and performed Appendix R Compliance Review/Modifications. Five plants were identified as follows: "1) Crystal River 3: Worley Parsons discussed the issue with Progress Energy and jointly concluded that Crystal River 3 is not impacted because their corresponding current transformer circuit design has a different configuration. The circuit design is not generic or programmatic. "2) TMI Unit 1: TMI is not impacted because their corresponding current transformer circuit design has a different configuration. The circuit design is not generic or programmatic. "3) Perry: The Appendix R Compliance Review was accomplished by a team of Worley Parsons and others. Since Worley Parsons was involved with the Appendix R analysis and the affected electrical drawings are not readily available at Worley Parsons, it was concluded that Worley Parsons could not complete the evaluation to determine if the Perry design condition could cause a substantial safety hazard. Worley Parsons issued letter PNPP-O-CO-011-WCLT-0001 to the Perry Design Engineering Manager, recommending Perry to complete the evaluation pursuant to 10CFR21.21(a). "4) V.C. Summer: V.C. Summer is the subject plant and is impacted. VC. Summer is issuing LER #2011-001-00, which constitutes the Part 21 Notification for this design defect, or omission. "5) R.E. Ginna: Worley Parsons did not perform the Appendix R analysis for Ginna. "Corrective Action: "V.C. Summer has implemented immediate compensatory measures for this condition until a permanent solution is identified. A root cause analysis was jointly performed with V.C. Summer. The root cause analysis and Worley Parsons corrective action program review considered this an isolated incident due to human error. No programmatic/procedure corrective actions were identified due to the historical nature of the issue. "Actions to preclude recurrence: Human performance issues from this event will be communicated to the Worley Parsons Nuclear Engineering staff under our corrective action and lessons learned program." Notified R1DO (Welling), R2DO (Franke), and R3DO (Lipa). Notified the Part 21 Group via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2011-06-29
46996 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-06-28 00:05 | 2011-06-28 23:10 | 2011-07-14 | FAILURE OF #2 FIRE WATER PUMP TO REALIGN "At 0005 CDT, on 06-28-2011, the Plant Shift Superintendent was notified that the C-631 High Pressure Fire Water (HPFW) pumps #2 and #3 automatically started in response to low HPFW header pressure created by a line leak and rendered inoperable. Following isolation of the water leak the #2 and #3 pumps were shut down and were being configured for automatic start. The RCW operator observed the 'Auto Start' Indicator for the #2 pump was not illuminated. The pump was declared inoperable and power was removed from the #2 pump for troubleshooting and repair by electrical maintenance (EM). When power was removed from the pump the HPFWS could not perform its intended safety function of providing 4875 gpm. Two HPFW system pumps are required to be operable according to TSR LCO 2.4.4.8. EM reset a disconnect interlock switch which reenergized the 'Auto Start' controls and the pump was declared operable and returned to service. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident Inspector has been notified of this event." * * * UPDATE FROM KEVIN BEASLEY TO PETE SNYDER AT 1613 EDT 6/29/11 * * * "Due to the uncertain nature of the leak on the 16 inch underground High Pressure Fire Water (HPFW) distribution main, it is not known at this time if the two operable HPFW pumps would have been able to satisfy the maximum sprinkler system demand of 4875 gpm. Upon completion of excavating the area of the leak, Engineering will evaluate the failure mode to determine if system requirements were maintained." The licensee notified the NRC Resident Inspector. Notified R2DO (M. Franke) and NMSS (R. Johnson). * * * RETRACTION FROM CALVIN PITTMAN TO KARL DIEDERICH AT 1423 EDT 07/14/11 * * * "Upon further evaluation it was determined that the (High Pressure Fire Water System) HPFWS was capable of fulfilling its intended safety function at all times during the incident. The safety function of the High Pressure Fire Water System established in SAR 3.15.7.2 is to provide sufficient fire suppression capability for the cascade process buildings to minimize the likelihood of a large fire. Fire scenarios were evaluated to establish the system design basis. A lube oil spill fire on the operating floor resulted in the highest sprinkler flow rate demand of 3200 gpm. A 500 gpm hose stream demand is added to the sprinkler system flow rate to obtain a maximum fire water flow rate of 3700 gpm for the evaluation basis fire event. As stated in the TSR 2.4.4.8 Basis Statement, the requirements for HPFWS operability established in TSR 2.4.4.8 are conservative with respect to the system evaluation presented in SAR 3.15.7.2. TSR SR 2.4.4.8-4 requires an annual flow rate verification of each HPFW pump. The most recent flow rate tests performed in Nov. 2010 demonstrate the capacity of each pump exceeds the evaluation basis flow demands. During the short time where only HPFW pump #3 was operable, this pump could have supplied more than the 3700 gpm required to satisfy the evaluation basis flow demand. The HPFWS remained capable of fulfilling its intended safety function. "In addition, when HPFW pumps #2 and #3 were running in response to the leak on the underground distribution system, system pressure was approximately 134 psig. Using the pump curves established by the annual TSR surveillance test discussed above, this equates to a flow rate of approximately 5900 gpm. Any sprinkler system activation on the HPFWS would drop the system pressure to around 125 psig, slightly lowering the flow rate through the leak. During the time frame the leak was active, the HPFWS remained capable of fulfilling its intended safety function. The combined pump capacity of pumps #2 and #3 (10,600 gpm) demonstrated by the annual surveillance test exceeds the combined demand from the leak (5900 gpm) and the evaluation basis flow requirements (3700 gpm). Therefore, the HPFWS remained operable throughout the incident of the underground piping leak and the following time period of only one pump operable. Thus, reporting per 10 CRF 76.120 was not required and the subject notification can be retracted." The NRC Senior Resident Inspector has been notified of this retraction by the licensee. Notified R2DO (Freeman) and NMSS (Rahimi). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2011-06-28
46995 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-06-28 05:35 | 2011-06-28 07:03 | 2011-06-28 | SAFEGUARDS REPORT The licensee discovered vulnerability in a safeguard system that could have allowed unauthorized or undetected access to a protected area. Compensatory measures have been taken. Contact the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-06-28
46994 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2011-06-26 | 2011-06-27 15:50 | 2011-07-20 | AGREEMENT STATE REPORT - STOLEN PORTABLE MOISTURE DENSITY GAUGE The following was received via fax: "Fairway Testing Co. license no. C2322, called 6/27/11 to report that a Troxler model 3411 s/n 4363 portable density gauge was stolen from a company vehicle on Sunday, June 26. The device contained 8 mCi Cesium 137 and 40 mCi of Americium 241/Beryllium. "The employee worked late on Friday, June 24 and did not have access to the permanent storage location since the building is locked after 5:00 p.m. The driver took the vehicle to his residence on Brookside Drive in Stony Point, Rockland County and parked it in his driveway. The device was in its transport container, which was doubly chained to the bed of the pickup truck. "On Sunday morning, the employee observed that the container was still in the bed of the pickup before he left his residence for the day in a family vehicle. When he came home that night he did not check the vehicle. "On Monday morning, he realized that both chains were cut and the transport box along with the device was stolen. Other items were also stolen from the vehicle which leads to speculation that the perpetrators were not specifically after the density gauge. "The local police were notified and a police report has been initiated. The licensee has thirty days to send a written response and to notify the NYS DOH (New York State Department of Health) of any substantial development in the case." NY State Event #: NY-11-11 * * * * UPDATED AT 1431 EDT ON 7/20/11 BY S. SANDIN * * * * The following update was received from NY DOH via fax: "On 7/5/11, DOH was notified via fax that a load of scrap metal tripped the alarm at Gerdau Ameristeel in Sayreville, NJ. The load was returned to the originator (Teplitz in Nanuet, NY) and then to Orange County Metal recycling (OCMR) in Middletown, NY. OCMR staff identified, isolated and secured the source of the trip and contracted Co-Physics to characterize. In cooperation with DOH, Co-Physics contacted Troxler with model and serial numbers from the item and identified it as the cesium source from the stolen gauge. Fairway Testing and Stony Point Police have been notified. "Fairway Testing is aware of its responsibility for proper disposition of the source. "The Am-Be source is still unaccounted for. A search of Teplitz is underway. "No Reward offered. No Press Release issued." Notified R1DO (Dentel), FSME (White) and Canada via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-30
46993 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-06-24 | 2011-06-27 09:18 | 2011-06-27 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was received from the State of Iowa via email: The Iowa Department of Public Health (IDPH) was conducting a field inspection of Midwest Industrial X-Ray on Friday, June 24, 2011. The licensee was conducting 1 minute, 15 second shots on 12" diameter gas pipeline in a 10 foot deep trench. They were using a SPEC model 150 camera with a 49 Curie Iridium-192 source and SPEC control cables. After completion of the third shot, the licensee was unable to retract the source. The lead radiographer disassembled the control cable crank mechanism and manually pulled the source back into the shielded position. The licensee then reassembled the crank mechanism and attempted a third shot. Once again, they could not retract the source. The radiographer disassembled the crank mechanism, pulled the source into the shielded position and secured from any additional radiography that day. The licensee indicated that they had similar problems with SPEC control cables in the past. The radiographer and assistant radiographer's pocket dosimeters both indicated less than 5 milliRem. The licensee will submit a written report within 30 days." The radiography was being performed in the Redfield Gas Storage facility in Redfield, IA. The event was reported by Midwest Industrial X-ray of Fargo, ND. Iowa Report No.: IA110004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-06-30
46992 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-06-26 18:00 | 2011-06-26 22:08 | 2011-06-26 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF REACTOR COOLANT PUMP "This notification is being made to report that Salem Unit 2 has experienced an automatic reactor trip. The trip was caused by 23 Reactor Coolant (RC) loop low flow and P-8 caused by 23 reactor coolant pump trip. The cause of the 23 Reactor Coolant Pump trip is under post reactor trip investigation. Main Feedwater to the Steam Generators was isolated due to the 'Feed Water Interlock' which is expected on a reactor trip. The Auxiliary Feed Water (AFW) system auto started on low Steam Generator levels. This is also expected on a reactor trip. 21, 22 and 23 AFW pumps all automatically started and fed the Steam Generators. 23 AFW pump has been shutdown by procedure and is available. "The crew entered EOP-TRIP-1, and then transitioned to EOP-TRIP-2 and stabilized the plant at no load conditions. Salem Unit 2 is currently in Mode 3. Reactor Coolant System temperature is 547 degrees F with pressure at 2235 psig NOP/NOT. 21, 22, and 24 Reactor Coolant Pumps are in service. "Decay heat removal is being provided by 21 and 22 AFW pumps via the Main Steam Dump System. All shutdown and control rods fully inserted on the reactor trip. The plant is aligned with normal electrical lineup from offsite power sources. "There were no personnel injuries associated with this event." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-26
46991 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-06-26 16:14 | 2011-06-26 19:39 | 2011-06-26 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 1614 EDT on 6/26/2011, Unit 1 reactor automatically tripped following a turbine trip from greater than 50% rated thermal power (P-9 interlock). "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically actuated as expected on loss of the operating main feedwater pumps. "Initially, the steam dump system functioned as expected (all valves opened). Subsequently, the steam dump system was manually turned off when 3 of the valves did not close when expected. Consequently, decay heat removal is via the Steam Generators' atmospheric relief valves. "No primary or secondary safety valves opened during or after this trip. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators." There is no indications of any primary to secondary leakage. All control and shutdown rods are inserted. The electrical alignment is normal, supplied from off-site power. There was no impact to Unit 2. Unit 2 is operating at 100% power / Mode 1" The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-26
46990 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-06-26 16:09 | 2011-06-26 18:00 | 2011-06-26 | REACTOR MANUAL TRIP DUE TO MAIN FEED PUMP TRIP "6/26/11 at 1609 CDT, the reactor was manually tripped due to the trip of the 'B' Main Feed Pump while operating in Mode 1 at approximately 82% reactor power. The unit was increasing power to 95% after the current refuel outage. The cause of the trip of the 'B' Main Feed Pump is not known at this time. All equipment functioned normally as expected. The investigation into the cause of the 'B' Main Feed Pump trip is ongoing at this time. "Current plant status is Mode 3. The NRC Senior Resident has been contacted." All rods fully inserted upon reactor trip. The unit is stable with Auxiliary Feedwater supplying the Steam Generators. Decay heat is being removed to the Main Condenser via steam dumps. The electrical system is in a normal post-trip alignment. The licensee characterized the reactor trip as uncomplicated. * * * UPDATE FROM MARCY BLOW TO DONALD NORWOOD AT 1923 EDT ON 6/26/2011 * * * "A valid Auxiliary Feed[water] actuation signal [occurred] due to trip of both of the Main Feed pumps from a turbine trip and low steam generator levels. This is reportable under 10CFR50.72 (b)(3)(iv)(A), 8-hour report. All auxiliary feed pumps started and operated as expected." The licensee will notify the NRC Resident Inspector. Notified R4DO (Deese). | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-26
46989 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-26 10:45 | 2011-06-26 12:22 | 2011-06-26 | OFFSITE NOTIFICATION DUE TO PETROLEUM RELEASE TO THE MISSOURI RIVER "At approximately 0125 CDT, the AquaDam providing enhanced flood protection for Fort Calhoun Station Unit 1 failed. This resulted in approximately 100 gallons of petroleum being released into the river after a protective barrier was breached and many fuel containers were washed out to the river. The fuel/oil containers were staged around the facility to supply fuel for pumps which remove water within the flood containment barriers. The spill was reported to the State of Nebraska at 10:45 AM CDT on 6/26/2011. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(xi) for News Release or Notification of Other Government Agency. Applicable governmental agencies have been notified per plant procedures." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-26
46988 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-26 | 2011-06-26 07:58 | 2011-06-26 | BOTH EMERGENCY DIESEL GENERATORS SUPPLYING PLANT EMERGENCY BUSES PER PLANT PROCEDURE "At approximately 0125 [hrs. CDT], the AquaDam providing enhanced flood protection for FCS [Ft. Calhoun Station] Unit 1 failed. At 0221, as a precautionary measure, DG-2 [Diesel Generator] was automatically started per plant procedure to divorce bus 1A4 from offsite power. At 0250, DG-1 was automatically started to divorce bus 1A3. Both Emergency Diesel Generators loaded on buses as designed. 345KV and 161KV offsite power remain available. "This is reportable pursuant to 10CFR50.72(b)(3)(iv)(A), 'System Actuation of the Emergency Diesel Generators'. All safety related flood protection barriers remain in place. "Current river level is 1006.5' MSL and stable. FCS remains in a NOUE [Notification of Unusual Event] due to high river level. "NRC personnel stationed onsite for flood monitoring have been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-06-26
46987 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2011-06-26 00:30 | 2011-06-26 05:25 | 2011-08-08 | PIPING LEAK ISOLATED ON HIGH PRESSURE COOLANT INJECTION "On 06/26/11, at 0030 [hrs. EDT], Peach Bottom Atomic Power Station Unit 3 declared the High Pressure Coolant Injection [HPCI] system inoperable for an ASME class 2 exempt piping leak found during operator rounds. Piping on the steam line pressure indication sensing line downstream of a sensing line root valve had an approximate 5 drop per minute leak. The leak has been isolated and the Unit 3 HPCI system was restored to an operable condition as of 0347 on 06/26/11. "This report is being submitted pursuant to 10CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 08/08/2011 AT 1432 EDT FROM DAVE FOSS TO RYAN ALEXANDER * * * "The purpose of this notification is to retract a previous report made on 06/26/11 at 0525 [EDT] (EN# 46987). Notification of this event to the NRC was initially made as a result of declaring the Unit 3 High Pressure Coolant Injection (HPCI) system inoperable on 06/26/11 at 0030 [EDT] when a small leak on an instrument sensing line was found during performance of routine operator rounds. Specifically, it was observed that the 1/2 inch instrument piping for the non-safety related HPCI steam supply pressure indicator was leaking at approximately 5 drops per minute. The location of the leak was downstream of the instrument line root valve. The leak was isolated and the Unit 3 HPCI system was considered operable at approximately 0347 [EDT] on 06/26/11. The ENS report on 06/26/11 was originally submitted to report a potential loss of safety function involving the Unit 3 HPCI system due to this leak. "Since the initial report, engineering has determined that HPCI was capable of performing its safety function at the time the instrument sensing line was leaking. The evaluation determined that the small sensing line leak would not have resulted in any significant equipment qualification, internal flooding or other equipment concerns that could have affected the HPCI system capability during any postulated design basis events. The pressure indicating instrument supplied by the sensing line is not safety related and is not required for any HPCI function or HPCI operability. Therefore, HPCI was determined to have maintained its operability during the time period that the HPCI sensing line was leaking. "The NRC resident has been informed of the retraction." Notified R1DO (Powell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-06-26
46986 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-06-25 16:15 | 2011-06-25 22:51 | 2011-06-25 | METEOROLOGICAL MONITORING INSTRUMENTATION INOPERABLE DUE TO LOSS OF POWER "At approximately 1615 [hrs. CDT] on 6/25/11, the Meteorological Monitoring Instrumentation at Browns Ferry Nuclear Plant was lost due to a loss of normal and backup power to the Meteorological Monitoring station. "This is reportable as an 8 hour ENS report in accordance with 10CFR50.72(b)(3)(xiii) as 'Any event that results in a major loss of emergency assessment capability...' "Meteorological monitoring was restored to operation at 1841 on 6/25/11. BFN Units 1, 2, and 3 remained in Mode 1 at 100% power throughout the event. "The NRC Resident has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-25
46985 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2011-06-25 07:55 | 2011-06-25 08:15 | 2011-06-25 | UNUSUAL EVENT DECLARED DUE TO FIRE LASTING GREATER THAN 15 MINUTES "Unit 1 experienced a confirmed fire in power board H12. The fire brigade has responded and the power board has been deenergized. Awaiting confirmation that the fire is out." At the time of the notification (0815 EDT), the licensee determined that the fire was out. Power board H12 supplies 480V non-safety plant loads. There was no damage to any safety related equipment and no injuries to personnel. Offsite assistance was not requested. During the notification, at 0825 EDT, the licensee terminated from the Unusual Event. Unit 2 was not affected by this event. The licensee will notify the NRC Resident Inspector as has notified State and local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-06-25
46984 | -1 | ST LOUIS UNIVERSITY |  |  |  |  | 2011-06-21 | 2011-06-24 19:45 | 2011-07-05 | DOSAGE DELIVERED GREATER THAN PRESCRIBED The following occurred at St. Louis University Hospital: A 30 mCi I-131 Sodium Iodide oral capsule was prescribed for administration to a patient for ablation of residual tissue following a thyroidectomy. However, a 115 mCi I-131 Sodium Iodide capsule was administered instead, due to conflicting information in the patient record. At this time, it is believed that there will be no adverse affect to the patient. The patient has been notified of this incident. The Radiation Safety Officer will be reviewing this incident to determine what actions to take to prevent recurrence. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM FELICITY BECKFIELD TO CHARLES TEAL ON 7/5/11 AT 1332 * * * After review by the licensee and NRC staff, it was determined that this was not a reportable event. Notified R3DO (Hills) and FSME EO (Turtil). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2011-06-30
46983 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-06-24 | 2011-06-24 14:54 | 2011-06-24 | AGREEMENT STATE REPORT - SHUTTER FAILURE DUE TO BROKEN CABLE The following information was obtained from the State of Pennsylvania via facsimile: The remote shutter actuator on a Texas Nuclear gauge, Model 5197 (serial #81623) with approximately 100 mCi of Cs-137 was found inoperable. The remote shutter actuator controller cable failed. The shutter is locked in the closed position and shall remain so until repairs are made. PA Report #: PA110013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-06-29
46982 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2011-06-24 13:53 | 2011-06-24 14:55 | 2011-06-24 | UNUSUAL EVENT DECLARED DUE TO INDICATIONS OF FUEL DAMAGE The reactor operated at 10 W to 25 kW steady-state power for a total of 25 minutes. At 1257 CDT the Reactor Manager noticed that the radiation monitor (AMS-4) was reading approximately 80 times the Derived Air Concentration (DAC) for Iodine. A second continuous air monitor and a portable thin-window ionization chamber both read background levels of radiation. A high-volume air sampler was used to sample the air near the sampling location of the AMS, which draws air from the reactor deck. The filter from the air sampler read 3700 DPM after drawing 50 cubic feet of air, indicating elevated levels of activity. An HPGe (High Purity Germanium Detector) spectrograph indicated some Cs-137 in the air filter sample, but no I-131. Primary water activity and conductivity were both at normal levels. The indicated DAC of Iodine increased to a value of 149 times DAC before decreasing to 145 times DAC. The Reactor Manager and Radiation Safety Officer agreed that fuel damage was unlikely, but the results of testing were inconclusive, and that it would be prudent to declare an Unusual Event. * * * UPDATE FROM JEFFREY GUTHER TO CHARLES TEAL AT 1528 EDT ON 6/24/11 * * * HPGe spectroscopy indicated only background levels of Cs-137 for a air sample, a primary water sample, and a swipe taken from the reactor deck. None of these samples showed I-131. A second portable air sample taken at the reactor deck, but on the opposite side of the deck from the radioactive sampling handling table, did not have elevated counts. The Reactor Manager and Radiation Safety Officer agreed that the AMS-4 was most likely mis-calibrated, and the elevated levels in the first high-volume air sample were probably due to the proximity of the radioactive sample handling table to the sampling location. Notified NRR (Grobe), NRR EO (Evans), R4DO (Deese), IRD (Grant), DHS (Hill), FEMA (Blankenship) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 4 | KS | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-06-24
46981 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2009-06-24 | 2011-06-24 12:41 | 2011-06-24 | AGREEMENT STATE REPORT - PATIENT INJECTED WITH WRONG ISOTOPE The following information was obtained from New York City via email: "On 6/24/09, a patient was brought to the Nuclear Medicine Department for a myocardial viability exam and was to be injected with Thallium-201. "The Nuclear Medicine Technologist instead injected the patient with Gallium-67 and immediately realized his mistake. The Gallium vial was right next to the Thallium vial in the storage case. The Head of Nuclear Medicine was informed. He then explained the situation to the patient and advised the patient to take a mild laxative to reduce radiation dose to the large intestine. The event was documented in the patient's chart, and the referring physician was informed. "Consequences: The estimated absorbed total body dose was 0.5200 rads and the dose to the liver was estimated at 1.2600 rads. The viability study was rescheduled. "Corrective actions taken: The Policy and Procedures Manual was revised to include specific instructions about double checking that the correct radioisotope was being chosen; training was conducted by the Radiation Safety Officer; and a sign was posted in the lab listing the steps that must be observed before injecting any patient with radioisotopes. "An inspection was conducted by the Office of Radiological Health on 7/16/09 and the inspector found that the licensee had made a timely report to the [New York City Bureau of Radiation Health (NYCBRH)], and the corrective actions taken were appropriate and effective. This case has been closed by the NYCBRH. "A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-30
46980 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-06-23 | 2011-06-24 08:25 | 2011-06-24 | AGREEMENT STATE REPORT - SOURCE DISCONNECT FROM DRIVE CABLE DURING RADIOGRAPHY ACTIVITIES The following report was received from the Texas Department of Health Radiation Branch via e-mail: "On June 23, 2011, the Agency [Texas Dept of Health] was notified by the licensee that a 67.5 Curie Iridium (Ir) - 192 source disconnected from its drive cable during radiographic operations. The licensee reported that the radiographer had completed the first shoot of the day and when he tried to retract the source to the QSA Global 880D camera, he noted that the source had disconnected from the drive cable. The radiographer isolated the area and contacted his Radiation Safety Officer (RSO). A source retrieval team was sent to the location. The source retrieval team verified that the source was in the collimator and then detached the guide tube from the camera. Using remote handling tools, the source was shaken out of the guide tube and placed into the camera. "The RSO stated that no overexposure occurred and that there was no exposure to any member of the general public. The personnel dosimetry devices of the retrieval team have been sent to the licensee's processor for immediate reading. The cause for the source disconnect is unknown at this time. The camera will be returned to the manufacturer for inspection and for assistance in determining why the connector between the source pigtail and the drive cable disconnected. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I - 8865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-06-29
46979 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-06-23 11:00 | 2011-06-23 17:39 | 2011-06-23 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "During performance of scheduled surveillance testing, the Unit 1 High Pressure Coolant Injection (HPCI) turbine control valve did not fully close when the system was secured. The HPCI system was removed from service and the control valve was inspected. The inspection identified a broken steam supply valve internal to the control valve. This condition would have prevented HPCI from fulfilling its safety function and is being reported for the inability of a single train system to mitigate the consequences of an accident." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-06-23
46978 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-06-22 | 2011-06-23 14:34 | 2011-06-23 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED GAUGE The following was received via fax: "During a routine test on June 22, 2011, the licensee determined the shutter on a fixed gauge failed to completely close. The gauge is used to monitor levels in a digester tank and was identified as a Berthold Technologies Model LB 7444, serial number 903-2-92. It contains a 7.8 milliCurie Cobalt-60 source. The licensee has contacted Berthold to repair or replace the gauge." Virginia Report #: VA-11-0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-06-28
46977 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-04-23 08:14 | 2011-06-21 18:40 | 2011-06-21 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO UNRECOGNIZED DESIGN CONFLICT "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) for invalid actuations reported under 10 CFR 50.73(a)(2)(iv)(A). This actuation was invalid since it was caused by maintenance activities and not by any actual plant condition warranting containment isolation. "On April 23, 2011, at 0814 hours, during implementation of a clearance order for ongoing work, Reactor Protection System (RPS) Bus A was transferred from the normal to alternate power supply. The power transfer functions as a break before make, and the momentary loss of power caused an unexpected actuation of the Groups 3 and 4 outboard containment isolation valves. Outboard isolations occurred in the reactor building drain and ventilation systems, and reactor closed cooling systems. Control room emergency ventilation and standby gas treatment systems also started. All systems functioned as designed, excluding those components that were already removed from service. Following the event, the RPS Bus A was re-energized and the plant was restored to normal operating condition for the current configuration per plant procedures. "The unexpected actuation was due to a latent design conflict between a new design modification and existing equipment that was not discovered until during the implementation phase of the modification. The subsequent investigation cited inadequate review and engagement in the design process by station personnel of the vendor supplied design change modification package as the cause. As part of the implementation of the modification package an interposing relay was introduced into the Nuclear Steam Supply Shutoff System (NSSSS) logic circuit. The work for this modification was performed on the two days prior to this event, April 21st and 22nd. The new design was such that the source of power for the added relay was the same power supply which supplied the alternate logic channel. The resulting condition created a scenario where loss of the RPS-A power supply would complete both halves of the NSSSS outboard trip logic. The design has been revised such that loss of RPS-A or RPS-B power supply will not result in loss of both halves of the NSSSS trip logic circuit. Planned corrective actions will enhance procedures to ensure key design parameters and performance objectives are established early in the design process. "There were no actual safety consequences associated with this event since all affected equipment responded as designed. The NRC Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-06-21
46976 | 0 | ELI LILLY & COMPANY |  |  |  |  | 2011-06-21 | 2011-06-21 15:47 | 2011-06-21 | TWO TRITIUM EXIT SIGNS DISCOVERED MISSING DURING ROUTINE INVENTORY Two (2) generally licensed tritium exit signs were discovered missing from their installed location in Building 80 at the Eli Lilly facility in Indianapolis, IN. Each exit sign contained a calculated activity of 19 Curies. Manufacturer information and serial numbers (S/N) as follows: Manufacturer - SRBT, Mfg date - April 2010, S/N - C077812 Manufacturer - SRBT, Mfg date - May 2010, S/N - C078813 Both signs were installed on 10/6/2010. The licensee is conducting an investigation and will determine appropriate corrective actions. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-06-21
46975 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-06-15 | 2011-06-21 12:37 | 2011-06-21 | AGREEMENT STATE REPORT - TWO I-125 INCIDENTS INVOLVING TOTAL DOSE LESS THAN PRESCRIBED DOSE The State of Wisconsin sent the following report via email: "On June 15, 2011, the licensee's Radiation Safety Officer reported the identification of two medical events that were discovered, involving permanent implants of I-125 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. During a routine inspection conducted on March 8, 2011, DHS (Department of Health Services) inspectors determined that the licensee was not reviewing prostate brachytherapy cases against the medical event criteria and identified numerous potential medical events. A Confirmatory Action Letter was sent on April 6, 2011 which required the licensee to have all of their manual brachytherapy prostate implants reviewed by an outside radiation oncologist. Upon completion of the external review of the licensee's manual brachytherapy program for prostate implants, the licensee identified the following underdoses to the prostate (using D90<80% and D90>120% as medical event criteria): "December 12, 2005: Prescribed dose 108 Gy. Prostate D90 was 67.16%. "July 26, 2007: Prescribed dose 144 Gy. Prostate D90 was 74.09%. "The licensee RSO stated that they will not be notifying the patients involved. DHS will send a special inspection team following the receipt of the licensee's 15 day written report." Wisconsin Event Report ID No.: WI10007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-06-27
46974 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-06-20 09:45 | 2011-06-20 17:10 | 2011-06-20 | UNPLANNED POWER OUTAGES AFFECT EMERGENCY RESPONSE SYSTEMS "On June 20, 2011, at approximately 0945 hours, electrical power was lost to non-essential 120 volt busses V-1-F and V-2-F. The busses supply electrical power to the plant integrated computer system (ICS). As a result of the power loss, the Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) were unavailable. "Preliminary investigation indicates the power loss was caused by receipt of a spurious high temperature alarm (greater than 95 degrees F) in the Technical Support Center (TSC) facility where the electrical busses are located. The alarm signal is believed to be invalid because the high temperature alarm came in for two minutes and reset, and the ambient temperature in the TSC remained steady at 65 degrees F. Electrical busses V-1-F and V-2-F were re-energized and restored to service at 1505 hours. "The ICS, SPDS, ERDS, and CADAP systems were fully restored at 1652 hours on June 20, 2011. In the event of an emergency while these systems were unavailable, contingency plans were in place to transmit plant parameter data and perform the dose assessment function. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of emergency assessment and communications capability. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-20
46973 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-06-20 11:56 | 2011-06-20 16:59 | 2011-06-20 | TECHNICAL SUPPORT CENTER CHARCOAL FAILED TESTING FOR METHYL IODINE "During 24 month Technical Support Center (TSC) Ventilation System Charcoal Analysis testing, the charcoal failed due to Methyl Iodine penetration of 3.1%, which is above the procedural limit of 1%. "The TSC non-emergency ventilation system remains functional. Charcoal replacement is planned. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning procedures and checklists. If radiological conditions require TSC facility evacuation prior to completion of charcoal replacement; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with applicable site procedures." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-20
46972 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-04-21 13:10 | 2011-06-20 13:30 | 2011-06-20 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO CONFLICTING WORK ACTIVITIES "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) for invalid actuations reported under 10 CFR 50.73(a)(2)(iv)(A). This actuation was invalid since it was caused by maintenance activities and not by any actual plant condition warranting containment isolation. "On April 21, 2011, at 1310 hours, upon de-energization of the Reactor Protection System (RPS) Bus A for maintenance, an unexpected actuation of the Groups 3 and 4 outboard containment isolation valves occurred. Outboard isolations occurred in the reactor building drain and ventilation systems, and reactor closed cooling systems. Control room emergency ventilation and standby gas treatment systems also started. All systems functioned as designed, excluding those components that were already removed from service. Following the event, the RPS Bus A was re-energized and the plant was restored to normal operating condition for the current configuration per plant procedures. "The subsequent investigation found that personnel involved with work planning and control did not recognize that de-energizing RPS Bus A would create a condition which completed the Nuclear Steam Supply Shutoff System outboard isolation logic. An associated relay for the second channel had been previously de-energized to support ongoing maintenance. The cause of allowing this conflicting work to occur was determined to be inadequate procedural guidance. Planned corrective actions will enhance procedures to identify logic impacts, conflicting equipment and recommended protection schemes. "There were no actual safety consequences associated with this event since all affected equipment responded as designed. The NRC Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-06-20
46971 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2011-06-20 11:52 | 2011-06-20 13:01 | 2011-06-20 | UNIT 2 REACTOR TRIP FOLLOWING THE LOSS OF THE "B" MAIN FEEDWATER (MFW) PUMP At 1152 EDT on 6/20/11 while operating at 60% power, the "B" MFW Pump tripped for reasons unknown. There was no maintenance or I&C work on-going at the time involving this pump. Operators initiated a manual reactor trip, however, [they] are not certain whether the automatic reactor trip setpoint of 49.5% Steam Generator Water Level Narrow Range (SGWL NR) was reached first. SGWL decreased to the Auxiliary Feedwater (AFW) setpoint of 26.8% NR causing the initiation of both motor-driven AFW Pumps. All Control Rods fully inserted. Unit 2 is currently stable in Mode 3, Hot Standby, removing decay heat via the Main Steam line to the Condenser. Operators secured AFW and will initiate feed to the Steam Generators using the "A" MFW Pump. Unit 2 is in a normal post-trip electrical lineup with all sources of offsite power available. The licensee has the cause of the "B" MFW Pump trip under investigation. The licensee informed both state/local (Waterford Dispatch) and the NRC Resident Inspector | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-20
46970 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-06-19 19:40 | 2011-06-19 22:36 | 2011-06-19 | RELEASE OF OIL TO THE MISSOURI RIVER "Notification is being made to the Nebraska Department of Environmental Quality regarding the release of oil to the Missouri River from the Cooper Live Fire Training Facility. Currently, levees separating the Training Facility and the Missouri River are being over topped due to flooding of the Missouri River. This condition has resulted in flooding of the burn pits in the fire training facility, with the subsequent release of the residue which includes unburned fuel oil. Any release of this water containing oil to the Missouri River is uncontrolled at this time. Then is no radiological contamination in this area. "Current river level is approximately 900.5 ft. MSL, approximately 3.0 feet below plant grade elevation. The fire training area is lower than plant grade. A press release is not planned at this time. River level is currently projected to be 899 ft. by Wednesday 6/22." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-19
46969 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-06-19 04:02 | 2011-06-19 05:27 | 2014-01-25 | UNUSUAL EVENT DECLARED DUE TO MISSOURI RIVER FLOODING At 0402 CDT on 6/19/2011 a Notification of Unusual Event was declared due to the elevation of the Missouri River reaching 899.1 feet above mean sea level. This is above the Emergency Action Level HU1.5 elevation of 899 feet. The Missouri River is expected to crest at 899.5 feet within the next couple of days. It is expected that the elevation of the Missouri River will remain above 899 feet for most of the summer. Actions are in progress in accordance with the site flooding procedure, including strategic placement of sand bags at building entrances and important facilities. There is no major plant equipment out of service at this time. Personnel access to the site is not presently impeded. Emergency evacuation routes remain available. The licensee notified the NRC Resident Inspector. The licensee notified the State of Nebraska Emergency Management Agency, the State of Missouri State Emergency Management Agency, the Nemaha County Emergency Operations Center, the Richardson County Emergency Operations Center and the Atchison County Emergency Operations Center. * * * UPDATED FROM BRIAN STANDER TO DONALD NORWOOD AT 0743 EDT ON 6/19/2011 * * * "On 6/19/2011 at 0447 CDT, Nebraska Public Power District issued a press release concerning the declaration of a Notification of Unusual Event declared today at 0402 for the Missouri River elevation above 899 feet above sea level. "This is a four hour report per 10CFR50.72(b)(2)(xi) for any event or situation for which a news release is planned or notification to other government agencies has been or will be made which is related to heightened public or government concern. State and local agencies were notified of the expected news release during the NOUE notification. "At 0402 CDT, Missouri River elevation was at 899.1 feet. No updated river projections are available at this time. Level is expected to remain at least below plant grade elevation. No deficiencies with the nearby protective levees have been identified surrounding the plant. Actions are in progress in accordance with the site flooding procedure, including strategic placement of sandbags at building entrances and important facilities. Personnel access to the site is not presently impeded, and required emergency evacuation routes remain available." The licensee notified the NRC Resident Inspector. Notified R4DO (Werner). * * * UPDATE AT 1121 EDT ON 7/12/2011 FROM MAURICE PALMER TO MARK ABRAMOVITZ * * * Cooper Nuclear Station exited the Notification of Unusual Event (NOUE) at 0947 CDT on 7/12/11. River level is currently at 895.8 feet MSL which is below the NOUE threshold of 899 feet MSL. River level is forecast to continue going down. The licensee is expecting to issue a press release today. The licensee notified the NRC Resident Inspector, State of Missouri, Nebraska Emergency Management Agency, Nemaha County Sheriff, Richardson County Sheriff, Missouri FEMA, and the Atchison County 911 center. Notified the R4DO (Cain), IRD (Morris), NRR (Thorpe), DHS (Strangfeld), and FEMA (Hollis). * * * UPDATE AT 1426 EDT ON 7/12/11 FROM JEREMY SIMS TO VINCE KLCO* * * "A press release has been issued to inform the public of Cooper Nuclear Station's exit from the Notification of Unusual Event, regarding high Missouri River level. The initial entry into the Notification of Unusual Event occurred on 06/19/2011 and was exited on 07/12/2011. The highest river level observed at [Cooper] was 900'-8". Plant grade is at 903'-6". The press release reports the current Missouri river level as 895.8' and forecasted to continue to lower." Notified the R4DO(Cain). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-06-19
46968 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-06-17 10:00 | 2011-06-17 12:40 | 2011-06-17 | AGREEMENT STATE REPORT - NUCLEAR CARDIAC PACEMAKER FOUND "At approximately 10:00 AM EDT on Friday, June 17, 2011, a resident telephoned the above licensee and reported finding an 8 Curie Pu-238 nuclear cardiac pacemaker (ARCO NU-5 s/n 001). The licensee's medical physicist who interviewed the caller, immediately contacted NJDEP RMP [New Jersey Department of Environmental Protection Radioactive Material Programs). After interviewing the medical physicist, it was learned that the resident, while cleaning and gathering personal belongings of her deceased parent, came across an envelope that contained the pacemaker. The pacemaker was initially implanted in 1973 at the licensee's location (Newark Beth Israel) and removed in 1975 at an unknown location. After the pacemaker was removed, for reasons not yet known, it came back to the residence other patient where it remained until it's discovery on 6/17/11. The medical physicist has arranged to go to the resident's apartment later in the day where he will package the pacemaker for it's return and storage at the licensee's facility. At 12:15 PM the same day, the medical physicist reported that the pacemaker was safely returned to the licensee's facility. The pacemaker was intact with no signs of damage. The licensee will attempt to locate any files/information pertaining to the patient that may still be stored from the 1970's. A full report is expected from the licensee." NJ Event ID No. NJ-11-17-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-06-22
46967 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-06-16 13:09 | 2011-06-17 13:04 | 2011-06-17 | CHEMICAL RELEASE FROM INTAKE PUMPING STATION. "A notification of the event discussed below was made to the Tennessee Department of Environment and Conservation (TDEC) at approximately 09:48 [hrs EDT] on June 17,2011. As a result of the notification made to the state, NRC is being notified in accordance with 10 CFR 50.72(b)(2)(xi), 'News Release or Notification of Other Government Agency.' "On June 16, 2011, a chemical treatment of the raw water system for Watts Bar Nuclear Plant (WBN) was underway. The treatment was a routine injection of biocide (Sodium Hypochlorite and Flogard MS6237) for the treatment of microbiologically induced corrosion (MIC) and to inhibit the growth of asiatic clams. At approximately 13:09 [hrs EDT] on June 16, 2011, WBN personnel noticed that a small stream of water was releasing through the splash guard of a trough on the outside (lake side) of the Intake Pumping Station (IRS) and entering the Intake Forebay. This initial leak was secured by approximately 14:30. At approximately 14:35, a second leak from a broken pipe was identified. The second leak was terminated at approximately 16:05. The cause of the initial leak was determined to be a tree growing in a trough in the intake structure and degraded sealant on the trough's splash guard. TVA's [Tennessee Valley Authority] biologist performed a survey of the intake channel and the river downstream from the plant and found no dead fish or abnormal bird activity. TVA's review of the chemical release to the lake determined that no Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA) reportable quantities were exceeded. "The reporting requirements contained in WBN's Environmental Protection Plan (EPP) were reviewed and not found applicable to this event. WBN's [NRC] Resident Inspector has been notified of the event and the need for the event notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-17
46966 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-04-24 21:44 | 2011-06-16 15:25 | 2011-06-16 | 60 DAY OPTIONAL NOTIFICATION OF INVALID START OF EMERGENCY DIESEL GENERATOR. "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of the 'B' Emergency Diesel Generator on 4/24/11 while performing a test of the diesel generator load and safeguard sequence. Emergency AC Electrical Power system including Emergency Diesel Generators is a system named in 50.73(a)(2)(iv)(6). "On 4/24/11, at 2144, [hrs. EDT] while testing the continuity of relay SI-20X that is part of the test of diesel generator load and safeguard sequence, an unexpected partial Safety Injection signal occurred. The initiating action was the testing of the continuity of relay SI-20X while the 'B' train Safety Injection DC breaker was closed. Once the testing of relay SI-20X was completed, the partial Safety Injection signal ceased and all the equipment that had started, or had been repositioned, was returned to its pre-test condition. The unexpected partial Safety Injection signal was the result of the improper sequencing of a separate test of process radiation monitors that was being performed concurrently with the test of the diesel generator load and safeguard sequence. "Specific information required per NUREG-1022: "a. The specific train(s) and system(s) that were actuated: The 'B' Diesel Generator actuated. In addition, (a) equipment that started, or was repositioned, were the 'D' Service Water pump, the 'B' Control Room Emergency Air Treatment System (CREATS), and Emergency Core Cooling System (ECCS) valves 871B and 852B; and (b) equipment that stopped was the containment purge supply and exhaust fans, and Control Room Air Handling Unit supply and return fans. "b. Whether each train actuation was complete or partial: The actuation was partial. "c. Whether or not the system started and functioned successfully: The 'B' Emergency Diesel Generator started and operated successfully. It was later secured by Operations personnel. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-06-16
46965 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-16 12:30 | 2011-06-16 14:46 | 2012-09-26 | ADDITIONAL PENETRATION IDENTIFIED FOR MITIGATION DURING WALKDOWN "Operations identified a potential flooding issue in the Intake Structure 1007 ft. 6 in. level. The area of concern is a the hole in the floor at the 1007 ft. 6 in. level where the relief valve from FP-1A discharge pipe goes through the raw pump bay and discharges into the intake cell. There is one penetration of concern. Flooding through this penetration could have impacted the ability of the station's Raw Water (RW) pumps to perform their design accident mitigation functions. "Efforts are in progress to seal the penetration. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 9/26/12 AT 1949 EDT FROM ROBERT KROS TO DONG PARK * * * "The penetration in question is not an external penetration and is not within the scope of the CLB [Current Licensing Basis] and therefore the condition is not reportable. The penetration is internal to the intake structure and does not affect internal flooding. "The failure to retract this notification in a timely fashion was identified while reviewing flood related station notifications from 2011 and has been entered into the corrective action system." The licensee has notified the NRC Resident Inspector. Notified R4DO (Werner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-06-16
46964 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-06-15 14:00 | 2011-06-16 12:14 | 2011-06-16 | ROSEMOUNT MODEL 710 TRIP UNITS WOULD NOT TURN ON DURING TESTING "On June 15, 2011, the Site Vice President was notified that the 10 CFR 21 evaluation of Rosemount Model 710 trip units supplied under purchase order 10174727 determined that the reporting criteria of 10 CFR 21.21 (d)(1) are met. "During pre-installation testing, it was found that 3 of 4 Rosemount Model 710 trip units would not turn on. The units were returned to Rosemount for failure analysis and it was determined that a resistor in the start-up circuit for the trip unit was failed. This prevented the trip unit from starting. Based on engineering analysis, some of the applications for the trip unit require it to energize to perform the associated safety functions. Therefore, the identified failure mechanism could have represented a substantial safety hazard if the components had been installed, and the condition is reportable. "The condition had no actual safety consequences as the deficiency was identified during pre-installation testing and if installed without pre-installation testing, the system could not have passed post maintenance testing. The three failed units were returned to Rosemount. This notification is made pursuant to 10 CFR 21(d)(ii)(3)(i)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0 | 2011-06-16
46963 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2009-10-06 | 2011-06-15 18:22 | 2011-09-23 | MEDICAL UNDERDOSE DURING BONE RADIATION THERAPY The following report was received via e-mail: "A patient was treated in the nuclear medicine department on October 6, 2009 with Quadramet (Sm-153 EDTMP) for bone pain administered by the user. The Nuclear Pharmacy prepared, assayed and dispensed 43.5 mCi of Quadramet. The dose was prepared with a needle attached to a syringe. After administration, the syringe and additional materials were returned to the Nuclear Pharmacy for re-assay to determine the activity remaining in the administering materials. Reassaying is a standard procedure. The assay revealed that 12.7 mCi of the Sm-153 remained in the syringe cap and the needle itself. The administered dose was determined to be 30.8 mCi, an underdose of approximately 30%. "[The] attending physician in consultation with the Authorized User agreed not to bring the patient back to add to the dose already administered and to await the result of response. In their opinion, there will be no adverse affect on the patient. "The Nuclear pharmacy will review whether a needle needs to be present on the dose syringe when dispensed. Nuclear pharmacy will also investigate availability and use of three-way lock to facilitate flushing of the syringe. "An update will be provided when an investigation is done by an inspector from the New York City Office of Radiological Health." * * * UPDATE FROM LICKERMAN TO KLCO ON 9/23/11 AT 1437 EDT* * * "The department inspector investigated the above medical event and determined information to be consistent with the initial report to NRC shown above. In addition, the inspector determined that the licensee has instituted corrective actions which should prevent an occurrence of this type of event in the future. In particular: -The nuclear pharmacy will dispense and calibrate syringe with a cap but without a needle attached; -Three-way stopcocks will be distributed as standard instruments with all Sm-153 doses to facilitate flushing of the syringe; -In annual training/retraining, it will be emphasized that Authorized Users must return syringe setups to the nuclear pharmacy for clarification if any setup is incorrect or appears to differ from that which is required per procedure. No violations were issued following the field inspection." Notified the R1DO (Newport) and FSME (O'Sullivan). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-21
46962 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2006-09-22 | 2011-06-15 18:53 | 2011-06-15 | PATIENT RECEIVED RADIATION THERAPY AND LATER DETERMINED TO BE PREGNANT The following report was received via e-mail: "Patient had thyroidectomy in 2005 and came into nuclear medicine dept. on Sept. 8, 2006 for consultation for I-131 treatment, the nuclear medicine [NM] resident interviewed her, explained precautions, stated importance of not becoming pregnant. A pregnancy test was performed on September 21, 2006 and the results were negative. The patient was then treated with 95 mCi of I-131 on September 22, 2006. "After missing one of her Endocrine clinic appointments following the radioactive iodine therapy treatment, on December 22, 2006, the patient went to the Endocrine clinic for a follow up visit. Following that visit, NM was informed by endocrinology that the patient was pregnant. NM contacted OB/GYN and learned that the patient visited her OB/GYN physician and that ultrasound confirmed that the patient was pregnant. The ultrasound revealed that the patient was approximately 8-weeks pregnant, putting the date of conception at approximately September 1-6, so the patient was already 2-3 weeks pregnant at the time of the pregnancy test. "It was estimated that the fetus received about 25 rad of radiation exposure. Upon discovery of the incident, patient was advised to see a genetic specialist immediately at the Montefiore Medical Park to discuss the radiation exposure to the fetus and possible consequences as a result of the radiation exposure. "An update will be provided when an investigation is done by an inspector from the New York City Office of Radiological Health." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-21
46961 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-06-15 15:30 | 2011-06-15 17:10 | 2011-06-15 | EVENT NOTIFICATION SYSTEM PHONE INOPERABLE "The NRC Event Notification System phone in the Unit 2 CCR [Control Room] and the EOF [Emergency Operations Facility] at IPEC [Indian Point Energy Center] has failed. Entergy's telecommunications department and Verizon have commenced troubleshooting. This constitutes a loss of emergency notification system as required by 10CFR50.72(b)(3)(xiii). NRC Operations Center has been notified via commercial phone line at time of event." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1827 ON 6/15/2011 FROM FRANCIS MULLEK TO MARK ABRAMOVITZ * * * The telephone contractor found a "cross connect missing" and it has been replaced. The Control Room Supervisor declared ENS operable at 1827 EDT. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Joustra). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-15
46960 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2011-06-15 08:35 | 2011-06-15 11:10 | 2011-06-15 | BODY DISCOVERED IN THE OWNER CONTROLLED AREA "A deceased individual was discovered this morning along the shoreline of the Fermi-2 property, outside of the Protected Area. Specifically, at 0835 (EDT), the Main Control Room was notified by Security that a body had been found on the shoreline, north of the cooling towers. The Monroe County Sheriff and the US Coast Guard were notified and were on-site. The identity of the body has not yet been determined. The body has been removed from site by the US Coast Guard helicopter, and all local law enforcement officials have left site. "A press release is not planned at this time." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-15
46959 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-06-14 18:30 | 2011-06-14 21:33 | 2011-06-14 | ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA Entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional information. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-06-14
46958 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-06-10 | 2011-06-14 15:58 | 2011-06-14 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE FOR PROSTATE IMPLANT The following information was received via e-mail: "On Tuesday, June 14, 2011 Mission Hospital notified the Department [California Department of Public Health] that a reportable medical event occurred on June 10, 2011. This event was discovered on June 13, 2011. A patient underwent prostate seed implantation of Pd-103 seeds. Two sets of Pd-103 seeds had been ordered for this patient, and the older set was mistakenly used in surgery. The licensee estimates that this resulted in under treatment of the target organ by 70%. Follow-up information will be provided within 15 days, per 10 CFR 35.3045. This investigation is on-going." California Event: 061411 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-06-20
46957 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-06-13 19:24 | 2011-06-13 23:29 | 2011-10-12 | AUTOMATIC REACTOR TRIP DURING STARTUP PHYSICS TESTING "On June 13, 2011 at 1924 CDT, an automatic reactor trip was actuated during Shutdown Bank Insertion for Beginning of Life Physics Testing. Neutron flux lowered from the intermediate range to the point of automatic energization of the Source Range Nuclear Instruments. Energization of the Source Range Nuclear Instruments during this step is anticipated and permissible per the test procedure. When it energized, the N-31 Source Range Nuclear Instrument (Red Channel) failed high which initiated an automatic reactor trip. "All plant systems functioned as required, including the Reactor Protection System. All control rods fully inserted into the core. There was no Emergency Core Cooling System or Auxiliary Feedwater System actuation. No Emergency Diesel Generators were started and power continues to be supplied from off site. The reactor coolant system has forced circulation and the atmospheric steam dumps are currently being used for decay heat removal from the steam generators. "There was no radiological release and emergency plan implementation was not required. "An investigation of the failure of the N-31 Source Range Nuclear Instrument is in progress" There is no known primary to secondary leakage. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RUSS PARKER TO DONALD NORWOOD AT 2155 EDT ON 6/14/11 * * * "At the time of the trip, the reactor was subcritical. This notification is updated to reflect reporting in accordance with 10CFR50.72(b)(3)(iv)(A). "An investigation of the failure of the N-31 source range nuclear instrument continues." This event was initially reported by the licensee as a four-hour report in accordance with 10CFR50.72(b)(2)(iv)(B). The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak). * * * UPDATE FROM ALEX RIVAS TO HUFFMAN ON 10/12/11 AT 1502 EDT * * * 'On June 14, 2011 at 2055 EDT, EN 46957 was amended to state the reactor was subcritical at the time of the trip. Subsequent review of this situation by the licensee resulted in a determination that at the time the test sequence was initiated, the reactor was critical and in MODE 2. Accordingly, this non-emergency report is amended to reflect EN 46957 as originally submitted on 06/13/11 at 2229 CDT. LER 301/2011-004-01 [submitted on July 25, 2011] will be revised accordingly.' The licensee has notified the NRC Resident Inspector. R3DO (Peterson) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-06-13
46956 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-05-04 | 2011-06-13 16:39 | 2011-06-13 | AGREEMENT STATE REPORT - MEDICAL EVENT DURING LIVER RADIATION THERAPY The following report was received via fax: "On May 4, 2011 a patient underwent a Y-90 therapy procedure. Two doses were to be administered to the right lobe of the patient's liver. The first dose was terminated when stasis was achieved. The second dose was terminated because of patient pain after 48% of the dose had been delivered. The pain during the second dose was considered most likely due to embolization. The licensee notified VDH (Virginia Department of Health) and requested guidance on whether the circumstances could be due to patient intervention. It was determined by VDH to be a medical event and not excepted because of patient intervention. A conference call was held with the licensee on June 10th and a written report submitted to VDH. The licensee indicated written directives, patient preparation, and pain control methods would be reviewed." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-06-19
46955 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-06-07 11:52 | 2011-06-13 16:04 | 2011-06-13 | NONCONSERVATIVE VALVE ACTUATOR PROGRAM SOFTWARE "In Kalsi Engineering Valve and Actuator Program (KVAP) Error Report 2011-02, Kalsi Engineering identified an error in the KVAP software that provides default flow and torque coefficients for ball and plug valves which can affect margin predictions. Communication between Kalsi and Duke Energy personnel confirmed that non-conservative torque values were calculated for select ball valves used at Oconee for containment isolation. As a result of the Kalsi error, the non-conservatively calculated torque values resulted in negative actuator margins, calling into question the actuators' capability to close the valves under all design conditions. Therefore, it has been determined that the KVAP software program error constitutes a defect, reportable under 10CFR21. "Four safety-related containment isolation valves in the High Pressure Injection system were impacted, requiring entry into TS 3.6.3, Containment Isolation Valves, on two Oconee units [Units 2 and 3]." Unit 1 was shutdown for a refueling outage at the time of this event and the actuator spring was replaced during the outage. The valves on units 2 and 3 required a Notification of Enforcement Discretion (NOED) which occurred on June 2, 2011. Three of the four valves were declared operable on June 10, 2011 and the remaining valve was declared operable the next day. The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Refueling | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2011-06-13
46954 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-04-14 20:43 | 2011-06-13 15:19 | 2011-06-13 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO CONNECTOR HIGH RESISTANCE "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73(a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 2043 on April 14, 2011, with the Duane Arnold Energy Center (DAEC) operating at 100% power, an invalid Group 3 isolation on the 'A' side of the Primary Containment Isolation System occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by a high resistance contact on connectors in the detector circuitry for the 'A' Reactor Building Vent Shaft Radiation Monitor. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-06-13
46953 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-13 12:00 | 2011-06-13 14:30 | 2011-06-13 | OFFSITE NOTIFICATION DUE TO SEWAGE SYSTEM RELEASE "At 0500 CDT, the lift station #4 sewage system, South of the Fort Calhoun Station Administration building, was released to the Missouri River. The release was a mixture of ground water and sewage; samples were taken by chemistry but dilution concentration is unknown. Approximately 105 gpm release started around 0500 on 6/13/2011. This condition is being reported pursuant to 10 CFR 50.72(b)(2)(xi) for an event related to the protection of the environment for which a notification of governmental agencies is required. Applicable governmental agencies have been notified per plant procedures." The licensee notified the State of Nebraska at 1200 CDT. The licensee also notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-13
46952 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-05-19 | 2011-06-13 13:01 | 2011-06-13 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via e-mail: "The Iowa Department of Public Health (IDPH) received a telephone notification on May 19, 2011 from the licensee concerning the loss of two tritium exit signs. They stated that during a remodeling process that the signs were taken down and mistakenly placed with the construction trash and sent to a landfill in Pike County, Illinois. The licensee stated that the signs were not retrievable. At the time of the notification, the licensee was not aware of the manufacturer, model number or activity of the signs. IDPH notified the Illinois Emergency Management Agency on May 20, 2011 regarding the exit signs in an Illinois landfill. IDPH was notified by the licensee on June 13, 2011 of the manufacturer, model number, serial number and activity of the sources." Manufacturer: EvenLite, Inc. Activity: 20 Ci each Model: LEX Series Serial Numbers: Z34957 and Z34946 Iowa event: IA110003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-06-16
46951 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2011-06-13 05:10 | 2011-06-13 10:17 | 2011-06-13 | MANUAL REACTOR SCRAM DUE TO STEAM LEAK IN TURBINE BUILDING "On June 13, 2011 at 0510 CDT, a manual scram was inserted on Unit 1 following discovery of a steam leak in the turbine building downstream of the Main Turbine Stop Valves. Following the reactor scram, reactor water level decreased to approximately -19 inches, which resulted in automatic Group II and Group III isolations (expected response). The steam leak was isolated by closure of the Main Turbine Stop Valves. All systems responded properly to the event. Unit 1 remains in Mode 3 [hot shutdown], maintaining reactor pressure with the Main Turbine Bypass Valves; reactor water level is in the normal level band. The cause of the event is still under investigation." "Unit 2 was unaffected by the event and remains at 100% power." "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 34 | 0 | 0 | -1 | 0 | 0 | M | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-13
46950 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-06-12 22:30 | 2011-06-12 23:23 | 2011-06-12 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO A PROTECTED AREA Attempted introduction of contraband into the protected area. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2011-06-13
46949 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-05-15 | 2011-06-10 17:17 | 2011-06-10 | AGREEMENT STATE REPORT - MEDICAL EVENTS INVOLVING USE OF SAVI BRACHYTHERAPY APPLICATORS The following information was provided by the State via facsimile: "On June 10, 2011, the licensee's Radiation Safety Officer reported the identification of two medical events involving a HDR [High Dose Rate] Partial Breast Treatment using SAVI applicators. For both patients, treatment was delivered twice a day for five consecutive days in May 2011. It was determined later that the distance as determine by use of a Varian VariSource check ruler was incorrect. The check wire was blocked approximately 4.5 cm from the end of the lumen. The preliminary results from re-planning indicates that in both cases the most distal half of the applicator was under dosed at least 20 percent and the proximal half received approximately 200 percent more dose than what was prescribed. The patients will be notified by the referring physician. The licensee has suspended SAVI treatments until the root cause can be identified. Further updates will be made through NMED. "The State of Wisconsin Department of Health Services will conduct a special inspection at the licensee's location." Wisconsin Report No: WI 110006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-06-16
46948 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-06-08 | 2011-06-10 14:43 | 2011-06-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received via facsimile: This event occurred at a construction job site in Northern Kentucky on the Westbound I-275 to Southbound KY-17 ramp, 30 feet up the ramp and approximately six feet from the outside edge of the roadway. A pickup truck backed over a Humboldt moisture density gauge (model 5001, S/N 3182, 11 mCi Cs-137, 44 mCi Am-241:Be) while the gauge was in "backscatter mode." The operator had stepped away as instructed during the backscatter reading. The operator could not stop the pickup driver. The insertion handle on the gauge broke. The gauge shutter could not be closed. There was no apparent contamination of the site per a survey. Readings around the gauge were near background except the beam from the non-closable shutter. The licensee placed the gauge on the ground in a storage building with the beam pointed into the earth. A survey was conducted around the broken gauge and the site was secured. A check was made for contamination at the job site, on the transport truck, and in the storage area. The gauge was transported on June 9, 2011 to the normal secure storage site at the DOT secure storage shed in Frankfort, KY. On June 10, 2011 the Kentucky Radiation Health Branch (KRHB) surveyed the gauge and inspected the site. KRHB advised the licensee that the device should not be disturbed until trained and licensed persons could package and ship the gauge. KRHP advised the licensee to secure the dosimetry of persons involved. KRHB will review, inspect and consider enforcement actions after the damaged device is secure. Dosimetry was not available at the time of this report, but it will be obtained for affected individuals. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-06-15
46947 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-06-10 08:02 | 2011-06-10 15:55 | 2011-06-10 | ALL FOUR CHANNELS OF RPS OVERPOWER FLUX/FLOW IMBALANCE PROTECTION TRIP DISCOVERED TO BE INOPERABLE "Event: During startup of Unit 1 on June 10, 2011, after increasing power to approximately 50 percent, it was noticed that power range nuclear instrumentation was not responding adequately to power imbalance differences. At 0802 EDT, all four channels of Reactor Protective System instrumentation were declared inoperable. TS 3.3.1., Reactor Protective System (RPS) instrumentation, Condition A, B, and C were entered. RPS Channel D was placed in trip per Condition A. Trouble shooting efforts were immediately initiated. "Initial Safety Significance: This issue constitutes a loss of safety function because the nuclear overpower flux/flow imbalance trip function of RPS was not operable. "Corrective Action(s): Trouble-shooting commenced. A wiring error was identified that affected all four RPS channels. At this time, all four channels have been restored to operability. All conditions of TS 3.3.1, Conditions A, B, and C have been exited as of 1438 EDT hours when all four channels of RPS were restored." The licensee stated that the wiring error is associated with a modification package that was completed during the recent refueling outage. The licensee has notified the NRC Resident Inspector. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-06-10
46946 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-06-10 11:45 | 2011-06-10 15:19 | 2011-06-14 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL DUE TO MALFUNCTIONING VENTILATION SYSTEM "The Technical Support Center (TSC) has been rendered non-functional due to a malfunctioning ventilation system. Investigation into elevated TSC temperature led to the discovery of a malfunctioning compressor. Repairs to TSC ventilation have commenced. "Per Emergency Plan Procedure IP-EP-220, an alternate location for the TSC staff has been identified and communicated to the TSC staff if the Emergency Director determines that the TSC is uninhabitable during an event." The licensee notified the State of New York Public Service Commission. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM CHARLES BRIAN ROAKES TO DONALD NORWOOD AT 1209 EDT ON 6/14/2011 * * * "On June 11, 2011, at 1300 hours, repairs to the TSC Ventilation / AC were completed and the TSC ventilation system returned to service and declared functional. The TSC is now functional as a result of returning the TSC ventilation system to service." The licensee notified the State of New York Public Service Commission and the NRC Resident Inspector. Notified R1DO (Joustra). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-10
46945 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2011-06-07 12:00 | 2011-06-10 12:01 | 2011-06-10 | AGREEMENT STATE REPORT - GAS CHROMATOGRAPH NICKEL-63 SOURCE FAILED LEAK TEST The following information was provided by the State via facsimile: "The RSO called to report a leaking Ni-63 sealed source in a gas chromatograph. The leak test result was 0.04 microCuries of removable contamination at ECD [Electron Capture Device] inlet. The RSO contacted the manufacturer, Agilent, about this event and they will be making a site visit to investigate. The system was shut down and isolated. The defective detector will be sent back to the manufacturer. There is no apparent cause. The system is only a year old and is used carefully. All other areas surveyed & swiped were negative for contamination." Event #: NY-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-15
46944 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2011-06-10 | 2011-06-10 11:29 | 2011-06-10 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following was received via fax: "The South Carolina Department of Health and Environmental Control (SCDHEC) was notified on Friday, June 10, 2011, at 0955 hrs., that a Troxler 3411-B gauge, s/n 4793, containing 8 mCi of Cs-137 and 40 mCi of Am-241:Be had been stolen during the armed theft of a company vehicle at approximately 0530 hrs. on June 10, 2011. The RSO called to report the theft of the material. He stated that the Varnville police had been notified and were handling the incident. The SCDHEC inspector took the initial report and proceeded to call the South Carolina Fusion Center to report the incident. "The RSO was advised by the SCDHEC inspector to submit a written report detailing this event to the SCDHEC within 30 days. The event is open and pending the licensee's investigation and report to the SCDHEC, updates will be made through the national NMED system." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2011-06-15
46943 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-06-09 14:22 | 2011-06-09 19:11 | 2011-06-09 | INADVERTENT SIREN ACTIVATION DUE TO LIGHTNING STRIKE "This siren affects both Dresden and Braidwood Stations. This notification is for both sites. "At approximately 1422 [CDT] on June 9, 2011, a Grundy County representative notified Exelon of an inadvertent siren activation. The Exelon representative contacted the siren contractor at 1423 [CDT] inquiring about siren activity in the shared Braidwood/Dresden Emergency Planning Zones. Upon review and polling of the system at 1444 [CDT], siren BD11 was identified in the area of concern with a communication failure. The siren contractor was immediately dispatched and arrived at the siren location at approximately 1520 [CDT]. Upon arrival, the siren was not sounding and significant damage was identified, which was indicative of a direct lightning strike. The siren was declared out of service and repairs will begin on June 10th." "This condition is reportable under 10CFR50.72(b)(2)(xi) - News release or notification of other governmental agency." The licensee notified the NRC Resident Inspector and Grundy County local authorities. See Braidwood Event #46942 concerning same event. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-09
46942 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-06-09 14:22 | 2011-06-09 19:03 | 2011-06-09 | INADVERTENT SIREN ACTIVATION DUE TO LIGHTNING STRIKE "This siren affects both Dresden and Braidwood Stations. At approximately 1422 [CDT] on June 9, 2011, a Grundy County representative notified Exelon of an inadvertent siren activation. The Exelon representative contacted the siren contractor at 1423 [CDT] inquiring about siren activity in the shared Braidwood/Dresden Emergency Planning Zones. Upon review and polling of the system at 1444 [CDT], siren BD11 was identified in the area of concern with a communication failure. The siren contractor was immediately dispatched and arrived at the siren location at approximately 1520 [CDT]. Upon arrival, the siren was not sounding and significant damage was identified, which was indicative of a direct lightning strike. The siren was declared out of service and repairs will begin on June 10th." The licensee notified the NRC Resident Inspector and Grundy County local authorities. See Dresden Event #46943 for same event notification. | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-09
46941 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-06-09 09:20 | 2011-06-09 14:00 | 2011-06-09 | OFFSITE NOTIFICATION CONCERNING INABILITY TO MEET SLUDGE POND DISCHARGE PERMIT DUE TO RIVER LEVELS "Notification was made to the Nebraska Department of Environmental Quality regarding the inability to conform to the NPDES permit, since the discharges from the sludge pond to the Missouri River are uncontrolled at this time. As a result of high Missouri River levels, the sludge pond was overtopped. The discharges into this pond are subject to NPDES requirements. The inputs into the sludge pond are described in the NPDES permit as low volume wastewater. There are three outfalls which discharge into the pond. Outfall 002B is described as Clearwell Discharge plus Outfall 004 Emergency Overflow. Outfall 002C is described as Floor Drains. Outfall 004 is described as Reverse Osmosis Reject and Boiler Blowdown Waste streams. There is no radiological contamination in the pond. "Additionally, the current and projected flooding conditions of the Missouri River high river levels have resulted in some media inquiries regarding potential changes in plant operation. Public information personnel and Management have responded to these inquiries with information on the impact of river level and preparations for additional actions should conditions warrant additional protective actions. "Current river level is approximately 896 ft. MSL, three feet below the elevation which requires declaration of a NOUE, and approximately 4.8 feet below the crest of the 1993 flood, which was the highest flood recorded at the site. Current river elevation is 7 feet below grade elevation. A press release is not planned at this time. River level is currently projected to be 897.5 ft by Tuesday 6/14. "Current river level is characterized as Moderate Flooding by the National Weather Service. There are currently no operational problems due to river conditions. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-09
46940 | 0 | HEMLOCK SEMICONDUCTOR CORPORATION |  |  |  |  | 2010-03-30 | 2011-06-09 12:30 | 2011-06-09 | FIXED PROCESS GAUGE SHUTTER FAILURE The RSO reported a shutter problem on a fixed mounted process gauge manufactured by Ohmart Vega (Model SHF-2) containing a 200mCi CS-137 source. The shutter problem was discovered during a semi-annual shutter test on 3/30/2010 when it was determined that the shutter would not close. The shutter is normally always open to support the manufacturing process and the failure to close did not pose any personnel risk at the time of occurrence. A representative from the gauge manufacturer repaired the shutter onsite and the shutter has functioned acceptably since the repair. The RSO noted that this event occurred over one year ago and he was unaware that it was reportable at the time. The RSO was alerted to the reportability requirements of this incident during his review of NRC Information Notice IN-2011-09. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-06-09
46939 | 0 | APPLIED TECHNICAL SERVICES, INC |  |  |  |  | 2011-04-13 07:30 | 2011-06-09 09:42 | 2011-07-13 | PART 21 NONCOMPLIANCE TO PERCENT ELONGATION REQUIREMENTS PER ASTM CODE Material used to fabricate standards used in ultrasonic testing failed to meet percent elongation standards per the code. Applied Technical Services has notified Areva. It is believed these standards were shipped to France from Areva in Aiken, S.C. NCR No. 2011-001; Corrective Action #2011-285 * * * UPDATE FROM JIM HILLS TO JOE O'HARA VIA FAX AT 1853 EDT ON 7/13/11 * * * Applied Technical Services determined that the questionable values did not affect the functionality of the standard. Notified R1DO(Dwyer), R2DO(Freeman), R3DO(Bloomer), R4DO(Cain), and the part 21 Group via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-06-09
46938 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-06-08 12:00 | 2011-06-09 09:10 | 2011-06-09 | AGREEMENT STATE - SHUTTER SEPARATED FROM GAUGE The following was received via fax: While removing the gauge the shutter became partially separated from the body. The source did not leave the gauge. The operator placed the gauge face down on the shutter assembly in a lead lined transport box. The gauge was surveyed and the max radiation field was 0.026 mR/hr. There was no exposure to personnel. The area was cordoned off and the manufacturer was notified to package and transport the device. The gauge was a Texas Nuclear Model 5193 S/N Bi449. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-06-14
46937 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-06-08 08:00 | 2011-06-08 14:12 | 2011-06-08 | SECONDARY CONTAINMENT INOPERABLE DUE TO VENTILATION ALIGNMENT ISSUE "Secondary containment was declared inoperable after transferring refuel floor supply fans. Secondary containment D/P [Differential Pressure] lowered to 0.17 inches of water vacuum which does not meet the surveillance requirement to have secondary containment vacuum greater than or equal to 0.25 inches of water vacuum. Refuel floor ventilation was restored back to the previous configuration and secondary containment D/P was restored back to greater than 0.25 inches of water vacuum. Vacuum was less than 0.25 inches of water for approximately 4 minutes. "There were no actual radiological releases associated with the event. "Actual secondary containment integrity was not challenged. The lowered secondary containment D/P was a result of a ventilation lineup change." The licensee has notified the NRC Resident Inspector and the State of Minnesota. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-06-08
46936 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-06-08 10:26 | 2011-06-08 12:08 | 2011-06-08 | NOTIFICATION OF UNUSUAL EVENT DUE TO FLOODING THAT POTENTIALLY AFFECTED SAFETY RELATED EQUIPMENT "Flushing activities were in progress on the 2A Auxiliary Feedwater (AF) Pump suction line from the Essential Service Water System (SX). At 1011 [CDT], during this flushing activity, the flushing hose ruptured and caused flooding in the Auxiliary Building that had the potential to affect safety related equipment needed for the current operating mode. This was due to the flood waters contacting the motors of the 1A and 2A AF Pumps. "At 1026, an Unusual Event was declared by the Shift Emergency Director because the conditions for EAL entry were met for EAL HU5. Specifically the EAL conditions were 'Flooding in the Auxiliary Building that has the potential to affect safety related equipment needed for the current operating mode.' Auxiliary Feedwater is required to be operable in Mode 1 for each unit. "The leak was immediately isolated (within 45 seconds of hose rupture) and remains isolated. Maintenance personnel are in the process of testing the 1A and 2A AF Pump motor to determine operability. The appropriate Tech Spec Action Statements have been entered on each Unit for the AF Pumps. The leak also caused the wetting of MCC [Motor Control Center] 132X1, which feeds the 1B AF Pump control power. The Unit 0 [Common] Component Cooling Pump feed breaker cubicle was also wetted. Investigation into these components are also in progress." The licensee has entered Technical Specification LCO 3.7.5 Condition A which requires restoration of the one of the AF pumps within 72 hrs. There were no personnel injuries. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT BUTLER TO HOWIE CROUCH AT 1227 EDT ON 6/8/11 * * * At 1122 [CDT] on 6/8/11, the Unusual Event was terminated due to the flooding conditions no longer existing. Evaluation of wetted components are still in progress. The NRC Resident Inspector has been notified of event. Notified IRD (Gott), R3DO (Lara), NRR EO (Thorp), FEMA (Blankenship), and DHS (Flinter). | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-06-08
46935 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-06-08 06:35 | 2011-06-08 08:25 | 2011-06-08 | INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Actual introduction of contraband into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-06-08
46934 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2011-06-07 13:49 | 2011-06-07 17:43 | 2011-07-29 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE DUE TO EXCESS OUTSIDE AMBIENT AIR TEMPERATURE "Outside ambient air temperature exceeded the maximum analytical value for operability for Unit 1 D1 and D2 Diesel Generators at 1349 CDT. The calculated limiting outside air temperature needed for equipment in the D1 and D2 rooms to meet their temperature limits is 100.5?F. Outside ambient temperature exceeded this limiting value and both Unit 1 safeguards diesel generators were declared inoperable at 1349 CDT on 6/7/2011. If outside ambient air temperature is above the maximum analytical value, components within the D1 and D2 diesel rooms may not be able to perform their required functions thus preventing them from fulfilling their safety function needed to mitigate the consequences of an accident (10 CFR 50.72 (b)(3)(v)(D)). "Unit 1 is currently in Mode 3, Hot Standby. Ambient outside air temperatures are at or near peak values for the day and expected to decrease approximately 1 to 2 degrees per hour which will restore ambient conditions to less than the maximum analytical value. "The NRC Resident Inspector has been notified." The outside air temperature has peaked at 101.4?F which is unusually high for this location and is expected to drop below the 100.5?F limit shortly. The licensee does not anticipate that this condition will be repeated again any time soon. * * * RETRACTION FROM STEVE INGALLS TO HOWIE CROUCH AT 1108 EDT ON 7/29/11 * * * "An eight hour report (EN #46934) per 10 CFR 50.72(b)(3)(v)(D) was made on June 7, 2011 for outside ambient air temperature exceeding the maximum analytical value for operability for Unit 1 D1 and D2 Diesel Generators. "Subsequent engineering analysis determined that D1 & D2 diesel generators would have performed their safety function with outside air temperatures of up to 102.5 degrees F. The outside air temperature did not reach 102.5 degrees F and the diesel generators were not inoperable. "The 10 CFR 50.72(b)(3)(v)(D) report, EN #46934, is retracted. "The NRC Resident Inspector has been notified." Notified R3DO (Giessner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-06-07
46933 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-06-07 08:00 | 2011-06-07 15:30 | 2011-06-07 | ERRORS IN METHODOLOGY USED FOR EMERGENCY CORE COOLING SYSTEM PERFORMANCE REQUIREMENTS "On Tuesday, June 7, 2011, at 0800 hours, Pilgrim Station reviewed General Electric Hitachi (GEH) 10 CFR 50.46 Notification Letters 2011-02 and 2011-03. These letters indicate that certain errors were discovered in the methodology application and inputs used by GEH for nuclear fuel core configurations with GE14 and GNF2 fuel, and when corrected may increase the Peak Cladding Temperature (PCT) limits in excess of 2200 degrees F under Loss of Coolant Accident (LOCA) conditions. Pilgrim's core contains both GE14 and GNF2 fuel. 10 CFR 50.46 paragraph (b) defines the acceptance criteria for the LOCA analysis process. The Pilgrim licensing basis PCT is evaluated for compliance with the criterion 50.46(b)(1) and must not exceed a PCT of 2200?F. "GEH had provided a compensatory measure in the form of multiplier to be applied to the MAPLHGR (Maximum Average Planar Linear Heat Generation Rate) limit so that Pilgrim operates within 50.46 limits. Entergy/Pilgrim implemented the compensatory measure and as a result the errors reported have no impact on current plant operation or public health and safety. This 8-hour notification is being reported for conservative purposes in accordance with 10 CFR 50.72 (b)(3)(ii)(B). "Based on 50.46(a)(3)(ii) criteria, Entergy/Pilgrim will submit a report within 30 days. "Entergy/Pilgrim has notified the NRC Senior Resident Inspector." The licensee also plans to notify the State of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-06-07
46932 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-07 09:40 | 2011-06-07 11:21 | 2011-06-07 | FIRE IN THE WEST SWITCHGEAR ROOM "At 0940 CDT an alert (HA 2, EAL 1) for operating Mode less than 210 degrees F [was] declared for a fire affecting the operability of plant safety systems required to establish or maintain safe shutdown. Time of fire was 0930 CDT. Control room received multiple alarms [and] 480 V bus 1B4A amps were observed to be oscillating. Bus 1B4A was secured [and] buses 1B3A and 1B3A-4A were lost. Halon activated properly. [At] 0956 CDT all notifications to applicable personnel were completed. At 1000 CDT 4160v buses 1A2 / 1A4 were secured to facilitate fire fighting. Spent fuel pool cooling was lost [as a result of the de-energized busses and the licensee] entered AOP-36 for loss of SFP cooling. Heat up rate [was] determined by STA. Current time to boil for SFP is 88.3 hrs. Spent fuel pool cooling is currently back in service. This condition is being reported pursuant to 10 CFR 50.72(a)(1)(i) for declaration of an emergency class specified in the licensee's approved emergency plan." Plant was in AOP-1 for flood mitigation. The fire is not believed to be flood related. Plant remains in AOP-1. At about 0930 CDT the licensee noted fire in the west switchgear room. The fire brigade responded and found a room filled with smoke but no active fire. Halon did discharge in the room. At 0956 CDT, offsite assistance was called and Blair Fire Department responded to the site. Blair Fire Department confirmed no active fire in the switchgear room. All offsite power remained available as well as the emergency diesel generators if needed. The licensee is currently attempting to ventilate the room. A thorough inspection of the affected area and determine the caused of the electrical fault will be facilitated once the room has been fully ventilated. The licensee has notified appropriate State and local government. The licensee notified the NRC Resident Inspector. A media or press release is also anticipated. * * * UPDATE FROM ROBERT KROS TO HOWIE CROUCH AT 1313 EDT ON 6/7/2011 * * * "Entered Alert for HA 3, EAL 1 access to a vital area (Switchgear and Turbine Building basement) due to toxic gases present from the fire in the West Switchgear room." The licensee entered HA 3 at 1144 CDT. Their exit criteria is that the switchgear room is cleared for unimpeded access. The licensee has notified the NRC Resident Inspector. Notified the R4IRC (Kennedy) * * * UPDATE FROM ROBERT KROS TO WILLIAM HUFFMAN 1421 EDT ON 6/7/11 * * * At 1315 CDT, Fort Calhoun Nuclear Station has exited Alert HA 2, EAL. It has been confirmed that no fire remained in the vital area. Plant shutdown cooling remained in-service and spent fuel pool cooling was restored and temperature verified to be lowering. The licensee has also exited Alert HA 3, EAL 1 after it was confirmed that the environmental conditions from the event and associated Halon discharge does not affect the ability to safely operate or safely shutdown the reactor due to being in Mode 5 and shutdown cooling remaining in-service. Fort Calhoun remains in Unusual Event HU 1, EAL 5 for River Level greater than 1004' elevation as reported under EN #46929. The licensee has notified appropriate State and local government. The licensee has also notified the NRC Resident Inspector. The NRC made notifications of the event termination to DHS, FEMA, DOE HHS and USDA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | ALERT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-06-07
46931 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2011-03-30 18:00 | 2011-06-06 20:34 | 2011-07-19 | AGREEMENT STATE REPORT - EXTREMITY OVEREXPOSURE DURING LABORATORY WORK The following information was provided via e-mail from the Washington State Department of Health, Office of Radiation Protection: "A Nuclear Medicine technologist received an overexposure to her extremity dosimeter for March 2011 while working in the basement of the Magnusen Health Sciences Building on the UW Campus. The Extremity Dose was reported as 56,440 mrem. During the month of March, she performed several cell-labeling procedures involving 75mCi, 111mCi, and 108mCi amounts of Y-90. There were also several labeling procedures involving the use of I-131 during the same time frame. However, because the whole body badge showed no significant exposure, it is believed the majority of the exposure came from the technologist's work with Y-90. "Licensee: University of Washington "City and State: Seattle, WA "License Number: WN-C001-1 "Type of License: Broad A "Date and time of Event: March 1 - March 30, 2011 "Location of Event: UW Magnusen Health Sciences Building "Investigation is ongoing." Washington Report #WA-11-030 * * * UPDATE ON 7/19/11 AT 1330 EDT TO HUFFMAN FROM THE STATE OF WASHINGTON VIA E-MAIL * * * "On 6 June 2011, the department [Washington Division of Radiation Protection] received notification via letter from the University of Washington (UW) that an employee, had received an extremity dose to the left hand of 56,440 mrem from Yttrium 90 for the month of March 2011. The department [Washington Division of Radiation Protection] was notified that the employee retired in May 2011. "An incident number WA-11-030 was assigned to the event. UW informed the technician of the overexposure and she agreed to meet to discuss the incident. "On 15 June 2011, a Health Physicist from the Department of Health met with the UW RSO, a UW Health Physicist, and the technician to discuss the incident. "The Y-90 comes in bulk and must be divided into smaller aliquots based on the desired dose for cell labeling. These aliquots must be handled several times during the cell labeling procedure by the technician. The small size of the aliquot tubes made it too difficult to use tongs or other devices that might have lessened their exposure during these parts of the procedures. Most of this work was done in a hood behind shielding so that the whole body dose remained normal. "Because the technician is right-handed, she would most often hold the tube containing the Y-90 in the left hand so she could use their right hand to add reagents or pipette the Y-90 solution into another tube. Although the exposure to the right hand did not exceed the annual limit, it was also unusually high for the month of March, 10.85 REM. "The technician stated that there was no spill or other unusual occurrence during the month of March. It is highly unusual to do multiple labeling procedures in a one month period and March 2011 is the only time she has done three in one month. The amounts received, 75mCi, 111mCi, and 108 mCi were also larger than average. There were also several procedures involving the use of large doses, up to 1 Ci, of I-131 in March. However, this was not out of the ordinary for the technician so it is believed to be more likely that the multiple labeling procedures involving Y-90 contributed to exceeding the annual exposure limit to the left hand. "Although, the technician is required to do surveys of the lab, the lab only has access to a GM detector and the area readings in the lab are often higher than background because of the large quantities of nuclides on hand. It is difficult for the technician to determine if contamination exists because of these high area readings. No swipe surveys are done by the technician. Swipe surveys are done by the radiation safety office staff. The last survey in which swipes were taken was January 2011. No contamination was noted at that time. The dose reconstruction was done to verify that the technician could in fact have received the reported dose given the time frame the technician was working with the Y-90. The dose reconstruction was also done to eliminate the possibility that the dose recorded by the ring dosimeter could have been caused by the ring being contaminated by Y-90 and that contamination remaining on the dosimeter. It was concluded by the UW RSO and the department [Washington Division of Radiation Protection] that handling these amounts of Y-90 could result in a dose of 56.4 REM in a very short period of time. Therefore, it is the conclusion of this investigation that the reported exposure is real. "As a result of this investigation, the technician has been informed that she cannot work in an environment which would further contribute to her 2011 radiation dose. Because she is retired and no longer employed as a radiation worker at any facility, this should not be a hardship. It was determined that although the technician received an exposure above the legal limit, it is unlikely to result in any adverse health effects and no medical intervention is warranted. "The Y-90 labeling has been halted at UW. No other person has done a labeling of this kind since the technician's retirement. No further work of this kind will take place at UW until a complete reworking of the procedures is completed and submitted to the Department, and their own RSC, for approval. "This incident is closed." R4DO (Campbell) and FSME EO (Zelac) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2011-06-09
46930 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-06-06 09:00 | 2011-06-06 16:26 | 2011-06-06 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR A contractor supervisor had a confirmed positive for an illegal substance during a random fitness-for-duty test. The employee's access has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2011-06-06
46929 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-06-06 08:00 | 2011-06-06 09:12 | 2011-08-29 | UNUSUAL EVENT DECLARED DUE TO RIVER LEVEL "At 0800 CDT a Notification of Unusual Event (HU 1, EAL 5) for operating mode less than 210 degrees F is being declared for a river level expected to exceed a 1004' MSL (Mean Sea Level), but less than or equal to 1009' MSL elevation. Currently Abnormal Operating Procedure AOP-1 is being implemented for high river level, as well as, PE-RR-AE-1001 for Flood Barrier and Sandbag Staging and Installation. This condition is being reported pursuant to 10 CFR 50.72(a)(1)(i) for declaration of an emergency class specified in the licensee's approved emergency plan. Applicable governmental agencies have been notified per plant procedures. No press release is expected at this time." * * * UPDATE FROM ERICK MATZKE TO PETE SNYDER AT 1121 EDT ON 6/6/2011 * * * "During the emergency notification the automated paging function did not cause the pagers to actuate. The issue is being investigated." A notification for 10 CFR 50.72(b)(3)(xiii) be added to the header. Notified R4DO (Whitten). * * * UPDATE FROM ERICK MATZKE TO HOWIE CROUCH AT 1305 EDT ON 6/6/2011 * * * "OPPD will be making a press release for this event at about 1220 CDT." The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Whitten) and HQPAO (Brenner). * * * UPDATE FROM AMY BURKHART TO HOWIE CROUCH AT 1449 EDT ON 8/29/11 * * * "At 1342 CDT on 08/29/11, FCS [Fort Calhoun Station] terminated the Notification of Unusual Event for flooding. Missouri river level receded to less than entry criteria and is currently 1003.56 ft MSL." The licensee has notified the State of Nebraska, Harrison County, Washington County, and Pottawattamie County of the termination. Notified R4DO (Proulx), IRD (Marshall), NRR (Thorp), DHS (Rickerson), and FEMA (Dennis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(xiii) |  |  | 0 | 2011-06-06
46928 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2011-06-06 03:29 | 2011-06-06 07:04 | 2011-06-06 | ERROR DURING REACTOR PROTECTION SYSTEM SURVEILLANCE LEADS TO REACTOR TRIP "On June 6, 2011, during the performance of Reactor Protection System Logic Matrix Testing, a Reactor Trip occurred. All CEA's [Control Element Assemblies] fully inserted into the core. Decay Heat removal was initially from Auxiliary Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently maintaining pressurizer pressure at 2250 psia, temperature maintaining at 532 degrees F. Auxiliary Feedwater actuated as designed. As of 0435, decay heat removal is via Main Feedwater and Steam Bypass control to Main Condenser. "During the transfer of Auxiliary Feedwater to Main Feedwater a second AFAS actuation occurred. "Unit 1 was unaffected and remains in Mode 1 at 100% power. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip, as well as 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Auxiliary Feedwater)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-06-06
46927 | 0 | ENI US OPERATING COMPANY |  |  |  |  | 2011-06-04 | 2011-06-05 16:11 | 2011-06-05 | FIXED PROCESS GAUGE FAILED SEMI-ANNUAL SHUTTER TEST A Tracerco 600DP series nuclear gauge licensed to ENI US Operating Company failed a semi-annual shutter test on June 4, 2011. The gauge is located at Oliktok Production Pad, Oliktok Point, Alaska. Specifically, the RSO for the gauge stated that the extension rod (attached to the arming rod with the cesium source) could not be withdrawn sufficiently to move the source behind the shutter mechanism. Binding of the arming and/or extension rods could be felt in attempts to move the source behind the shutter mechanism. Mechanical restrictions were felt as the RSO successfully returned the source to its in-service position following the failed shutter test. The gauge is currently in-service and there is no immediate operational or safety requirement to lock this gauge out. Tracerco has been notified of the deficiency by phone. Tracerco will provide a technician to repair this discrepancy. The 600DP gauge houses a 925 MBq Cs-137 source with serial #RM510. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-06-05
46926 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-06-05 12:02 | 2011-06-05 15:46 | 2011-06-05 | OFFSITE NOTIFICATION OF A SEWAGE SPILL INTO A STORM DRAIN "On June 5, 2011 at 1202 [EDT] the Hope Creek Shift Manager was notified of a sewage spill at the site sewage treatment plain. Approximately 1000 gallons of intimated sewage entered a nearby storm drain. The onsite Fire Department responded to the scene to contain the spill. Offsite support from a local sanitary waste disposal vendor was requested who responded to the site to assist in the cleanup. "A 15 minute notification to the State of New Jersey Department of Environmental Protection was required and completed on June 5, 2011 at 1214 [EDT]. "At 1320 [EDT] the sewage input into the storm drain was terminated. Site personnel continue with the cleanup, with support from the vendor. The spill had no effect on plant operations and the unit remains at 100% power. "The station has initiated as investigation to determine the cause of the sewage spill, and initiate immediate corrective actions. No personnel injuries resulted from the event "The NRC resident inspector has been notified. Lower Alloways Creek Township has been notified." * * * UPDATE FROM KEPLEY TO HUFFMAN AT 2017 EDT ON 6/5/11 * * * "Hope Creek has determined that the spill reported to the New Jersey Department of Environmental Protection on 6/5/11 at 1214 [EDT] was not reportable. The spill was considerably smaller than originally believed, and it did not enter the river. "Cleanup and pump out of sewage that entered the storm drains is complete. Additionally the sewage that spilled to the ground is also being cleaned up. [The licensee's] site environmental personnel will follow up with NJDEP Southern Enforcement personnel tomorrow morning. To confirm, this spill is not reportable." The licensee states that the spill is now estimated at approximately 25 gallons. The NRC Resident Inspector will be notified. R1DO (Conte) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-06-05
46925 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-06-04 16:14 | 2011-06-04 23:05 | 2011-07-22 | BOTH CONTROL STRUCTURE CHILLERS OUT OF SERVICE "On 06/04/2011, personnel observed the temperature control valve for the 'B' control structure chiller not operating properly. To investigate control valve operation, the controller was taken to the manual mode (from automatic) at 1614 [EDT]. The control valve stem was lubricated, and the valve was operated with the controller in the manual mode. The 'B' control structure chiller was inoperable in this condition until control valve responsiveness was validated (total of 35 minutes, until 1649 [EDT]). The 'B' chiller continued to operate during this period. "The 'A' control structure chiller was out of service during this timeframe to perform maintenance activities. Hence, neither chiller was operable. "The control structure chillers provide control building habitability during unit operation. The control structure chillers also provide cooling water for emergency switchgear room cooling on unit one only. "This condition is being reported as an event or condition that could have prevented fulfillment of a safety function per 10CFR 50.72(b)(3)(v)(D)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 7/22/2011 AT 1519 FROM LONNIE CRAWFORD TO MARK ABRAMOVITZ * * * "On June 4, 2011, Susquehanna reported the simultaneous inoperability of both control structure (CS) chillers as an event or condition that could have prevented fulfillment of a safety function in accordance with 10CFR 50.72(b)(3)(v)(D). After further investigation, Susquehanna has concluded that the 'A' and 'B' CS chillers were not inoperable at the same time. "On June 3, 2011 at 1608, fluctuating amperage was observed on the 'A' CS chiller and the chiller was declared inoperable. As a result, the 'B' CS chiller was placed in service with the 'A' CS chiller placed in standby. Subsequent troubleshooting of the 'A' CS chiller included replacing the chiller temperature controller with a spare while the original controller was evaluated in the shop. The original controller was re-installed on June 4, 2011 at approximately 1030 but did not resolve the issue. The 'A' CS chiller was later shutdown and removed from standby on June 4, 2011 at 1727. "Originally, Susquehanna believed that the fluctuating amperage on the 'A' chiller was an operability issue. Subsequent engineering evaluation has determined that the observed oscillations were not rapid enough and did not have sufficient amplitude to cause damage to the chiller motor and were within design limits. The conclusion is that the 'A' control structure chiller was operable and would continue to operate for its 30 day mission time with the observed current oscillations. Although the 'A' chiller was inoperable as a result of troubleshooting at various times on June 3 and 4, the 'A' chiller was available and operable during the short period of time on June 4 when the 'B' chiller was inoperable. . "Based on the above information, this ENS report is retracted." The licensee notified the NRC Resident Inspector. Notified the R1DO (Dentel). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-06-04
46924 | 0 | FLOWSERVE LIMITORQUE ACTUATORS |  |  |  |  | 2010-09-28 | 2011-06-03 16:30 | 2011-07-15 | POSSIBLE DEFICIENCY IN ENVIRONMENTAL TESTING OF LIMITORQUE GEARED LIMIT SWITCH FOR INSIDE CONTAINMENT The following is a summary of a Part 21 fax notification received from Flowserve-Limitorque Actuators: This Part 21 evaluation is for Geared Limit Switch - Nylon Bearing Retainer Cage. Flowserve has provided the NRC an interim report that provides information concerning an evaluation that is being performed by Flowserve - Limitorque regarding a possible deficiency in previous EQ test programs which qualified Limitorque SMB-000 & 00 actuators to IEEE-382 requirements for inside containment service. An investigation to date has revealed that the non-metallic retainer cage material of the radial ball bearing may not have been properly considered when determining thermal aging requirements during EQ testing. The safety related component affected is the geared limit switch (GLS) assembly on actuator type / size Limitorque SMB/SB/SBD-000 and SMB/SB/SBD-00 only qualified for inside containment to Limitorque EQ report number B0058 and B0212. The sub-component of the GLS under evaluation is a radial ball bearing (manufacturer's part # 1604-DC and 7304-DC) manufactured by Nice / RBC Bearing Corp / SKF which has been used in the cartridge assembly. This bearing provides partial support to the input pinion shaft of the GLS. This bearing was manufactured with a nylon (polyamide 6/6) retainer cage. a) This bearing is used on the 2-train and 4-train geared limit switch cartridge assembly of the SMB/SB/SBD-00 and the 4-train GLS cartridge of the SMB/SB/SBD-000 only. b) The GLS assembly used in SMB/SB/SBD-0, 1, 2, 3, 4 & 5 actuators use a slightly different cartridge construction that does not contain this bearing. The functionality of the cartridge bearing in the GLS assembly may not have been properly validated in an accident environment test with the non-metallic nylon material properly thermally aged to "end of life" condition. Limitorque is continuing the evaluation of this issue in an effort to finalize this position. At this point of the evaluation, Limitorque does not feel that the safety related function of the subject actuators will be affected by the existence of the nylon bearing retainer cage in the GLS assembly. Limitorque will continue the evaluation of this issue and will submit a status update on or before July 15, 2011. To date, the use of the nylon cage bearing in the GLS assembly has shown no negative affects on operability of the switch. * * * UPDATE ON 7/15/11 AT 1500 EDT BY HUFFMAN * * * The following information was received from Flowserve Limitorque Actuators via e-mail: "As identified in the interim report above, the SMB-000 & 00 geared limit switch assembly contains a ball bearing which includes a nylon ball retainer cage. A review of previous EQ testing identified that the retainer cage material may not have been thermally aged to an end of life condition prior to High Energy Line Break / Main Steam Line Break exposure. The concern was that degradation of the retainer cage could result in loss of functionality of the limit switch assembly in safety related applications. "This bearing is a subcomponent of the geared limit switch (GLS) assembly. The purpose of the bearing is the partial support of the input pinion shaft of the GLS cartridge. The input pinion shaft connects the GLS to the mechanical drive train of the actuator. This shaft is also supported by a bronze sleeve bushing in the cartridge. The purpose of the retainer cage in a radial ball bearing is to position the individual balls in the bearing assembly. As part of the evaluation, a sample bearing was installed in a GLS cartridge. Subsequently, the nylon ball retainer cage was intentionally removed from the bearing to simulate a worst case scenario of total degradation of the retainer cage. The removal of the ball retainer cage and the subsequent uncontrolled alignment of the individual balls inside the ball bearing race did not result in loss of GLS functionality. The input pinion shaft remained adequately supported by the sleeve bushing such that it is reasonable to conclude the GLS would perform its safety related function. "To further evaluate the adequacy of the nylon retainer cage equipped bearing for the accident environment, a thermal screening test of an SMB-00 geared limit switch assembly containing the subject bearing was performed. This test consisted of continuous exposure to a 340?F ambient temperature while cycle testing the limit switch. The test was halted after 270 hours (11.25 days) and 1600 operational cycles without failure. Post test inspection showed that the nylon retainer cage remained intact and functional which indicates that the degradation of the bearing discussed above is highly unlikely. No loss of functionality of the limit switch occurred during the test indicating acceptability of the bearing for the application. This screening test is documented in report # STLO-1125 retained on file and available for audit at Flowserve - Limitorque "Based upon the evaluation described above and the existing EQ test data, Limitorque has determined that this issue is not reportable under 10CFR21 guidelines. The investigation has shown that in the unlikely event of degradation of the bearing retainer cage, safety-related functionality of the geared limit switch assembly will not be affected. Environmental qualification of the SMB/SB/SBD-000 & 00 actuators by Limitorque EQ reports B0058 and B0212 remains valid." R1DO (Dwyer), R2DO (Freeman), R3DO (Bloomer), and R4DO (Cain) notified. The Part 21 Group was informed via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-06-03
46923 | 0 | VELAN INC |  |  |  |  | 2011-04-12 | 2011-06-03 16:30 | 2011-06-03 | POTENTIAL DEFECT IN CERTAIN VELAN SUPPLIED GLOBE VALVES The following is a summary of a Part 21 e-mail notification received from Velan Inc: Velan Inc., a valve vendor, has identified a potential defect in certain lots of 0.5, 0.75 and 1 inch NPS globe valves sold to Areva and Fenoc. The failure could result in the valve travelling into the bonnet cavity and became jammed between body and bonnet. The analysis revealed that the failure was caused by the wrong bonnet being installed on the valve which ultimately allowed the disc to travel too far into the bonnet cavity and consequently the disc dropped into the body-bonnet gap. This prevented the valve from being closed during manual operation. Internal analysis also determined that this failure mode is very plausible in valves installed with the stem in a horizontal orientation. Valves installed with the stem in vertical orientation are far less likely to fail but we cannot guarantee that; on valves that are normally fully open certain flow conditions may cause the disc to tilt and jam between body and bonnet. Nevertheless, operational history seems to suggest that valves installed with the stem in vertical orientation have not experienced this type of failure. Velan has requested that each affected utility reviews the individual applications for the specific valves identified in this notification; in the event of any application where the valves inability to close will impact significantly the safe operation of the plant. Velan will work with the utility towards reaching a suitable solution. Velan does not have specific information concerning the specific system and function applicable to these globe valves and therefore we cannot assess whether a substantial safety hazard exists as a result of their inability to close after falling as described above. Velan's investigation and review of the available manufacturing records revealed that the same bonnet, with an oversized lift, was installed in all valves identified hereunder. CUSTOMER ORDER QTY. VALVE FIGURE No. VALVE SERIAL No. AREVA NP 8 W04-2074B-02AA 971022-1 to-8 AREVA NP 12 W03-2074B-02AA 971042-1 to -12 AREVA NP 27 W04-2074B-02AA 971048-1 to -27 AREVA NP 5 W03-2074B-02AA 981028-1 to-5 AREVA NP 5 W03-20748-02AA 981030-1 to-5 AREVA NP 10 W05-20748-02AA 001012-1 to-10 AREVA NP 13 W03-20748-02AA 001029 -1 to -13 AREVA NP 26 W04 20748-02AA 001056 -1 to -26 ARE VA NP 10 W04-20748-02AA 011035-1 to-10 FENOC 4 W05-2074B 02AA 001033 -1 to-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2011-06-03
46922 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-31 | 2011-06-03 16:44 | 2011-06-03 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The following information was received via e-mail from the Texas Department of State Health Services concerning an event that occurred at the Calaveras Power Station in San Antonio, Texas: "On June 3, 2011, at 1330 CDT, the agency [Texas Department of State Health] received a phone call from the licensee's Radiation Safety Officer reporting a fixed nuclear gauge failure. He stated that on Tuesday, May 31, 2011, the licensee's employees had closed the gauge shutter while they were calibrating the detector. When one of the employees attempted to re-open the shutter, the employee said he felt something 'sort of give' and the shutter would not open. The handle was loose. The RSO was called and he came to the location of the gauge. He checked the handle and it was loose, so rather than try to open the gauge he left it closed. He verified that the shutter was completely closed by performing a survey with a portable survey meter. The equipment the gauge was mounted to was not necessary to be in operation so it was shut down until the gauge could be repaired. "On Friday, June 3, 2011, ThermoFisher Scientific (TFS) service came on-site and repaired the handle. The RSO stated that the TFS said the pin at the bottom of the handle had corroded and broke. The pin that holds the handle to the mechanism that opens/closes the shutter is inside the gauge housing. Gauge is a K-Ray Model, 7062BP, serial number 27118E, which contains a 50 millicurie cesium -137 source. "An investigation by the licensee into the cause and potential corrective actions in underway." Texas Report I-8860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-06-08
46921 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-06-02 | 2011-06-03 15:40 | 2011-06-03 | AGREEMENT STATE REPORT - DELIVERED DOSE DIFFERENT THAN PRESCRIBED DOSE The following information was sent by the State of Florida Bureau of Radiation Control via email: "[On June 2, 2011], a patient with over 100 tumors was being treated. One lesion was supposed to get 16 gray, but received only .85 gray. The physicist forgot to adjust for the weight factor. The physicians have been notified. The patient will receive the correct dose during the next visit. The licensee will submit a written report to the Radioactive Materials. Any further action is referred to Radioactive Materials. No further action will be taken on this incident by this office." The patient was undergoing Gamma Knife Stereotactic Radiosurgery using 3073 Ci of Co-60. Florida Incident: FL11-046 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-06-09
46920 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-06-03 | 2011-06-03 15:19 | 2011-06-03 | AGREEMENT STATE REPORT - MISSING DEVICES POSSIBLY MIXED WITH SCRAP METAL The following information was sent by the State of Florida Bureau of Radiation Control via email: "[The licensee's two] fill detectors were bought in the 1990's and were not in use. The fill detectors were stored in a spare room full of scrap metal. The room was cleaned out in early May and the scrap sent to Alpha Metal Recycling, 2392 NW 147 Street, Opa-Locka, Florida 33054. The recycling plant manager said that the load has already been sent overseas to either China, Pakistan or India. Loss of the material was found when the application for license renewal was being filled out. The licensee will send a written report to Radioactive Materials. Any further action is referred to Radioactive Materials. This office will take no further action on this incident." The two fill detector sealed sources each contained 100 mCi of Am-241 and were manufactured by Industrial Dynamics (Fil Tech; Model Number FT50; Serial Numbers 1296 and 126). Florida Incident: FL11-045 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-06-08
46919 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-06-03 10:21 | 2011-06-03 12:06 | 2011-06-03 | AUTOMATIC SCRAM FOLLOWING A TURBINE TRIP "Limerick Unit 1 automatically scrammed from 100% power at 1021 EDT hrs on 6/3/11. The RPS actuation occurred as designed upon an automatic trip of the Main Turbine. The cause of the Main Turbine trip is under investigation. Plant response to the Main Turbine trip was per design without complications. "All control rods fully inserted. No ECCS or RCIC initiations occurred. No Primary or Secondary Containment isolations occurred. "The plant is currently in Hot Shutdown with the normal Feedwater system maintaining reactor water level, and the Main Turbine Bypass valves maintaining reactor pressure. "Limerick Unit 2 was unaffected." The post-scram electrical alignment is normal. The licensee has notified the NRC Resident Inspector and plans to notify appropriate state and local authorities. The licensee is also planning a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-06-03
46918 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-06-02 13:25 | 2011-06-03 11:20 | 2011-06-03 | CONTRACTOR SUPERVISOR ATTEMPTS TO SUBVERT FITNESS FOR DUTY TEST A non-licensed supervisory contractor admitted to attempting to subvert a Fitness for Duty test. The contractor's access to the site has been suspended. The NRC Resident Inspector was notified. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2011-06-03
46917 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2011-06-03 00:39 | 2011-06-03 05:54 | 2011-07-26 | UNEXPECTED EMERGENCY DIESEL GENERATOR ACTUATION "On 6/3/2011 at 0039 hours, during the performance of a work order to test components associated with Service Water Isolation, Emergency Diesel Generator (EDG) 'A' unexpectedly started automatically and its supply breaker to Safeguards Bus 14 closed. The Control Room staff observed normal voltage on Diesel Generator 'A'. Bus 14 voltage was never lost during this event, however, they also noted an associated Bus 14 undervoltage annunciator on the Main Control Board. Seconds later, Emergency Diesel Generator 'A' tripped on Reverse Power and its supply breaker to Bus 14 tripped open. The initiating action was the removal of the Bus 14 Normal Feed Breaker Control Power Fuses as part of the work order package. "The Ginna EDG's have the following automatic start signals and logic: manual, safety injection signal (1/2 trains), undervoltage on respective safeguards bus, 'A' EDG Bus 14 or 18 (1 out of 2 degraded voltage + 1 out of 2 loss of voltage), 'B' EDG Bus 16 or 17 (1 out of 2 degraded voltage + 1 out of 2 loss of voltage). "Investigation has commenced to determine the cause of the EDG start and undervoltage signal. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 7/26/11 AT 1214 EDT FROM SLABY TO HUFFMAN * * * "The purpose of this report is to retract the event discussed in Emergency Notification System report #46917 submitted on June 3rd, 2011. The ENS notification reported an unexpected start of Emergency Diesel Generator `A' during testing of a service water valve isolation circuit. As reported, Emergency Diesel Generator 'A' unexpectedly started and its supply breaker to Bus 14 closed. Seconds later, the Emergency Diesel Generator tripped on reverse power and its output breaker to Bus 14 opened. At the time of the event it was not understood why the diesel generator started. Subsequent troubleshooting and causal investigation identified that the signal was caused by a degraded control relay that unexpectedly changed state when control power was removed. This relay was expected to remain mechanically latched and would have remained in the desired position had control power not been removed as part of the test. Bus 14 voltage remained in the normal operating range throughout the event. Since this was not a valid undervoltage signal, the June 3rd, 2011 event is being retracted. A follow-up report will be made in accordance with 10CFR50.73(a)(1) and 10CFR50.73(a)(2)(iv)." The NRC Resident Inspector has been notified. R1DO(Henderson) notified. See related EN #47094. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-06-03
46916 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-06-02 21:15 | 2011-06-02 23:07 | 2011-06-17 | SAFEGUARDS REPORT- LOSS OF CONTROL OF SAFEGUARDS INFORMATION Safeguards information was lost and uncontrolled for a period of time and then recovered. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/17/11 AT 1717 FROM BILL ARENS TO PETE SNYDER * * * Upon further review it was determined that the subject information was not lost or uncontrolled but rather unattended for only a short period of time. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-06-02
46915 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-06-01 15:15 | 2011-06-02 14:50 | 2011-06-02 | MEDICAL TREATMENT WITH CONTAMINATION "An employee was treated in the site dispensary for irritation to the eye. The employee's coveralls, knee area, and boots were surveyed and determined to be contaminated (coveralls 2,643 dpm per 100 cm2 [centimeters-squared], boots 3,126 dpm per 100 cm2). Employee stated that they were cleaning out the bottom of the cone on A1 HF filter bowl from the top of the filter when something entered their eye. The individual stated that they saw a small amount of dust in the bottom of the filter bowl, but did not actually see dust near their eye. Other employees were present at the time but, did not notice what had occurred and the affected employee did not tell them what had happened. The individual returned to work after treatment." The licensee will be making a notification to NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-06-02
46914 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2011-06-02 10:07 | 2011-06-02 14:09 | 2011-06-02 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR A contractor supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2011-06-02
46913 | 0 | DOW CORNING |  |  |  |  | 2011-05-31 17:00 | 2011-06-02 10:38 | 2011-06-02 | PROCESS INSTRUMENT SHUTTER FAILURE During a routine semiannual periodic inspection, a process gauge with a 15 milliCurie Cs-137 source was identified to have a stuck shutter. The gauge was an Ohmart Model SHF1-A45, S/N 09236K. The instrument is permanently installed on a distillation column about 30 - 35 ft. from the ground. The integrity of the gauge is fine. Surveys indicated that radiation levels surrounding the gauge were less than 1 millirem per hour. The licensee plans on having the gauge repaired by the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-06-02
46912 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-06-01 08:45 | 2011-06-02 09:32 | 2011-06-02 | EMPLOYEE SUFFERING CHEST PAINS TRANSPORTED OFFSITE "A contract employee complained of chest pains. The individual was taken into the dispensary and then transported to a local medical facility by ambulance. The individual had been performing janitorial duties at the time of the occurrence. The individual had approximately 12,700 dpm per 100 cm2 [centimeters-squared] contamination on the bottom of plant issued shoes. "There was no other contamination detected on the individual's plant clothing or person. Before being transported to the offsite medical facility the individual's shoes and plant clothing were removed. The individual was free of contamination before being transported to the offsite medical facility. "Subsequently the individual was released from the medical facility and released to return to work." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-06-02
46911 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-06-01 14:00 | 2011-06-02 07:49 | 2011-06-03 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE DAMAGED AT A LANDFILL The following information was received via fax: "The licensee's portable density gauge operator was performing compaction studies with a Troxler Model 3430 on the slopes of a landfill. The source was in the locked position and the operator was present and standing about 30 feet away. A bulldozer came up over the slope and impacted the gauge. The gauge was intact except for damage to the shutter. The operator immediately contacted the RSO who responded to the site with a survey meter within minutes. Readings were within guidelines. The gauge was returned to its case, and loaded for transport. The RSO surveyed the area to check for contamination. No elevated readings were found. The gauge is in its locked storage area pending instructions from Troxler." NJ Report ID No. NJ11004 * * * UPDATE FROM CATHERINE BIEL TO VINCE KLCO ON 6/3/2011 AT 1530 EDT * * * The gauge electronics and outside cover were crushed and the shutter was damaged. However the source housing and the source rod were not damaged and were intact. Notified the R1DO (Conte) and FSME (Von Till). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-06-07
46910 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-05-01 | 2011-06-01 17:03 | 2011-06-01 | AGREEMENT STATE REPORT - PORTABLE NUCLEAR GAUGE STOLEN AND THEN RECOVERED The following information was received by fax: "On May 31, 2011 the Department [Wisconsin Radiation Protection Section] received notification via email from the licensee's RSO that the licensee had reported a portable nuclear gauge stolen from their storage location in Lodi, WI (Columbia County). The Department called the licensee for additional information on June 1, 2011. The gauge was a Seaman model R-50 roofing gauge containing a maximum of 40 mCi of Americium-241:Be. In the call the licensee stated that on May 1, 2011 they had discovered their storage location had been broken into, their security barriers to the gauge had been defeated, and their portable nuclear gauge had been removed from the premises. Law enforcement had been notified on May 1, 2011 and investigated the theft. The gauge was recovered on May 28, 2011 in Madison, WI and had already been returned to the licensee at the time this conversation took place. The Department performed a reactive inspection on June 1, 2011, and confirmed that the gauge was recovered in good condition and placed in secure storage. The Department is waiting for additional information regarding this theft from both the Madison Police Department and the Columbia County Sheriff's Office." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-06-06
46909 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-06-01 13:15 | 2011-06-01 17:07 | 2011-07-26 | BOTH TRAINS OF COMPONENT COOLING WATER DECLARED INOPERABLE DUE TO VOIDING "At 1315 (CDT), while in Mode 3 at normal operating pressure and 552?F, both trains of Component Cooling Water (CCW) were inoperable due to indications of voiding. The 'A' Train CCW had been declared inoperable at 1000 (CDT) when review of pump test data indicated a potential void and Technical Specification LCO 3.7.7, 'Component Cooling Water (CCW) System,' Condition A was entered. At 1315 (CDT), indications of voiding were identified in the common service loop piping, which was aligned to the 'B' Train CCW. The 'B' Train CCW was declared inoperable and the plant entered LCO 3.0.3 due to both CCW Trains being inoperable. "At 1410 (CDT) plant cool down to Mode 4 was commenced. The 'A' Train CCW has subsequently been vented and void volume is currently within allowable limits for operability. However, further evaluation of this voiding is underway prior to declaring the 'A' Train CCW operable." The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 7/26/11 AT 1305 EDT FROM ISCH TO HUFFMAN * * * The licensee is retracting this event based on the following: "Further engineering evaluation concluded the amount of gas ingested by the 'A' CCW pump would not cause any degradation to the pump. The remainder of the gas in the system was less than the acceptance criteria for the CCW system. The 'A' CCW train was capable of performing its specified safety function and therefore would have been considered operable. The condition would not have prevented the CCW System from fulfilling its safety function and would not be reportable under 10 CFR 50.72." The licensee has notified the NRC Resident Inspector. R4DO (Gaddy) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2011-06-01
46908 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-05-31 11:45 | 2011-06-01 13:05 | 2011-06-01 | AGREEMENT STATE REPORT- DAMAGED RADIOGRAPHY SOURCE RETRIEVAL GUIDE TUBE The following information was received by fax: "Radiographers set up a shot on a 2 inch diameter pipe which was laying in jackstands. They were working with a SPEC 150 exposure device containing a 42 Ci Iridium-192 sealed source. The jobsite was a large laydown yard in an industrial setting. The pipe fell from the stands and hit the guide tube. The guide tube was hit about 2 inches from the exposure end, and attempts at retracting the source were unsuccessful. The radiographers re-established boundaries and contacted the local [Assistant] RSO (ARSO) from the new boundary at approximately 1200 [EDT]. The ARSO is authorized to perform source retrieval for JANX. [The licensee] maintained surveillance while awaiting his arrival. The ARSO arrived onsite at 1240 [EDT], assessed the situation and interviewed the crew. He noted that the source tube appeared to have 2 crimps. The ARSO was in contact with the Corporate RSO in Michigan during the operation. "The ARSO used lead blankets to shield the source and surveyed. Survey revealed need for more shielding that was delivered to the site by [1345 EDT] and acceptable dose rate was achieved. He proceeded to remove the crimped section from the guide tube, observed that the drive cable was unaffected, connected the tube together with tape, and was able to retract the source into the exposure device. The event concluded by [1520 EDT]. The licensee will be making a full report with corrective actions within 30 days of the occurrence." New Jersey Event: NJ 11003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-06-06
46907 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-06-01 08:18 | 2011-06-01 11:08 | 2011-06-01 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO VENTILATION CONDENSER UNIT FAILURE "The Technical Support Center (TSC) has been rendered non-functional due to a malfunctioning TSC ventilation system. Investigation into the cause of elevated TSC room temperature led to the discovery of a malfunctioning condensing unit compressor. Repairs to the ventilation system were immediately initiated with high priority. "Compensatory measures per FNP-0-EIP-6.0 (TSC Setup and Activation) for maintaining emergency assessment, off-site response, and off-site communication capabilities are being put in place. These measures include the conditional relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC to be uninhabitable." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-06-01
46906 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-05-30 11:50 | 2011-05-30 15:46 | 2011-05-30 | SPECIFIED SYSTEM ACTUATION - MANUAL REACTOR SCRAM DUE TO DUAL RECIRC PUMP TRIP DURING STARTUP "Limerick Unit 2 was 'manually scrammed' from 0% power on 5/30/11 at 1150 hours in accordance with plant procedure OT-112 'Recirculation Pump Trip', when both the '2A' and '2B' Recirculation Pumps tripped. The cause of the pump trip is currently under investigation at this time. "At the time of the 'manual' SCRAM: The Reactor Mode Switch was in 'Startup' Mode 2. All control rods were inserted to 'full-in' position (00). Reactor Shutdown was in-progress in accordance with Plant procedure GP-3 'Normal Plant Shutdown'. No primary or secondary containment isolations occurred. "The plant is currently in HOT SHUTDOWN maintaining normal Reactor level with Control Rod Drive (CRD) hydraulic and Reactor Water Cleanup (RWCU) systems." Licensee is investigating a potential issue with the relay logic associated with the scram bypass feature. Offsite power circuits and emergency diesel generators are operable and available. There was no increase in plant risk associated with this event. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-30
46905 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-05-30 08:08 | 2011-05-30 14:59 | 2011-05-30 | SPECIFIED SYSTEM ACTUATION - AFW INITIATION "Surry Unit 2 is in Intermediate Shutdown and was supplying steam generators with a main feed pump. The second main feed pump is tagged out for maintenance. The running main feed pump exhibited a low oil flow condition. The operating team took the deliberate action to secure the running main feed pump to prevent bearing damage with the knowledge that an Auxiliary Feedwater actuation signal would be generated. The plant was realigned to flow to the steam generators with the condensate pumps and the auxiliary feed pumps were then secured [at] 0821. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(iv)(A) for 8-hour notification of automatic actuation of AFW. Plant responded as expected. The NRC Resident Inspector has been notified of this event and is on site. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events." Offsite power is normal and emergency diesel generators are operable and available. There was no increase in plant risk as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Intermediate Shutdown; FMode2: Intermediate Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-30
46904 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-05-29 09:57 | 2011-05-29 15:01 | 2011-05-29 | OFFSITE NOTIFICATION DUE TO AN ON-SITE SULFURIC ACID SPILL "This notification is for San Onofre Units 2 and 3 and is being made in accordance with 10CFR50.72(b)(2)(xi) to report that on 5/29/2011 at 0957 PDT Government agencies were notified of a sulfuric acid spill. "On 5/28/2011 [at] 1440 PDT, during resin bed regeneration operations at the High Flow Makeup Demineralizer (HFMUD), a sulfuric acid transfer was in progress. When process piping was pressurized, a valve on the discharge side of the process pump experienced a diaphragm failure causing a body to bonnet leak. Operators secured the acid transfer. All the sulfuric acid was contained within the bermed area of the HFMUD. "Hazardous material teams have contained and cleaned up the spill. Area is secured until repairs can be implemented. All HFMUD operations have been stopped until repairs are completed. "On 5/29/2011 at 0926, the hazardous material team determined that this event was reportable to government agencies. The following reports were made: "[At] 0957 PDT San Diego Department of Enviornmental Health [was] called with [a] voice message left. "[At] 0959 PDT California Emergency Management Agency [was] called. Report number 11-3246. "[At] 1008 PDT National Response Center [was] called. Report number 977718." The licensee has notified the NRC Resident Inspector, | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-05-29
46903 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-05-29 05:02 | 2011-05-29 07:10 | 2011-05-29 | AUTOMATIC REACTOR TRIP DUE TO LOW PRESSURE IN EHC SYSTEM "Limerick Unit 2 automatically scrammed from 75% power while restoring EHC (Electro Hydraulic Control) fluid to number 3 Turbine Control Valve following maintenance work. Preliminary indications as to the cause of the scram indicate a low pressure condition in the EHC system resulting in an RPS actuation. "All control rods inserted as required. "No ECCS or RCIC initiations occurred. "No primary or secondary containment isolations occurred. "The plant is currently in Hot Shutdown maintaining normal reactor water level with feedwater." Decay heat is being removed via the bypass valves to the condenser. The plant is in a normal shutdown electrical lineup. There was no impact on Unit 1. The NRC Resident Inspector has been informed. The licensee will inform the Pennsylvania Emergency Management Agency, Montgomery, Burke, and Chester counties. | 0 | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-05-29
46902 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-29 01:55 | 2011-05-29 04:25 | 2011-05-29 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0155 EDT, the Watts Bar Unit 1 reactor tripped from 100% power due to a turbine trip above P-9 (reactor trip on turbine trip permissive). The cause of the turbine trip is under investigation at this time. All systems functioned as designed with the exception of Pressurizer Backup Heaters which failed to energize on lowering Pressurizer pressure. "The unit is stable in Mode 3 with Auxiliary Feedwater supplying the Steam Generators. The electrical system is in normal shutdown alignment with all Emergency Diesel Generators available in standby. There are no abnormal radiological conditions at this time." The reason the Pressurizer Backup Heaters failed to energize is unknown at this time. All control rods fully inserted. No relief valves or safety valves lifted. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-05-29
46901 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-05-28 09:12 | 2011-05-28 17:46 | 2011-05-28 | LOSS OF INBOUND PHONE CALL CAPABILITIES ON COMMERCIAL AND FTS LINES "During normal operations, Dresden Station identified issues with site commercial phone lines. Normal commercial phone lines are functioning for outgoing calls and will be used for any required notifications. Incoming calls, however, cannot get through to Dresden. A test of the ENS phone system failed. In addition, the HPN phone line is also affected by this issue. A cell phone number has been provided to the NRC until this issue is corrected. Repair personnel have been contacted and are expediting repairs. "This condition is reportable under 10 CFR 50.72(b)(3)(xiii) Major Loss of Emergency Preparedness Capabilities." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-28
46900 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-27 12:12 | 2011-05-27 20:12 | 2011-05-27 | LOSS OF UNIT 1 STARTUP POWER RESULTS IN STARTING ALL EMERGENCY DIESEL GENERATORS "On May 27, 2011, at 1212 PDT, Unit 1 startup power was lost due to actuation of startup transformer 1-1 overcurrent/differential relay 51-87UT11-1, which isolated the 12 kV feeder to startup bus. The loss of offsite startup power caused all Unit 1 emergency diesel generators (EDGs) to start in the standby mode. The EDGs started as designed with no issues observed. No vital loads were affected as a result of the 12 kV bus loss. On May 27, 2011, at 1241 PDT, all Unit 1 EDGs were shut down and returned to auto. Subsequently, startup transformers 1-1 and 1-2 were energized, followed by the 12 kV underground loop, and on May 27, 2011, at 1337 PDT, Unit 1 startup power was declared operable. "The cause of the event was a human performance error while attempting to test the startup transformer 2-1 overcurrent/differential relay. The maintenance electrical worker inadvertently installed a jumper on the overcurrent/differential relay for startup transformer 1-1. "Unit 2 startup power was cleared at this time and there was no effect on Unit 2. "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-27
46899 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-05-27 12:00 | 2011-05-27 14:50 | 2011-05-27 | SAFETY INJECTION INITIATED DUE TO A HIGH DIFFERENTIAL PRESSURE BETWEEN MAIN STEAM LINES "At 1200 hours on May 27, 2011, the plant was in Mode 3 during startup from a refueling outage with the main steam isolation valves closed. When the 'C' main steam isolation valve was opened for stroke testing, a safety injection occurred. The safety injection was due to a differential pressure of greater than 97 PSIG between the 'C' main steam line and the other main steam lines. The emergency core cooling system started and injected water into the Reactor Coolant System. All systems responded as expected. Safety injection was secured and the plant was stabilized in Mode 3." The licensee has notified the NRC Resident Inspector. Licensee will be notifying the State and local government. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-05-27
46898 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2011-04-03 14:44 | 2011-05-27 15:13 | 2011-05-27 | 60-DAY OPTIONAL NOTIFICATION OF INVALID START OF THE 'A' EMERGENCY DIESEL GENERATOR "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This report is being made under 10 CFR 50.73 (a) (2) (iv) (A) for a reportable invalid actuation. "On April 3, 2011, at approximately 1444 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 2 experienced an invalid actuation (start) of the 'A' Emergency Diesel Generator (EDG). EDG 'A' inadvertently started during integrated safeguards surveillance testing to demonstrate that the EDG overspeed trip is not bypassed. Prior to the test, the EDG overspeed governor was actuated, but the butterfly valve was not verified to be fully closed as required. The valve closure actuates a limit switch which activates the interlock that prevents the EDG start following an overspeed trip. The test requires the operator to ensure the butterfly valve is fully closed because it may not fully close as the EDG is not running when it is actuated for the overspeed test. "When the demand signal was inserted, the EDG started unexpectedly since the butterfly valve was not fully closed and the limit switch was not engaged. EDG 'A' Train completely actuated in the Emergency Mode and the EDG came up to rated speed and voltage as designed. The supporting 'A' train Essential Spray Pond System, used for engine cooling, was already running prior to the test. The Essential 'A' Train EDG Exhaust Room air handling unit started as required. "No damage occurred to the EDG or related equipment as a result of the unplanned actuation. The EDG was secured and the test was successfully re-performed. "This report is not considered an LER." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-27
46897 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-03-31 21:28 | 2011-05-26 19:55 | 2011-05-26 | 60-DAY TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) for invalid actuations reported under 10 CFR 50.73(a)(2)(iv)(A). This actuation was invalid since it was caused by a loss of power to the Reactor Protection System (RPS) power system bus and not by any actual plant condition warranting containment isolation. The RPS power system provides 120 VAC power to logic and system components including the RPS and the containment isolation system. "On March 31, 2011, at 2128 hours [PDT], normal power was lost to RPS Bus 'A' resulting in a half scram and actuation of the Groups 2, 5, 6 and 7 primary containment outboard isolation valves. The immediate investigation found that the associated RPS motor generator (MG) set was running with normal 120 VAC output and that the two electrical protective assemblies between the MG set and RPS Bus 'A' were closed with no abnormal indications. A visual inspection of the RPS power panel revealed a cleared fuse for the normal feed. The RPS Bus 'A' was subsequently transferred to the alternate supply at 2135 hours. The actuations and isolations were reset at 2154 hours. "The RPS power system is supplied from either of two sources: the normal power source from the MG set or the alternate source from a non-Class 1E distribution panel. Transfer between the normal and alternate power supplies is manually initiated by the control room operator. Troubleshooting activities determined that the cleared fuse was due to an internal short in the windings of the 120 VAC coil on the RPS Bus 'A' normal feed contactor. The cause of the internal short was attributed to a random isolated occurrence. The contactor was subsequently replaced and RPS Bus 'A' was returned to the normal power supply. "There were no actual safety consequences associated with this event. The affected equipment responded as designed. Valves affected by the invalid signal fulfilled their isolation function by successfully closing. "The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-26
46896 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-26 | 2011-05-26 14:54 | 2011-05-26 | TWO TRITIUM EXIT SIGNS STOLEN FROM MOVIE THEATER The following information was provided by the State of Texas via email: "On May 26, 2011, the Agency [Texas Department of Health] was notified during routine inspections of the facility's site safety systems, it was discovered that two tritium exit signs were missing from their fixed mounting positions. These signs were affixed to the walls near exits in a secure manner such that they could only be removed by means of removing safety capped mounting screws and then the use of tools to remove them. In this case, it is apparent that these signs were removed by way of vandalism and were essentially pulled off the walls leaving evidence that they were removed without the knowledge of the site personnel. A report was made to the local police department. The signs were installed new in 2010. "In addition, this same vandalistic act occurred at the same location as reported to the Agency [Texas Department of Health] on February 2, 2011. At that time, four tritium exit signs were removed. A report was made to local law enforcement. The exit signs are Isolite Model 2040-95S-B-15-WS, and each contain 9.5 Curies of tritium." Texas Incident: # I-8858 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-31
46895 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2005-01-01 | 2011-05-26 14:29 | 2011-05-26 | AGREEMENT STATE REPORT - DOSE ADMINISTERED >20% DIFFERENT FROM PRESCRIBED DOSE The following information was provided by the State of New York via email: "A patient was prescribed 11 mCi of Iodine-131 for hyperthyroidism but received 7 mCi. Discovered during routine NYS DOH [New York State Department of Health] inspection on 10/18/2007. DOH staff reviewed a memo from the physicist to the RSO discussing the event, but their concern was only that the expiration date on the capsule was 12/28/04 (consultation with the pharmacy after the fact indicated that it was still acceptable to us this dose). A 'left-over' capsule from the previous week (15 mCi on 12/27/2004) with activity of 7 mCi on 01/01/2005 was administered to a patient who was prescribed 11 mCi with the permission of the RSO. Additional dose was ordered and an additional 4 mCi was administered the following day so they RSO did not think it was a misadministration. Follow-up letter from RSO concluded that there was no adverse effect on the patient. Corrective actions included changing procedures and staff training on proper course of action to take in the future and incident reporting requirements. Incident is closed." New York Report Id No.: NY-11-09 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-06-01
46894 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-26 02:26 | 2011-05-26 12:57 | 2011-05-26 | LOSS OF STARTUP POWER DUE TO FAULT IN SWITCHYARD CAUSES ALL EDGS TO START "At 0226 PDT on May 26, 2011, Unit 1 startup power was lost following actuation of the 230 KV line pilot wire differential relay 287X. Loss of power to the Unit 1 12 KV startup bus produced an undervoltage signal that caused all Unit 1 emergency diesel generators (EDGs) to start in a standby mode. The EDGs started as designed with no problems observed. No vital loads were affected as a result of the 12 KV bus loss and subsequent undervoltage. The cause of actuation of the differential relay 287X is under investigation at this time. "At 0255 PDT on May 26, 2011, all Unit 1 EDGs were shutdown and returned to their normal at-power standby configuration. "Unit 2 startup power was cleared at this time and there was no effect on Unit 2. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-26
46893 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-05-26 00:15 | 2011-05-26 06:24 | 2011-08-22 | POTENTIAL FLOODING PATH DISCOVERED "Operations identified a potential flooding issue in the Intake Structure 1007' 6" level. The areas of concern are the holes in the floor at the 1007' 6" level where the screen wash header penetrates the ceiling of the Raw Water Vault. There are five of these penetrations of concern. Flooding through the penetrations could have impacted the ability of the station's Raw Water (RW) pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). "A one foot sandbag berm has been placed around each penetration of concern." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO ERIC SIMPSON AT 1142 EDT ON 8/22/11 * * * "Following additional review of the reported condition, it has been determined that the Raw Water pumps are adequately protected during flooding conditions and that the open penetrations would not impact the ability of the Raw Water pumps to perform their design accident mitigation functions." The licensee notified the NRC Resident Inspector. Notified R4DO (Haire). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-05-26
46892 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2011-05-25 15:30 | 2011-05-25 16:53 | 2011-05-25 | AGREEMENT STATE REPORT - MISSING SEALED ROD SOURCE The following information was received via email: "At approximately 3:30 p.m. on Wednesday, May 25, 2011, the radiation safety officer (RSO) of Nuclear Diagnostic Products of Philadelphia called to inform the [New Jersey Department of Environmental Protection's Radioactive Materials Program] NJDEPs RMP that a sealed rod source containing approximately 2.68 microCuries of cobalt-57 was unaccounted for at their facility. The source had been returned to the licensee by one of their customers for disposal. The source was secured at their location prior to being shipped for final disposal. In the interim, the room where the source was being secured was painted and materials were moved to a different room while the painting activities occurred. The painting activities began about three weeks ago. "When the removed materials were returned to the room after the painting was concluded recently, the source could not be found. A search was conducted by the licensee, but, to date, the source cannot be located. The licensee believes the box that contained the source was either inadvertently placed in the garbage for routine disposal or the source was placed into a sharps container for incineration with biohazard materials. The licensee will continue to look, but informed us of the matter after what they believe is a comprehensive search." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46891 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2008-08-11 | 2011-05-25 16:33 | 2011-05-25 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE FROM A GAS CHROMATOGRAPH The following information was received via fax: "Event location: 14 Parker Hall, 3435 Main Street, Buffalo, NY, 14214 "The RSO at [SUNY at Buffalo] called on 08/21/08 to report a leaking nickel 63 sealed source located in a HP gas chromatograph unit. Location of unit is Farber Hall room 2128. Apparently on Monday, August 11, 2008, the researcher was cooking 'stuff' in the oven portion of the unit. Product exploded in the oven and spilled over into the other parts of the unit and landed on the sealed source compromising integrity. Contamination was found in the oven of the unit. SUNY EH&S [State University of New York Environment, Health and Safety] staff performed decontamination of the unit until <100 dpm. No contamination was found outside of the unit. SUNY EH&S staff also surveyed the rooftop of the building as the unit is vented and no contamination was found. SUNY EH&S [gave] the researcher until Friday, 08/29/08 to submit his report of the incident to EH&S. NYS staff visited [SUNY at Buffalo] on 08/26/08 and interview [an individual] who reported that the leak was found during the routine leak testing. When the swipe came back high, he re-swiped the unit and noticed a white powder all over the oven and inside the tubing. [When] asked, the researcher stated that she had dried a silica gel in the oven on 08/11/08. Apparently, the foil cover blew off of the beaker, and the silica gel went all through the machine via an inlet port possibly 'sandblasting' the foil compromising its integrity. Swipe testing by liquid scintillation showed contamination on inlet and outlet and no contamination on the housing or outside the machine. EH&S has decontaminated the machine as much as possible and taken it out of service. EH&S has also contacted the manufacturer of HP 5890. Manufacturer states there is no way to clean it and the machine should be scrapped. EH&S plans to take out the source, scrap metal parts that are not contaminated and hold remaining pieces until a disposal option is available. Written report [was] received [on] 9/11/2008 . "The unit [is] to be handled as indicated above, and additionally, all researchers will be in-serviced on keeping the inlet to the foil capped when using ovens for other than GC [gas chromatograph] analysis. Incident is closed." New York Event Report ID Number: NY - 11 - 08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46890 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2010-05-26 | 2011-05-25 16:33 | 2011-05-25 | AGREEMENT STATE REPORT - POTENTIALLY DAMAGED TRITIUM SIGN The following information was received via fax: "Event location: 401 South Oyster Bay Road. Plainview, NY, 11803 "[On] 7/15/10, [Bed Bath and Beyond] BBB reported that Shaw Group, Inc. visited Bed Bath and Beyond to package their tritium exit signs for removal. They discovered two signs with letters that did not illuminate. Neither sign showed evidence of damage to the tubes. Both signs were packaged and secured in an electrical room. On June 15, 2010, a Shaw Representative took surveys of the floor and space where the sign was located. All results were below 1000 dpm per 100 square centimeters. Bed Bath & Beyond plans to send the damaged signs to Shield Source, Inc (SSI) and will provide a report within 30 days of the transfer of the damaged signs. "A letter received [on] July 30, 2010, showing that the lights were returned to Shield Source, Inc. Incident is closed. New York Event Report ID Number: NY - 11 - 07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46889 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2010-03-31 | 2011-05-25 16:33 | 2011-05-25 | AGREEMENT STATE REPORT - DAMAGED TRITIUM SIGN The following information was received via fax: "Event location: 3064 Route 50, Saratoga Springs, NY, 12866 "A tritium exit sign was found damaged on March 31, 2010, at Bed Bath & Beyond in Saratoga Springs. On April 6, 2010, Shaw Environmental Group was granted reciprocity to survey, decontaminate and package the broken sign. All measurements were found to be below MDA. The broken sign was shipped to Shield Source, Inc, a tritium light manufacturer based in Canada. Written report [was] received [on] 4/29/2010. "Bed Bath and Beyond has implemented and communicated protocols to its stores for the proper handling of [Tritium Exit Signs] TES. It has also inventoried all of the TES at its sites across the U.S. to re-establish the accuracy of its records and to track the location of TES for proper accounting and handling. This incident is closed. New York Event Report ID Number: NY - 11 - 06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46888 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2009-07-01 | 2011-05-25 16:33 | 2011-05-25 | AGREEMENT STATE REPORT - LOST TRITIUM SIGN The following information was received via fax: "Event location: Utica Compression Station, 1103 Higby Road, New Hartford, NY, 13417 "[On] 4/23/10, Dominion Resources called to inform [New York State Department of Health] that one tritium exit sign was found missing after some demolition work at their Utica, NY facility. A written report [was] received [on] 4/29/10. "During a company wide effort to inventory all tritium exit signs it was discovered that one was missing at their Utica facility. An investigation ensued, and it was determined that during July of 2009, the entire wall on which the exit sign was located was removed during remodeling. The exit sign was likely disposed of in a 30 cubic yard roll-off container owned by Waste Management and is likely in the local AVA landfill. Dominion is reinforcing and enhancing established processes and programs for handling tritium exit signs. This event will be incorporated into training and lessons learned. All other signs at the facility are accounted for, [and] this incident is closed." New York Event Report ID Number: NY - 11 - 05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46887 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2008-03-01 | 2011-05-25 16:33 | 2011-05-25 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATORS CONTAINING POLONIUM The following information was received via fax: "Event location: 800 Phillips Road, Webster, NY 14580 "Reported to [New York State Department of Health] NYS DOH [on] 11/17/2008. Twelve NRD static eliminators containing polonium 210 were inadvertently thrown out in March 2008. The total activity of all twelve sources would have been 334 microCuries in March 2008. They were most likely sent to Genesee Scrap and Tin Baling Co., Inc., at 80 Steel Street in Rochester as part of a large roll-off of assorted scrap. Attempts to locate the missing devices were fruitless. NRD has been contacted with the serial number information. "A written report received from Xerox November 17, 2008. Procedures have been modified to prevent recurrence. Xerox will inventory their sealed sources two times a year to prevent other losses. NRD has been instructed to send correspondence to Xerox RSO regarding shipment of devices instead of the Xerox end user. Incident Closed." New York Event Report ID Number: NY - 11 - 04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46886 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2011-05-24 12:20 | 2011-05-25 15:35 | 2011-05-25 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE The following information was received via email: "While using a QSA Global 880D radiographic exposure device, the licensee's crew was unable to move the drive cable forward or backward. It appeared that the source was moved slightly out of the fully shielded position when the device was unlocked prior to the attempt to crank out the source. The crew was unable to retract the source and lock the device. A licensee employee trained in source retrieval was sent to the site. The employee disassembled a portion of the drive cable which gave him access to manually pull the drive cable in the direction that would retract the source. The cable was moved approximately 1/4 inch. This placed the source in the fully shielded position and the source was locked in the shielded position. "Only licensee personnel were potentially exposed to radiation from the device during the incident. Licensee personnel stated that they did not step in front of the camera at any point during the incident. The radiographer used the survey meter to determine where to stand to receive the least exposure while checking the camera. At one point he reached forward with the survey meter and measured 200 mR/hr at the front port of the device. Dose estimates for licensee personnel associated in the incident were well below the limits for occupationally exposed individuals." Utah Event Report ID Number: UT - 110004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46885 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-14 14:28 | 2011-05-25 14:41 | 2011-05-25 | VIOLATION OF LICENSE CONDITION "On May 16, 2011, at 2013 Eastern Daylight Saving Time (EDT), Watts Bar Nuclear Plant Unit 1 (WBN) entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, Condition B, because based on performance of Surveillance Requirement (SR) 3.7.5.2, the Turbine Driven Auxiliary Feedwater system was determined to be inoperable. Failure of the surveillance was caused by loss of the ability to control the turbine driven auxiliary feedwater pump (TDAFWP) manually. This was the first operation of the TDAFWP since the turbine had been rebuilt and had a new governor and servo installed during the WBN refueling outage 10 in May 2011. Misalignment of the servo caused the controller to stick, so that the TDAFWP pump could not be controlled in manual. The servo was replaced and the TDAFWP subsequently passed its required surveillance. LCO 3.7.5 was exited at 1745 on May 19, 2011. "Although the TDAFWP was not known to be inoperable until performance of the surveillance, TVA has concluded that the inoperability existed from the time that WBN entered Mode 3. "WBN had entered Mode 3 at 1428 EDT, on May 14, 2011. LCO 3.0.4 prohibits MODE changes when an LCO is not met except under certain conditions that were not applicable to this event. Therefore, TVA considers that WBN entered Mode 3 without the required three operable trains of AFW. "TVA also determined that the TDAFWP was inoperable for a period of 123 hours and 17 minutes while the plant was in Mode 3, which exceeded the 96 hours allowed for an inoperable train of AFW in LCO 3.7.5. (72 hours to restore, 6 hours to be in MODE 3, and 18 hours to be in MODE 4). It should be noted that actions were taken and completed within the required time from time of discovery of the condition. "Changing MODEs when LCO 3.7.5 was not met, and exceeding the time allowed for an inoperable train of auxiliary feedwater (AFW) were determined to be reportable as a condition prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(b). "Since these conditions are a violation of the requirements contained in Section 2.c of the WBN License (Technical Specifications), this notification is made in accordance with Watts Bar License condition 2.G. "The NRC Resident [Inspector] has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2011-05-25
46884 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-24 | 2011-05-25 14:36 | 2011-05-25 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE The following information was received via email: "Event Location: Flint Hills Resources LP, 2825 Suntide Road, Corpus Christi, Texas 78403. "On May 24, 2011, the agency [State of Texas] was notified by a licensee that they were unable to retract a 27.7 Curie iridium (Ir) - 192 radiography source into a QSA Delta 880 camera at a field site. The licensee stated that when setting up for a shot, the radiographer ran the crank cables for the camera over a hot pipe. The licensee stated that while conducting a shot, the plastic on the crank cable shield melted. The licensee believes that this may have prevented the radiographer from retracting the source to the fully shielded position. The licensee's source recovery team went to the location and was able to return the source to the fully shielded position. The camera was taken to the licensee's facility for inspection. No one involved in the source recover exceeded any regulatory limits. The investigation into this event is on going. Additional information will be provided as it is received." Texas Incident number: I - 8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-30
46883 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-04-02 12:18 | 2011-05-25 11:36 | 2011-05-25 | LOSS OF RPS/UPS POWER SUPPLY "On Saturday, April 2, 2011, Unit 2 refueling outage activities were in progress. The 2A RPS/UPS Static Inverter was out of service and bypassed with loads transferred to the primary alternate power supply. At 1218 hours, a post maintenance test was performed on the secondary alternate power supply. The inverter alternate power manual transfer switch was transferred from the 'primary alternate' to 'secondary alternate' position to support the post maintenance test. Since the transfer switch is 'break before make' the alternate power supply was interrupted momentarily. This deenergized the 2A RPS/UPS power distribution panel loads including the Division IA and IIA RPS relays and Division IA and IIA NSSSS [Nuclear Steam Supply Shutoff System] relays. Primary containment isolation valves (PCIVs) automatically closed on more than one system. The IB and IIB channels were unaffected. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The isolation was a partial actuation of the isolation actuation instrumentation. "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to report invalid automatic actuations of systems listed in paragraph (a)(2)(iv)(B). The listed system that actuated was general containment isolation signals affecting containment isolation valves in more than one system. Primary containment isolation valves (PCIVs) closed on drywell chilled water (DWCW), reactor enclosure cooling water (RECW), primary containment instrument gas (PCIG), and suppression pool cleanup." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-25
46882 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-05-24 08:20 | 2011-05-24 19:31 | 2011-05-24 | FITNESS FOR DUTY REPORT INVOLVING A MAINTENANCE SUPERVISOR A maintenance supervisor had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's access has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2011-05-24
46881 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-03-26 20:05 | 2011-05-24 18:09 | 2011-05-24 | 60-DAY TELEPHONIC NOTIFICATION OF INVALID PRIMARY CONTAINMENT ISOLATION SIGNAL DUE TO MAINTENANCE "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(1) to describe an invalid actuation of multiple secondary containment isolation signals affecting more than one system. "On March 26, 2011, at 2005 hours Central Daylight Time (CDT), following planned maintenance activities, an unplanned actuation of secondary containment isolation signals affecting containment isolation valves in more than one system occurred and resulted in a partial Primary Containment Isolation System (PCIS) (Group 6, Secondary Containment) isolation and receipt of a Unit 2 Reactor Building Ventilation Abnormal Alarm. Unit 2 was in Mode 4, in a refueling outage, and at 0 percent power (0 MWT). Units 1 and 3 were both in Mode 1 and operating at approximately 100 percent power. "Plant Conditions, which initiate PCIS (Group 6, Secondary Containment) actuations, are Low Reactor Vessel Water Level, High Drywell Pressure, High Reactor Zone Exhaust Radiation, or High Refueling Floor Exhaust Radiation. At the time of the event, these conditions did not exist; therefore, the partial actuations were invalid. "For this occurrence, equipment normally affected by a complete Group 6 isolation responded as follows. Trains 'B' and 'C' of Standby Gas Treatment (SGT) System started while Train 'A' did not. Train 'B' of the Control Room Emergency Ventilation System (CREVS) started while Train 'A' did not. Secondary containment (Unit 1, 2, and 3 Reactor and Refuel Zones) normal ventilation isolated - fans stopped and dampers closed. Suppression Chamber Exhaust Inboard Isolation Valve 2-FSV-64-32 and Drywell Exhaust Inboard Isolation Valve 2-FCV-64-29 did not close. Because only a partial (B part of the logic) PCIS isolation was relayed, only the affected Group 6 equipment received the isolation demand. All equipment that received the isolation demand responded and performed as designed. "Control Room personnel commenced actions of the applicable Alarm Response Procedure and the Group 6 Ventilation System Isolation Abnormal Operations Procedure. Train 'A' of the SGT System was later started. "This event was entered in the Corrective Action Program as Service Request (SR) 344609 and Problem Evaluation Report (PER) 344680. "There were no safety consequences or impact on the health and safety of the public as a result of these events. "The NRC Resident Inspector has been notified of this event." Although Group 6 PCIS testing occurred earlier that day, the licensee could not determine the signal initiator and considered it spurious. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-24
46880 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-03-30 14:43 | 2011-05-24 18:03 | 2011-05-24 | 60-DAY TELEPHONIC NOTIFICATION OF INVALID RPS SIGNAL DUE TO LOSS OF VARIABLE LEG OF LEVEL TRANSMITTER "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(1) to describe an invalid RPS (SCRAM) actuation. "On March 30, 2011, at 1443 hours Central Daylight Time (CDT), during a refueling outage, Browns Ferry Unit 2 received an invalid Common Accident Signal (CAS) as a result of maintenance activities. "The CAS caused a full Unit 2 Reactor SCRAM and associated system initiations. The CAS was initiated due to invalid indications on both Channels A and B of low-low-low reactor water level, which did not exist; therefore, the actuation was invalid. "The affected equipment responded as designed. All four Unit 1/2 Emergency Diesel Generators auto started and all four Unit 3 Emergency Diesel Generators auto started. Unit 2 received a full Reactor SCRAM and Core Spray Pumps A, B, C, and D auto started and injected into the reactor. Unit 2 Division I Residual Heat Removal (RHR) System was in Shutdown Cooling with only the C pump in service. The 'A' RHR pump auto started and Shutdown Cooling flow increased, as expected. Unit 2 Division II RHR System had been tagged out for maintenance and did not respond. High Pressure Coolant Injection and Reactor Core Isolation Cooling received auto initiation signals; however, their steam isolation valves were tagged closed and the systems did not start. The Inboard Main Steam Isolation Valves (MSIVs) isolated as a result of the CAS signal. The outboard MSIVs had been previously closed and tagged for refueling outage purposes. "This event was entered in the Corrective Action Program as Service Request (SR) 346544, which generated Problem Evaluation Report (PER) 346568. "There were no safety consequences or impact on the health and safety of the public as a result of these events. "The NRC Senior Resident Inspector has been notified." The shutdown reactor water level transmitters share a common variable leg. When maintenance unrelated to the transmitters was performed, the variable leg was lost causing the low-low-low reactor water level SCRAM signal to be generated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-24
46879 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-24 09:18 | 2011-05-24 17:56 | 2011-05-24 | LOSS OF POWER TO THIRTY-TWO EMERGENCY SIRENS "This 8-hour notification is being made per the reporting requirements specified by 10 CFR 50.72(b)(3)xiii. "At 0946 CDT on May 24, 2011, the TVA Corporate Operations Duty Specialist notified the Nuclear Power Group Emergency Duty Officer that the fifteen minute communication test for Lawrence County indicated a loss of communications with the Lawrence County siren activation system. "At 0958 CDT, Lawrence County Alabama Emergency Management Agency (EMA) staff reported that a transformer had de-energized at 0918 CDT and that both the primary siren activation point (Lawrence County EMA office) and the backup activation point (Moulton, Alabama Fire Department) were without power. The EMA offices normally have backup power supplied by a diesel generator. However, the generator had failed during EMA operations associated with the April 27, 2011 tornadoes. The State of Alabama had supplied a generator for temporary use but this generator required manual actions for making connections in order for it to be placed into service. "At 1003 CDT, electrical power was restored and the primary and backup siren activation points were returned to service. "Browns Ferry has 100 ANS sirens and 32 are located in Lawrence County. All of the 32 Lawrence County sirens were affected. The duration of the condition was estimated to be approximately 45 minutes (0918 CDT through 1003 CDT). (Note that the polling system that provides the out of service times polls the system every 15 minutes so the timeframe by necessity is an approximation.) "Both primary and backup activation systems were operable at 1003 CDT. A silent test was performed from the Lawrence County EMA office at 1159 CDT with all 32 Lawrence County sirens satisfactorily responding." The licensee has notified the State of Alabama, the Lawrence County EMA and the NRC Resident Inspector of this report. | 19 | 18 | 0 | 19 | 18 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-24
46878 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-05-24 13:24 | 2011-05-24 14:49 | 2011-12-09 | SAFEGUARDS REPORT - DISCOVERY OF UNMARKED SAFEGUARDS INFORMATION The licensee discovered unmarked Safeguards Information on an unclassified computer system. Compensatory measures are being taken. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM ERICK MATZKE TO CHARLES TEAL ON 9/23/11 AT 1319 EDT * * * Additional information has been obtained from the licensee. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified R4DO (Drake), ILTAB (Johnson), and Part 73.71 group via email. * * * UPDATE FROM ERICK MATZKE TO PETE SNYDER ON 9/29/11 AT 1222 EDT * * * Additional information has been obtained from the licensee. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified R4DO (Werner), and Part 73.71 group via email. * * * UPDATE FROM ERICK MATZKE TO JOHN KNOKE ON 12/09/11 AT 1510 EST * * * Additional information obtained from the licensee states that this event is retracted. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified R4DO (Neil O'Keefe), ILTAB (Matt Hahn), and Part 73.71 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-05-24
46877 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-05-24 11:20 | 2011-05-24 13:40 | 2011-05-24 | LO-LO LEVEL IN STEAM GENERATOR RESULTS IN SPECIFIED SYSTEM ACTUATIONS "At 11:20 [CDT] on 5/24/11, the unit, while in Mode 4, had a reactor trip and Aux Feedwater actuation/Feedwater Isolation Signal due to lo-lo level on 'B' Steam Generator. Reactor Trip breakers were closed to support DRPI [Digital Rod Position Indication] testing. Steam Generator levels were being maintained approximately 30% to support Aux Feedwater pump full flow testing." The trip occurred at 23.5% level in the steam generator. Reactor trip breakers opened and the motor-driven auxiliary feedwater pump fed the steam generators. The feedwater isolation valves fully closed. No other actuations occurred. Operators are in the process of resetting plant conditions to support completion of the testing in progress at the time of the trip. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-24
46876 | 0 | ECS CAROLINAS, LLP |  |  |  |  | 2011-05-24 12:30 | 2011-05-24 13:24 | 2011-05-25 | TROXLER MOISTURE DENSITY GAUGE STOLEN At approximately 1230 EDT on 5/24/11, a Troxler Moisture Density Gauge, Model #3440, S/N 20641, with 8 mCi Cs-137 and 40 mCi Am-241/Be was stolen from a truck at Camp Lejeune Marine Corps Base. The RSO reported the theft to the Base Safety Officer. * * * UPDATE FROM HARRY SLATER TO HOWIE CROUCH ON 5/24/11 @ 1431 EDT * * * The Troxler Moisture Density Gauge was located on the job site off the side of the road in a ditch. There was no damage to the gauge, and the gauge was placed back into service. * * * UPDATE FROM HARRY SLATER TO CHARLES TEAL ON 5/25/11 @ 0732 EDT * * * The following was excerpted from an email: "Initial investigation indicated that the [technician] did not have the gauge locked in the case while not in use. The gauge was also placed out of [the technician's] sight more than 10 feet from him. The case and the locking equipment were in the truck and are in working condition. The gauge did still have the lock trigger in place. The lack of securing the gauge when not in use is in direct violation of the company policies as indicated on the license and on the document signed by [the technician]." Notified R1DO (Dentel), FSME EO (McIntosh), and ILTAB (Pearson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-05-24
46875 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-05-23 22:00 | 2011-05-23 23:41 | 2011-05-24 | OFFSITE NOTIFICATION DUE TO AN OIL SPILL "On May 23, 2011, at 2200 CDT, the station needed to notify the State of Nebraska, Department of Environmental Quality and the National Response Center due to an oil leak from the stations lube oil system. A quantity of oil spilled into the turbine building basement and an undetermined amount drained to the turbine building sump which discharges to the Missouri River. Some amount of oil was discharged to the river, which resulted in discoloration and a visible sheen noted on river sampling. Per Fort Calhoun Nuclear Station's National Pollutant Discharge Elimination System (NPDES) permit, the notifications will be made and samples will be taken for off site analysis to determine the quantity discharged involved. Also, the oil quantity in the turbine building sump (out fall L02) is expected to have exceeded 20 ppm oil and grease which does violate the State NPDES permit NE00000418. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi), 4 hour non-emergency notification due to a notifications being made to Government [Agencies] (State of Nebraska, Department of Environmental Quality and the National Response Center)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-05-24
46874 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2011-05-22 14:44 | 2011-05-23 17:03 | 2011-06-07 | SAFE SHUTDOWN OPERABILITY CONCERN ASSOCIATED WITH OFFSITE POWER CIRCUITS "On May 22, 2011, at 1444 hours, the Fermi 2 Control Room was notified by the Central System Supervisor that the switchyard voltage for both the 345kV (Division II) and 120kV (Division I) offsite power circuits following a generator trip would not be sufficient to sustain operability of the safety-related loads. Technical Specification (TS) 3.8.1 'AC-Sources Operating,' Condition E was entered at 1444 hours. At 1535, both offsite power circuit voltages were at acceptable levels and the offsite circuits were declared operable. Technical Specification (TS) 3.8.1, Condition E was exited at 1535 hours. Abnormal Operating Procedure (AOP) 20.300 GRID was entered. The Emergency Diesel Generators (EDG) remained operable during the degraded voltage condition. The ability of the EDGs to fulfill their design function was not affected by this condition. "The event is being reported per 50.72(b)(3)(V)(A), as any event or condition that at the time of discovery could have prevented fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition." The NRC Resident Inspector was notified. * * * RETRACTION FROM JEFF GROFF TO HOWIE CROUCH AT 1458 EDT ON 6/7/2011 * * * "This event is retracted. The original report was based on calculated unit trip voltage drop results reported to Detroit Edison by ITC Transmission Company that exceeded acceptance criteria. ITC has subsequently informed Fermi 2 that this notification was in error due to a software feature of their real time contingency analyzer that resulted in inappropriately high results. Based on the results of other similar real time contingency analyzers employed at that time, without the problematic software feature, none of the acceptance criteria were exceeded and both divisions of offsite power were capable of supporting operability of safety-related loads. Additionally, Fermi 2 has determined that even at the inappropriately high voltage drop originally reported, the Division II system could have performed its safety related functions. Therefore, there was no loss of safety function." The licensee has notified the NRC Resident Inspector. Notified R3DO (Lara). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2011-05-23
46873 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-05-23 15:35 | 2011-05-23 16:00 | 2011-05-23 | ALERT DECLARED DUE TO HALON DISCHARGE IN EMERGENCY DIESEL GENERATOR BUILDING "At 1535 EDT, Brunswick Units 1 & 2 declared an Alert condition due to a discharge of Halon gas into the basement of the emergency diesel generator building (EAL H.A.3.1 for toxic gas discharge into a vital area). Initial inspection indicates that there is no fire. No offsite assistance was required and no personnel injuries as a result of the discharge. Both reactors continue to operate at 100% power. The licensee is investigating the cause of the discharge and will terminate the Alert when the area is ventilated and can be reoccupied. "The licensee has notified State and local authorities and the NRC Resident Inspector." * * * UPDATE FROM CHRIS CINDRIC TO DONG PARK AT 1659 EDT ON 5/23/11 * * * A later report confirmed that one individual was inside the diesel generator building at the time of the Halon discharge. The individual evacuated the building but complained of chest pains about an hour after the incident. An ambulance was dispatched to transport the individual to the hospital. * * * UPDATE FROM CHRIS CINDRIC TO DONG PARK AT 1945 EDT ON 5/23/11 * * * The licensee terminated the Alert at 1943 EDT based on restoring normal atmosphere conditions in the emergency diesel generator building. The initiating cause of this event is still being investigated. The NRC Operations Center has notified the federal agencies initially notified of this event. Notified R2DO (Shaeffer), NRR EO (Brown) and IRD (Grant). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-05-23
46872 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-22 17:37 | 2011-05-22 22:34 | 2011-05-22 | VALID REACTOR PROTECTION SYSTEM (RPS) ACTUATION SIGNAL - SCRAM DISCHARGE VOLUME (SDV) HIGH WATER LEVEL "At 1737 CDT on 05/22/2011, with BFN U3 [Browns Ferry Unit 3] in Mode 4, a valid RPS actuation signal was received by both channels of the RPS due to Scram Discharge Volume (SDV) High Water Level. "At 1735, while performing IRM range 6 to 7 correlation, Instrument Maintenance technicians were measuring high voltage on IRM 'G' while reconnecting a high voltage cable. A spike occurred on IRM's 'C' and 'D' causing a full Reactor Scram. This IRM [Intermediate Range Monitor] Scram was not a valid actuation, the safety function had already been completed, and is not reportable. At 1737, after diagnosing the cause of the IRM Scram, operators reset the Scram signal and received a valid RPS Scram signal due to SDV High Water Level. Investigation is ongoing. "This condition is reportable under 10CFR50.72(b)(3)(iv)(A) - A valid actuation of any of the systems named in 50.72(b)(3)(iv)(B). "This is also reportable as 60 day written report IAW 10CFR 50.73(a)(2)(iv)(A). "This event was entered into the licensee's Corrective Action Program as SR# 373366." There are no compensatory measures or LCO's in effect for this event, and all EDG's and offsite power lines are operable. There was no increase in plant risk as a result of this event. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-22
46871 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-04-04 09:00 | 2011-05-21 16:33 | 2011-05-21 | AGREEMENT STATE REPORT - MEDICAL EVENT MISADMINISTRATION OF PROSTATE SEEDS The following was received via e-mail: "The patient underwent a permanent seed prostate implant in the UCLA 200 Medical Plaza outpatient surgery suite on 4/4/2011. The patient returned to the UCLA Department of Radiation Oncology on 5/3/2011 for a follow-up visit and a post-implant CT scan. A post-implant treatment plan was performed to verify seed placement and final dosimetry endpoints. The post-implant dosimetry plan indicated a significant number of seeds were implanted outside of the prostate. "A detailed dosimetry analysis is being performed but is unavailable at the time of this report. This report will provide the details of the intended dose versus the received dose, as well as other supplemental information. This report will be included in the final investigation packet. "UCLA has notified CDPH RHB [California Department of Public Health Radiologic Health Branch] that the permanent seed implant program has been placed on temporary hold pending review of this procedure. No further procedures have been performed since this discovery. "This investigation is ongoing." CA Report Number: 052011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-05-27
46870 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-20 22:17 | 2011-05-21 01:56 | 2011-05-21 | HPCI CHECK VALVE LEAKAGE RESULTS IN SYSTEM LEAKAGE DURING MAINTENANCE "On 5/20/2011 at 2217 [CDT], while performing 1-SR-3.5.1.1(HPCI) MAINTENANCE OF FILLED HPCI DISCHARGE PIPING, operators opened 1-FCV-73-44, HPCI Injection Valve, to fill and vent portions of the system. Once open, the HPCI discharge piping rapidly pressurized to 1000 psig. Operators immediately shut the 1-FCV-73-44 valve. A flood level alarm was received in the control room and water was confirmed to have been leaking from the Gland Seal Condenser. All leakage has stopped. "It is suspected that leakage past 1-CKV-73-45, HPCI TESTABLE CHECK VALVE, caused the rise in discharge piping pressure. An investigation into this event is ongoing. "In accordance with TS LCO 3.6.1.3 Condition A, the affected line has been isolated by one closed and deactivated valve. "This incident is reportable as an 8-hour ENS notification under 10CFR 50.72 (b)(3)(v) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: d. Mitigate the consequences of an accident.' "It also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(vii). The NRC Resident Inspector has been notified." The volume of leakage was not specifically known but the leakage resulted in approximately 2 inches of water on the HPCI pump room floor before it was isolated. | 22 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-05-21
46869 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-05-20 12:00 | 2011-05-20 23:27 | 2011-05-20 | AGREEMENT STATE REPORT - STOLEN TRITIUM EXIT SIGN The following report was received via fax: "On 5/20/2011, the PA DEP [Pennsylvania Department of Environmental Protection] Bureau of Radiation Protection (BRP) was notified by the Safety Manager from Ursinus College, explaining that during their dormitory inspection performed this morning, a tritium exit sign with perhaps 10 to 20 curies of H-3 is missing and presumed stolen." Pennsylvania Event: PA110011 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-05-25
46868 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-20 18:00 | 2011-05-20 22:57 | 2011-05-20 | UNANALYZED CONDITION MARINE LIFE INSIDE AFW PIPING "The past operability of the 2A train of Auxiliary Feedwater has been called into question based on finding clam shells in the safety related water source piping. During performance of valve strokes on 5/9/2011 per an Operations Department surveillance, clam shells were found while draining a section of the safety related water source piping. System Engineering collected the shells as part of troubleshooting. Based on analysis performed by System Engineering, the 2A Train of Auxiliary Feedwater was not operable with clam shells in the pipe. The amount of shells present would have caused an unacceptable differential pressure across the 2A train Auxiliary Feedwater System flow control valves. The extent of condition has been evaluated for the other Auxiliary Feedwater trains for both units and it has been determined that the only affected train is 2A. The 2B Auxiliary Feedwater train has also been inoperable at various times over the past 3 years for maintenance. "The clams were flushed out of the 2A Train Auxiliary Feedwater suction piping during a recent refueling outage and both trains of Auxiliary Feedwater on Unit 2 are operable. " The licensee has not implemented any compensatory measures nor are they in any LCO's as a result this event. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-05-20
46867 | -1 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-05-13 | 2011-05-20 16:36 | 2011-05-24 | AGREEMENT STATE REPORT - EARLY TERMINATION OF RADIATION THERAPY BECAUSE OF POWER SUPPLY VOLTAGE VARIATION "On Wednesday May 18th, the licensee's radiation safety officer contacted the agency [Illinois Emergency Management Agency] to advise that a medical event had likely occurred the prior Friday. Based on their initial evaluation, 1 of the 10 fractions prescribed for a patient was not delivered as intended such that less than 50% of the expected dose was delivered during a fraction. "The written directive indicates that the patient was scheduled to undergo 10 treatments to her breast twice a day over a period of 5 days. Each treatment involved 340 centiGy for a total written directive prescription of 3,400 centiGy. During the 6th fraction after completion of treatments in channels 1 and 2, the unit experienced a power supply error. Sensing the power variation, the device automatically withdrew the source and did not complete the treatment for channel 3. Although additional attempts were made to clear the error and continue the treatment, none of the remaining 4 channels could be finished. The licensee had experienced similar problems with the device the previous week which had resulted in a service call on May 10. At that time the power supply was adjusted to ensure operation within specifications. The unit operated normally following the repair until the event on the 13th. The power supply as well as main controller board was subsequently replaced by the manufacturer Saturday morning and the patient returned that afternoon to complete the remaining portion of the 6th fraction. All the remaining fractions were delivered without incident. The fraction which finished the overall treatment was completed Tuesday. There have been no errors or incidents noted since the replacement of the above components. "The licensee is still investigating this incident with the manufacturer to conduct an engineering evaluation of the power supply failure, however the 'fail safe' design of the system operated as expected. The licensee's initial estimate was that the patient received 133 centiGy of the 340 centiGy intended fractional dose. The patient and the referring physician were advised of the event but since the remaining fractions of the treatment were completed under the revised treatment plan, no adverse affect on the patient is expected and no other additional action is anticipated." The intended dose for this fraction was 3.4 Gy. The dose received was 1.3 Gy. Illinois Report Number: 11058 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM DAREN PERRERO TO VINCE KLCO ON 5/24/11 @ 0902 EDT * * * The following information was received via email: "On May 23, 2011 the licensee's medical physicist provided information to the agency [Illinois Emergency Management Agency] which demonstrated that the target volume involved in the interrupted fraction received a dose of 217 cGy of the prescribed 340 cGy rather than the conservatively estimated 130 cGy. This dose to the patient treatment volume represents 63% of the prescribed dose and therefore does NOT constitute a medical event as identified in regulations." Notified R3DO (Cameron) and FSME EO (McIntosh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-05-26
46866 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-05-20 12:00 | 2011-05-20 13:23 | 2011-05-20 | MEDIA CONCERN ABOUT BOAT NEAR THE SITE "On 05/20/2011 at approximately 0728, an unidentified man was reported to be floating on a raft in the James River offshore of the Hog Island Wildlife Management Area. The individual had chains wrapped around his body and a suitcase and duffel bag in the raft. Station Security responded to facilitate local law enforcement actions. The individual in the raft was pulled to the shore and taken into custody. At no time was the operation of Surry Power Station threatened by the man's actions. "The site NRC Resident Inspector has been notified. "This notification is being transmitted in accordance with 10CFR50.72(b)(2)(xi) to ensure that the NRC is made aware of issues that may cause heightened public concern for the safety of the station." The man was approximately a mile offshore during this incident. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling Shutdown |  | Power Operation | Refueling Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-05-20
46865 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-05-18 | 2011-05-20 11:32 | 2011-05-20 | AGREEMENT STATE REPORT - LOST AND SUBSEQUENTLY RECOVERED TROXLER GAUGE The following information was received from the North Carolina Radiation Protection Section via e-mail: "On May 18, 2011, an employee of S&ME parked a company truck at his house. The truck had a Troxler 3411B Portable Nuclear Gauge double locked in an aluminum box in the bed of the truck. "The next morning, he discovered the truck missing. Company management was notified, who in turn notified Local Law Enforcement and the agency [State of North Carolina]. About 15 minutes after the Agency notification. the police determined that the vehicle had been towed. The explanation for the towing of the vehicle was that the vehicle, which was in front of the employees residence, had its wheels on the grass. "The vehicle was retrieved from the towing company. The gauge was still locked in its storage box and appeared untouched." "Device/Material Info: Troxler 3411B S/N 13772 Cs-137 S/N 50-2590 9 mCi Am-241 S/N 47-9185 44 mCi" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-05-25
46864 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-18 09:00 | 2011-05-19 20:22 | 2011-05-19 | AGREEMENT STATE REPORT - RADIOACTIVE SHIPMENT LOST IN TRANSIT "On May 19, 2011, the Agency [State of Texas] was notified by a shipper that on May 18, 2011, a package carrying a 297 Giga Becquerel Iridium (Ir) 192 source manufactured by Alpha-Omega Laboratory and shipped from Vinton, Louisiana was lost near the intersection of Rankin and Albine Westfield Roads in Houston, Texas. The source is used in a high dose afterloader. The source was being transported to DHL in Houston, Texas for shipment to the country of Brazil. The shipper stated that the door on the back of the truck popped opened and the driver could not see it open or any of the contents from the truck fall onto the road. The truck is a large truck with doors that swing open in the back. A member of the general public (MGP) saw several letters setting on the road and stopped to pick them up. He stated that he saw the small drum the source was packaged in across the road in a church parking lot and did not indicate that he saw any damage to the drum. He could not retrieve the drum because of the traffic and he was taking his wife to a doctor's appointment. On his way back from the doctor office about an hour later the MGP went back by the location where the drum had been and it was gone. He took the letters by a FedEx office and told them what had happened. FedEx responded by driving to the location and searching for the source. They also traced the path traveled by the truck three times, but they did not locate the source. The package the source is contained in is a Type A package, 34 cm in length, 34 cm wide, and 37 cm high and is similar to a 5 gallon paint bucket. The shipper stated that there was a locking device on the container. The container is labeled with a Yellow III label with a transport index of 1.3. Additional information will be provided as it is received in accordance with SA-300." Later, the state reported that the source has been located at a Houston Area Fire Department. The state will provide additional information as it is received. Texas Incident #: I - 8854 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-24
46863 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-19 14:07 | 2011-05-19 17:00 | 2011-05-19 | MANUAL REACTOR TRIP AFTER A MAIN CONDENSER TUBE LEAK "At 1407 CDT CPNPP [Comanche Peak Nuclear Power Plant] Unit-2 was manually tripped due to indication of a main condenser tube failure. The trip was uncomplicated, all control and shutdown banks fully inserted, neither emergency diesel generator started, all safety systems functioned as designed. Both motor driven and the turbine driven AFW [auxiliary feedwater] pumps started as required to restore steam generator level as a result of the trip. The turbine driven AFW pumps has been returned to auto start status. Currently Unit-2 is in mode 3, no-load Tave 557 degrees F with temperature being maintained with AFW and steam dumps to the main condenser. Recovery actions are currently being planned. All electrical busses are powered from offsite power and grid conditions are stable." The reactor was manually tripped because of rising sodium concentration in the main condenser/feedwater. The licensee notified the NRC Resident Inspector, State of Texas, and local government. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-05-19
46862 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-19 15:15 | 2011-05-19 16:40 | 2011-05-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN On May 19, 2011, the Agency [State of Texas] received notification from Texas A & M University's Radiation Safety Officer [RSO] that while removing all tritium exit signs (TES) from a dormitory prior to its demolition, they noted that a TES was missing. The RSO could not provide any additional information at this time. Additional information will be provided as it is received. Texas Event Number: I-8853 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-24
46861 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-10-02 | 2011-05-19 14:03 | 2011-05-19 | AGREEMENT STATE REPORT - PATIENT RECEIVED TWICE THE PRESCRIBED DOSE The following report was received via fax. "New York law prohibits the release of any identifiers in cases of medical events. Therefore, the facility name etc. is not contained in this report. "The licensee reported on 10/3/2007 that on 10/2/2007, a patient received 4 mCi 131 Iodine for a whole body scan instead of the 2 mCi that was ordered. The error was discovered after the radiopharmacy tried to reconcile their orders and shipments and found that a vial with 4 mCi [milliCurie] of 131 Iodine was missing and called the hospital. The nuclear medicine department staff inspected the waste sent from the department to the environmental services section of the hospital and found that the box they had sent did trigger an alarm and had been isolated. On closer inspection, they found one vial containing 2 mCi Iodine 131. An extra vial of Iodine 131 of 4 mCi (meant for another order) had been placed by the nuclear pharmacy in the box and sent along with the 2 vials of 2 mCi each. The technologist retrieved this mCi vial and one 2 mCi vial and gave the 4 mCi iodine capsule to the patient. "The NM [Nuclear Medicine] technologist had retrieved 2 vials from the box on 10/2/2007. The order was for 2 vials, one for the patient dose and the other the standard. Failures: 1. She failed to verify that the labels on the dose vials matched the labels on the shipping box. 2. She failed to read the label on the vial containing the capsule that she gave to the patient. 3. She failed to assay the patient dose using the dose calibrator. 4. She failed to survey the box before sending it to the environmental services for disposal. All 4 failures are in violation of the licensee's protocol for the use of radioactive materials. "The authorized user physician believes that the dose of 4 mCi for a whole body scan is still within the range in use at the facility and does not expect any harm to the patient as result of this event. A health physicist was consulted and doses to various organs were estimated and documented. To prevent a recurrence, they have implemented a TlME OUT protocol for administration of RAM [radioactive material], which requires that 2 technologists must agree on the correctness of the activity, assay and document it on both a hard copy log and the computer in the hot lab. "These steps are adequate. "This event is closed." New York Event Number: NY-11-03 New York State DOH Internal Tracking Number 566 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-25
46860 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-06-20 | 2011-05-19 14:36 | 2011-05-19 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION USING HDR AFTERLOADER The following was received from the State of New York via fax: "New York law prohibits the release of any identifiers In cases of medical events. Therefore, the facility name etc. is not contained in this report. "The licensee telephoned [the State of New York] on 6/20/07, to report misadministration on 6/19/07. Patient was a 73 year old woman receiving the second of her 5 fractions of HDR for cancer of the cervix. It was a ring and tandem setup. 600 cGy prescribed to point A in the cervix. Patient moved about halfway through the treatment and with the applicator about 6 cm inferior to the cervix, the cervix received about 382 cGy while the vagina received about 218 cGy. "During a conference call between Bureau staff and facility staff including radiation oncologist, physicist, and administrator, it was learned that the patient had had 10 children and muscles were not tight. Prior to the start of the treatment, she complained of discomfort from the foley catheter due to bladder distention and the clamp was loosened a bit. She continued to be uncomfortable and moved during the treatment of 644 seconds. Therapists reassured her and completed the treatment, despite the movement. It was discovered later that the applicator had slid inferior by about 6 cm. "The radiation oncologist believes that the 218 cGy to the vagina will not impact the patient adversely because there is some disease in that area. The patient and the referring physician have been informed. The physician does not plan to make up for the deficit dose to point A in the cervix. Facility submitted an RCA and to prevent recurrence, they have implemented the following measures. (1) Minimize time between applicator insertion and treatment. (2) Use of stabilizing devices at the time of insertion to minimize applicator movement (3) Use anatomical markings at the time of device insertion to help verify applicator position just prior to and during treatment (4) Expand patient instruction with increased emphasis on need to remain still and (5) Staff education on patient monitoring prior to and during treatment, with applicator position verification added to physics checklist. "These are sufficient. "As of 5/13/09, the patient is free of disease and complications. "This event may be closed." HDR Brachytherapy misadministration (NYS DOH Internal Tracking No. 548). New York Event Number NY-11-01. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-25
46859 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-07-02 | 2011-05-19 13:03 | 2011-05-19 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION USING HDR AFTERLOADER The following was received from the State of New York via fax: "New York law prohibits the release of any identifiers in cases of medical events. Therefore, the facility name etc. is not contained in this report. "The licensee called on 7/2/07 to report an event involving HDR unit. Patient did not get incorrect treatment. In fact patient did not receive any therapeutic dose on this session. Here is what happened. "A patient was receiving mammosite therapy with the Nucletron HDR unit. During this session, the therapist went into the treatment room, and placed the transfer tube on the patient (across from right superior to left inferior) but did not connect it to the catheter in the patient's breast. Then she went out to get the doctor. Neither of them checked to make sure that the catheter was connected to the transfer tube through the connector. Then they delivered the treatment. Since the mammosite connector (closed end) was attached to the transfer tube tune, there was no interlock. But there was no sensor or interlock to inform them that there was nothing connected to the other end of this connector. So the source proceeded as programmed and stuck out 16 cm from the end of the transfer tube in the connector tube. They saw this only when they went in to disconnect after treatment. According to their calculations, the source was at distance of 38 cm from the patient's left leg. Notice that the transfer tube is part of Nucletron equipment. The connector that connects from the transfer tube to the catheter is part of mammosite (Cytec) equipment. There was no sensor to ensure that this connection was made. It appears that the connector's closed end was sticking out in the air by the patient's leg and the programmed positions for treatment resulted in the source being in the connector in air about 16 cm from the patient's left leg. Physician/RSO admitted over the phone that the treating physician did not check the applicator and connection prior to treatment. The patient received the correct treatment later. "Policy and procedure reviewed. 'The physician will log into the treatment system to initiate treatment delivery and he will be responsible to ensure that all treatment parameters and connections are satisfied'. A copy of the Cytec and Medwatch correspondence was included with the documentation. "This case can now be closed." HDR Brachytherapy event (NYS DOH Internal Tracking No. 553). NY Event Report Number: NY-11-02. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2011-05-25
46858 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-18 14:00 | 2011-05-19 12:00 | 2011-05-19 | AGREEMENT STATE - STUCK OPEN GAUGE SHUTTER "On May 19, 2011, the Agency [State of Texas] was notified by the licensee that the shutter on an Ohmart/Vega model SH- F2 containing 1.6 curies of Cesium (Cs) - 137 would not close. The licensee stated that they were making preparations to enter a steel vessel that is 12 inches thick to perform maintenance. The gauge shutter was to be closed before maintenance was started. Open is the normal position for the shutter therefore the gauge does not pose any additional exposure hazard. Access to the tank has been secured and will not be granted until the gauge is repaired. The licensee has contacted a service provider to make the repairs. The gauge was installed in October 2009. The cause for the failure is under investigation. Additional information will be provided as it is received in accordance with SA-300." Texas Incident number: I - 8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-24
46857 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-05-17 10:30 | 2011-05-17 18:40 | 2011-05-17 | TEMPORARY BLOCKAGE OF SUCTION SOURCE FOR CONTAINMENT COOLING SERVICE WATER "On 5/17/2011, at 1404 CDT, Dresden Operations was notified by a Mechanical Maintenance Supervisor that both intake bay 13 stop logs were mistakenly installed during routine bay cleaning on 5/17/2011 at 1030. Installation of both bay 13 stop logs removes the suction source for the Containment Cooling Service Water (CCSW) system and renders the CCSW systems inoperable for both Dresden Units 2 and 3. Appropriate Technical Specification Required Actions were entered which direct restoration of at least one train of CCSW within 8 hours on each unit. Mechanical Maintenance was directed to remove the stop logs from Bay 13. At 1410 stop logs were removed and CCSW was declared operable for both Unit 2 and Unit 3. This event is reportable under 10 CFR 50.72 (b) (3) (v) an "Event or Condition That Could Have Prevented Fulfillment of a Safety Function." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT RHR INOP |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-05-17
46856 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-17 09:54 | 2011-05-17 15:42 | 2011-05-17 | EMERGENCY DIESEL GENERATORS START DUE TO MAINTENANCE ACTIVITIES "At 0954 [PDT] on May 17, 2011, Unit 1 startup power was lost following actuation of the 230 kV line pilot wire differential relay 287X. Loss of power to the Unit 1 12 kV startup bus produced a startup undervoltage signal that caused all Unit 1 emergency diesel generators (EDGs) to start in a standby mode. The EDGs started as designed with no problems observed. No vital loads were affected as a result of the 12 kV bus loss and subsequent undervoltage. Actuation of differential relay 287X was due to maintenance activities on the safeguard relay board where differential relay 287X is installed. "At 1056 on May 17, 2011, the Unit 112 kV startup power system was made available to supply power to the 4 kV vital buses. All Unit 1 EDGs were shutdown and returned to their normal at-power standby configuration, and differential relay 287X [was] reset. "Unit 2 was unaffected by this event. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-17
46855 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-02-16 | 2011-05-17 14:14 | 2011-05-17 | AGREEMENT STATE REPORT - DOSE TO FETUS DURING THYROID SCAN The following report was received from the state via fax: "A patient having a thyroid scan was administered 4 mCi of I-131 while in a pregnant condition. The circumstances under which the dose was administered are under investigation. The dose to the developing fetus is also under investigation. The whole body dose to the fetus is estimated to be 1 rad at this time. "The discovery date [of 4/15/11] is an estimate. The real dose of discovery will be reported during the investigation. Also, the licensee was allowed 15 working days to issue a report to [the Massachusetts Radiation Control Program]. [The Massachusetts Radiation Control Program] received that report on May 12, 2011." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-05-20
46854 | -1 | LANTHEUS MEDICAL IMAGING |  |  |  |  | 2011-05-13 12:00 | 2011-05-16 14:09 | 2011-05-17 | MEDICAL EVENT - WRONG RADIOPHARMACEUTICAL ADMINISTERED TO PATIENT On 5/13/2011, a patient at the Lantheus Medical Imaging center was administered Indium 111 (Oxine - for labeling white blood cells) instead of Indium 111 (DTPA - for brain study), which was the prescribed radiopharmaceutical. Less than 1 milliCurie of Indium 111 (Oxine) was injected into the patient. The dose received by the patient was less than 5 Rem, and no injury was caused to the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 5/17/11 AT 0939 FROM EDWARDO DIAZ TO MARK ABRAMOVITZ * * * This event has been determined by the licensee not to be a medical event because the total dose is less than 0.05 Sv (5 Rem) required in 10CFR35.3045. Notified the R1DO (Gray) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | PR | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2011-05-22
46853 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-05-15 12:54 | 2011-05-15 21:39 | 2011-05-20 | PORTION OF HIGH PRESSURE FIRE WATER SYSTEM DECLARED INOPERABLE "At 1254 CDT, on 05/15/2011, the Plant Shift Superintendent was notified that the C-333 High Pressure Fire Water (HPFW) Sprinkler System C-14 had been inspected by Fire Services and eleven sprinkler heads had visible corrosion on them. The system configuration was evaluated using EN-C-822-99-047, 'Effects of Impaired Sprinkler Heads on System Operability' and determined that with these heads potentially impaired, a portion of the building would not have sufficient sprinkler coverage. The HPFW system is required to be operable according to TSR LCO 2.4.4.5. HPFW system C-14 was declared inoperable and TSR LCO 2.4.4.5 Required Action B was implemented for the area without sprinkler coverage. Based on past testing results, there is a possibility that the heads would have been able to perform their specified safety function. Once the heads are removed from the system, testing will be performed to determine the actual affect on operability. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident Inspector has been notified of this event. "PGDP [Paducah Gaseous Diffusion Plant] Assessment and Tracking Report No. ATR-11-1192; PGDP Event Report No. PAD-2011-08; Responsible Division: Operations "An hourly fire patrol is being conducted in the affected area. [Licensee] estimated correction date: 5/20/2011." * * * RETRACTION FROM BILLY WALLACE TO JOE O'HARA AT 1145 EDT ON 5/20/11 * * * "Subsequent to the event, the corroded sprinkler heads were replaced with new heads and the removed heads were tested in the laboratory. Testing by the laboratory has shown that six of the 10 removed sprinkler heads would have performed their safety function, five of the heads would not have performed their safety function, but these heads would not affect the system operability. The conclusion of the tests is that the C-333 sprinkler system C-14 would have performed its intended safety function if called upon. "The NRC Senior Resident Inspector has been notified of this retraction." Notified R2DO(Shaeffer) and NMSS EO(Damon) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2011-05-15
46852 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-05-14 02:45 | 2011-05-14 04:32 | 2011-05-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INABILITY TO MAINTAIN SPECIFIED DIFFERENTIAL PRESSURE BETWEEN DRYWELL AND SUPPRESSION CHAMBER "Following startup from RFO [Refueling Outage] 18, at approximately 14% reactor power, PNPS [Pilgrim Nuclear Power Station] was unable to set the conditions required to demonstrate the drywell to suppression chamber decay rate is less than 25% of the differential pressure decay rate for the maximum allowable bypass area of 0.2 ft2 [as required by] TS [Technical Specification] 3.7.A.4(b). "Prior to exceeding 15% power, PNPS Technical Specifications require differential pressure between the drywell and suppression chamber to be greater than 1.17 psid. The licensee was not able to achieve this delta pressure and initiated troubleshooting to determine the cause. A plant shutdown is being initiated to continue this effort. "The plant is in a stable condition. Investigation is continuing into the failure to establish test conditions. There is no threat to the health and safety of the public as a result of this condition." The licensee suspects leakby in the Drywell to Torus vacuum breaker but will not be able to verify until the plant is shutdown. The licensee has notified the NRC Resident Inspector and will be notifying the State of Massachusetts. | 14 | 0 | 0 | 14 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-05-14
46851 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-05-13 09:00 | 2011-05-13 12:39 | 2011-05-13 | SHIPPING CONTAINER CONTAMINATION LEVEL EXCEEDS THE SURFACE CONTAMINATION LIMITS The following information was received by e-mail: "Empty [Model] LR-230 shipping containers received from off-site where one (1) LR-230 had removable surface contamination above limits for alpha/beta activity on the outer surface of the container (~7,800 dpm/100 sq cm alpha and 13,300 dpm/100 sq cm beta). The LR-230 shipping containers are used to transport uranyl nitrate (<5.0 wt % U-235). Contamination was not related to container integrity. Contamination appears to be related to minor drips during unloading. Areas have been successfully decontaminated. "There were no actual or potential safety consequences to workers, the public, or the environment." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2011-05-17
46850 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-11 | 2011-05-13 08:00 | 2011-05-18 | AGREEMENT STATE REPORT - SHUTTER STUCK OPEN ON NUCLEAR GAUGE The following information from the State was received by email: "On May 12, 2011, the Agency [Texas Department of Health] was notified by the licensee that while performing a routine inspection of a Ohmart/Vega model SH-F2 nuclear gauge containing 200 milliCuries of Cesium (Cs) - 137 they found the shutter for the device stuck in the open position. The licensee believes the probable cause for the event is a buildup of debris in the operating mechanism of the gauge. The gauge is used for level detection on a vent stack in an area of the plant not routinely occupied. The licensee is lubricating and trying to cycle the shutter frequently. The licensee has contacted a service provider to assist them if needed. No exposure to any personnel has occurred due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No: I-8849 * * * UPDATE FROM ART TUCKER TO CHARLES TEAL VIA EMAIL ON 5/18/11 @ 0915 EDT * * * "On May 16, 2011, the licensee reported that the repeated lubrication of the shutter was successful and that the shutter was now working as designed. The report also stated that the event was discovered on May 11, 2011, not May 12, 2011, as first reported." Notified R4DO (Shannon) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-18
46849 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-18 | 2011-05-13 07:59 | 2011-05-13 | AGREEMENT STATE REPORT - MISSING SHUTTER ON NUCLEAR GAUGE The following information from the State was received by email: "On May 12, 2011, the Agency [Texas Department of Health] was notified by the licensee that on April 18, 2011, while conducting a routine inspection of a NDC model 8000 TDI nuclear gauge containing 80 milliCuries of Americium (Am) - 241 they found the shutter for the device was missing. The licensee conducted a search for the shutter, but it was not found. The licensee contacted the manufacturer for assistance in repairing the gauge. The licensee placed a lead plate over the shutter to prevent exposure to personnel. The gauge was repaired by the manufacturer on April 29, 2011. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No: I-8848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-18
46848 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-12 | 2011-05-13 07:50 | 2011-05-13 | AGREEMENT STATE REPORT - STUCK SHUTTER ON NUCLEAR GAUGE The following information from the State was received by email: "On May 12, 2011, the Agency [Texas Department of Health] was notified by the licensee that the shutter on a Ohmart/Vega Model BAL nuclear gauge containing 100 milliCuries of Strontium (Sr) - 90 was stuck in the closed position. The gauge has an electronic shutter, which is not functioning. The licensee contacted their service provider for assistance in repairing the gauge. The cause for the failure is being investigated. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No: I-8847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-18
46847 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-12 18:25 | 2011-05-13 01:53 | 2011-05-13 | LOSS OF SHUTDOWN COOLING "At 1825 CDT on 05/12/2011, with Browns Ferry Nuclear Plant Unit 3 in Mode 4, Browns Ferry Nuclear Plant PCIS [Primary Containment Isolation System] relay maintenance activities for a Group 1 PCIS relay inadvertently interrupted the neutral for a Group 2 PCIS relay and a Group 2 PCIS isolation occurred resulting in a loss of Shutdown Cooling. Relays were reset and Shutdown Cooling was restored at 1905 CDT. Moderator temperature prior to the event was 112.5 degrees F and the highest moderator temperature recorded during the loss of Shutdown Cooling was 122 degrees F. "This condition is reportable under 10CFR50.72(b)(3)(v) - Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: B.) Remove residual heat. "This is also reportable as a 60 day written report IAW 10CFR 50.73(a)(2)(v). "The NRC Resident Inspector has been notified of this event. "This event was entered into the licensee's Corrective Action Program as SR# 368205". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-05-13
46846 | 0 | ASCO VALVE |  |  |  |  | 2011-05-12 | 2011-05-12 16:14 | 2011-05-12 | U-RINGS FABRICATED WITH INCORRECT MATERIAL "The following was received via facsimile: "This report relates to two NP8344E series four-way solenoid valves found to be leaking through the exhaust port in both the energized and de-energized states. "Background - On January 21, 2011, ASCO Valve, Inc. (ASCO) was notified by AREVA that a four-way solenoid valve NP8344A75E AC, (serial number F623557002-002) from the Dresden Station was leaking from the exhaust port in both the energized and de-energized states. AREVA reported that Exelon Labs had performed a Fourier Transform Infrared Spectroscopy (FTIR) analysis which indicated the piston U-ring exhibited properties consistent with a Nitrile compound instead of Teflon« coated Ethylene Propylene as required by the ASCO design drawing. The valve itself was not returned to ASCO. At ASCO's request, Exelon returned the U-ring on January 27, 2011. ASCO provided a letter to Dresden Station on February 3, 2011 (Reference A) maintaining the correct U-ring material was installed at the time of shipment and that no additional action was required. "The second occurrence involved another four-way solenoid valve, NPK8344A072E DC, (serial number F337837-2), from PSEG Nuclear's Salem station, returned to ASCO on Service RMA 47113 on February 25, 2011. The valve was brought to ASCO where testing confirmed the valve was leaking through the exhaust ports in both the energized and de-energized states. The inspection of parts showed that the U-ring material had become brittle. If the U-ring becomes brittle, it may no longer perform its sealing function. "ASCO Investigation Results - The above referenced valves were manufactured in 1992 (Dresden) and 1995 (Salem) respectively. It was determined that both valves used the same piston U-ring, part number 029043-024-S. This U-ring is common to both the 3/8" and 1/2" NPT valve constructions, A review of ASCO's incoming and dedication inspection records indicated that these U-rings were Teflon« coated Ethylene Propylene. The piston U-rings from the Salem and Dresden valves, along with a piston U-ring from ASCO's current stock, were sent to a third party laboratory for a FTIR analysis. The U-rings from both the Salem and Dresden valves were determined by the laboratory to be Nitrile. The U-ring from current stock was determined to be Teflon« coated Ethylene Propylene, as called for by the design drawings, "Impact on Performance - The use of a Nitrile piston U-ring could potentially reduce the valve life and result in leakage through the exhaust port. "Initial Action - FTIR analysis confirmed that the piston U-ring in ASCO's current stock was Teflon« coated Ethylene Propylene. ASCO records disclosed no prior cases of piston U-rings fabricated with incorrect material. Discussions with the distributor of the U-rings disclosed no other cases of improper material. "Corrective Action - The customers that were shipped potentially affected NP8344E valves are being notified of the potential deviation. All variations of NP8344A72E, NP8344A73E, NP8344A74E, NP8344A75E, NP8344850E, NP8344B52E, NP8344B62E, and NP8344B64E manufactured from 1992 through 1995 are recommended to be monitored for leakage. Due to the qualified service life and date of manufacture, it is believed a majority of these valves are no longer in service, Subsequent to 1995, ASCO has implemented a more rigorous lot and batch control to verify the material compound at incoming and dedication inspection. This action further enhanced traceability of resilient materials used in specific production lots. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-05-12
46845 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-05-12 08:15 | 2011-05-12 11:47 | 2011-05-12 | CONTRACT EMPLOYEE ADMITTED TO USING ILLEGAL SUBSTANCE A contract employee was questioned and admitted to using an illegal substance. The employee's access to the plant been suspended. Local law enforcement has custody of the individual. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | OFFSITE NOTIFICATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.719 | 50.72(b)(2)(xi) |  |  | 0 | 2011-05-12
46844 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2011-03-20 07:24 | 2011-05-12 11:29 | 2011-05-12 | "A" TRAIN REACTOR PROTECTION SYSTEM UNEXPECTEDLY DE-ENERGIZED RESULTING IN A HALF SCRAM SIGNAL "On March 20, 2011, at approximately 7:24 a.m. CDT, the 'A' reactor protection system (RPS) bus was unexpectedly de-energized. Plant systems responded as designed, resulting in a half-scram signal and the actuation of the Division 1 primary containment isolation sub-system. The Division 1 primary containment isolation valves closed in several balance-of-plant systems. After confirming that no valid RPS trip signal had occurred, operators executed the appropriate procedures to return the affected systems to the proper configuration, and to reset the half-scram signal. Plant capacity was not affected by this event. "This event is being reported in accordance with 10CFR50.73(a)(1) as an automatic actuation of the Division 1 primary containment isolation valves in multiple systems resulting from an invalid signal. "Each of the two redundant distribution buses in the RPS system is normally powered by its own motor-generator (MG) set. The investigation of this event determined that the output breaker of the 'A' MG set had tripped open. The most likely cause for this trip was a malfunction of the over-voltage relay circuit card in the MG set. Although the troubleshooting was inconclusive, there apparently was a momentary transient in the output of the trip setpoint adjustment potentiometer on the card, likely caused by oxidation on the contacting surface between the wiper arm and the windings. "The over-voltage relay card on the 'A' MG set was replaced, and the unit was restored to service. Preventative maintenance tasks are being revised to periodically cycle all potentiometers in the MG set control circuits to wipe oxidation from the windings." The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-12
46843 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-11 | 2011-05-12 11:29 | 2011-05-12 | AGREEMENT STATE REPORT - OPERATING MECHANISM FAILED ON GAUGE The following information was obtained from the State of Texas via email: "On May 12, 2011, the Agency [state] was notified that the operating mechanism on an Ohmart Model SHLM-BR-2 nuclear gauge containing 1,000 milliCuries of Cesium (Cs) 137 had failed. The operating mechanism consists of two rods. The source is mounted on one rod and the other rod is used to move the source into and out of the source holder. The pin used to connect the two rods together broke so the source can not be manipulated. The source is currently located inside the vessel in its normal operating position. There is no increased risk of radiation exposure to any individual. The licensee is making arrangements to have the gauge repaired. The cause for the failure is still being investigated. Additional information will be provided as it is received in accordance with SA-300." TX Incident Number I-8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-17
46842 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-09-27 | 2011-05-11 17:11 | 2011-05-11 | AGREEMENT STATE REPORT - DELIVERED DOSE DIFFERENT THAN PRESCRIBED DOSE The following information was received by e-mail: "The Director of Oncology Services at Decatur Memorial Hospital contacted the Agency [state] to give a preliminary notification of a medical event that happened in September 2006. Following the receipt of additional training by their oncologists regarding medical event criteria, they began to conduct a retrospective review of past prostate cancer treatments that have been performed at their facility since 2002. A particular case was readily notable when the comparison of dose intended vs. dose received was made. Using 81 I-125 seeds, the prescribed dose to the target (D100) was 132.5 Gray, the delivered dose was 32.5 Gray which is only 24.5 percent of the intended dose. However the review showed all seeds intended to be implanted were successfully placed under guided ultrasound and post operative x-ray imaging showed all seeds to be within the target volume. Subsequent follow-ups with the patient over the past 5 years have shown a significant reduction in PSA levels, no evidence of recurrent cancer and no adverse side effects to the bladder, rectum, urethra or other associated dysfunction for the now 87 year old patient. At the time of implant, there were no notes in the surgical file to suggest a change in shape or size of the prostate which would suggest pre-treatment planning performed was invalid. Routine CT imaging conducted at 30 days post treatment as part of the follow-up process showed the prostate had expected swelling present. When dosimetry calculations were performed using the increase in volume, the total delivered dose value for the intended treatment site fell, resulting in the criteria for a medical event being met. The attending oncologist does not intend to notify the patient of this recent discovery. The doctor believes that such a notification would be against his medical judgment and would do unnecessary harm to the patient in this instance considering the success of the treatment. "The responsible oncologists and the rest of the treatment team were interviewed by the [Illinois Emergency Management] Agency yesterday afternoon regarding additional details of this event and planned actions. The team indicated that [they] would continue review of the 240 cases but didn't believe that any changes to its current program were warranted at this time based on this one observation. Anecdotally, none of the physicians could remember any of their patients having adverse or unexpected effects during subsequent follow-ups. Nor had any [patients] required additional or supplemental treatment of any kind (i.e. hormonal, surgery, external beam, additional seeds) for recurrent cancer. [The team] couldn't rule out that a similar medical event requiring reporting wouldn't be discovered as they continued their review." Illinois Event: IL11053 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-05-17
46841 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-05-11 09:00 | 2011-05-11 15:50 | 2011-05-12 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO VENTILATION ROLL FILTER MAINTENANCE "During an Emergency Preparedness drill on May 11, 2011 the Hatch Nuclear Plant's Technical Support Center (TSC) HVAC [Heating, Ventilation and Air-Conditioning] system's Roll Filter Indicating Light on the 1X75B001 TSC Air Handling Unit was illuminated. The ARP [Alarm Response Procedure] response actions in the 73EP-EIP-016-0 indicated that the roll filter needed to be replaced. Reference [Hatch] Condition Report 2011106603. "The TSC HVAC is being considered non-functional during the performance of this corrective work activity. If an emergency condition occurs during the time these work activities are being performed, which requires activation of the TSC, the contingency plan calls for utilization of the TSC, as long as radiological conditions allow for habitability of the facility. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described In NUREG-1022, Rev. 1 since this activity affects the functionality of the TSC emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM KENNY HUNTER TO VINCE KLCO ON 5/12/2011 AT 1443 EDT * * * The TSC has been returned to service following completion of filter maintenance. The licensee notified the NRC Resident Inspector. Notified the R2DO (Guthrie). | 100 | 55 | 0 | 100 | 55 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-11
46840 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-11 02:01 | 2011-05-11 07:30 | 2011-05-11 | LOSS OF >25% OF EMERGENCY NOTIFICATION SYSTEM SIRENS DUE TO ADVERSE WEATHER "Greater than 25% of the Catawba offsite Alert and Notification Sirens are unavailable due to severe thunderstorm related power outages in the area. As of approximately 0200 EDT, 40 of 89 sirens were unavailable. Power restoration efforts in the area are underway." As of 0730 EDT, 27 of the 89 sirens remain out of service. The licensee notified the State of North Carolina including Mecklenburg and Gaston Counties, and the State of South Carolina including York County. They also will be notifying the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-11
46839 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-05-09 15:18 | 2011-05-11 01:21 | 2011-05-11 | POTENTIAL VALVE MISPOSITIONING LED TO A CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS "On May 9, 2011, at 1518 Eastern Daylight Saving Time (EDT), WBN [Watts Bar Nuclear] started a Safety Injection Pump and began to inject into the Reactor Coolant System contrary to Technical Specification Limiting Condition for Operation 3.4.12, which requires in part for Mode 5 that a Cold Overpressure Mitigation System (COMS) shall be OPERABLE with a maximum of one charging pump and no safety injection pump capable of injecting into the RCS and the accumulators isolated. "The RCS pressure rise was recognized immediately, and the pump was secured within 27 seconds. The pressure reached a maximum of 328 psig. which is below the relief valve setpoint, so no structure, system, or component pressure limit was exceeded at any time. LCO 3.4.12 Condition A was entered immediately. At 1521, the pump breaker was directed to be racked out, and the breaker was reported racked out and verified by 1600, at which time LCO 3.4.12 was exited. "This event was determined to be reportable as a condition prohibited by Technical Specifications in accordance with 10 CFR 50.73(a) (2)(i)(b). This notification is made in accordance with Watts Bar License condition 2.G. "The NRC Resident Inspector has been notified of this event and event notification." The licensee is investigating the likelihood of a valve mispositioning. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2011-05-11
46838 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-05-10 18:38 | 2011-05-10 19:16 | 2011-05-18 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for more details. * * * UPDATE AT 1022 EDT ON 5/18/11 FROM CORY LASSEIGNE TO CHARLES TEAL * * * The licensee is retracting this report after further assessment and has informed the NRC Resident Inspector. Notified R2DO (Shaeffer) and 73.71 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-05-10
46837 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-05-10 13:15 | 2011-05-10 16:15 | 2011-05-10 | REACTOR PROTECTION SYSTEM ACTUATION DURING START-UP "At 1315 hours on Tuesday, May 10, 2011, with the Reactor Mode Select Switch in Startup, the Reactor Protection System (RPS) actuated due to a valid Hi-Hi trip signal from the Intermediate Range Monitors (IRMs) of the Neutron Monitoring System. At the time of the RPS actuation, reactor thermal power was four (4)% and control rods were being withdrawn as part of a planned reactor startup from a refueling outage. The RPS actuation signal resulted in a reactor scram. The IRMs were in range 7 when the scram occurred. "All control rods automatically inserted in accordance with design. No other ESF actuation signals were generated. The reactor scram was not part of pre-planned test or reactor operation. The cause of the Hi-Hi IRM trip signal is under investigation. "This event had no impact on the health and/or safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This 4-hour notification is being made in accordance with 10CFR50.72(b)(2)(iv)(B)." The unit is in a normal post trip electrical alignment. Decay heat is being removed via the main steam line drains to the main condenser. The licensee will notify the Massachusetts Emergency Management Agency. | 0 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-05-10
46836 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-05-05 | 2011-05-10 14:28 | 2011-05-10 | AGREEMENT STATE REPORT - STUCK FIXED GAUGE SHUTTER MECHANISM The following information was received via facsimile: "On May 5, 2011, the Licensee's Radiation Safety Officer reported via phone message that the shutter mechanism on an installed fix gauge failed to close. The gauge is an Ohmart model SHRM-3 with a 500 mCi Cesium-137 source. This malfunction was discovered during routine maintenance testing. No persons were exposed to radiation as a result of the malfunction. The Licensee has restricted access to the area and has scheduled repairs to be done by the manufacturer. DHS plans to perform a follow up inspection within the next 6 months." Wisconsin Event Report # WI-110004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-05-13
46835 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-10 | 2011-05-10 12:43 | 2011-05-10 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE "On May 10, 2011, the Agency [Texas Department of Health] was notified by a licensee that while conducting radiography operations at a temporary job site, a pipe fell on the guide tube of a QSA Model 880D camera. The pipe damaged the guide tube preventing the radiographer from retracting the 34.1 curie Iridium (Ir) -192 source into the camera. The radiographer contacted his supervisor and a source recovery team was sent to the location. "The recovery team was able to repair the guide tube enough to retract the source into the camera. The camera was returned to the licensee's facility for inspection. There was no exposure to a member of the general public and the highest exposure to a member of the recovery team was 28 millirem for the event. "The investigation into this event is ongoing. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No. I-8844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-13
46834 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-19 | 2011-05-10 12:16 | 2011-05-10 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY CAMERA SOURCE The following information was received via facsimile: "On May 10, 2011, the Agency [Texas Department of Health] received written notification from a licensee that on April 19, 2011, at approximately 12:45 p.m. while performing radiographic operations on a tank, a radiographer found he was unable to retract a 58.6 Curie Iridium (Ir) -192 source into to a QSA Model 880D radiography camera. The radiographers working with the camera immediately repositioned the restricted area barricade to ensure that the barricade was set at less than 2 millirem per hour. The radiographers contacted their office and two source retrieval supervisors immediately proceeded to the jobsite. The Site Radiation Safety Officer was contacted and went to the location. "The source retrieval team arrived at the secured barricaded area at 1:40 p.m. The radiographers maintained visual surveillance to ensure no members of the public had entered the area. The exposure device was adjacent to the tank's exterior; secured by a magnetic plate lifter, and located approximately 40 feet above ground. The exposure device was removed from the tank using a JLG lift and lowered to the ground. The guide tube was removed from the front of the camera and it was discovered that the source pigtail was sticking out of the front of the camera about one and a half inches. The source was manually retracted to the shielded position and locked in place. A radiation survey of the camera found the readings to be normal. No one exceeded any exposure limits and there was no exposure to any member of the general public. The camera was transported to the licensee's facility and inspected. The camera has been returned to the manufacturer for inspection and repair. The investigation into this event is on going. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-8843. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-13
46833 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-05-10 09:15 | 2011-05-10 09:10 | 2011-05-10 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "Dose assessment cannot be performed onsite. "Pursuant to 10CFR50.72 (b)(3)(xiii), Monticello Nuclear Generating Plant is reporting a planned loss of emergency assessment capability scheduled for 0915 hours on May 10, 2011 for system maintenance. Dose assessment in the control room, TSC, and EOF are non-functional. Main meteorological tower data is unavailable. Projected outage duration is approximately 7 hours. Control room and local instrumentation/annunciation remain available for accident assessment. Telephone lines remain available between site emergency response facilities and offsite agencies for communication of plant status information. Dose assessment capabilities will exist at the backup EOF. Backup meteorological data will be available in the control room, TSC, and EOF. " The licensee will not be in any Technical Specification action statements as a result of this evolution. The NRC Resident Inspector has been notified. * * * UPDATE FROM JEFF OLSON TO PETE SNYDER ON 5/10/11 AT 1650 EDT * * * The licensee has restored their dose assessment capability. Notified R3DO (Passehl). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-10
46832 | 0 | ESCANABA PAPER COMPANY |  |  |  |  | 2011-05-09 11:00 | 2011-05-09 17:07 | 2011-05-09 | BROKEN SHUTTER HANDLE ON LEVEL GAUGE While performing a shutter check on a Kay Ray Model 7050, serial number 1019, level gauge, the shutter handle broke. The gauge is still in service at this time. No personnel exposures occurred as a result of this event. The gauge manufacturer will be contacted for repair guidance. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-05-09
46831 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-05-08 07:30 | 2011-05-09 11:10 | 2011-05-09 | 24 HOUR REPORT DUE TO LOSS OF VACUUM PUMPS FOR AIR AND STACK MONITORING "At approximately 0740 [CDT on 5/8/11] the plant experienced a total power outage. [The air monitoring vacuum pumps were not available during a power outage. This is a 24-hour reportable item under 10 CFR 40.60(b)(2)]. The power failure procedures were followed and a plant census was conducted and all personal were accounted for. Power was restored to the plant at approximately 0900 [CDT on 5/8/11]. The [loss of power to the site was due to a loss of power at the Joppa electrical substation]. The power was rerouted through Metropolis." The loss of power to the site had no other impacts on plant safety. Normal offsite power has been re-established. Reported to Richard Gibson Region II Senior Fuel Cycle Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2011-05-09
46830 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-05-09 07:22 | 2011-05-09 08:44 | 2011-05-09 | AUTOMATIC REACTOR TRIP UPON TURBINE TRIP DUE TO MAIN GENERATOR LOCKOUT "With Unit 2 at 100% power and Unit 1 in Mode 6 and severe weather in the vicinity, [a] Unit 2 Main Generator Lockout trip occurred at 0722 [CDT]. The reactor trip was 'Turbine Trip'. Procedure 2E-0, 'Reactor Trip or Safety Injection' was completed at 0725 hrs. [with] no Safety Injection required. [Procedure] 2ES-0.1, 'Reactor Trip Recovery' is in progress. Offsite power remains on all safeguards buses for both units. [The] 21 and 22 AFW [Auxiliary Feed Water] pumps automatically started on steam generator low level and are supplying Unit 2 steam generators. Unit 1 shutdown cooling was not affected. "Reportable actuations are: Unit 2 Reactor Protection (scram), Unit 2 AFW pumps automatic start." The licensee has notified the State of Wisconsin, the State of Minnesota, the Prairie Island Indian Nation and the NRC Resident Inspector. They will be issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-05-09
46829 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-05-08 08:25 | 2011-05-08 13:48 | 2011-05-08 | MALFUNCTIONING TECHNICAL SUPPORT CENTER VENTILATION "The facility Technical Support Center (TSC) has been rendered non-functional due to a malfunctioning TSC ventilation system. Investigation into the cause of elevated TSC room temperature led to the discovery of a tripped condensing unit compressor. Repairs to the TSC ventilation system were immediately initiated with high priority. "Compensatory measures per site procedure FNP-0-EIP-6.O (TSC Setup and Activation) for maintaining emergency assessment, off-site response, and off-site communication capabilities were immediately put in place. These measures include the conditional relocation of the TSC staff in the event of a declared emergency if the Emergency Director deems the TSC to be uninhabitable." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-08
46828 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2011-05-07 08:27 | 2011-05-07 08:33 | 2011-05-07 | EMERGENCY DATA SYSTEMS OUT OF SERVICE DUE TO PLANNED MODIFICATION "At 0827 hours EDT, on May 7, 2010, the Emergency Response Facility Information System (ERFIS) computer system was removed from service to perform a planned modification of the ERFIS. This modification will upgrade the electrical infrastructure. The expected duration of ERFIS inoperability is approximately 4 hours. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above-described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. An additional message will be provided when the ERFIS is restored. It should also be noted that during the period of ERFIS inoperability, it is likely that the system could be restored within one hour to support Emergency Response Facility activation. This report is provided to conservatively cover the possibility that restoration within one hour may not be able to be accomplished if facility activation were to occur. "The NRC Resident Inspector has been notified." * * * UPDATE FROM WARREN WONKA TO JOHN KNOKE AT 1516 EDT ON 5/7/11 * * * The licensee reported that the Emergency Response Facility Information System (ERFIS) computer system was returned to service. The NRC Resident Inspector has been notified. Notified R2DO (David Ayres) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-07
46827 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2011-05-06 13:00 | 2011-05-06 16:46 | 2011-05-06 | CHANGES IN FUEL VENDOR CALCULATION METHODOLOGY TO COMPLY WITH THE ECCS PERFORMANCE REQUIREMENTS OF 10 CFR 50.46(b) "Nine Mile Point Nuclear Station Unit 1 has been informed of a change in its fuel vendor's (General Electric Hitachi) Calculation of the Peak Cladding Temperature (PCT) and Maximum Local Oxidation (MLO). This change was required to address four individual errors and model changes identified by the fuel vendor for the previous calculation of record. Based on 10 CFR 50.46 Appendix K inputs and assumptions, correction of one of the identified errors resulted in a calculated 60 degrees F increase in PCT and a calculated 4 percent increase in MLO, which results in exceeding the PCT and MLO acceptance criteria specified in 10 CFR 50.46 (b). In addition, corrections for two of the other identified items resulted in calculated MLO values that also exceeded the MLO acceptance criterion. However, the cumulative effect of all four of the identified errors/changes was determined to result in calculated PCT and MLO values that remain within the 10 CFR 50.46(b) acceptance criteria. "To ensure compliance with the 10 CFR 50.46 requirements, adjusted Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) limits have been implemented to maintain the PCT and MLO values within the 10 CFR 50,46(b) acceptance criteria and restore design margins. These changes were made prior to the Nine Mile Point Unit 1 startup from the recent spring 2011 refueling outage 21 through a plant monitoring system update. The updated MAPLHGR limits have also been included in the NMP1 Core Operating Limits Report (COLR) for the current operating cycle (Cycle 20), which commenced following the 2011 refueling outage. As such, Nine Mile Point Unit 1 Cycle 20 is in full compliance with the 10 CFR 50.46 requirements. "This notification is being made in accordance with the 10 CFR 50.46(a)(3)(ii) requirement to report this issue in accordance with 10 CFR 50.72 and 10 CFR 50.73. "Based on current core thermal power level and existing margin to limits on power operation, there is sufficient margin for analyzed accident scenarios requiring Emergency Core Cooling System (ECCS) operation, including appropriate MAPLHGR compensation, to maintain the calculated PCT and the MLO within the 10 CFR 50.46 acceptance criteria; therefore, there is no impact on safe operation of the plant. The current LOCA analysis of record remains applicable and therefore, the calculated radiological consequences are still bounded by our current safety analysis. Therefore, this event is not significant with respect to the health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-05-06
46826 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2009-06-15 | 2011-05-06 13:05 | 2011-06-30 | AGREEMENT STATE REPORT - STUCK LEVEL GAUGE SHUTTER In June 2010, Shell identified a stuck level gauge shutter during scheduled maintenance testing. The licensee removed the gauge from service. "The licensee intends to leave the gauge secured in storage until an undetermined future date when it is needed. This facility is a research facility and uses the gauge in its research and testing operations." The gauge was a Berthold Model LB-440 with a 50 milliCurie Cs-137 source. Texas Report Number: I-8842 * * * UPDATE FROM ART TUCKER TO JOE O'HARA VIA E-MAIL AT 1520 ON 6/30/11 * * * "During the review of this file prior to closing, it was noted that the date of the gauge failure was reported to you [NRC] as June 2010. The investigation determined that the gauge failure occurred in June 2009." Notified R4DO(J.Drake) and FSME(D.Jackson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-11
46825 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2011-05-05 15:30 | 2011-05-06 10:11 | 2011-05-06 | LICENSED OPERATOR TESTED POSITIVE DURING RANDOM FITNESS FOR DUTY TEST A licensed operator had a confirmed positive for an illegal drug during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2011-05-06
46824 | 0 | WATERFORD | 3 |  |  | [3] CE | 2011-05-06 02:09 | 2011-05-06 04:07 | 2011-05-06 | DISCOVERY OF AN AFTER-THE-FACT UNUSUAL EVENT Operators were making preparations to fill the Containment Spray System riser to support outage activities. At 0204 CDT, when Containment Spray Riser Isolation Valve CS-125A was opened, pressurizer level began to lower. The licensee suspects leak by of a valve in the Shutdown Cooling System. At 0214 CDT, the leak was stopped. Pressurizer level was lowered by 2.6%. After reviewing the event, the licensee determined that the leak rate was greater than 25 gpm which would have resulted in a declaration of an Unusual Event under EAL CU1. Since the event had concluded, no declaration was made. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2011-05-06
46823 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2011-05-05 10:35 | 2011-05-05 16:50 | 2011-05-05 | TECHNICAL SUPPORT CENTER (TSC) VENTILATION SYSTEM DEGRADED "At 1035 hours CDT on May 5, 2011, the TSC ventilation was secured due to the performance degradation of the air handling unit's fan. The air handling unit is required to maintain a positive pressure in the TSC when the ventilation system is in the emergency mode. At this time, repair activities are being pursued for the fan. "If an emergency is declared requiring TSC activation, the TSC will be staffed and activated using existing procedures. In the event TSC evacuation is warranted due to radiological conditions, key emergency response organization members would be relocated in accordance with existing procedures. "This event is reportable per 10 CFR 50.72 (b)(3)(xiii) given the impact on the emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-05
46822 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-05-05 04:00 | 2011-05-05 02:06 | 2011-05-05 | TECHNICAL SUPPORT SYSTEM VENTILATION OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the James A. FitzPatrick (JAF) Nuclear Power Plant will remove the Technical Support Center (TSC) ventilation system from service. The TSC ventilation system will be rendered non-functional during the course of the work activity. The TSC ventilation is expected to be out of service for approximately 9 hours from 0400 to 1300 today. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification is being made in accordance with 10CFR50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided one the TSC ventilation has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM JON DEFALCO TO JOHN KNOKE AT 1334 EDT ON 05/05/11 * * * As of 1215 EDT on 05/05/11, the planned maintenance activity on the TSC ventilation system is complete. Post work testing is complete and the system has been restored to its fully functional state. The NRC Resident Inspector has been informed. Notified R1DO (Harold Gray) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-05-05
46821 | 0 | SOR INC PROCESS INSTRUMENTATION |  |  |  |  | 2011-05-04 | 2011-05-04 12:14 | 2011-05-04 | PRESSURE SWITCH WITH POSSIBLE SUB-STANDARD ELECTRICAL LEAD TERMINATIONS SOR Process Instruments has determined that certain model pressure switches it has manufactured may have leads attached to the terminal blocks that are not in conformance with good manufacturing practice. The pressure switches in question may have lead wire attached to the terminal block in which the connection between the stripped, stranded wire and a crimped terminal may not be flush with the terminal end. SOR states that there have been no known field problems associated with this issue. This condition applies to SOR model switches with terminal block "X" options 9013-737, 9013-747, 9013-7674. SOR has provided this information to those customers that purchased these switches. The U.S. plants that received these switches are Braidwood and Duane Arnold. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21 |  |  |  | 0 | 2011-05-04
46820 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2011-05-04 16:13 | 2011-05-04 17:57 | 2011-05-04 | CHANGES IN FUEL VENDOR CALCULATION METHODOLOGY TO COMPLY WITH THE ECCS PERFORMANCE REQUIREMENTS OF 10 CFR 50.46(b). "Oyster Creek has been informed of a change in its vendor's calculation of Peak Cladding Temperature (PCT) and the Maximum Local Oxidation (MLO) that is based on corrections to errors in the previous calculation of record the vendor has identified. Based on 10 CFR 50.46 Appendix K inputs and assumptions, the correction of errors resulted in an increase of 115 degrees F in the PCT for GE11 fuel and 145 degrees F for the GNF2 fuel. The impact on the MLO due to these errors resulted in an increase of 16.0% for GE11 fuel and 33.0% for the GNF2 fuel. "To ensure compliance with the 10 CFR 50.46 requirements, administrative Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) limit adjustments have been applied to bring the PCT and MLO limits below the 10 CFR 50.46 criteria of 2200 degrees F and 17% acceptance criteria. The current LOCA analysis of record remains applicable with the applied MAPLHGR limit adjustments. "This notification is being made as a result of the 10 CFR 50.46(a)(3)(ii) requirement to report this issue in accordance with 10 CFR50.72 and 10 CFR50.73. "Based on current core thermal power level and existing margin to limits on power operation there is sufficient margin for analyzed accident scenarios requiring ECCS operation including appropriate MAPLHGR compensation to restore the PCT and the MLO within 10 CFR 50.46 acceptance criteria and therefore there is no impact on safe operation. As a result of the MAPLHGR limit adjustment the current LOCA analysis of record remains applicable and therefore, the offsite dose is still bounded by our current safety analysis. Therefore this event is not significant with respect to the health and safety of the public. "Corrective Action(s): "(1) Administrative adjustments to allowable MAPLHGR limits have been imposed to restore the applicability of the current LOCA analysis of record. "(2) Revised MAPLHGR limits have been provided by the fuel vendor and will be implemented into the plant monitoring system, followed by removal of the administrative adjustments to the MAPLGHR. "(3) A 10 CFR 50.46 report will be submitted within 30-days." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-05-04
46819 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-04-12 | 2011-05-04 12:00 | 2011-05-04 | AGREEMENT STATE - MISSING PO-210 STATIC ELIMINATOR SOURCE The following report was received from the Commonwealth of Massachusetts via fax: "On March 15, 2011, BAE systems called the Massachusetts Radiation program to report a missing Po-210 static eliminator. "In 2009, BAE ordered an air nozzle and unexpectedly received it with a Po-210 source. It is assumed that the RSO at that time removed the source from the nozzle and placed into storage. In March, 2009, the RSO left the company and did not inform the Safety, Health, and Environment Manager that an additional source had been received. It was discovered during a February, 2011 internal audit that there was a discrepancy between shipped and inventoried ionizers. "The former RSO has been contacted and does not recall where the source was stored. BAE believes the source was never put into their laboratories for use. A search for the source in the BAE laboratories and former RSO work area, etc. has not uncovered the source. "The source is a Staticmaster In-line Alpha Ionizer, model P-2021-2002 leased from NRD. It has Serial Number A2GP089, and contained 10 mCi on 3/4/2009. "Corrective Actions: "BAE has created an inventory log form, and will perform more frequent inventory checks. BAE has also assigned the inventory checks to dedicated lab technicians, who will be overseen by the site RSO." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-05-09
46818 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-05-03 10:30 | 2011-05-04 09:58 | 2011-05-09 | AGREEMENT STATE REPORT - SHUTTER MECHANISM FAILURE The following information was obtained from the State of Pennsylvania via facsimile: "It was determined that the remote shutter actuator on a device is inoperable due to foreign material in the shutter mechanism. The device is identified as Texas Nuclear, Model 5197 (Serial No. 81637) with approximately 100 mCi of Cs-137. "The cause of the event was equipment failure. "The shutter is locked in the closed position and shall remain so until repairs are made. Licensee will notify the Department [Pennsylvania Dept. of Environmental Protection] when licensed repairs are made." PA Event Report ID: PA110009 * * * UPDATE FROM JOE MELNIC TO DONALD NORWOOD AT 1431 EDT ON 5/9/2011 VIA FACSIMILE * * * "Upon further investigation it was determined that the remote actuator on the device is inoperable due to a crack in the mechanism that holds the actuator to the gauge. This prevents the shutter from operating as designed by the manufacturer. The device is identified as Texas Nuclear, Model 5197 (Serial No. B1637) with approximately 100 mCi of Cs-137." Notified R1DO (DeFrancisco) and FSME (Diaz-Toro). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-05-09
46817 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-15 17:16 | 2011-05-04 10:35 | 2011-05-04 | INVALID ACTUATION OF THE STANDBY SERVICE WATER PUMP "On March 15, 2011 with Beaver Valley Power Station Unit 2 in Mode 6 during a scheduled refueling outage, the 'A' Standby Service Water (SWE) pump 2SWE-P21A automatically started at 1716 hours when electrical power was removed from the Secondary Process Rack 'A' . The removal of power from the process rack caused pressure transmitter 2SWS-PT113A (Service Water Pump Discharge Pressure Transmitter) to read low resulting in an invalid automatic start of pump 2SWE-P21A. As a result of the automatic start of the SWE pump, the SWE pump discharge isolation valve (2SWE-MOV116A) also opened to provide a flow path from the SWE header to the main service water supply header. The SWE pump is designed to automatically start on a low service water header pressure (i.e. < 34 psig). At the time of the actuation, the service water header pressure was stable at 93 psig. This invalid actuation resulted in a successful start of the Train 'A' SWE system which functioned properly. Plant operators secured the SWE pump after determining that the pump start was invalid and entered the issue into the corrective action program for evaluation. "The SWE system is required by the Beaver Valley Unit 2 Licensing Requirements Manual requirement number 3.7.5 to be Functional in plant operating Modes 1, 2, 3, and 4. The SWE system is not normally in operation and serves as a backup cooling water supply on a loss of the main intake structure. The non-safety related automatic start of the SWE pump on low service water pressure is provided to prevent an inadvertent plant trip on a loss of a running service water pump and is not required for the design basis event. The plant was in Mode 6 when the invalid actuation occurred. The automatic start of the SWE pump was not initiated in response to any plant event. "This event is reportable 10 CFR 50.73(a)(2)(iv)(A) since it involved an actuation of an emergency service water system as per 10 CFR 50.73(a)(2)(iv)(B)(9). Pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification, in lieu of a written Licensee Event Report, since the automatic actuation of the Train 'A' SWE was invalid." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-04
46816 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-07 11:18 | 2011-05-04 10:25 | 2011-05-04 | INVALID ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM "On March 7, 2011 at 1118 hours with Beaver Valley Power Station Unit 2 in Mode 5 during a scheduled refueling outage an invalid actuation of the Auxiliary Feedwater (AFW) System occurred. Instrumentation & Control (I&C) technicians were using a procedure to place simulated signals in two out of three channels of the narrow range level indication on all three steam generators (SG). During this activity, I&C technicians repositioned the input test relays to the test position on both channel 1 and channel 2 in two out of three SGs before inserting the simulated signals. This action resulted in a zero level input to the SG level circuits in two out of three SGs. An Engineered Safety Feature Actuation System (ESFAS) actuation signal for the Auxiliary Feedwater (AFW) System was generated based on having a two out of three low-low level signal in at least one SG (starts turbine driven AFW pump) and subsequently having a two out of three steam generators low-low level signal in at least two SGs (starts motor driven AFW pumps). The AFW initiation signal resulted in a successful automatic start of both the Train A and Train B motor driven AFW pumps. The AFW pump discharge flow control valves were closed per procedure prior to this event, so the motor driven AFW pumps operated on 100% recirculation flow following their automatic start. The turbine driven AFW pump did not start since steam pressure was not present in the main steam lines due to the plant being in Mode 5. A Reactor Protection Signal (RPS) signal was also generated due to having a two out of three low-low level signal in at least one SG. The RPS actuation signal did not result in opening of the reactor trip breakers since the breakers were previously opened as part of the plant shutdown procedures. The reactor control rods had been fully inserted into the reactor core prior to this event. Plant operators took appropriate actions to secure AFW flow after determining that the actuation was invalid and the issue was entered into the corrective action program for evaluation. "The initiation of an ESFAS and RPS actuation signal, due to a SG low-low level signal, was not in response to any valid system or plant condition. There was no event, transient or condition that required any type of mitigation in Mode 5. Plant equipment responded as expected based on the conditions prior to the event. 'The invalid actuation of the AFW system is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved an actuation of a PWR auxiliary feedwater system train per 10 CFR 50.73(a)(2)(iv)(B)(6). Per 10 CFR 50.73(a)(2)(iv)(A)(2)(ii), the actuation of the RPS due to a SG low-low signal is not reportable since the actuation was invalid and occurred after the safety function had already been completed (i.e. the RPS actuation occurred after the control rods had already been inserted in the core). "Pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification, in lieu of a written Licensee Event Report, since the automatic actuation of both trains of AFW was invalid." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-05-04
46815 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-03 04:30 | 2011-05-03 20:12 | 2011-05-09 | AGREEMENT STATE - STOLEN TROXLER MODEL 3430 "On May 3, 2011, the Agency [Texas Department of Health] was notified by the licensee that a Troxler Model 3430 moisture/density gauge had been stolen from the back of one of their trucks. The gauge was stolen at the intersection of Nalor and North Main in Houston, Texas. The gauge contains a 40 milliCurie Americium (Am) - 241 source, and an eight milliCurie Cesium (Cs) -137 source. The licensee reported that their technician had completed his work and returned to the licensee's facility. When the technician went to the back of the truck to get the gauge, he found the gauge missing, one chain and lock missing, and the other lock had a busted bail. The technician contacted the other licensee's technicians who were at the work site to see if any of them had the gauge. No one did. The technician contacted his manager and reported the missing gauge. The licensee contacted local law enforcement and notified them of the theft. The Agency has sent notification of the theft to the Texas Association of Pawn Brokers. Additional information will be provided as it is received in accordance with Reporting Material Events SA-300." The serial number of the gauge is 63670. The source numbers are 78-6298 and 77-9880. Texas Incident: I-8841 * * * UPDATE FROM CHRIS MOORE TO DONALD NORWOOD AT 1347 EDT ON 5/9/2011 VIA FACSIMILE * * * "On May 7, 2011, local law enforcement reported to a residence due to a domestic dispute call. The police saw a radiation symbol on the gauge case, confirmed it was stolen, and confiscated the case and gauge. The Troxler model 3430 moisture/density gauge serial # 63670 was returned to the licensee. The gauge was inspected and returned to service." Notified Mexico via fax. Notified R4DO (Walker), FSME DEO (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-06
46814 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-05-03 10:36 | 2011-05-03 17:55 | 2011-05-03 | NOTIFICATION TO OFFSITE AGENCY REGARDING POTABLE WATER RESIDUAL CHLORINE LEVEL "The following is a non-emergency notification in accordance with 10CFR50.72(b)(2)(xi), Offsite Notification. "At 1036, May 3, 2011, Callaway Plant notified the Missouri Department of Natural Resources (DNR) of an issue with the potable water supply system at the facility. This notification to the Missouri DNR was made in accordance with 10 CSR 60-4.055, 'Disinfection Requirements,' due to circumstances that adversely affect the quality of potable water. "Specifically, loss of function of the potable water chlorine pumps resulted in residual chlorine in the potable water system falling below the levels specified by the regulation. DNR has not restricted drinking of Potable Water at Callaway Plant. "Required compensatory actions have been initiated, including planned repairs of the potable water chlorination system. "The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-05-03
46813 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-05-03 13:44 | 2011-05-03 15:39 | 2011-05-04 | ALERT DECLARED DUE TO FIRE AFFECTING ACCESS TO SAFETY RELATED EQUIPMENT The licensee has declared an Alert due to a hydrogen fire on the hydrogen pad outside the protected area that resulted in evacuating outbuildings (pump house and air compressor buildings) that contain safety related equipment. The Alert is classified under Emergency Action Level HA-3.2 based on report or detection of gases in concentrations higher than lower flammability limit or contiguous to a safe shutdown or vital area. The licensee has also suspended certain security measures under 50.54(x) and 50.54(y). Security measures were suspended due to risks from the fire with no compensatory measures in-place at this time. The fire involves hydrogen cylinders delivered to the site to a trailer pad outside the protected area. The fire developed while exchanging a newly delivered trailer of hydrogen cylinders with an expended hydrogen cylinder trailer. The fire brigade has responded and offsite fire departments have responded to the site. Fire water is currently being sprayed on the hydrogen cylinders. There is no indication of any damage to any plant equipment other than the hydrogen trailer area equipment. The driver of the hydrogen supply truck was reported to have sustained some injuries. There are no other reported injuries to plant personnel. The hydrogen water chemistry system has been isolated and makeup hydrogen to the main generator is isolated. The hydrogen isolation has no impact on the licensee at this time. The plant continues to operate at full power and there have been no immediate impacts from the fire to plant operation. The licensee has notified State, and local authorities and the NRC Resident Inspector. * * * UPDATE FROM SCHWERTFEGER TO TEAL AT 1550 EDT ON 5/3/11 * * * The licensee made a one-hour notification of deviation from technical specifications under 10 CFR 50.54(x) and (y) due to the ongoing hydrogen fire. This was due to safeguards system degradation related to monitoring and detection of the OCA. Contact the Headquarters Operations Officer for details. R3 IRC was notified of this report. * * * UPDATE FROM SCHWERTFEGER TO HUFFMAN AT 1925 EDT ON 5/3/11 * * * The licensee reported all safeguards systems have been restored and they have exited 10 CFR 50.54(x) and (y). R3 IRC was notified of this report. * * * UPDATE FROM CARLSON TO HUFFMAN AT 2023 EDT ON 5/3/11 * * * At 1855 CDT, Duane Arnold has re-classified the hydrogen trailer fire event to an Unusual Event level. The event is classified as an UE under EAL HU-5.1 based on other conditions that exist which, in the judgment of the emergency director, indicate events are in progress or have occurred which indicate a potential for degradation for the level of safety of the plant. The licensee has allowed access to all areas that were previously restricted due to potential safety concerns from the ongoing fire. The hydrogen trailer cylinders are still being sprayed with water and several cylinders are still showing thermal images above ambient. The licensee will evaluate event termination when the fire can be conclusively demonstrated to be extinguished. The licensee has notified state and local authorities and the NRC Resident Inspector. NRC Region 3 continues to monitor the event. Notified R3 (West), NRR EO (Holian), FEMA (Via), and DHS (Knox). * * * UPDATE FROM RUSHWORTH TO KLCO AT 0302 EDT ON 5/4/11* * * At 0135 CDT on 5/4/11, Duane Arnold terminated from the Unusual Event. The fire was verified to be out, with no hot spots. The hydrogen tanks have been isolated and the licensee verified no hydrogen is present in the area of the hydrogen pad. The licensee has notified State, local authorities and the NRC Resident Inspector. R3 IRC was notified of this report. Notified R3 (West), NRR (Boger), FEMA (Via), DHS (Hill), HHS (Collins), USDA (Timmons) and DOE (Yates). Will notify R3DO (Ring), NRR EO (Holian), IRD (Marshall). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | DEVIATION FROM T SPEC |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | IA | POW |  | 50.72(a) (1) (i) | 50.72(b)(1) |  |  | 0 | 2011-05-03
46812 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-03 | 2011-05-03 14:18 | 2011-05-03 | CONTRACT SUPERVISOR TESTED POSITIVE FOR ILLEGAL DRUG A contract supervisor had a confirmed positive for an illegal drug during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Under Construction; FMode2: Under Construction | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2011-05-03
46811 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-05-03 05:14 | 2011-05-03 13:02 | 2011-05-03 | TWO APPENDIX R VIOLATIONS THAT CAN ADVERSELY IMPACT ABILITY TO SHUT DOWN PLANT "On 05/03/2011 at 0514 [EDT] V.C. Summer Nuclear Station (VCSNS) determined the following: "During circuit analysis review for transitioning the Fire Protection Program to NFPA-0805, VCSNS identified two violations of the Appendix R requirement to maintain one train of systems necessary to achieve and maintain hot shutdown conditions in accordance with Appendix R. Both instances apply to postulated fires in the Main Control Room and Cable Spreading Room. "In the first instance, circuits were identified in the Main Control Room and Cable Spreading Room that impact a control power circuit that could result in the loss of ability to start the 'B' Emergency Diesel Generator using local controls. Because fires in these areas can result in the need to evacuate the Main Control Room, the inability to start the diesel using local controls could have an adverse impact on the ability to safely shut down the plant. "In the second instance, VCSNS determined that a fire in either the Main Control Room or Cable Spreading Room could result in a hot short that could actuate a relay and trip all incoming breakers to the B-train essential electrical bus (Bus 1DB). Because fires in these areas can result in a loss of power to the bus, this could have an adverse impact on the ability to safely shut down the plant." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-05-03
46810 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-05-01 | 2011-05-03 11:25 | 2011-05-04 | AGREEMENT STATE REPORT - STUCK SHUTTER ON OHMART/VEGA MODEL GAUGE "On May 2, 2011, the Agency [Texas Department of Health] was notified by the licensee that during routine checks on an Ohmart/Vega nuclear gauge model SHD containing 250 millicuries of Cesium (Cs) 137 (original activity), the shutter was found stuck in the open position. The gauge is mounted on a tank and is located 100 feet above ground and does not create an exposure risk. The gauge is used for level detection. The licensee has lubricated the operating mechanism several times to get the shutter to operate, but it remains stuck. A service provider will be contacted to conduct repairs if needed. The gauge was installed in 1990 time frame and is to be replaced in the future. Addition information will be provided as it is received in accordance with SA-300." Texas Incident Number I-8840 * * * UPDATE FROM ART TUCKER (VIA EMAIL) TO HOWIE CROUCH AT 0827 EDT ON 5/4/11 * * * "On May 3, 2011, the Agency was notified by the licensee that the gauge was working as designed. The repeated lubrication of the operating mechanism was the only method used to make the repair to the gauge. Additional information will be provided as it is received in accordance with SA - 300." Notified R4DO (Proulx) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-06
46809 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-05-03 07:00 | 2011-05-03 07:32 | 2011-05-03 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into the protected area. Compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM MCCORKLE TO HUFFMAN AT 1618 EDT ON 5/3/11 * * * The licensee has determined that this event is not reportable to the NRC Operations Center based on further assessment. Since the contraband never entered the site protected area the licensee and there was no malevolent intent involved, it was concluded that this event is only required to be logged. The NRC Resident Inspector has been notified. Contact the Headquarters Operations Officer for additional details. NRC R2DO (Ayres) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-05-03
46808 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2011-05-02 20:51 | 2011-05-02 22:55 | 2011-05-02 | AUTOMATIC REACTOR SCRAM "Nine Mile Point Unit 1 experienced an automatic RPS actuation (scram) on Monday, May 02, 2011 at 2051. Cause of the RPS actuation is not understood at this time. All control rods inserted to position 00. N1-EOP-2 entered due to low reactor water level following trip (expected plant response). Reactor pressure stabilized 800 to 1000 psig, reactor water level restored and maintained 53 to 95 inches. Automatic initiation of the High Pressure Coolant Injection system occurred following plant trip (normal actuation)." The reactor is stable in Hot Shutdown. The licensee characterized the scram as uncomplicated. All rods fully inserted, normal feed water is supplying the reactor with decay heat being removed to the condenser. The unit is in a normal shutdown electrical lineup and the scram had no impact on Unit 2. All systems functioned as required. The unit was operating at 47% power at the time of the event due to feed pump maintenance. The licensee does not have a first-out indication for the reactor scram and is still investigating the cause of the scram. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-05-02
46807 | 0 | ABB INC |  |  |  |  | 2011-05-02 | 2011-05-02 17:12 | 2011-09-28 | NOTIFICATION OF POTENTIAL DEFECT IN SOLID STATE RELAY Identification of the subject component is as follows: SS5 Solid State Relay, Part Number 611130-T13-N. "The instantaneous trip function of the relay may actuate at 16 times normal current instead of the design value of 24 times normal current. "On 3 March, 2011, ABB was notified by Progress Energy - Brunswick plant that spare relays being tested prior to being placed in service were tripping at approximately 4700 amps instead of the expected 7200 amps. Brunswick stated that their applications require having a short time delay for all faults up to the 24 times instantaneous value is critical for system design and compliance with their design basis and licensing documents. "Subsequent evaluation by ABB Engineering determined that the relay works as intended. However, if there is a fault at the same time the relay is energized, the instantaneous unit becomes more sensitive, and will operate at lower than expected current level. "For conditions where a fault occurs downstream of an associated in-service circuit breaker, the relay works as intended, for single phase, phase to phase, and three phase fault conditions. "Sales records show that only four orders of the subject relay were ever shipped, and each of these four orders was with Progress Energy, with the orders all being processed via ABB Medium Voltage Service, in Florence, SC. The order numbers and quantities are as follows, with the first three orders being shipped from ABB Coral Springs, FL and the fourth order shipped from ABB Allentown, PA: AA027730 qty. 10, AA319168 qty. 7, AA319152 qty. 7, and PC06895 qty. 3. "ABB is taking, or has taken, the following corrective actions: - Reworked Qty. 23 units for Brunswick to convert the units to Part Number 611130-T11-N, by removing the target circuit. This prevents the pre-mature trip at lower current. - One additional unit has been retained at ABB Coral Springs to support continued testing to confirm the fault condition. - Three units have not been accounted for, and are assumed to be in service. (Purchased by ABB Florence for Progress Energy Brunswick 4/11/08, Sales Order PC06895, Relay Serial Numbers 85948, 85949, and 85950) - The 611130-T13-N relay has been obsoleted to prevent future sales. - ABB Engineering is determining whether other similar relays of different ratings have a similar defect. Action to complete by July 1, 2011. "ABB does not have the capability to perform the evaluation to determine if a defect exists, so we are informing the purchasers or affected licensees of this determination so that the purchasers or affected licensees may evaluate the deviation or failure to comply, pursuant to º 10CFR 21.21(a). "ABB recommends that the affected licensees evaluate their specific application and determine whether the deviation described in this notice affects their design basis. If the licensee determines that it does, the relays may be returned to ABB for conversion by removing the target circuit." * * * UPDATE FROM DENNIS BATOVSKY TO JOE O'HARA AT 1529 ON 9/28/11 * * * This update information regarding the notification of a failure to comply with specifications associated with the SS5 Relay, Part Number 611130-T13-N. "The instantaneous trip function of the relay may actuate at 16 times normal current instead of the design value of 24 times normal current. "Subsequent evaluation by ABB Engineering determined that the relay works as intended. However, if there is a fault at the same time the relay is energized, the instantaneous unit becomes more sensitive, and will operate at lower than expected current level. "For conditions where a fault occurs downstream of an associated in-service circuit breaker, the relay works as intended, for single phase, phase to phase, and three phase fault conditions. "ABB Engineering determined that other similar relays of different ratings may have a similar deviation from technical specifications. "ABB is taking, or has taken, the following corrective actions: - Affected relay part numbers have been made obsolete to prevent future sales. - Stopped production of all affected relays until corrective action is implemented. - The Circuit board assembly, 611856-T1, T2, T3, will be made obsolete and replaced by 611857-T1, T2, T3 accordingly, which do not exhibit this deviation. - ABB acknowledges the response time for this report is beyond the required reporting window and has initiated a separate corrective action to address this problem. "ABB does not have the capability to perform the evaluation to determine if a defect exists, so we are informing the purchasers or affected licensees of this determination so that the purchasers or affected licensees may evaluate the deviation or failure to comply, pursuant to º10CFR 21.21 (a). "ABB recommends that the affected licensees evaluate their specific application and determine whether the deviation described in this notice affects their design basis. If the licensee determines that it does, the licensee should contact ABB to determine appropriate corrective action." Notified R2DO(Nease) and Part 21 GRP via e-mail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-05-02
46806 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-30 10:00 | 2011-05-02 12:40 | 2011-05-02 | MEDICAL TREATMENT DUE TO POTENTIAL EXPOSURE TO HYDROGEN FLUORIDE "An employee who had been working in the fluorine plant was treated in the site dispensary for redness around the right eye. The individual was treated for potential HF exposure using saline solution and calcium gluconate. The employee's work coveralls and boots were monitored by Health Physics and were contaminated. The employee returned to work. The licensee has notified NRC Region II (Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-05-02
46805 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-05-02 06:26 | 2011-05-02 11:28 | 2011-05-02 | SPECIFIED SYSTEM ACTUATION DUE TO A EMERGENCY DIESEL GENERATOR OUTPUT BREAKER TRIP "At 0626 [CDT] on 05/2/2011, with BFN U1 in Mode 4, Browns Ferry Nuclear Plant, received an 'A' Emergency Diesel Generator output breaker trip for unknown reasons that de-energized the 'A' 4kV Shutdown Board, resulting in a loss of power to RPS 'A' and a subsequent half scram, 'B' CREV and 'B/C' SGT automatic initiation, and Primary Containment isolation for Groups 2, 3, 6 and 8. The PCIS isolation (Group 2) also caused a loss of Shutdown Cooling on U1 which was restored at 0723 following restoration of power to the 'A' 4kV Shutdown Board from offsite 161kV power. "The general containment isolation signals affecting containment isolation valves in more than one system is reportable as an 8 hour notification to the NRC IAW 10CFR50.72(b)(3)(iv), as any event or condition that results in a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "This is also reportable as 60 day written report IAW 10CFR50.73(a)(2)(iv). "The NRC Resident [Inspector] has been notified of this event. "This event was entered into the licensee's Corrective Action Program as PER# 362340." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-05-02
46804 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-05-02 09:04 | 2011-05-02 11:01 | 2011-05-05 | UNAUTHORIZED ACCESS TO THE PROTECTED AREA A contract employee with unescorted access authorization entered the protected area under a circumstance for which he was unauthorized. When discovered, the individual was immediately escorted from the protected area and the unescorted access has been terminated. Contact the Headquarters Officer for additional details. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ALTON DEWEESE TO PETE SNYDER AT 1343 EDT ON 5/5/11 * * * Upon further investigation the individual in question would not have been denied unescorted access for the circumstances existing at the time. The individual is not considered unauthorized and this report is retracted. The licensee has notified the NRC Resident Inspector. Notified R2DO (Ayers), and 73.71 Group (e-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-05-02
46803 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2011-04-29 11:00 | 2011-04-29 13:29 | 2011-04-29 | OFFSITE NOTIFICATION DUE TO FATALITY OF A CONTRACT EMPLOYEE "On April 29, 2011, at approximately 1100 hours, a contract employee was found unresponsive in a vehicle, off the road, inside the Perry Nuclear Power Plant owner controlled area. At 1120 hours, it was confirmed by the Perry Fire Department that the individual was deceased. Notification has been made to the Lake County Sheriffs department and the Lake County Coroner. The death does not appear to be work related or the result of an accident. A preliminary diagnosis by the coroner is the individual suffered a heart attack. The Lake County Coroner is conducting a routine investigation into the death. "A press release is not planned at this time. The individuals name has not yet been released pending notification of next-of-kin. A notification to OSHA per 29CFR1904.39 will be made for this event. "The plant is currently in MODE 5 (Refuel) for a refueling outage. This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as an event or situation, related to the health and safety of the public or on-site personnel, for which notification to other government agencies has been or will be made. Such an event may include an on-site fatality. The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-29
46802 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2011-04-29 08:52 | 2011-04-29 12:42 | 2011-04-29 | TRITIUM DETECTED IN UNIT 2 TURBINE BUILDING SUMP "On 4/28/2011, Grand Gulf Nuclear Station Unit 2 turbine building sump samples indicated tritium presence. The Unit 2 turbine building is an abandoned, partially constructed building. Follow-up review and investigation confirmed that water from Unit 2 turbine building sump had been pumped to the environment through installed sump pumps and piping connected between the sumps and roof drains on the Unit 2 turbine building. The release has been terminated by turning off the sump pumps located in the Unit 2 turbine building. Site procedures require notification of off-site agencies, therefore the NRC is being notified in accordance with 10 CFR 50.72(b)(2)(xi)." The NRC Resident Inspector has been informed. The state will be informed. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-29
46801 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-04-28 23:38 | 2011-04-29 07:26 | 2011-04-29 | PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO LOSS OF POWER FROM A DIESEL GENERATOR "At 2338 [CDT] on 04/28/2011, with Browns Ferry Nuclear Unit 1 and Unit 2 in Mode 4, Browns Ferry Nuclear Plant, performed a shutdown of the Unit 1/2 Emergency Diesel Generator 'C,' due to an oil leak coming from its governor causing voltage and frequency fluctuations. Following securing of the Unit 1/2 Diesel Generator 'C,' the 4kV Shutdown Board 'C,' which was being powered by DG 'C,' de-energized. This resulted in a loss of power to the 1B RPS, causing a Primary Containment Isolation System (PCIS) actuation and the automatic initiation of the three trains of Standby Gas and 1 train of CREV [Control Room Emergency Ventilation System]. The PCIS isolation (Group 2) also caused a loss of Shutdown Cooling on Unit 1 which was restored at 0025 [CDT] 04/29/2011 . "In addition, the loss of power to the 4kV Shutdown Board 'C.' also caused the loss of 2B RHR Pump, leading to a momentary suspension of shutdown cooling to Unit 2. Shutdown cooling was immediately restored to Unit 2 using the 2D RHR Pump at 2342 [CDT]. "The general containment isolation signals affecting containment isolation valves in more than one system is reportable as an 8 hour notification to the NRC IAW 10CFR50.72(b)(3)(iv)(A), as 'Any event or condition that results in a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "There were no new Technical Specification LCO's entered as a result of this event. "This is also reportable as 60 day written report lAW 10CFR50.73(a)(2)(iv). "The NRC Resident [Inspector] has been notified of this event. "This event was entered into the licensee's Corrective Action Program as SR# 361382." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-04-29
46800 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2011-04-28 | 2011-04-28 17:42 | 2011-05-02 | MISSING THERMO MEASURETECH MODEL 5201 DENSITY GAUGE The State of Utah is making a preliminary report that a Thermo MeasureTech Model 5201 density gauge was discovered missing. The gauge was attached to a pipe that was removed. That section of pipe had been locked shut and not in use for a period of over 3 years. The last time the gauge was accounted for was October 29, 2010. The licensee is conducting a search of the site to locate the gauge. * * * UPDATE FROM PHILIP GRIFFIN TO CHARLES TEAL ON 5/2/11 AT 1759 EDT * * * "The Radiation Safety Officer (RSO) and the Assistant RSO (ARSO) were performing a routine 6-month physical inventory of the devices in the licensee's possession containing radioactive material when they noticed that one of the fixed gauging devices was missing. The device was a Thermo Measuretech Model 5201 (serial #B3988) densitometer containing a 100 mCi Cs-137 source that was attached to a pipe. The device had not been used for more than 3 years prior to the incident, and the licensee had 'locked out' the device at that time with the shutter in the 'closed' position. The RSO had accounted for the gauge during a physical inventory on October 29, 2010. At the time of the incident, the device and the pipe were gone. "At the time of this report, the RSO and ARSO are continuing to contact anyone who may have any knowledge as to the location/disposition of the device. The RSO and ARSO are also contacting various waste companies and scrap metal companies to see if they received a gauge containing radioactive material, if the company has the capability of measuring for radiation, and to ask them to keep a watch out for the gauge. "The licensee is undergoing expansion, and employs a number of contractors. The licensee stated that all of the licensee's employees are thoroughly instructed in radiation safety, and that the employees are told that no work involving the licensee's gauges can be done without the RSO or ARSO being present. The licensee's contractors are provided general radiation safety training twice a year. "The licensee's working theory regarding the loss of the gauge is that a contractor was working in that area of the licensee's facility and was instructed to demolish that portion of the facility. Since contractor often use a demolish that portion of the facility the licensee speculates that a contractor may have placed the gauge in the waste bin with the other materials from the demolition, and the waste bin was then hauled off by a waste disposal company. The licensee is currently attempting to identify any contractors who may have been working in the area of the gauge during the time period from October 29, 2010, to the present." Notified R4DO (Proulx) and FSME EO (Piccone). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2011-05-03
46799 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-28 03:30 | 2011-04-28 17:23 | 2011-04-28 | MEDICAL TREATMENT ONSITE OF A CONTAMINATED EMPLOYEE "[An] employee was treated for a chemical exposure at 0330 hours CDT on his ring finger. The employee had contamination on his shoes and coveralls. Contamination levels were 1500 dpm/100cm2 on his coveralls cuff and 200 dpm/100cm2 on the soles of his boots. There was no detectable contamination on the employee's skin. The employee was treated for the chemical exposure [weak hydrofluoric acid or caustic] and returned to work. Reporting IAW 10CFR40.60(b)(3)." There was no release of contamination offsite involved in this incident. The licensee informed the NRC Senior Inspector RII (R. Gibson) of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-04-28
46798 | -1 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-04-28 00:15 | 2011-04-28 03:32 | 2011-06-14 | SAFEGUARDS REPORT DUE TO ADVERSE WEATHER Safeguards system degradation related to monitoring and detection of the OCA. Compensatory measures taken. Call the Headquarters Operations Officer for details. The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM TIM TAYLOR TO DONALD NORWOOD AT 1610 EDT ON 6/14/2011 * * * After evaluation of the event, this event was determined to be not reportable based upon the reporting guidance disseminated in Generic Letter 91-03, "Reporting of Safeguards Events." Call the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R2DO (Bartley). Notified 73.71 Group via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Hot Shutdown | Hot Shutdown | Hot Shutdown | Hot Shutdown | Hot Shutdown | Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-04-28
46797 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-27 19:29 | 2011-04-27 20:19 | 2011-04-28 | BOTH OFFSITE POWER SOURCES DECLARED INOPERABLE DUE TO EFFECTS OF INCLEMENT WEATHER "At 1929 EDT, both off-site A.C. power sources to Sequoyah were declared inoperable due to the effects of inclement weather on the TVA transmission system. This determination was made after a review of grid conditions confirmed that pre-analyzed grid/offsite power requirements could not be met. Both Sequoyah Units have entered TS LCO 3.8.1.1, action d, for two inoperable offsite power sources. It has not been determined when this condition will no longer exist. "Although inoperable, off-site A.C. sources remain connected to Sequoyah; emergency diesel generators are not running nor required to be at this time." T.S. LCO 3.8.1.1, action d, requires verifying EDG operability within 8 hours and restoration of both offsite power sources within 24 hours or placing both Units in mode 3. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM JEFF EPPERSON TO PETE SNYDER AT 0203 EDT ON 4/28/11 * * * As of 0119 EDT the licensee has two operable offsite power sources qualified through transmission and reliability analysis. The licensee exited their LCO Condition. The grid condition is now yellow. Notified R2IRC (Gody). | 100 | 92 | 0 | 100 | 92 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2011-04-27
46796 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-27 19:10 | 2011-04-27 20:00 | 2011-04-27 | SAFEGUARDS REPORT DUE TO ADVERSE Safeguards system degradation related to monitoring and detection of the OCA. Compensatory measures taken. Call the Headquarters Operations Officer for details. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-04-27
46795 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-04-27 18:00 | 2011-04-27 19:05 | 2011-04-29 | EMERGENCY SIRENS INTERMITTENTLY INOPERABLE DUE TO UPGRADING "Fort Calhoun Station is improving (upgrading) the emergency siren system. This evening during the upgrade the sirens will be inoperable for a short period between 1830 and 2400 today. Fort Calhoun will inform the HOO when the sirens are returned to operation following this evenings maintenance." The licensee notified the states of Nebraska and Iowa and local authorities in both states of the siren outage. * * * UPDATE FROM JOHN FICKLE TO DONG PARK AT 0210 EDT ON 4/28/11 * * * The emergency siren system maintenance was complete and all sirens were restored to service at 0010 CDT on 4/28/11. The licensee notified the states and local authorities. Notified R4DO (Powers). * * * UPDATE FROM ERIK MATZKE TO CHARLES TEAL AT 1236 EDT ON 4/28/11 * * * "Fort Calhoun Station is improving (upgrading) the emergency siren system. Today during the upgrade, the sirens will be inoperable for a short period between 1130 CDT and 1210 CDT today. Fort Calhoun will inform the HOO when the sirens are returned to operation following this maintenance." Notified R4DO (Powers), State and local government. * * * UPDATE FROM ERIK MATZKE TO CHARLES TEAL AT 1251 EDT ON 4/28/11 * * * The emergency siren system maintenance was complete and all sirens were restored to service at 1150 CDT on 4/28/11. The licensee notified the states and local authorities. * * * UPDATE FROM ERIK MATZKE TO CHARLES TEAL AT 1415 EDT ON 4/28/11 * * * "Continuing maintenance on the sirens determined that they are not responding correctly. Troubleshooting is in progress. There is not an estimated time to return the sirens to service at this time. Emergency planning personnel have been contacted and contingency actions are in place. The station will contact the HOO when the issue is resolved." Notified R4DO (Powers). * * * UPDATE FROM ERIK MATZKE TO CHARLES TEAL AT 1529 EDT ON 4/28/11 * * * The emergency siren system maintenance was complete and all sirens were restored to service at 1529 CDT on 4/28/11. The licensee notified the states and local authorities. Notified R4DO (Powers). * * * UPDATE FROM ERIK MATZKE TO DONG PARK AT 0848 EDT ON 4/29/11 * * * "Fort Calhoun Station is improving (upgrading) the emergency siren system. Today during the upgrade, the sirens are anticipated to be inoperable for an hour or two during the period between 0755 [CDT] and 1000 [CDT] today. The emergency planning staff has been informed and compensatory measures are in place. Fort Calhoun will inform the HOO when the sirens are returned to operation following this maintenance." The licensee notified the states and local authorities, as well as the NRC Resident Inspector. Notified R4DO (Powers). * * * UPDATE FROM ERIK MATZKE TO CHARLES TEAL AT 1201 EDT ON 4/29/11 * * * The emergency siren system maintenance was complete and all sirens were restored to service at 1030 CDT on 4/29/11. The licensee notified the states and local authorities. Notified R4DO (Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2011-04-27
46794 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-04-27 16:19 | 2011-04-27 18:30 | 2011-06-20 | SAFEGUARDS REPORT DUE TO ADVERSE WEATHER Safeguards system degradation related to monitoring and detection of the OCA. Compensatory measures taken. Call the Headquarters Operations Officer for details. The licensee informed the NRC Resident Inspector. * * * UPDATED AT 1315 EDT ON 6/20/11 FROM JOHN RIDINGER TO S. SANDIN * * * The licensee corrected the event time from 1719 CDT to 1619 CDT. Notified R2DO (Bartley) and 73.71 Group (via email). | 76 | 73 | 100 | 76 | 73 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-04-27
46793 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-04-27 17:01 | 2011-04-27 18:23 | 2011-05-02 | NOTIFICATION OF UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 1701 CDT, the licensee declared a Notification of Unusual Event under Emergency Action Level 5.1U due to loss of offsite power for >15 minutes. The loss of offsite power occurred at 1635 CDT and was due to severe weather and winds in the vicinity. When offsite power was lost, all 3 units automatically scrammed. The units are currently stable in Mode 3 with their respective 4KV busses being supplied by the onsite Emergency Diesel Generators[EDG]. The 161KV Athens line is the only offsite power source energized. All onsite safe shutdown equipment is available with the exception of the Unit 3 "B" EDG which was out of service for planned maintenance. * * * UPDATE FROM BILL BAKER TO HOWIE CROUCH AT 1942 EDT ON 4/27/11 * * * The system actuations that occurred during the loss of offsite power were actuations of the Reactor Protection System, Primary Containment Isolation System (PCIS) and Emergency Diesel Generators. All primary containment valves actuated by the PCIS operated as expected. Unexpectedly, the Unit 3 "B" Main Steam Isolation Valve indicates intermediate. Unit 1 High Pressure Coolant Injection actuated when reactor water level reached -45". Reactor Core Isolation Cooling (RCIC) was already initiated at the time. * * * UPDATE FROM BILL BAKER TO S. SANDIN AT 2153 EDT ON 4/27/11 * * * Following the loss of offsite power only 12 of the required 100 offsite emergency sirens are operable. The licensee will inform both state/local agencies and the NRC Resident Inspector. Notified R2IRC (Wert) of this update. * * * UPDATE FROM BILL BAKER TO HOWIE CROUCH AT 2303 EDT ON 4/27/11 * * * As a result of the loss of offsite power, the Diesel-driven Fire Pump auto-started. While the pump was running, the licensee discovered that approximately one quart of oil had leaked from the fire pump into the cold water channel which discharges into navigable waterways. The licensee confirmed this at 1950 CDT by visually identifying a sheen in the channel. The licensee notified the National Response Center of the spill and, in accordance with their site discharge permit, notified the State of Alabama. This constitutes an Offsite Notification in accordance with 10CFR50.72(b)(2)(xi). The licensee notified the NRC Resident Inspector. Notified NRC R2IRC (Wert). * * * UPDATE FROM BILL BUTLER TO HOWIE CROUCH AT 2338 EDT ON 4/27/11 * * * At 2120 CDT, operators on Unit 1 were controlling reactor water level between 2 and 51 inches when RCIC became sluggish and water level dropped to +2" causing a valid RPS Scram signal as well as PCIS signals 2, 3, 6, and 8. All valves operated as expected and all isolations were completed. The licensee notified the NRC Resident Inspector. Notified NRC R2IRC (Wert). * * * UPDATE FROM WILLIAM BAKER TO CHARLES TEAL AT 2338 EDT ON 4/28/11 * * * "At 1635 CDT following offsite power grid oscillations (due to inclement weather), and a subsequent Unit 1 power reduction from 100% to 75% to attempt to correct the condition, BFNP experienced a complete loss of the 500kV offsite power system. This resulted in an automatic turbine trip and reactor scram of Units 1, 2 and 3. One 161 kV offsite power system (Athens) remains available. This condition is reportable IAW 10CFR50.72(b)(2)(iv)(B) - Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (4-hour notification). This notification was reported to NRC (Crouch) at 1723 CDT. "At 1701 CDT, a NOUE was declared (EAL Designator 5.1-U) due to loss of normal and alternate voltage to all 4kV SD (Shutdown) Boards for greater than 15 minutes and at least two Diesel Generators supplying power to unit specific 4kV SD Boards. This condition is reportable IAW 10CFR 50.72(a)(1)(i) - The declaration of any of the emergency classes specified in the licensee's emergency plan (1-hour notification). This notification was reported to NRC (Crouch) at 1723 CDT. "Following the initial scrams, there were valid actuation signals for RPS (U1/2/3), Containment Isolation Groups 2, 3, 6 and 8 (U1/2/3), HPCI (U1 only), and Emergency Diesel Generators A, B, C, D, 3A, 3C and 3D (EDG 3B is out of service for maintenance). MSIV's (U1 and 3) closed on loss of A and B RPS power, and the U3 B inboard MSIV is indicating 'double lit' (not fully closed) at this time. All other systems responded as expected. This condition is reportable IAW 10CFR50.72(b)(3)(iv)(A) - Any event or condition that results in the valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (8-hour notification). The systems with a valid actuation were RPS, Containment Isolation, HPCI and Emergency Diesel Generators. This was reported in an EN# 46793 update to NRC (Crouch) at 1842 CDT. "At 1820 CDT a determination was made that offsite emergency notification sirens did not meet the minimum required number operable. Seventy of the one hundred sirens are required to be operable and twelve of the sirens are operable at this time. This condition is reportable IAW 10CFR50.72(b)(3)(xiii) - Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, emergency notification system, or offsite notification system) (8-hour notification). This was reported in an EN# 46793 update to NRC (Crouch) at 2053 CDT. "Following auto-start of the diesel driven fire pump, subsequent to the loss of offsite 500kV power system, approximately one quart of oil leaked from the drain plug in the diesel engine of the pump to the plant cold water channel (waters of the United States). This oil produced a "sheen" on the water (confirmed at 1950 CDT) that required a response to the National Response Center IAW 40CFR112.7(a)(4). This condition was reported to the National Response Center at 2055 CDT and assigned spill number 974232. In addition, IAW the BFNP NPDES (National Pollution Discharge Elimination System) permit, the State of Alabama was notified at 2100 CDT of the spill and subsequent notification of the National Response Center. The notification of these outside agencies is reportable IAW 10CFR50.72(b)(2)(xi) - Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification of other government agencies has been or will be made. Such an event may include an onsite fatality or inadvertent release of radioactive contaminated materials (4 hour notification). This was reported in an EN# 46793 update to NRC (Crouch) at 2203 CDT. "At 2120 CDT, Unit 1 received a low reactor water level scram due to reactor water level lowering to +2 inches following sluggish RCIC response at low reactor pressure. At the time of this event RCIC and CRD were injecting to the vessel and the reactor level band specified was +2 to +51 inches. A valid Containment Isolation signal was received and groups 2, 3, 6 and 8 isolated as expected. Water level was immediately restored to within the specified band (RCIC). This condition is reportable IAW10CFR 50.72(b)(3)(iv)(A) - Any event or condition that results in the valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation (8-hour notification). The systems with valid actuations were RPS and Containment Isolation. The Emergency Diesel Generators were already running at the time of the event. This was reported in an EN# 46793 update to NRC (Crouch) at 2238 CDT. "The NRC resident has been notified of these 1, 4 and 8 hour reports and EN#46793 updates. "These conditions and notifications will be captured in the licensee's Corrective Action Program." * * * UPDATE FROM GIVENS TO HUFFMAN AT 2200 EDT ON 5/2/11 * * * "At 2050 CDT, on 05/02/2011, the previously declared and reported NOUE (EAL Designator 5.1U) due to loss of normal and alternate voltage to all 4kV SD Boards for greater than 15 minutes and at least two Diesel Generators supplying power to unit specific 4kV SD Boards was terminated due to the conditions requiring entry being resolved. At this time, offsite power has been restored from two 161kV sources (Athens and Trinity), all eight 4kV SD boards are being powered from offsite sources, and six of eight Emergency Diesel Generators (B, C, D, 3A, 3C, 3D) are operable and in standby readiness. Emergency Diesel Generators A and 3B are not operable but are available at this time. All three units remain shutdown, in Mode 4, pending return of the 500 kV grid system. A timeline for return of the 500 kV grid system is yet to be finalized. "In addition, the previous 8-hour notification of offsite emergency sirens not meeting the minimum required is being updated to reflect current conditions. As of 1015 CDT, on 05/02/2011, repair activities have resulted in 92 of 100 sirens being in operable status, thereby meeting the minimum requirement of 70 operable." The licensee has notified the NRC Resident Inspector and the State of Alabama. Notified R2DO (Seymour), NRR EO (Nelson), IRD (Grant), DHS (Daly), and FEMA (Dennis). | 0 | 0 | 0 | 75 | 75 | 100 | -1 | -1 | -1 | A/R | A/R | A/R | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | LOSS COMM/ASMT/RESPONSE |  | Power Operation | Power Operation | Power Operation | Hot Shutdown | Hot Shutdown | Hot Shutdown | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(xiii) |  | 0 | 2011-04-27
46792 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2011-04-27 | 2011-04-27 17:30 | 2011-04-27 | AGREEMENT STATE REPORT - UNDERDOSE DUE TO CLUMPING IN THE DELIVERY DEVICE The following information was obtained from the State of Illinois via email: "The Radiation Safety Officer at Northwestern Memorial Hospital contacted the Illinois Emergency Management Agency on April 26th and reported that a medical event involving radiolabled Theraspheres had occurred. The treating physician attempted to perform radioembolization by placing the Y-90 microspheres in the treatment site using the appropriate Nordion Microsphere Delivery Device. However, increased resistance was felt in the administration syringe and a clump of microspheres developed between the needle injector assembly and the microcatheter connection during the initial bolus flush. Administration was halted as soon as the microsphere flow was slowed and a clump was visualized. Following a second attempt to complete the flush, the microspheres began layering within the outlet tubing. Further flushing of the system with saline did not alter the position of the remaining microspheres. The procedure was halted. Analysis of the system showed that a significant amount of the original dose had not been delivered as intended to the right hepatic lobe of the liver. Approximately 80 percent of the dose was not administered as a result of the failure. The primary cause of this incident is due to the clumping of the microspheres. However, the reason for the clumping is unknown." The intended dose of Y-90 was 59.4 mCi (2198.8 Mbq) for an exposure of 9750 rad (97.5 Gy). The administered dose was 22.7 mCi (839.9 Mbq) for an exposure of 3760 rad (37.6 Gy). Illinois Report Number: IL11049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-05-02
46791 | 0 | BEAUMONT HOSPITALS |  |  |  |  | 2011-04-27 10:45 | 2011-04-27 16:05 | 2011-04-27 | PATIENT RECEIVED LESS THAN PRESCRIBED DOSE DUE TO AN OCCLUSION IN THE DELIVERY CATHETER A patient received 14.8 Gray rather than the 63 Gray prescribed treatment to the upper portion of the liver using SIRSpheres manufactured by Sirtex. Only 0.7 GBq of the 3 GBq Y-90 microspheres were delivered to the treatment site due to an occlusion in the micro catheter. The treating physician terminated the dose administration after encountering difficulty in "pushing" the syringe contents through the micro catheter. While removing the catheter a small release of microspheres occurred due to the trapped pressure. The spill was contained and immediately cleaned up. The Hospital contacted the manufacturer and will return the dose unit for analysis. Both the patient and the referring physician have been informed. There was no adverse impact to the patient who has been rescheduled for a compensatory dose next week. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2011-05-03
46790 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-27 10:30 | 2011-04-27 13:06 | 2011-04-29 | LOSS OF EMERGENCY SIRENS DUE TO LOSS OF ELECTRIC POWER "At approximately 1030 EDT on April 27, 2011, [Sequoyah Nuclear Plant] received notification from TVAs Operations Duty Specialist that >30% of offsite sirens are not functional resulting in a 'major loss' of offsite [automatic] public notification [capabilities]. The loss of offsite sirens is due to loss of electrical power caused by severe thunderstorms and high winds in the area. Thirty five sirens are not functioning (32 sirens are considered 30%). Efforts are in place to restore offsite sirens to service. "At 1044 EDT on April 27, 2011, power was restored to 2 offsite sirens leaving 33 offsite sirens not functional. "At 1050 EDT on April 27, 2011, TVA's Operations Duty Specialist made a notification to Tennessee Emergency Management Agency (TEMA) and Hamilton County Emergency Response." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JEFF EPPERSON TO DONG PARK ON 4/29/11 AT 0514 EDT * * * Sequoyah Nuclear Plant reported that 28 of 108 sirens are not functional (26%) which is below the 'major loss' of offsite automatic public notification capabilities threshold. The licensee has notified the Tennessee Emergency Management Agency (TEMA) and Hamilton County Emergency Response. The licensee will notify the NRC Resident Inspector. Notified R2DO (Seymour). | 100 | 92 | 0 | 100 | 92 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2011-04-27
46789 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-25 22:00 | 2011-04-27 09:30 | 2011-04-27 | AGREEMENT STATE REPORT - INABILITY TO RETRACT SOURCE INTO RADIOGRAPHY CAMERA "On April 26, 2011, the Agency [Texas Department of State Health Services] was informed by a licensee that on April 25, 2011, at 2200 [CDT] hours a QSA model 880D radiography camera containing 92 curies of Iridium (Ir) 192 fell from a 16 inch pipe it was sitting on. The camera landed on the guide tube side of the camera crimping the guide tube near the connection of the guide tube to the camera. This prevented the radiographer from retracting the source into the camera. The radiographers used a hammer and were able to remove the crimp from the guide tube enough to retract the source. No individual involved with the event exceeded an exposure limit based on their electronic dosimetry readings. The radiographer doing most of the source retraction work, radiographer 'A', had an electronic dosimeter reading of 1.5 Rem. The second radiographer, radiographer 'B', received 200 milliRem. The licensee stated that the exposure to the radiographer 'A' was high due to the inability to place shielding over the source due to the crimp being so close to the camera. The personnel dosimetry of the two individuals involved have been sent to the licensee's dosimetry processor for reading. The licensee stated that the camera would be leak tested on April, 26, 2011. The licensee is investigating the event. Additional information will be provided as it is received in accordance with Reporting Material Events SA-300." Texas Incident Report # I-8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-05-02
46788 | 0 | MN DIVISION OF ENVIRONMENTAL HEALTH |  |  |  |  | 2011-03-26 15:39 | 2011-04-26 13:06 | 2011-04-26 | AGREEMENT STATE REPORT - ATTEMPTED BREAK-IN OF RADIOGRAPHY WAREHOUSE The State of Minnesota reported that Midwest Industrial X-Ray, Inc. had an attempted break-in at their Increased Controls facility. No unauthorized access to the facility occurred. Contact the Headquarters Operations Officer for details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 1 | 2011-04-29
46787 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-26 | 2011-04-26 09:58 | 2011-04-26 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA GUIDE TUBE The following information was provided via email: "On April 20, 2011 the Agency was notified that a radiography source had failed to retract to the shielded position because the material being radiographed had fallen on the guide tube and crimped it. Following company procedures, the Radiation Safety Officer was notified and the area was restricted to avoid public or excessive employee exposures. "Several entries were made to shield the source and allow an authorized individual to straighten the crimped portion of the tube within tolerable radiation fields. After several other trips to place lead shot on the source, four additional trips were required before the crimp in the source tube was straightened and the source was retracted into the shielded position. "The source retriever and his assistance received nominal radiation exposures during the procedure and no public exposures reportedly occurred. No violations were cited." Texas Incident #: I-8838. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-04-29
46786 | -1 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-26 00:20 | 2011-04-26 03:58 | 2011-06-23 | SAFETY RELATED PIPING HAD UNACCEPTABLE AIR VOID "Engineering reported that an ultrasonic [test] had identified an unacceptable air void in the horizontal run of suction piping from the Refueling Water Storage Tank (RWST) to the Safety Injection pumps, Residual Heat Removal pumps, and Containment Spray pumps. Technical Specification 3.0.3 was entered at 0020 CDT [on] 04/26/2011, and actions were started to remove the [air] void by venting of the suction pipe. Unit 2 was in progress of low power physics testing following refueling outage 2RF12. Inspection for [air] voids is in response to NRC generic letter on voiding in ECCS piping. "The void was removed from the system by venting. Engineering confirmed with ultrasonic [test] that the void was removed, and Technical Specification 3.0.3 was exited at 0143 CDT [on] 04/26/2011." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MIKE NIEMEYER TO DONALD NORWOOD AT 1628 EDT ON 6/23/2011 * * * "Further analysis demonstrated that the declaration of inoperability was a conservative action, and RHR and SI would have fulfilled their respective safety functions and been operable. This analysis is based on a detailed study of the void transport and piping design. The analysis confirmed that one (1) train of containment spray was inoperable, however the containment spray safety function would have been fulfilled with the remaining operable [containment spray] train. Based on the above, it is concluded that the health and safety of the public were unaffected by this condition and this event has been evaluated to not meet the definition of a safety system functional failure per 10CFR50.72(b)(3)(v)(D). The NRC Resident Inspector has been notified of this retraction." Notified R4DO (Deese). | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-26
46785 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2011-04-20 17:00 | 2011-04-25 18:33 | 2011-04-25 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECTED FROM CAMERA Radiography was being performed at a manufacturing shop and warehouse. The source became disconnected while in the guide tube. The radiographer unsuccessfully attempted to reconnect the source. The RSO was contacted and was able to reconnect the source and return it to the radiographic camera. The camera has been returned to service. The radiographers pocket dosimeter read off scale high. His dosimeter was later read and indicated a dose of 950 mR. The RSO pocket dosimeter read 150 mR. The licensee estimated the extremity dose was 2 R for each individual. The state does not consider this an abnormal occurrence. Camera: SPEC 150 serial number 0876 Source: 59 Ci Ir-192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2011-04-28
46784 | -1 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 5000 KW TANK RESEARCH HW | 2011-04-24 07:00 | 2011-04-25 16:42 | 2011-04-27 | VIOLATION OF TECHNICAL SPECIFICATION 3.2.3, REACTOR PROTECTION SYSTEM During a committee review, it was determined that during reactor operations on 4/24/11, the reactor was in operation when it became xenon precluded. Technical Specifications require two period monitoring channels in service during power operations. Because of xenon, one period monitor was indicating below scale and was considered inoperable. When the reactor operator identified the condition, he notified the reactor supervisor who ordered the operator to shutdown the reactor. The reactor operated in this condition for approximately 30 minutes. The licensee notified their Project Manager who advised them to notify the NRC Operations Center. * * * RETRACTION FROM JOHN BERNARD TO HOWIE CROUCH ON 4/27/11 AT 1653 EDT * * * Upon further review, it was determined that since the reactor was subcritical at the time this event occurred, Technical Specification 3.2.3 was not applicable. Therefore, the licensee has retracted this event. R1DO (Schmidt) and NRR (Adams) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MA | NPR | [5 empty] | 0 | 2011-04-25
46783 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 5000 KW TANK RESEARCH HW | 2011-04-21 22:30 | 2011-04-25 16:42 | 2011-04-25 | VIOLATION OF TECHNICAL SPECIFICATION 3.3.2.2, CORE PURGE BLOWER During a committee review, it was determined that during reactor operations on 4/21/11, the core purge blower was inoperable for greater than 5 minutes with reactor power greater than 100 KW which was a violation of Technical Specification 3.3.2.2. The licensee notified their Project Manager who advised them to notify the NRC Operations Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MA | NPR | [5 empty] | 0 | 2011-04-25
46782 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-04-25 09:50 | 2011-04-25 16:06 | 2011-04-29 | SINGLE TRAIN CHARGING PUMP DECLARED INOPERABLE "During normal operation with 23 Charging pump in service, an unusual sound was noticed by Operations. All other parameters were normal for the pump, but 21 Charging pump was placed in service as a precaution. Subsequent investigation was unable to conclusively identify the source of the unusual sound and a lower-than-expected crankcase oil pressure was observed on a maintenance run. Therefore, 23 Charging Pump was declared inoperable. This is the alternate safe shutdown pump responsible for inventory control for remote shutdown. NRC guidance indicates that a loss of a single train system not credited in accident analysis is reportable when identified in LCD 3.3.4 'Remote Shutdown.'" The licensee notified the NRC Resident Inspector and the New York Public Service Commission. * * * UPDATE AT 1408 EDT ON 04/29/11 FROM MIKE BURNEY TO S. SANDIN * * * The licensee is retracting this report based on the following: "Indian Point Unit 2 is retracting the 8-hour non-emergency notification made on April 25, 2011, at 1606 EDT (EN #46782). The notification on April 25, 2011, reported a loss of a single train system identified in LCO 3.3.4 'Remote Shutdown' (SSFF [safety system functional failure]) as a result of declaring the 23 Charging Pump (CP) inoperable. The 23 CP exhibited unusual sound during operation. Because the 23 CP is credited in Technical Specification (TS) 3.3.4 for Remote Shutdown, the inoperable condition was determined to be a loss of safety function. The TS 3.3.4 Allowed Outage Time (AOT) for inoperable conditions is 30 days. In accordance with recent NRC guidance provided to Indian Point for loss of single train systems, although not credited in the accident analysis and specified in Technical Specification 3.3.4, this condition is reportable as a SSFF. "Subsequent investigations determined that the documented condition does not pose a challenge to the operability of the 23 CP. The noise was associated with the normal operation of the charging pump internal check valves. This condition is a long term issue that does not affect the current operation of the pump. The pump was in operation with no abnormal parameters noted at the time the noise was noted. No SSFF occurred." The licensee will inform the NRC Resident Inspector. Notified R1DO (Schmidt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(2)(xi) |  |  | 0 | 2011-04-25
46781 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-23 17:00 | 2011-04-23 22:08 | 2011-04-23 | LOSS OF POWER SHUTS DOWN AIR MONITORING VACUUM PUMPS "The air monitoring vacuum pumps were disabled for approximately 3 hours. A severe weather windstorm blew down an electrical power pole inside the plant property at 1700 CDT. Because of the electrical issue, it took approximately 3 hours to reestablish cooling water to the vacuum pumps. These pumps provide vacuum for the stack monitoring and personnel area monitoring systems in the Feed Materials Building. The pumps were restored to service at approximately 2000 CDT." There was no damage, no release, and no exposure from this event. The licensee notified the Fuel Facility Inspector (Hartland) in Region-2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2011-04-23
46780 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-23 09:21 | 2011-04-23 12:37 | 2011-04-23 | VALID AUXILIARY FEEDWATER PUMP START WHILE COOLING DOWN REACTOR "At 0921 [EDT] on 4/23/11, CNS Unit-1 received an auxiliary feedwater pump auto start due to low-low level in the 1B steam generator. The 1A auxiliary feedwater pump started and restored steam generator level to the normal operating band." A cooldown was in progress at the time of the event and the tagout isolated feedwater flow to the 1B steam generator. The licensee notified the NRC Resident Inspector. The states of North and South Carolina, and York, Gaston, and Mecklenburg Counties will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-04-23
46779 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2011-03-25 | 2011-04-22 18:07 | 2011-09-01 | AGREEMENT STATE REPORT - MISPLACED SOURCE The following information was received by e-mail from the State of Nevada: "A vial with serial # S358015-011, containing 198 microcuries of Cs-137, belonging to the licensee, is unaccounted for. Cardinal Health removed all equipment from the licensee's office on the last day of patient care and stored it at Advanced Isotopes. The source was originally from Biotech (currently Cardinal Health). The licensee allegedly tried working with Cardinal Health to clear this up, but to no avail. The licensee plans to contact the RSO of Advanced Isotopes, who is currently out of town, and let the [Nevada] Radiation Control Program know if they have any additional information. The matter is being taken very seriously and is being investigated." This incident is documented as Nevada Incident- NV110012 and was initially reported to the State of Nevada on 4/12/2011. * * * UPDATE AT 1705 EDT ON 09/01/11 FROM SNEHA RAVIKUMAR TO S. SANDIN * * * The following update was received from the State of Nevada via email: "NV 110012 has been closed. The source has been deemed missing. The license had been revoked. The Responsible Person for the license had been prohibited from being listed on a RML in Nevada, for a period of 3 years, from the date of revocation, though his eligibility to perform work under the supervision of an authorized user is not affected by this prohibition. Since the radiological material license is being revoked, not terminated, the licensee remains responsible for the proper disposal of the lost Cs-137 source. Should the source be found or discovered, the licensee is responsible and liable for the costs associated with disposal of the source, any damages or losses caused by source, and, if necessary, any cleanup, remediation, and/or decommissioning efforts that may be required as a result of the source." Notified R4DO (Proulx) and FSME (Hsueh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2011-04-27
46778 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-21 15:30 | 2011-04-22 15:29 | 2011-04-22 | AGREEMENT STATE REPORT - MALFUNCTIONING GAUGE INVOLVING A CESIUM-137 SOURCE "On April 21, 2011, at approximately 1530 CDT, a malfunction occurred when a repaired gauge was being installed on a process vessel at the licensee's facility. The device has two 2-curie Cesium-137 sources, each attached to a separate chain, that are lowered into place in the insertion tube via hand crank. When the first source was being lowered into the tube, the mechanism seized and the source could not be raised or lowered. The device was removed from the vessel, the chain was cut, and the source was pulled up and placed into shielded container. The device and two sources were transported back to the service company for repair. "Gauge information: Thermo Scientific (TFS) model 5220. Device SN: B-36. Source SNs: MB-3946 and MB-3956." Texas Incident: I-8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-04-27
46777 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-04-21 19:10 | 2011-04-22 14:21 | 2011-04-22 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED CONTRACTOR SUPERVISOR A non-licensed contractor supervisor tested positive for alcohol during a follow-up fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2011-04-22
46776 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2011-04-22 | 2011-04-22 12:46 | 2012-01-04 | POTENTIAL DEFECT IN SUBMERSIBLE VALVE POSITION SENSORS "This letter is issued to provide notification of a potential defect in QualTech NP Top Potted Generation 3 Quick Disconnect Connector Pin Side assemblies installed on Topworx C7 and SV7 switches. All assemblies supplied prior to April 20, 2011 are potentially affected. These assemblies were supplied to Topworx [as] submergence qualified in accordance with our Test Report EGS-TR-23009-14. It was discovered during supplemental qualification testing that previously supplied assemblies may not properly seal against moisture intrusion if utilized in a submergence application. "The recommended corrective action for existing assemblies is to pressure test and, if required, repair them. Corrective actions already implemented will be effective in preventing recurrence of this condition. Additionally, all future assemblies will be required to pass pressure testing prior to acceptance. "It has been confirmed that all assemblies previously supplied are for use in Chinese Nuclear Power Plants and therefore, no US plants are affected." Most of the assemblies are still in this country and the remainder are in Switzerland awaiting shipment. All assemblies will be recalled and pressure tested. * * * UPDATE RECEIVED VIA FAX FROM TONY GILL TO JOE O'HARA AT 1545 ON 8/12/11 * * * "The purpose of this letter is to provide additional information concerning the status of all affected assemblies. As stated in the previous notifications all serial numbers affected by this defect have been identified and to date only 30 production units remain to be returned for testing/repair. We are still experiencing 100% success when repair is needed. "It was previously reported that 'all affected assemblies were for use in Chinese Nuclear Power Plants and therefore no US Plants are affected'. This is no longer a correct statement. Our customer, Topworx, notified us on August 9 that one of their customers, Flowserve, had supplied valve packages containing 16 of these assemblies to Pilgrim Station in Plymouth, MA. It has been reported to us that these assemblies were never installed and are in the process of being returned for testing/repair. "These 16 assemblies are included in the 30 production units remaining to be tested/repaired. It has been identified that 4 of the remaining assemblies are still in China and the other 10 were supplied to Flowserve. "Additional information concerning these assemblies will be provided as it becomes available. A final letter will be issued once corrective actions for these 30 assemblies are complete." Notified R1DO(Powell), Part 21 GRP via e-mail * * * UPDATE RECEIVED VIA FAX FROM TONY GILL TO CHARLES TEAL AT 1623 EST ON 1/4/12 * * * "On April 22, 2011 QualTech NP, Huntsville issued an initial notification letter to the Nuclear Regulatory Commission and our Customer Topworx concerning a potential defect in QualTech NP Top Potted Generation 3 Quick Disconnect Connector Pin Side assemblies installed on Topworx C7 and SV7 Switches. A total of three notification/status letters associated with this subject have been previously issued. "As of this date all affected production units have been returned and tested/repaired. We have experienced 100% success when repair was needed. "This letter provides the final status and closeout of the above referenced 10CFR21 notification." Notified R1DO (Holoday) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21 |  |  |  | 0 | 2011-04-22
46775 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2011-04-21 17:00 | 2011-04-21 19:32 | 2011-04-21 | POTENTIAL INADVERTANT ACTIVATION OF ONE EMERGENCY SIREN "On April 20, 2011, several hours after a severe lightning storm in the early morning hours, RE Ginna Nuclear Power Plant received a report that a siren may have activated. There was no specific location provided in the report. A review of the siren computer history showed no indication of any siren activation during that time frame. During the daily silent test of the siren system, one siren was determined to have failed due to loss of its AC power. "During an inspection of the siren on April 21, 2011, it was reported that the siren appeared to have been struck by lightning. A number of electronic components in the siren had to be replaced and as a result the technicians were unable to determine if the siren had activated. As such. there is a potential that the siren may have been the source of the initial report. The siren has been tested and returned to service. "The NRC Resident Inspector was notified by the licensee." The licensee notified the Public Utilities Commission and Wayne and Monroe Counties. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-21
46774 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-21 16:01 | 2011-04-21 19:16 | 2011-04-21 | MANUAL REACTOR TRIP DUE TO CIRCULATING WATER PUMPS OUT OF SERVICE "A manual trip of Salem Unit 1 was initiated due to a loss of circulating water pumps from heavy grassing at the circulating water intake. All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the steam dump system. All Auxiliary Feed Water (AFW) pumps auto started as expected on low steam generator levels from the trip. "During a period of heavy grassing with one circulating water pump out of service for maintenance and another out of service for water box cleaning, a third circulating water pump's screen stopped and this circulating water pump was emergency tripped. When this circulating water pump was emergency tripped, the adjacent circulating water pump received a large intake of grass and automatically tripped. "The abnormal operating procedure provides guidance to trip the plant if less than three circulating water pumps are in service and power is above P-10. At this point the manual reactor trip was initiated. "The crew entered EOP-TRIP-1, appropriately transitioned to EOP-TRlP-2 and stabilized the plant at no load conditions. "Salem Unit 1 is currently in mode 3. Reactor Coolant System temperature is 547F with pressure at 2235 psig. All ECCS and ESF Systems are available. Salem Unit 2 is currently defueled in a planned refueling outage and there is no impact to Salem Unit 2. "No personnel injuries have occurred as a result of the trip. "This event is reportable per 10CFR50.72(b)(3)(iv)(A) due to the auto start of the AFW pumps. "This event is reportable per 10CFR50.72(b)(2)(iv)(B) due to the manual reactor trip." The plant is aligned with a normal electrical line-up from offsite power sources. The Licensee has notified the NRC Resident Inspector. The Licensee will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. * * * UPDATE FROM MATTHEW MOG TO VINCE KLCO ON 4/21/2011 AT 2241 EDT * * * "During the post-trip data review for the manual reactor trip that occurred on April 21, 2011 at 1601 [EDT], 2 additional automatic Auxiliary Feedwater (AFW) pump start signals were identified. Operators were controlling AFW level to maintain steam generator levels within the band required by the emergency operating procedures. At approximately 1615 [EDT] the 13 steam generator level had cleared the low level setpoint but subsequently dipped below the low level setpoint at 1623 [EDT]. At approximately 1640 [EDT], the 14 steam generator had recovered above the low level setpoint and subsequently dipped below the low level setpoint. The Unit 1 reactor had been previously tripped at 1601 [EDT] and all AFW pumps had automatically started. The 13 turbine driven AFW pump was stopped at approximately 1625 [EDT]. The two motor driven AFW pumps continued to run throughout this event. Low level in one steam generator generates an automatic start of the motor driven AFW pumps and is reportable per 10CFR50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector and will notify Lower Alloways Creek Township and the States of New Jersey and Delaware. Notified the R1DO (Cook). | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-04-21
46773 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-04-21 14:05 | 2011-04-21 16:57 | 2011-04-21 | OFFSITE NOTIFICATION DUE TO INADVERTENT SEWAGE DISCHARGE "On [Thursday], 4/21/2011, at 1405 [EDT], Oconee Nuclear Station notified the South Carolina Department of Health and Environmental Control (SCDHEC) that sanitary sewage had been collected and inadvertently discharged without processing through the sanitary sewage system. The event was identified at 0730 [EDT] on 4/21/2011. The suspected cause is plumbing blockage. It is estimated that intermittent discharges over approximately three months resulted in a total discharge of approximately 4500 gallons. The Oconee NRC Senior Resident Inspector was notified. This event notification is being made pursuant to 10 CFR 50.72 (b)(2)(xi) due to notification of SCDHEC. "Immediate corrective action was taken to isolate the affected portion of the sanitary sewage system. "This event has no significance with respect to the health and safety of the public." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-21
46772 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-20 17:34 | 2011-04-20 20:45 | 2011-04-20 | AUTOMATIC REACTOR TRIP "At 1734 EDT, [Vogtle] unit one automatically tripped from 100% power. No significant activities were in progress that should have challenged the Reactor Protection System. All control rods fully inserted. AFW system actuated as expected on S/G Lo-Lo-Level and AMSAC [ATWS Mitigation System Actuation]. System responses allowed for an uncomplicated reactor trip response. Plant is stable and will remain in Mode 3 during cause investigation. "Cause of the reactor trip is under investigation." The plant is in its normal shutdown electrical lineup. Decay heat is being sent to the main condenser through the turbine bypass valves. The steam generators are being fed from auxiliary feedwater. There was no effect on unit two. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-04-20
46771 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2011-04-20 09:15 | 2011-04-20 18:05 | 2011-06-08 | WATERTIGHT DOORS LEFT AJAR SIMULTANEOUSLY DURING ROOM CHECKS "During the performance of operator rounds in the Lake Screenhouse Safe Shutdown System (SX) pump rooms, two water tight doors were left opened simultaneously during the room checks. These two doors opened simultaneously [which] allowed for communication between the Division 1 SX room and Division 2 SX pump room. The operator was in constant attendance in the Division 2 SX pump room during the performance of the equipment checks. "During site review, it was determined that a flood in either the Division 1 or Division 2 SX pump rooms would not be isolated to the initiating room, but potentially affect both trains of SX. This could result in a loss of cooling for both Residual Heat Removal systems, therefore, a condition that could have prevented fulfillment of a safety function under 10CFR50.72(b)(3)(v)(B). "The NRC Senior Resident has been notified." Offsite power is normal and emergency diesel generators are operable and available. * * * RETRACTION FROM ED TIEDEMANN TO PETE SNYDER ON 6/8/11 AT 1141 EDT * * * "A subsequent plant barrier impairment evaluation consistent with Exelon Procedure CC-AA-201, 'Plant Barrier Control Program' has determined that no loss of safety funct ion would have occurred. Each of the following door functions and related postulated events were reviewed for impact: ventilation; flooding, internal and external; high energy line breaks; missiles; radiation protection; and fires. For the condition with the SX pump room water tight doors being open with an operator in the area, the conclusion is an SX division remains protected to ensure that in any of the evaluated events the safety function of SX has been maintained." The licensee has notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-04-20
46770 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-18 | 2011-04-20 17:38 | 2011-04-20 | AGREEMENT STATE REPORT - MALFUNCTIONING GAUGE INVOLVING A 2 CURIE CESIUM-137 SOURCE The following was received from the state via fax: "On April 18, 2011, a gauge malfunction occurred at the licensee's facility during a device installation on a process vessel. When the 2 Curie Cesium-137 source was inserted into the vessel, the chain connecting the source to the nuclear gauge broke allowing the source to travel to the bottom of the insertion tube. The source being at the bottom of the insertion tube is its normal operating position. A radiation survey was conducted by the licensee indicating radiation levels were normal. The device was removed from the vessel, [and] the source [was] retrieved from inside of the vessel. The device and the 2 sources were taken by the service company to their facility for repair. There was no additional radiation exposure to any members of the general public or radiation workers due to this incident. Gauge information: TFS model 5220 containing (2) 2-Ci Cesium-137 sources. Device SN: B-36. Source SNs: MB-3946 and MB 3956. "Additional Information: "The sources had been removed from the process vessel back in January 2011 and were put into storage while the unit was down for repairs (a 'turnaround'). There are 6 of these custom devices on 3 vessels. The insertion tube is a divided tube and one source is lowered down each side; 2 sources each tube. Five of the sources lowered with no problems. As they were lowering the 6th one down the insertion tube, the chain attached to the source broke and the source fell to the bottom of the tube (which is its normal position when unit is in operation, so no exposure to any individual resulted from it being there). The insertion tube is approximately 25 feet down to the bottom. They were able to 'fish' the top of the chain and pulled the chain with the source out of the tube and put the source directly into a pig. All other individuals had been moved back a safe distance for ALARA. The service company took the device and sources to their facility for repair. The unit will remain out of operation until device is repaired and installed." Texas Incident #: I - 8836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-04-25
46769 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2011-04-19 14:30 | 2011-04-19 20:29 | 2011-04-19 | BOTH DIVISIONS OF RESIDUAL HEAT REMOVAL INOPERABLE "At 1430 hours, a water leak was discovered on the Unit 1 Emergency Diesel Generator Cooling Water Pump (EDGCWP) room cooler. As a result, the Unit 1 EDG (Division II) was declared inoperable and Technical Specification (TS) 3.8.1 was entered. "At this time, Division I RHR was inoperable for planned maintenance on the Division I RHR room cooler. In the event of a LOOP/LOCA scenario, RHR would not have been able to perform its safety function (i.e., Division I RHR was impacted by the ongoing room cooler maintenance and Division II RHR would not have had an operable on-site emergency power source). Given the impact on the RHR system, this event is reportable under 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function required to mitigate the consequences of an accident. "Note that at the time of discovery, offsite power was available to Division II RHR as well as the Division I and Division II Core Spray systems. "At 1816 hours, the Division I RHR system room cooler was restored and Division I RHR was declared operable." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-19
46768 | 0 | NAVAL UNDERSEA WARFARE CENTER |  |  |  |  | 2011-04-18 | 2011-04-19 14:21 | 2011-04-19 | UNACCOUNTED FOR IONIZING AIR GUNS CONTAINING 10 MILLICURIES OF Po-210 Naval Undersea Warfare Command (NUSW) located in Keyport, Washington has identified fifty seven (57) ionizing air guns that are unaccounted for. The devices were manufactured by NRD, LLC of New York, NY and contained 10 milliCuries of Po-210. NUSW is missing five (5) Model P-2021 devices and fifty-two (52) P-2051 devices. These are general license devices. The unaccounted devices were found during a command inspection after questions arose surrounding the number of devices in the command. The inspection revealed the majority of the devices seem to have gone unaccounted for during the 1994 - 1995 timeframe. Contamination surveys have confirmed there are no contamination issues or workforce exposure issues associated with this event. A command investigation is ongoing. The following serial numbers were identified as unaccounted for: For Model P-2021: A2GQ217, A2GQ241, A2BY498, A2AW678, and A2AQ471. For Model P-2051: 95609, 83722, 79841, 79225, 76422, 76423, 76424, 76425, 76427, 76428, 76429, 76430, 76431, 76432, 76433, 72859, 72860, 72861, 70708, 70709, 70710, 70711, 70712, 70713, 70714, 67850, 67851, 67853, 67854, 67855, 67856, 67857, 67860, 67861, 67862, 67863, 67881, 67882, 67883, 67884, 67888, 56477, 56303, 55244, 46840, 46844, 46914, 46952, 46954, 46963, 38242, AND 38348. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | WA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-04-19
46767 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2011-04-19 10:45 | 2011-04-19 12:50 | 2011-04-19 | OFFSITE NOTIFICATION DUE TO FATALITY OF A CONTRACT EMPLOYEE "This notification is a 4-hour Non-Emergency notification being performed in accordance with 10CFR50.72(b)(2)(xi) for notification to an off-site government agency. "At 0708 [EDT] on 4/19/2011, off-site medical assistance was requested for a Turkey Point Nuclear Power Plant Station contract employee experiencing an apparent heart attack while being in-processed to the plant. The individual was transported to the hospital and was later pronounced dead. "At 1045 on 4/19/2011, the Occupational Safety and Health Administration (OSHA) was notified. The Turkey Point Unit 3/4 control room was notified of the OSHA notification at 1058 on 4/19/2011. "Unit 3 remains in Mode 1 at 100% power. "Unit 4 is in a planned refueling outage. "The NRC Resident Inspector was informed." The contract employee was outside of the Protected Area and had not performed any work at the facility. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-19
46766 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-18 23:09 | 2011-04-19 00:44 | 2011-05-10 | PLANT PROCESS COMPUTER REMOVED FROM SERVICE FOR PLANNED REPLACEMENT "At 2309 [CDT] on April 18, 2011, the Unit 2 Plant Process Computer (PPC) was removed from service for planned replacement in the current Unit 2 refueling outage. The Unit 2 PPC feeds the Safety Parameter Display System (SPDS) used in the Main Control Room (MCR) and the Technical Support Center (TSC). The Unit 2 PPC also feeds the Emergency Response Data System (ERDS). The Unit 1 and Unit 2 PPCs also feed the Plant Parameter Display System (PPDS) used in the MCR, TSC and Emergency Operations Facility (EOF). Meteorological data will remain available. The dose assessment program will remain functional as the Unit 1 Plant Process computer will be capable of providing the necessary data through PPDS to run the program. The dose assessment program is not affected by the Unit 2 PPC being out of service. As compensatory measures, the backup method to fax or communicate via a phone circuit applicable data to the NRC, TSC and EOF exists. There is no impact to the Emergency Notification System (ENS) or Health Physics Network (HPN) communications systems. "The new Unit 2 PPC is scheduled to be functional on April 23, 2011. However, based on the mode Unit 2 will be in, this will limit the number of points that would provide usable data. The Unit 2 PPC will be tested as mode changes occur. The Unit 2 PPC is planned to be declared functional by Mode 2. A follow-up ENS call will be made once the Unit 2 PPC is declared functional. "The loss of SPDS and ERDS is a 'major loss of assessment capability' and is reportable under 10CFR50.72(b)(3)(xiii). "The NRC Senior Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS call." * * * UPDATE FROM SCOTT BUTLER TO JOE O'HARA AT 0932 ON 5/10/11 * * * "As of 0815 CT on May 10, 2011, the Unit PPC is considered operational with respect to the Safety Parameter Display System (SPDS), Plant Parameter Display System (PPDS) and Emergency Response Data System (ERDS). Therefore, a Major Loss of Assessment Capability no longer exists on Unit 2. The EP Manager will contact the NRC Computer Center today to conduct an ERDS test for Unit 2 to ensure the data is being satisfactorily sent to the NRC. "The NRC Resident Inspector and the State of Illinois (through the Illinois Emergency Management Agency Resident Inspector) have been notified of this ENS update. Notified R3DO(Passehl) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-19
46765 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-04-18 08:00 | 2011-04-18 13:24 | 2011-04-18 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR PLANNED MAINTENANCE "The facility Technical Support Center (TSC) has been rendered non-functional due to a pre-planned and scheduled maintenance period for the Technical Support Center ventilation system. The maintenance activities include replacement of the evaporator coil, fan, and expansion valve. The TSC ventilation maintenance will be worked with high priority and is expected to be complete prior to 1200 EDT on 4/19/11 . "Pre-arranged compensatory measures for maintaining emergency assessment, off-site response, and off-site communication capabilities were put in place prior to the beginning of the TSC ventilation maintenance and will remain in place for the duration of the maintenance period. These measures include the relocation of the TSC staff in the event of a declared emergency IF the Emergency Director deems the TSC uninhabitable." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-18
46764 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-16 14:30 | 2011-04-17 11:44 | 2011-04-17 | AIR MONITORING VACUUM PUMPS DISABLED "The air monitoring vacuum pumps were disabled for approximately 30 minutes. The soft water supply to the air monitoring vacuum pump seals on the 2nd floor of the Feed Materials Building (FMB) was shut down for Annual Shut Down. These pumps provide vacuum for the stack monitoring and personnel area monitoring systems in the FMB. While the soft water system was shut down, a sanitary well water supply was being used for the vacuum pump seals. A back flow preventer in the sanitary water supply line malfunctioned and interrupted flow to the pump seals. This caused the vacuum pumps to be shut down until a temporary water supply could be established. A temporary water supply was reestablished to the pump seals. The pumps were restored to service at approximately 1500 [CDT]. The back flow preventer has been replaced and the system is currently working properly." There were no indications that activities performed in the FMB caused a release during the time period that the stack and personnel monitoring system was out of service. The licensee notified R2 (Hartland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2011-04-17
46763 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-04-16 22:52 | 2011-04-17 04:21 | 2011-04-17 | HPCI INOPERABLE DUE TO LUBE OIL PRESSURE LOW OUT OF BAND "Event Description: On 4/16/2011 at 2252 [EDT], the Unit 2 High Pressure Coolant Injection (HPCI) System was declared inoperable due to the determination that its Lube Oil System was not providing adequate lube oil pressure and flow to the HPCI Turbine/Pump bearings. This was determined following the high steam pressure operability run (i.e., within 48 hours of achieving adequate test pressure following a scheduled refueling/maintenance outage) as required by Technical Specification Surveillance Requirement 3.5.1.7. The HPCI system is inoperable in accordance with Technical Specification 3.5.1. "This report is being made in accordance with 10 CFR 50.72(b)(3){v)(D), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "Initial Safety Significance Evaluation: The safety significance of this event is considered minimal. The Reactor Core Isolation Cooling (RCIC) system, Automatic Depressurization System (ADS). and Low Pressure Emergency Core Cooling systems (ECCS) remain operable at this time. Actions have been taken to protect redundant safety systems. "Corrective Actions: The HPCI system remains inoperable pending further troubleshooting of the low lube oil pressure condition." The NRC Resident Inspector has been notified. * * * RETRACTION FROM LEE GRZECK TO HOWIE CROUCH AT 2051 EDT ON 4/17/11 * * * "Upon further review, it has been determined that the HPCI system was not rendered inoperable as a result of the condition identified on April 16, 2011. During performance of 0PT-09.2, the Control Room received a HPCI turbine bearing oil pressure low alarm. Following 0PT-09.2, preventive maintenance procedure 0PM-TRB507, 'High Pressure Coolant Injection (HPCI) Operational Inspection', was performed. During performance of 0PM-TRB507, the turbine governor end oil pressure was found indicating 8.5 psig. The procedure specifies a normal value of 10-12 psig. Due to the above condition, HPCI was conservatively declared inoperable at 2252 [EDT] on April 16, 2011. "Subsequent Engineering evaluation has determined that HPCI could have run long enough to complete its intended safety function [24 hrs.]. Pressure outside of the normal band specified in 0PM-TRB507 is a condition that requires correction, but is not detrimental to the bearing itself. The critical characteristic of proper bearing lubrication is to assure a film of oil between the tilting pads and the rotating shaft of the HPCI turbine. Bearing outlet temperatures are recorded during each performance of 0PT-092 for trending and no abnormal temperatures were noted during the last performance of 0PT-09.2 on April 16, 2011. This indicates there was a film of lubrication between the rotating shaft and the tilting pads of the journal bearing. The two hour turbine operation of the most recent 0PT-09.2 performance resulted in higher oil temperature, which can result in lower oil pressure. Adjustments can be made to the ball valve of the HPCI governor end bearing to attain the specified supply pressure to each bearing. These adjustments are not unexpected, as discussed in the Electric Power Research Institute (EPRI) maintenance guide for HPCI turbines. A slight adjustment was made to the HPCI governor end bearing on April 17, 2011 to establish pressure at 11.5 psig. At 1009 hrs. on April 17, 2011, 0PT-09.2 was performed satisfactorily, with the HPCI governor end oil bearing supply pressure verified to be within the 10-12 psig range at 2100 rpm and 4100 rpm. Oil flow to and from the bearing is required only for lubrication and cooling and does not provide any lift or other force to assist the bearing in performing its function. The oil flow during this event was still adequate to provide sufficient lubrication and cooling of the bearings. Therefore, the slight decrease in oil pressure to the HPCI governor end bearing did not indicate degradation in performance. "On this basis, the HPCI system was capable of performing its safety function to mitigate the consequences of an accident and this issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 460134. "The NRC Resident Inspector was notified of this retraction." Notified R2DO (O'Donohue). | 0 | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-17
46762 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-04-16 18:49 | 2011-04-17 02:50 | 2011-04-17 | SAFEGUARDS REPORT - POTENTIAL DISCOVERED VULNERABILITY Discovered vulnerability in a safeguard system that could potentially allow access to a controlled access area for which compensatory measures had not been employed. Upon discovery, compensatory measures were established. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-04-17
46761 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-04-16 18:55 | 2011-04-16 19:24 | 2011-04-19 | UNUSUAL EVENT DECLARED DUE TO LOSS OF ALL OFFSITE POWER FROM TORNADO DAMAGE "At 1849 hrs, Surry Power Station (SPS) Unit 1 and Unit 2 experienced an automatic Reactor Trip from a Loss of Offsite Power, as a result of a tornado touching down in the station's switchyard. Unit 1 reactor tripped as a result of a Loss of Coolant Flow > P-8 (35% power), and the Unit 2 reactor tripped as a result of a 500 kV Leads Differential Turbine-Generator trip. Both units responded as designed. "Unit 1 electrical power is being provided by Number 1 Emergency Diesel Generator (EDG) to the 1H emergency bus, with the Station Blackout (SBO) diesel loaded on to the 1J emergency bus. Unit 2 electrical power is being supplied by the number 2 EDG to the 2H emergency bus, with the number 3 EDG loaded on to the 2J emergency bus. "All Unit 1 control rods inserted on the reactor trip, and all Unit 2 control rods inserted on its respective reactor trip. The Low Level Intake Structure (LLIS) is without power. All three Emergency Service Water Pumps are running to supply the intake canal. Efforts are underway to restore Bus 7, which will give each unit an emergency bus powered by offsite power (Unit 1 1J, Unit 2 2H) and restore power to the LLIS. "Decay heat is being removed by auxiliary feedwater on both units and atmospheric steam release via the steam generator PORVs. Both units are currently on natural circulation. All other system parameters are normal and stable. "At 1855 hrs a NOUE was declared due to a loss of offsite power (applicable to U1 and U2). Additionally, due to an estimated 100 gallon fuel oil spill from an above ground storage tank near the station's garage, the Virginia State Department of Environmental Quality was notified at 2041 and the Surry County Local Emergency Planning Coordinator was notified at 2114. At 2334, the Virginia State Department of Environmental Quality was notified and the Surry County Local Emergency Planning Coordinator was notified at 2336, due to an estimated 200 gallon oil leak to the ground from a station switchyard transformer damaged during the tornado. "The NRC Resident Inspector has been notified and is on-site." Notified DHS (Rickerson), FEMA (Boscoe), DOE (Turner), HHS (Hoskins), and USDA (Russell). See related EN #46762 * * * UPDATE FROM TUCKER CARLSON TO CHARLES TEAL ON 4/19/11 AT 0756 * * * The licensee exited the emergency condition at 0745 EDT on 4/19/11. Offsite power has been restored, and the plant is shutdown and cooled down. Notified R2DO (O'Donohue), NRR EO (Thorpe) and IRD (Gott). Informed the following Federal Agencies via Blast Dial: DHS, FEMA, USDA, HHS and DOE. | 0 | 0 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2011-04-16
46760 | -1 | ENGINE SYSTEMS, INC |  |  |  |  | 2011-04-15 | 2011-04-15 17:29 | 2011-05-13 | POTENTIAL DEFECT IN MAGNETROL LEVEL SWITCH FROM ENGINE SYSTEMS INCORPORATED "Engine Systems, Incorporated (ESI) began an evaluation of a level switch on February 16, 2011. Monticello Nuclear Plant returned a level switch for failure evaluation. The reported condition was that the switch mechanism would not actuate throughout the entire level range. ESI supplied the level switch in July, 2008. The switch was functionally tested prior to shipment and it worked properly at that time. It remained in customer inventory until recently when it was tested and the problem was identified. "This level switch is used in the fuel oil day tank of some EMD 999 emergency diesel generators and controls the fuel transfer pump. Malfunctioning of this switch could prevent the fuel transfer pump from operating and therefore the diesel generator could shut down due to insufficient fuel supply; thus preventing the diesel generator from performing its safety related function. The EMD 999 fuel system also incorporates a backup fuel transfer pump that is controlled by the level alarm switch within the day tank. The backup transfer pump turns on when the low level alarm is actuated and turns off when the high level alarm actuates. "ESI has been conducting tests and inspections of the returned level switch and will be coordinating with the manufacturer (Magnetrol) to complete our evaluation. To date, no other similar failures with this Magnetrol level switch have been reported to ESI." Component: Magnetrol level switch, ESI P/N: 8277780-ESI, Magnetrol type A10 Report No: 10CFR21-0101-INT * * * RETRACTION FROM TOM HORNER TO DONG PARK ON 5/13/11 AT 1146 * * * The following information was received by facsimile: "COMPONENT: Magnetrol level switch ESI P/N: 8277780-ESI Magnetrol type A 10 "PURPOSE: This report is a follow-up to an interim report (10CFR21-0101-INT) issued by Engine Systems, Inc. (ESI) on 04/15/11 which identified a deviation with a Magnetrol level switch. The interim report was issued because ESI was not able to complete the evaluation within the 60 day requirement of 10CFR21. "SUMMARY: Evaluation of the level switch failure at Monticello was completed on 5/12/11 and it has been determined that the deviation is not a reportable defect as by defined by 10CFR21. Based on the data collected by ESI and through evaluation by and discussion with Magnetrol (manufacturer of the level switch), it is ESI's conclusion that the level switch was delivered to the customer in working order and that it must have been damaged subsequent to ESI's involvement. Furthermore, within the fuel oil system in which the level switch is installed, there is an inherent redundancy whereby the high/low level alarm switch will actuate to turn on or turn off a secondary fuel transfer pump in the event this level switch (or its associated fuel transfer pump) does not function properly. Therefore, ESI does not consider this as a reportable defect. Notified R2DO (Guthrie), R3DO (Passehl), and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-04-15
46759 | 0 | ABB, INC. |  |  |  |  | 2011-04-15 | 2011-04-15 14:47 | 2011-04-15 | POTENTIAL DEVIATION IN SEISMIC RATINGS OF ABB, INC. KF RELAY FAMILY ABB, during an internal review, discovered that their KF family of relays were originally qualified to meet IEEE-STD-344 (1971) but were incorrectly certified to meet IEEE-STD-344 (1975/1987), which requires different testing. Relay samples have been sent to an independent lab to determine if the subject relays would meet IEEE-STD-344 (1975/1987). Expected date of the final engineering evaluation is July 1, 2011. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2011-04-15
46758 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2011-03-23 | 2011-04-15 15:12 | 2011-04-15 | POTENTIAL DEFECT IDENTIFIED IN A VARIAN MEDICAL SYSTEMS HIGH DOSE RATE AFTERLOADER On March 23, 2011, a technician was installing a VariSource High Dose Rate (HDR) Afterloader - Model VariSource IX when the active wire composed of a 10 Ci Ir-192 source failed to extend. After troubleshooting it was discovered that the wire was stuck on the wedge block which is part of the emergency retract mechanism. (See NRC Event Notice 46695) Engineering evaluation by the vendor, Varian Medical Systems, Inc., has identified a very small amount of material in the wedge block which has a small bore that the source wire passes through. Otherwise, nothing remarkable was identified. This machine is a new unit with a very low number of source extensions. There is no history of similar events with new units of this type. The vendor has issued a Tech Tip for all new sites and is investigating a new design for the wedge block with a goal of implementing any new design by April 30, 2012. Additionally, all VariSource HDR customers have received a copy of Customer Technical Bulletin CTB-VS-640A that discusses the potential of source wire path constriction and source wire jamming. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-04-15
46757 | 0 | TEAM INDUSTRIAL SERVICES |  |  |  |  | 2011-04-15 | 2011-04-15 14:42 | 2011-04-15 | RADIOGRAPHY CAMERA LOST DURING SHIPPING On 4/13/11, two radiography cameras were picked up by the shipper from the licensee facility in Hammond, IN. The cameras were being sent to QSA in Baton Rouge, LA. On 4/14/11, one camera arrived at QSA while the other was still shown in the shipper's hub in Memphis, TN. On 4/15/11, the licensee contacted the shipper when tracking indicated that the camera was still in Memphis. The shipper could not find the package and is conducting a search of the facility at this time. The missing camera is a QSA 8880D, serial no. D4264 and contains a 15.9 Ci Ir-192 source, serial no. 66411B. * * * UPDATE FROM DAVID TEBO TO JOHN KNOKE AT 1545 EDT ON 04/15/11 * * * At 1540 EDT, the licensee was notified by the shipper that the missing camera was returned to the licensee's office in Hammond, IN. The licensee confirmed that the missing camera is now at their office, the source is in the camera, and the serial number matches. Licensee is investigating this matter further. Notified R2DO (O'Donohue), R3DO (Orth), ILTAB (Pearson), IRD MOC (Gott), and FSME EO (Giantelli) THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-04-15
46756 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-04-14 16:25 | 2011-04-14 19:54 | 2011-04-14 | OFFSITE NOTIFICATION TO NEBRASKA DEPARTMENT OF ENVIRONMENTAL QUALITY "On 4/14/11 at 1625 CDT, NPPD/CNS notified the Nebraska Department of Environmental Quality (NDEQ) of a violation of the National Pollutant Discharge Elimination System (NPDES) requirements during March 2011. "The NPDES conditions for Total Suspended Solids (TSS) for reverse osmosis (RO) Reject and Boiler Blowdown Waste streams (Outfall 004 - sludge pond), for the month of March exceeded the maximum daily value of 100 mg/L and 30-day average of 30 mg/L. The value of the TSS for the month of March was 190 mg/L. This exceeds the NPDES conditions for TSS during the month of March. The April TSS for NPDES Outfall 004 was verified to be within limits at 6.4 mg/L. This outfall discharges to the Missouri River. "This is a 4 hour report per 10 CFR 50.72(b)(2)(xi) for any event or situation related to the protection of the environment, for which notification to another government agency has been made." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-14
46755 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2011-04-14 12:35 | 2011-04-14 16:52 | 2011-04-14 | OFFSITE NOTIFICATION TO STATE OF CALIFORNIA DUE TO HYDROGEN LEAK "During a scheduled delivery of Hydrogen to Unit 2's active and reserve hydrogen banks, a hydrogen leak was detected at the hydrogen fill connection isolation valve. A notification was made for an uncontrolled release of hazardous material to San Diego Department of Environmental Health at 12:35 PST and California Emergency Management Agency at 12:40 PST. Upon detection, the leak was isolated." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-14
46754 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2011-01-11 | 2011-04-14 13:59 | 2011-04-14 | AGREEMENT STATE- UNDER DOSE ADMINISTERED TO PATIENT The following was received via facsimile. "In January 2011 a patient was administered 1.58 millicuries of (Iodine) I-I31 for a whole body scan. The written directive specified a 2.0 millicurie dosage. The difference was discovered during a routine audit by the licensee's health physics consultant in March 2011. Calculations by the health physicist indicated the difference between the written directive and the administered dose differed by more than 20 percent, that the difference in the effective dose exceeded 5 rem and that the difference in the dose to the thyroid exceeded 50 rem. A report dated March 24, 2011 was received by (Virginia Department of Health) VDH on April 4, 2011. An on-site investigation by VDH was performed on April 8, 2011. The licensee indicated that the quality of the whole body scan was not compromised and that because the administered dose was less than the written directive, there is no radiological hazard to the patient." Virginia Radioactive Materials Program Event Report ID.: VA-11-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2011-04-20
46753 | 0 | MEMORIAL HEALTHCARE HOSPITAL |  |  |  |  | 2010-02-23 | 2011-04-14 12:02 | 2011-04-14 | MEDICAL EVENT - BRACHYTHERAPY UNDERDOSE TO PROSTATE GLAND On 2/23/10, a patient went to Memorial Healthcare Hospital for brachytherapy treatment to the prostate gland. The prescribed treatment was 125 Gy (75 seeds) to the prostate gland. Due to swelling, the enlarged organ resulted in a lower radiation dose within the prostate. Even though all 75 seeds were implanted, the actual dose to the patient was 81.07 Gy. On 4/12/10 the physician notified the patient of the underdose and made arrangements for a second treatment. On 5/4/10 the second brachytherapy treatment of 57.26 Gy (8 seeds) was performed on the patient. In evaluating the patient's second treatment results, no further action was required. This event is being reported due to a finding from an NRC audit. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2011-04-20
46752 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-13 09:32 | 2011-04-13 17:10 | 2011-04-13 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE A non-licensed employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's unescorted access has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2011-04-13
46751 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-04-14 04:00 | 2011-04-13 16:15 | 2011-04-15 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE FOR MAINTENANCE "This is a voluntary notification for planned maintenance that affects the TSC ventilation system. "At approximately 0400 EDT an April 14, 2011 the North Anna TSC [Technical Support Center] air conditioning and filtration systems will be rendered non-functional to perform preventive maintenance on electrical buses supplying power. This condition has the potential to render the TSC unavailable due to the inability of the ventilation and filtration system to maintain a habitable atmosphere. Temporary ventilation is being established for the TSC computer room. The maintenance is expected to last less than 24 hours. Compensatory measures exist to relocate the TSC to alternate locations, if needed. "The NRC Resident Inspector has been notified." * * * UPDATE FROM PATRICK FRENCH TO HOWIE CROUCH AT 1738 EDT ON 4/15/11 * * * The maintenance on the TSC ventilation system has been completed and the TSC has been returned to service. The licensee will be notifying the NRC Resident Inspector. Notified R2DO (O'Donohue). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-13
46750 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-04-12 10:35 | 2011-04-13 12:00 | 2011-04-13 | AGREEMENT STATE REPORT - FIRE IN PORTABLE DARKROOM The following information was received from the state via email: "On 4/12/2011, at 10:35AM the corporate RSO for TEAM Industrial Services informed the PA DEP Bureau of Radiation Protection (BRP) of a temporary job site fire which occurred earlier in the day. This event type is 'An unplanned fire... damaging any licensed material or any device, container, or equipment containing licensed material' which is reportable under 10CFR30.50(b)(4). "A fire occurred in the portable darkroom which was housed within the bed of a pickup truck at the job site. A QSA Model 880 Delta radiographic exposure device containing approximately 75 curies of Iridium-192 (Ir-192) was stored in its metal over-pack inside the darkroom. The metal over-pack sustained significant fire damage, however, the radiographic exposure device was undamaged with the exception of a melted plastic handle. Surveys revealed radiation levels to be in the normal range and consistent for the source being in the locked position. It appears that the Ir-192 source was undamaged by the fire, however, the housing and source will be returned to the manufacturer for examination. Early indications are that an electrical problem started the fire. "An immediate reactive inspection occurred on 4/12/11. BRP responded, examined the damaged truck and confirmed radiation surveys and measurements taken by the licensee. The camera was taken out of service and will be returned to QSA for inspection once a suitable shipping container is received. Further details [from the State] will be reported as received." PA Event Report No. PA110007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-04-18
46749 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-04-13 08:30 | 2011-04-13 09:29 | 2011-04-15 | ACUTE CHEMICAL EXPOSURE FROM HYDROGEN FLUORIDE TO A MAINTENANCE WORKER "A maintenance employee was involved in a pipe replacement project in the Hydrogen Fluoride (HF) Building. The employee was leaning on a pipe and received a HF exposure through his PPE [personal protective equipment and clothing] onto his abdomen. The employee was immediately placed under a safety shower and an on-site emergency response was initiated. EMT's applied calcium gluconate and the employee was transported to on-site medical clinic. The employee was not contaminated with any radioactive material. The employee was later transferred to off-site medical. The employee's abdomen was reddened and had some blistering, but exposure is not considered life threatening. "AII work in the HF building has been stopped pending the completion of an investigation." The licensee stated that the pipe had been flushed with water and steam prior to starting the maintenance evolution. The amount of fluid in the pipe was described as residual. There was no ongoing release of HF and no other employees were involved. The licensee is providing this as a notification under 10CFR70 App A (a) and 10CFR70.61(b)(4). The licensee plans to notify the NRC Regional Staff (Thomas). * * * UPDATE FROM PHILLIP OLLIS VIA FAX TO JOHN KNOKE AT 1226 EDT ON 4/13/11 * * * "The employee was released from the hospital with no restrictions. As such, the event classification is being amended to 10 CFR 70.61(c)(4)." Notified NMSS (King Stablein), R2DO (Kathleen O'Donohue) * * * UPDATE FROM PHILLIP OLLIS (VIA FAX) TO HOWIE CROUCH AT 1548 EDT ON 4/15/11 * * * "As a result of the root cause analysis, additional IROFS [Items Relied On For Safety] are needed and will be declared. Additional reporting for this event to include 10 CFR 70 Appendix A(b)(1) as the GNF [Global Nuclear Fuels] ISA [Integrated Safety Analysis] did not consider HF as a high consequence event." Notified NMSS (Stablein) and R2DO (O'Donohue). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ACUTE CHEMICAL EXPOSURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(3) |  |  |  | 0 | 2011-04-13
46748 | -1 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-12 22:15 | 2011-04-13 01:57 | 2011-04-14 | ESF ACTUATION FOLLOWING LOSS OF A SAFEGUARD BUS DURING EDG TESTING The following event occurred with the unit in a "No Mode" defueled condition. "On the 12th of April at 2215 CDT Comanche Peak Nuclear Power Plant Unit 2 had a Train B ESF Actuation (Black Out) reportable per 10CFR50.72(b)(3)(iv) for [the 6.9KV Train B] Emergency AC Electrical power systems including Emergency Diesel Generator (EDG). "At the time of the event, Unit 2 was in 'No Mode' - the core was off loaded and post maintenance testing was being performed on the 2-02 Emergency Diesel Generator. The scope of the EDG testing was to verify proper operation of the EDG when it was the sole supply to the Unit 2 Train B 6.9KV safeguards buses. Unit 2 Train B 6.9 KV buses have 3 AC sources - XST1 (138KV) preferred source, XST2 (345KV) alternate source and the 2-02 Emergency Diesel Generator. "The 2-02 EDG was started normally and was operating in parallel with XST1 (preferred AC source) just before the event. The event was triggered when the preferred AC supply breaker to the Train B 6.9KV Safeguard bus was opened per plan. The opening of the preferred feeder breaker resulted in the 2-02 EDG being the sole AC source to the Train B 6.9KV bus. Immediately following this breaker operation, the EDG tripped on an Auto Voltage Regulator failure. This caused the Train B 6.9KV safeguard bus to de-energize which resulted in the automatic closure of the alternate AC (XST2) feeder breaker. This in turn triggered the Train B Solid State Sequencer to sequence on Train B Black Out loads - as designed. "The Train B Black Out Solid State Sequencer operated as designed. No abnormalities were noted. All available equipment operated as designed. "The 2-02 EDG is currently tagged out and the problem associated with the [Auto Voltage Regulator] failure is being investigated. "[The] NRC Resident Inspector has been informed and is currently located on site." No fuel movement was in progress during this event. Train A safeguard power was unaffected and available throughout. Non-safety related power was also not affected. The only operational impact was the loss of a Train B spent fuel pool cooling pump for approximately 10 minutes. The spent fuel pool temperature increased approximately 1/2 degree during before cooling was restored. * * * RETRACTION FROM DAVID BUTLER TO HOWIE CROUCH AT 1830 EDT ON 4/14/11 * * * "Further investigation of this event has determined that the 2-02 Emergency Diesel Generator (EDG) auto voltage regulator functioned as designed. The EDG did not receive an emergency start signal, which was consistent with the design for the plant conditions present. In addition, Unit 2 was defueled and in a 'No Mode' condition, and there was no actuation of any of the systems listed in paragraph 50.72 (b)(3)(iv)(B) by the sequencer operation. Therefore, this event is not reportable because it did not meet the criteria for a system actuation per 50.72(b)(3)(iv)(A) and the guidance in NUREG-1022." The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-04-13
46747 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-04-12 09:15 | 2011-04-12 14:34 | 2011-04-20 | UNSEALED FLOOD BARRIER PENETRATION "During investigations of flood barrier penetrations, a flood barrier sealing a diesel driven fire pump exhaust was found to be cracked. This exhaust pipe penetrates the west wall of the intake structure. Flooding through the penetration could have impacted the ability of the station's raw water pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). "The penetration is at an approximate elevation of 1012 feet mean sea level (MSL). The river level has been less than 997 feet MSL since prior to December 1, 2010. The raw pumps are operable. There are not any indications of conditions that might result in a flood. Actions are in progress to plug the penetration." The NRC Resident Inspector has been notified. * * * UPDATE FROM ERICK MATZKE TO JOE O'HARA AT 1641 ON 4/20/11 * * * "This event is being retracted. "Additional review and evaluation determined that the seal flaw is above the station design flood level of 1014 feet mean sea level, and is therefore, not reportable." The NRC Resident Inspector has been notified. Notified R4DO (Hay). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-12
46746 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-04-11 02:30 | 2011-04-11 06:30 | 2011-04-11 | INJURED WORKER TAKEN OFFSITE FOR MEDICAL TREATMENT "An ambulance responded to the site to assist a worker with a head injury. The worker was transported as potentially contaminated to an offsite medical facility. "Follow-up to the above information, it was later determined that the worker was not contaminated." The contract worker was in secondary containment climbing a ladder when he hit his head on a scaffold pole. He was transported to Pottstown Memorial Hospital. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2011-04-11
46745 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-04-10 08:40 | 2011-04-10 10:42 | 2011-04-10 | OFFSITE NOTIFICATION OF AN OIL SHEEN IN THE DISCHARGE CANAL "Report has been made to the New York State Department of Environmental Conservation and the Westchester County Department of Health related to a visible oil sheen identified on the discharge canal. NRC report required per 10CFR50.72(b)(2)(xi) due to notification of other government agencies." Initially, the National Response Center was not notified as it does not appear that the oil had reached the Hudson River from this occurrence. After further discussion with the Indian Point Environmental Supervisor, the National Response Center and the Coast Guard were notified concerning this event. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-04-10
46744 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-04-10 03:45 | 2011-04-10 06:40 | 2011-04-10 | MANUAL REACTOR TRIP WHILE PERFORMING A TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On April 09, 2011, at 2349 [EDT], Beaver Valley Power Station [BVPS] Unit No. 2 was operating at 15% power while preparing to synchronize the main unit generator to the grid. At that time, the 'A' Auxiliary Feedwater Injection Header was declared inoperable due to a water leak identified from a vent valve fillet weld between the inside and outside Containment Isolation Valves (outside of containment) for containment penetration X-79. "In accordance with Technical Specification 3.7.5, Auxiliary Feedwater (AFW) System, Condition D, at 0345 [EDT], April 10, 2011, BVPS Unit 2 commenced a Reactor Shutdown to Mode 3. Required action is to be in Mode 3 within 6 hours. This event is being reported as a Technical Specification required shutdown pursuant to 10CFR50.72(b)(2)(i), 4 hour notification. Repairs are in progress. The following additional shutdown actions may be required from the time the Injection Header/Containment Penetration was declared inoperable: Technical Specification 3.7.5, Condition D, Mode 4 in 18 hours and Technical Specification 3.6.1, Condition A, Mode 5 within 37 hours. This event is also being reported as a degraded condition for Containment pursuant to 10CFR50.72(b)(3)(ii)(A), 8 hour notification. "Additionally, at 0357 [EDT], during the Reactor Shutdown, at 4.6% Reactor Power, the BVPS Unit 2 Reactor was manually tripped due to reaching a pre-established manual trip criteria of 25% Steam Generator Level for the 21A Steam Generator. This was conservative criteria set above automatic actuation setpoint of 20.5% level. This event is being reported as a RPS Actuation pursuant to 10CFR50.72(b)(2)(iv)(B), 4 hour notification. "Control room personnel entered Emergency Operating Procedure E-0, 'Response to Reactor Trip and Safety Injection.' Safety systems and equipment functioned as designed following the manual reactor trip. "Due to the cooldown and subsequent shrink of level in the 21A Steam Generator, an automatic start of the Steam Driven Auxiliary Feedwater Pump [2FWE-P22] occurred at 20.5%. This event is being reported as an Auxiliary Feedwater System Actuation pursuant to 10CFR50.72(b)(3)(iv)(A), 8 hour notification." All control rods fully inserted into the core. The plant electrical system is aligned to normal offsite power sources. Decay heat from the reactor coolant pumps is being directed to atmospheric dump valve. There is no primary to secondary leakage. There was no impact on Unit 1. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | DEGRADED CONDITION | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(iv)(A) | 0 | 2011-04-10
46743 | 0 | THREE MILE ISLAND | 1 | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP | 2011-04-08 14:05 | 2011-04-08 14:54 | 2011-04-08 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS INTO PROTECTED AREA An unauthorized person was allowed unescorted access to the plant. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Decommissioned |  | Power Operation | Decommissioned |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-04-08
46742 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-04-08 06:27 | 2011-04-08 13:44 | 2011-04-08 | TECHNICAL SUPPORT CENTER INOPERABLE "Technical Support Center (TSC) was non-functional due to inability to maintain pressure boundary for function of the TSC HVAC system. This morning the latch to one of the doors to the TSC was discovered broken. The door would not latch shut. The station has repaired the door. Compensatory measures were in place for the nonfunctional facility. The TSC is now functional." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-08
46741 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-04-08 10:24 | 2011-04-08 13:40 | 2011-04-08 | UNSEALED FLOOD BARRIER PENETRATION "During investigations of flood barrier penetrations, one approximately 4 inch conduit has been identified that is not sealed. Reducers are installed in the conduit on the exterior side. This conduit penetrates the auxiliary building into room 56. Flooding through the penetrations could have impacted the ability of the station's safety related equipment in the auxiliary building to perform their design accident mitigation functions. "During investigations of flood barrier penetrations, a drain flow path from the CARP building into Room 23 of the Auxiliary Building [was identified]. There is no specific procedural guidance to isolate this flow path in the event of a flood above 1007 feet. Flooding through this flow path could have impacted the ability of the station's safety related equipment to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v)(D). "The penetrations and CARP building drains are at an approximate elevation of 1007 feet. The river level has been less than 997 feet Mean Sea Level (MSL) since prior to December 1, 2010. The safety related equipment is currently operable. There are not any indications of conditions that might result in a flood. Compensatory actions have been identified." "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-08
46740 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-04-07 17:40 | 2011-04-08 01:02 | 2011-04-08 | LOSS OF THE CONTROL ROOM EMERGENCY VENTILATION SYSTEM "At approximately 1740 hours on April 7, 2011, a loss of the Control Room Emergency Ventilation (CREV) system occurred. At the time of the event, the plant was performing 0MST-DG13R. 'DG-3 Loading Test.' During performance of this test, the 480 VAC Emergency Bus E-7 main feeder breaker tripped unexpectedly. As a result, the CREV emergency makeup damper 2-VA-2J-D-CB closed on this loss of power, resulting in two CREV subsystems required by TS 3.7.3, 'CREV System,' being inoperable. As a result, this condition could have prevented the fulfillment of the safety function for this system. Brunswick has a shared control room, but only Unit 1 was required to enter TS 3.7.3 Required Action C.1. for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours). Unit 2 was operating in Mode 4 for a scheduled refueling outage and did not meet any applicability conditions for TS 3.7.3. "Operability of the CREV subsystems was restored and the related LCO was exited at 1931 hours following the restoration of CREV damper 2-VA-2J-D-CB. Investigation of the E-7 bus trip is ongoing. This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition existed for approximately 1 hour and 51 minutes. Plant staff took immediate action to return the equipment to service. For the brief time the CREV systems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-04-08
46739 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2011-04-07 16:07 | 2011-04-07 19:22 | 2011-04-08 | UNUSUAL EVENT DECLARED DUE TO HYDROGEN BURN DURING MAINTENANCE "[The licensee declared an Unusual Event at 1607 PDT due to a small hydrogen burn when opening the stator cooling water system for maintenance. There were no injuries or equipment damage." The licensee entered EAL 93U3 'Toxic Gases inside the Protected Area Boundary.' The licensee notified state/local agencies and will inform the NRC Resident Inspector. The licensee plans to issue a press release. * * * UPDATE FROM MATT HUMMER TO DONG PARK AT 0003 EDT ON 04/08/11 * * * "[At 2053 PDT,] Columbia has terminated the Unusual Event declared at 1607 [PDT] on 04/07/11. Conditions throughout the plant have remained stable. Columbia has confirmed there is no hazard to personnel safety nor a challenge to safe plant operation." The licensee will notify the NRC Resident Inspector. Notified R4DO (OKeefe), NRR EO (Blount), IRD (Grant), DHS (Jenkins), and FEMA (O'Connell). * * * UPDATE FROM MATT HUMMER TO JOE O'HARA AT 2318 ON 4/8/11 * * * "At 1922 EDT on April 7, 2011, NRC was notified of an Unusual Event at Columbia Generating Station (EN#46739), The NRC was notified the event was terminated at 2353 EDT on April 7, 2011. "Based on further investigation, this event is being retracted. "The stator cooling water system contains a mixture of water and hydrogen when in operation. The system had been removed from service, drained and blanketed with nitrogen prior to commencing maintenance. There was no active source of hydrogen in the system. Although the system had been tested for hydrogen and none was detected, the event occurred when workers cut into a section of the system piping where a small amount of residual hydrogen remained. "Immediately following the event, tape was placed over the cut to prevent any debris from entering the pipe. Hydrogen measurements were taken in the vicinity of the cut section of pipe and in the general area and concentrations were below hazardous levels. The only elevated reading occurred directly at the cut location when the tape was removed, This indicated that hydrogen, residual in nature, was confined to the inside of the pipe. Since the system was not in use and the residual hydrogen was confined, plant operations were not affected, "As a result of this event, no personnel were injured, no equipment was damaged, and there was no impact to structures needed for plant operation. "The licensee will notify the NRC Resident Inspector, the media, and local, state, and other government agencies of this update." Notified R4DO(O'Keefe) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-04-07
46738 | 0 | OREGON STATE UNIVERSITY |  |  |  | 1000 KW TRIGA MARK II | 2011-04-06 | 2011-04-07 15:25 | 2011-04-07 | VIOLATION OF LIMITING CONDITION OF OPERATION 3.8.1, REACTIVITY LIMITS "Summary of Events: "The Oregon State University TRIGA« Reactor (OSTR) staff is designing a new experiment which will utilize reactivity oscillation to measure reactor parameters. During attempts to measure the maximum worth of the oscillating absorber on Wednesday, April 6, it was determined that the worth of the preliminary test absorber is $0.60 at the mid-plane of the core. Technical Specification 3.8.1, Reactivity Limits states in part that 'The absolute value of the reactivity worth of any single unsecured experiment shall be less than $0.50.' Measurements were taken in a manner such that the apparatus qualifies as a movable experiment, and moveable experiments are taken to be a subcategory of unsecured experiments. "A neutron absorber was fabricated by crushing an existing ¢ inch segment of B4C absorber and placing 29.8 grams of the material in a sealed aluminum TRIGA« tube. The reactivity of the absorber was not formally calculated, but it was believed that the worth of the absorber would be less than $0.20. This was based on the fact that a full length control rod absorber (15 inch) is worth about $2.00, depending on position in the core. Past experience has also shown that several grams of Cadmium, a very strong thermal neutron absorber, have a reactivity worth of ~$0.20 in the B-1 position where the absorber was being tested. "To characterize the worth of the absorber, the reactor was first taken critical with the In-Core-Irradiation-Tube (ICIT) installed in the B-1 position. Critical rod heights were measured and core excess was calculated. The reactor remained critical at 15 watts in automatic mode. The absorber was then manually lowered to the bottom of the ICIT by an operator using a length of nylon line. The regulating rod was observed to behave as anticipated, automatically withdrawing until some maximum worth position near core center was reached by the absorber, and then automatically inserting as the absorber was lowered to the bottom of the core. The worth of the absorber when resting at the bottom of the core was estimated to be less than $0.07. "When power and reg rod position were stable, the absorber was slowly withdrawn 7.5 inches to the geometric center of the core. The reg rod automatically withdrew to compensate. The difference between reg rod position with no absorber present and reg rod position with the absorber at core center indicated that the worth of the absorber at core center was $0.60. As soon as absorber worth was determined, the reactor was shut down and the absorber was withdrawn from the ICIT. Although oscillatory operation was not planned, the fact that the absorber was moved while the reactor was critical qualified the experiment as a moveable experiment. Since $0.60 is in excess of L.C.O. 3.8.1, reactor operation was secured in accordance with Technical Specification 6.6.2.a." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2011-04-07
46737 | 0 | ROTORK CONTROLS, INC |  |  |  |  | 2011-04-07 | 2011-04-07 15:22 | 2011-04-07 | DEFECT IN ROTORK'S 30NA1 MOTOR COVER CASTING A manufacturing defect was discovered in Rotork's 30NA1 motor cover casting part number 4748. When stroking the valve, the motor cover supports the loads developed from the stator torque and the rotor thrust reactions. The failure occurred at the rotor end bearing support. Investigation has shown that the casting was not manufactured to the drawing specification. The manufacturer is searching their spares database to determine where it has supplied the motors and will inform the utilities once this list is complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2011-04-07
46736 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-06 12:05 | 2011-04-07 11:26 | 2011-04-07 | CONTAMINATED WORKER TREATED AT DISPENSARY "A Honeywell employee (Senior Process Control Engineer) entered the Dispensary at 1205 on 04/06/11 and reported he had foreign material in his right eye. He was on the 1st floor of the FMB (Feeds Material Building) by the glycol heat exchanger closing a valve with a wrench (lazy rod). The wrench struck another pipe and knocked rust off and into his eye. The rust was removed with simple irrigation and a swab. The employee was sent back to work with no additional issues. He was monitored by HP (Health Physics) in the Dispensary and was found to have 5300 dpm/100cm2 (beta, gamma) on his boots and 280 dpm/100cm2 on his coveralls. The individual was not transported offsite. Reported IAW 10CFR40.60 b(3). "NRC Region II (Richard Gibson) was also informed of this occurrence" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-04-07
46735 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2011-04-06 15:30 | 2011-04-06 21:20 | 2011-04-07 | DEGRADED FIRE BARRIER "During walk downs for a planned site modification on April 6, 2011 at 1530 EDT, two degraded fire barrier seals were identified in the wall between the Auxiliary Building Basement and the Charging Pump Room. The wall is listed as an Appendix R wall between Fire Area (FA) ABBM and FA CHG. The wall separates redundant safe shutdown equipment. "Two cylindrical six inch penetrations through the wall did not contain the required material to conform to a 3-hour fire rated barrier. This has been identified as a missing fire barrier such that the required degree of separation for redundant safe shutdown trains is lacking. "A fire watch was established as a compensatory measure on 4/6/11. The discovery of this non-compliance is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified of this event." * * * RETRACTION FROM ALAN MODZELEWSKI TO JOE O'HARA AT 1628 EDT ON 4/7/11 * * * "The purpose of this report is to retract the event discussed in Emergency Notification System report #46735 submitted on April 6th, 2011. The ENS notification reported an inadequate fire barrier penetration seal discovered on April 6th, 2011 when maintenance inspected the penetration in preparation for a modification. Initial investigation concluded that the fire barrier penetration seal between the Charging Pump room and Auxiliary Building Basement was inoperable because there was inadequate seal material to provide the required three hour barrier rating. It appeared that when looking in the penetration sleeve that a fire board from the opposite room was visible and no foam material was present. "Subsequently, an engineering review of the penetration has been completed. The review determined that a minimum of 8 inches of foam is required to maintain a 3-hour rating. Engineering identified that the design also requires a fire board on each side of the foam. Upon measurement it was confirmed that at least 11 inches of the penetration was filled, with a fire board on each side. Based on these measurements, the fire barrier met design requirements and was operable. The individuals performing the initial investigation did not recognize the thickness of the wall. On April 7th, Maintenance proceeded to penetrate the fire barrier for the modification and it was confirmed that foam was behind the fire board. With a 24 inch thick wall, a large portion at the penetration sleeve can be void of material and still meet the 3 hour rating. As such, the April 6th, 2011 event is being retracted. "The licensee notified the NRC Resident Inspector." Notified the R1DO (Caruso) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-04-06
46734 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2011-03-22 | 2011-04-06 17:50 | 2011-06-13 | AGREEMENT STATE REPORT - SOURCE DISLODGED FROM OHMART VEGA MODEL SHLM-BR The following was received via e-mail: "Licensee's RSO notified DRH [state] by phone on 3-22-11, and by letter received on 3-22-11, of a dislodged source from an Ohmart Vega Model SHLM-BR, fixed gauge Ser. No. 13530993. The source became dislodged from the main rod during the gauge's shutter test and fell into the gauge well. The licensee's surveys around the gauge well were less than 0.5 mR/hr. A gauge representative has been called in to repair the gauge. "DRH [state] requested licensee send in manufacturer's service report with the licensee's written 30-day report." The source is 40 millicurie Cs-137, ser. No. 6965GK. Mississippi Incident Number MS-11004. * * * UPDATE FROM JAYSON MOAK TO JOE O'HARA VIA E-MAIL AT 1200 EDT ON 4/7/11 * * * "Licensee was contacted [by the state] on 4/7/11, for further clarification of the location of the source. The licensee's RSO said the source was at the bottom of the well inside a vessel. This would also be the case during normal operations. Surveys were also confirmed by the RSO to be 0.5 mR/hr around the vessel. Licensee's RSO said a new well is being built for the vessel and a service representative has been notified. Source retrieval and replacement of the gauge is scheduled for the middle of April once the new well is built, and the material in the vessel has cooled." Notified R4DO(O'Keefe) and FSME(McIntosh) * * * UPDATE AT 1603 ON 6/13/2011 FROM JAYSON MOAK TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "Licensee submitted a field service report from the gauge service company on 6/9/2011. The service report indicated the roll pin in the rod was sheared and the source carrier fell to the bottom of the well. The service report claimed the roll pin was corroded due to the harsh environment that the source was in. Part of the rod was still attached to the source which was retrieved and inserted back into the source holder. The source was replaced, and the old source has been transferred." Notified the R4DO (Werner) and FSME (Persinko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-04-11
46733 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-04-06 | 2011-04-06 16:34 | 2011-04-06 | AGREEMENT STATE REPORT - STUCK SHUTTER ON OHMART MODEL SH-F1 GAUGE "On April 6, 2011 the Agency [State of Texas] was informed by the licensee that on April 6, 2011, while conducting shutter operational checks, the shutter on an Ohmart Model SH-F1 containing 60 millicuries of Cesium (Cs) -137 was found to be stuck in the open position. The licensee stated that this is the normal operating position for the gauge and because of its location it does not create an exposure risk to any individuals. The licensee has contacted a contractor to repair the gauge. The cause for the failure is under investigation. Additional information will be provided as it is received in accordance with SA - 300." Texas Incident Number I-8832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-04-11
46732 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-07-01 | 2011-04-06 16:27 | 2011-04-06 | AGREEMENT STATE REPORT - STUCK GAUGE SHUTTERS The following information was provided by the State of Mississippi via e-mail: "During inspection and review of licensee's gauge service reports, two gauges were discovered to have stuck shutters. Both gauges are Ronan models SA1-F37. Ronan service engineering was called in to repair gauges and determined that on gauge serial # 9473GG, the bottom bushing was found frozen to the shutter shaft. On gauge serial # M4122, the roll pin was broken and the shutter handle was rotated 45 degrees out of alignment. Both gauges were repaired. Both gauges had a Cs-137 source. Gauge #M4122 was 5 millicuries and gauge #9473GG was 200 millicuries. MS Report: MS-11003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-04-11
46731 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-04-06 04:00 | 2011-04-06 02:44 | 2011-04-06 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO PLANNED MAINTENANCE "At 0400 EDT on Wednesday, April 6, 2011, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems will be removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary. "TSC ventilation system maintenance is scheduled to be completed by 1600 EDT on Wednesday, April 6, 2011. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of an emergency response facility." * * * UPDATE FROM DEAN BRUCK TO DONG PARK ON 4/6/11 AT 1514 EDT * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1455 EDT." Notified R3DO (Daley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-06
46730 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-05 11:00 | 2011-04-05 18:34 | 2011-04-05 | UNPLANNED MEDICAL TREATMENT INVOLVING CONTAMINATION "Employee was treated for KOH exposure at 1100 [CDT on 4/5/11]. The employee had contamination on his plant issued shoes. Contamination levels were estimated to be approximately 16,800 dpm/100 cm squared. The employee was treated using ammonium sulfate and returned to work. "Isotope, quantities and chemical form: Caustic [potassium hydroxide KOH], uranium ore concentrates." The employee was treated onsite by site personnel. The employee was decontaminated before leaving the site. The licensee notified the Senior Fuel Facility Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-04-05
46729 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-04-04 21:00 | 2011-04-05 18:34 | 2011-04-05 | UNPLANNED MEDICAL TREATMENT INVOLVING CONTAMINATION "Employee was treated for HF exposure at 2100 [CDT on 4/4/11]. The employee had contamination on his shoes and coveralls. Contamination levels were estimated to be approximately 10,000 dpm/100 cm squared. The employee was treated using calcium gluconate and returned to work. "Isotope, quantities and chemical form: Weak hydrofluoric acid, uranium ore concentrates." The employee was treated onsite by site personnel. The employee was decontaminated before leaving the site. The licensee notified the Senior Fuel Facility Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-04-05
46728 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2011-04-05 08:01 | 2011-04-05 18:08 | 2011-04-05 | CONTRABAND FOUND INSIDE THE PROTECTED AREA Contraband was discovered inside a vehicle brought into the Protected Area. The contraband was confiscated and unescorted access for the driver has been administratively withdrawn. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2011-04-05
46727 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-04-05 14:30 | 2011-04-05 15:42 | 2011-04-05 | PLANNED LOSS OF EMERGENCY ASSESSMENT CAPABILITY FOR SCHEDULED MAINTENANCE Monticello Nuclear Generating Station reported a planned loss of emergency assessment capability for maintenance, at 1430 (CDT) on 04/05/11. Unavailable systems and functions include the Safety Parameter Display System (SPDS), communications between the Process Computer System (PCS) and the Man-Machine Integration Design and Analysis System (MIDAS) computer, and data transfer capability via Emergency Response Data System (ERDS) link to the Nuclear Regulatory Commission (NRC). Projected outage duration is approximately 4 hours. Control Room and local instrumentation, and annunciators remain available for accident assessment. Telephone lines remain available between site emergency response facilities and offsite agencies for communication of plant status information. During this period, MIDAS remains available to perform dose assessment in the manual input mode. The licensee will notify the NRC Resident Inspector and the State Emergency Response Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-05
46726 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-03-30 | 2011-04-05 12:03 | 2011-04-05 | AGREEMENT STATE - FIVE TRITIUM EXIT SIGNS DESTROYED The following information was received via facsimile: On February 4, 2011, the NC Radiation Protection Section (NCRPS) received notice of a bankruptcy sale for Townsend in Pittsboro, NC. On March 15, 2011, the Radiation Safety Officer (RSO) for Townsend was contacted to check the status of 5 exit light signs they had registered. The Townsend RSO informed NCRPS that Townsend had paperwork for the signs, however, in October 2003 the facility had been changed from a chicken slaughter facility to a chicken process facility. During this construction, the 5 exit signs were destroyed. On March 30, 2011, NCRPS performed an inspection at the facility and no exit signs or evidence of signs containing tritium were found. A total of 71.9 Curies of tritium were destroyed at the facility and NCRPS considers the incident closed. NC Report #11-22. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-04-08
46725 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-04-05 11:49 | 2011-04-05 12:01 | 2011-04-21 | ALERT DECLARED DUE TO ACID LEAK GREATER THAN THE 40 CFR LIMIT The licensee secured their process after an acid leak greater that the 40 CFR limit developed at a piping joint. The leak consisted of a mixture of hydrofluoric and nitric acid. A licensee response team was dispatched to the site of the leak to evaluate the condition. No injuries resulted and there were no evacuations nor health and safety consequences at the site. Additionally notified USDA (R. Jones), HHS (J. Dennis) and Fuels OUO Group. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DONNA MILLER TO PETE SNYDER AT 1241 EDT ON 4/5/11 * * * The licensee exited the emergency condition at 1237 EDT on 4/5/11. The spill is contained and no longer poses any threat to employees or the environment. * * * UPDATE AT 1558 ON 4/21/2011 FROM KENNY KIRBY TO MARK ABRAMOVITZ * * * "On April 5, 2011 during a line inspection at B&W NOG-L, a leak was discovered coming from a 6 inch waste acid line. The leak was in a location that the technician could visually inspect but with limited accessibility because of its proximity to an embankment obstruction. After finding a way to safely determine that waste was leaking from the line at a pH <2, the site Emergency Operation Center was activated and Emergency Team was notified to respond. It was determined that a Reportable Quantity (RQ) of an acidic waste solution (D002) had been released. Notifications were made to EPA Region III, VA DEQ, National Response Center, Nuclear Regulatory Commission, and other Emergency Response organizations as required by the site Emergency Plan. Efforts were taken to ensure the spill was contained to the immediate paved and soil areas. The accumulating liquid was contained with absorbent booms and neutralized with soda ash . It is estimated that 200 gallons of waste solution leaked onto the ground. Approximately seven 55 gallon drums (@ 1500 Pounds) of clean up waste were generated and will be disposed of appropriately. "There were no injuries during the spill or during the cleanup operations. The threat to the environment and human health was minimal due to the leak's isolated location . Access to the area was limited and air monitoring in the area did not show any concerns. All released material was contained to the spill area or the cleanup zone. "Plant operations draining to this line were halted until the repair was completed . Restart of operations was authorized on April 6, 2011. An investigation of the incident to determine the root cause is in progress and corrective actions will be implemented to prevent reoccurrence ." The licensee submitted a follow-up notification to the Virginia Department of Environmental Health, EPA Region III, and will notify the NRC Resident Inspector. Notified NMSS (Easton), R2DO (Bartley), and Fuels OUO Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | OFFSITE NOTIFICATION/NEWS REL | [8 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) | PART 70 APP A (c) |  |  | 0 | 2011-04-22
46724 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-02-04 13:54 | 2011-04-05 11:58 | 2011-04-05 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO A FAILED RELAY COIL "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73 (a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 1354 on February 4, 2011, with the Duane Arnold Energy Center (DAEC) operating at 100% power, an invalid Group 3 isolation on the 'B' side of the Primary Containment Isolation System occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by a high resistance contact on relays in the trip circuitry for the 'B' Fuel Pool Exhaust Radiation Monitor logic. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-04-05
46723 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-04-04 15:00 | 2011-04-04 19:51 | 2011-05-27 | SCAFFOLDING AFFECTING SAFETY RELATED EQUIPMENT "At 1500 [CDT], a concern was raised with regard to scaffolding that had been constructed around safety related equipment in the Auxiliary Building which contains both trains of safety injection and containment spray. As a result T.S. 2.0.1 was entered (which is the Fort Calhoun equivalent to standard T.S. 3.0.3). The scaffolding in question was removed and the equipment was returned to operable status and T.S. 2.0.1 was exited at 1726 [CDT]." The NRC Resident Inspector has been notified. * * * RETRACTION FROM ERICK MATZKE TO HOWIE CROUCH @ 2027 EDT ON 5/27/11 * * * "Following the initial report, Fort Calhoun performed a seismic analysis of the impact of the scaffolding previously reported to determine if the equipment in the room would be capable of performing its required safety functions. The evaluation determined that the safety related function of the affected equipment would be able to be accomplished. Therefore, this event is being retracted." Notified R4DO (Haire). The licensee has notified the NRC Resident Inspector of this retraction. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2011-04-04
46722 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2011-04-04 | 2011-04-04 17:35 | 2011-04-04 | PRESS RELEASE CONCERNING ADDITIONAL CONTAINMENT DELAMINATION "Progress Energy Florida, Inc. has notified the Florida Public Service Commission (FPSC) that the Crystal River Unit 3 (CR-3) Nuclear Plant will remain out of service while the company conducts a thorough engineering analysis and review of a new delamination. Options to return the plant to service will be analyzed after the report is complete. The company cannot estimate a return to service date for CR-3 at this time. "In mid-March, final retensioning of tendons within the CR-3 containment building was suspended while engineers investigated evidence of an additional delamination (or separation) resulting from the tendon retensioning work. The initial damage occurred in late 2009 in the concrete at the periphery of the containment building while creating an opening in the structure to facilitate the replacement of the steam generators inside. The unit was already shut down for refueling and maintenance at the time the damage was found. "The plant has been shut down since September 2009 and there continues to be no threat to public health and safety. Progress Energy continues to coordinate repair and restart plans with Nuclear Regulatory Commission officials." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2011-04-04
46721 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-04-04 02:24 | 2011-04-04 11:02 | 2011-04-04 | TRANSPORT OF CONTAMINATED INJURED PERSON TO AN OFFSITE FACILITY "On 4/4/11, South Texas Project Unit 1 was in a scheduled refueling outage with workers performing activities in the Reactor Containment Building (RCB). At 0224 [CDT], the Unit 1 control room received a report of an individual in the reactor cavity with a medical emergency. An ambulance left the site at 0400 [CDT] on 4/4/11 to transport the contaminated individual to the Matagorda Regional Medical Center. The individual was decontaminated at Matagorda Regional Medical Center. It was determined that the contamination levels on the individual were low with 400 - 500 cpm on clothing and 1200 cpm in the individual's hand. There was no spread of contamination in either the ambulance or at the hospital. "This was determined to be reportable within 8 hours as required by 10 CFR 50.72(b)(3)(xii)." Site Health Physics personnel accompanied the injured individual in the site-owned ambulance. Decontamination was performed by the South Texas HP technicians. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2011-04-04
46720 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-04-04 00:30 | 2011-04-04 01:51 | 2011-04-04 | EMERGENCY SIRENS OUT OF SERVICE DUE TO SEVERE WEATHER "[Three] of the [eleven] emergency notification sirens became non functional when a severe thunderstorm passed through the area. The Coffey County Sheriffs office reported that they received telemetry notifications that the sirens were out of service. Pursuant to 50.72(b)(3)(xiii), the loss of alert systems (sirens) greater than one hour require an 8-hour notification. The exact cause of the siren loss (i.e. power outage, downed pole, etc) is not known and, as of the time of reporting, the duration of the siren outage cannot be determined. "No damage to plant equipment or structures was identified from the severe weather and all outside work activities has resumed. "The NRC Resident Inspector has been notified." * * * RETRACTED AT 1430 EDT ON 04/04/11 FROM WARREN BRANDT TO DONG PARK * * * "The licensee is retracting this event based on the following: "The emergency notification sirens have a battery backup when normal power is lost. Normal power was restored in approximately four hours. It was verified that the three sirens were powered from the battery backup during the time that normal power was unavailable and were always functional. Therefore, this event is not reportable per 10 CFR 50.72. "The NRC Resident Inspector has been notified." Notified R4DO (OKeefe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-04
46719 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2011-04-01 | 2011-04-01 16:24 | 2011-04-01 | AGREEMENT STATE REPORT - I-131 ADMINISTERED DOSE LESS THAN PRESCRIBED DOSE The following was received from the State of Florida via email: "A patient was scheduled to receive a 150 mCi dose of I-131 for thyroid cancer therapy treatment on 3/31/11. The dose was two 75 mCi capsules. Only one pill was taken. The other pill was discovered sticking on the bottom of the vial on 4/1/11 (capsules are sticky and the label around the vial prevented direct observation of the capsule from the side). Patient was under dosed by 50%. The tech failed to ensure that both pills were taken. The physician has been notified and he will notify the patient. The patient will be redosed to bring the dose up to prescription. The dosing procedure will be changed to require the tech to verify that the vial is empty. Licensee will submit a written report. Any further action on this incident is referred to Radioactive Materials. This office will take no further action on this incident." Florida Incident Number: FL 11-028 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2011-04-07
46718 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-03-16 | 2011-04-01 16:03 | 2011-05-06 | AGREEMENT STATE REPORT - YTTRIUM-90 MICROSPSHERES ADMINISTERED DOSE LESS THAN PRESCRIBED DOSE The following was received from the State of Arkansas via email: "On March 16, 2011, a patient was scheduled for two administrations of Y-90 microspheres. The first dose administration was conducted without incident. As the second dose was being delivered, the syringe plunger was accidentally rotated so that the stopper inside the syringe was engaged momentarily causing a pause in administration. Due to the pause, the microspheres in the catheter at the time of the pause settled in the catheter and were not administered to the patient. "The facility has contacted the manufacturer of the administration device. "On the morning of March 17, 2011, Interventional Radiology informed the referring physician, and patient of the event. "Conditions requiring reporting of this event: "The dose differs from the prescribed dose by more than 50 Rem to an organ The delivered dose of 69.56 Gy was 24.44 Gy (2444 rads) less than the optimal dose of 94 Gy and 10.44 Gy (1044 rads) less than the minimal dose in the prescription range. And the total dose delivered differs from the prescribed dose by twenty percent (20%) or more. The total dose delivered, 69.56 Gy, differed by twenty-six percent (26%) from the optimal dose of 94 Gy and was outside the treatment prescription range of 80-150 Gy. "Arkansas Event Number: 03-11-03" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM KAYLA AVERY (VIA EMAIL) TO HOWIE CROUCH AT 0821 EDT ON 5/6/11 * * * "Corrective actions concerning the TheraSphere medical event were submitted to the Arkansas Department of Health. The University of Arkansas for Medical Sciences (UAMS) now requires that all Interventional Radiology staff and residents who will participate in the injection of Y-90 TheraSpheres will receive training on the injection technique prior to administering the radioisotope. The staff will practice the injection process by using normal saline. The staff has also been instructed to administer the dose in a continuous manner without pause. Lastly, the catheter tubing was previously being flushed three times, as recommended by the manufacturer, but the tubing will now be flushed at least five times. The Arkansas Department of Health considers this incident to be closed." Notified R4DO (Proulx) and FSME EO (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2011-04-07
46717 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-04-01 04:04 | 2011-04-01 06:12 | 2011-04-01 | AREA TELEPHONE OUTAGE AFFECTS EMERGENCY NOTIFICATION SYSTEM PHONE "Baxley phone lines were discovered out of service. [This affects the] 366 and 367 [prefix] exchange. Upon further investigation, [it was] determined that Emergency Notification System phone in the Main Control Room was out of service." According to the licensee, and AT&T circuit in the Baxley Central Office was disabled, possibly due to a fiber cable cut. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-04-01
46716 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-31 21:26 | 2011-03-31 23:32 | 2011-03-31 | IDENTIFIED UNSEALED FLOOD BARRIER PENETRATIONS "During investigations of flood barrier penetrations, two approximately 4 inch conduits have been identified that are not sealed. These conduits penetrate the south wall of the auxiliary building near the transformers into room 19. Flooding through the penetrations could have impacted the ability of the station's auxiliary feedwater (AFW) pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). "The penetrations are at an approximate elevation of 1007 [feet]. The river level has been less than 997 feet Mean Sea Level (MSL) since prior to December 1, 2010. The AFW pumps are operable. There are not any indications of conditions that might result in a flood. Actions are in progress to plug the penetrations." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-31
46715 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-03-31 14:32 | 2011-03-31 20:50 | 2011-05-26 | UNANALYZED CONDITION IDENTIFIED FOR INOPERABLE RWST LEVEL "In response to a condition identified in late 2010 concerning the control and removal of hazard barriers in the plant, a review of the basis and analysis for high energy line breaks (HELBs) and the barriers for protecting against such events has been underway at Callaway in accordance with the plant's corrective action program. While following up on a question from the NRC Resident Inspector, and as a result of an additional question from the Nuclear Oversight organization at Callaway, it was identified that non-safety piping located in the valve room associated with the Refueling Water Storage Tank (RWST) could potentially [make] all four RWST low water level pressure transmitters inoperable in the event of a malfunction of the non-safety piping concurrent with a design-basis loss-of-coolant accident (LOCA) and/or following a seismic event. The RWST water level transmitters (which are located in the RWST valve room) perform a safety-related function for the emergency core cooling system (ECCS) by automatically swapping suction sources for the ECCS during a LOCA from the RWST to the containment sumps when a low water level condition is reached in the RWST. These instrument channels are required to be OPERABLE in Modes 1, 2, 3 and 4 per Callaway Technical Specification 3.3.2, 'Engineered Safety Feature Actuation System (ESFAS) Instrumentation.' "The subject non-safety piping delivers steam supplied by the Auxiliary Steam system to (and from) heaters surrounding the RWST for maintaining RWST contents above the minimum required temperature during winter conditions. The piping passes through the RWST valve room containing the noted RWST water level transmitters which were designed only for a mild environment. It has been identified, however, that the non-safety Auxiliary Steam piping constitutes a high energy line and that its failure could create harsh (hot and wet) conditions in the valve room to which the RWST water level instrumentation was not designed. "Per the Callaway FSAR, where non-safety piping interfaces with safety-related piping or systems, the design must be such that failure of the non-safety piping does not adversely affect the safety function(s) of the interfacing safety-related piping or system (since non-safety piping may be assumed to malfunction in conjunction with a design-basis accident). In this case, and based on a conservative interpretation of the FSAR, if the non-safety piping in the RWST valve room is assumed to malfunction (i.e., break), a failure of the RWST instrumentation could occur, thereby preventing the ECCS suction swap over from occurring as required or assumed for LOCA mitigation. "This condition required declaring all four RWST water level channels inoperable. In light of recognizing that the RWST water level instruments could be subject to a harsh environment when they were only designed for a mild environment, and could thus fail as a result, this condition represents an unanalyzed condition that significantly degrades plant safety. With regard to the impact on the required ECCS suction swap over function that requires the RWST water level channels to be operable, the inoperability of all four instrument channels is a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe condition, remove residual heat, control the release of radioactive material, and mitigate the consequences of an accident. "Upon declaring the RWST water level instrument channels inoperable, TS Limiting Condition for Operation (LCO) 3.0.3 was entered at time 1432 CDT on 3/31/2011. At 1634 CDT, the Auxiliary Steam system was isolated and depressurized. This removed the energy that could be released from a break in the non-safety piping, thereby restoring Operability for the RWST water level instruments. "The NRC Senior Resident Inspector was notified." * * * RETRACTION FROM ADAM SCHNITZ TO HOWIE CROUCH AT 1511 EDT ON 05/26/11 * * * "On March 31, 2011, event notification EN 46715 documented that a harsh environment from a postulated High Energy Line Break (HELB) in the Refueling Water Storage Tank (RWST) valve room could affect RWST level transmitters. These level transmitters provide RWST water level indication in the main control room, which is identified as a safe shutdown function in the Callaway FSAR. They also provide low RWST water level signals for effecting automatic swap over of suction sources for the Emergency Core Cooling System in the event of a loss-of-coolant accident (LOCA). This break may be postulated to occur on non-safety related auxiliary steam lines that run through the RWST valve room and on to the RWST heaters. This condition was initially reported both as an unanalyzed condition that significantly degraded plant safety and as a condition that could have prevented fulfillment of a safety function. "When EN 46715 was reported, it was assumed that breaks were required to be postulated at any intermediate fitting, welded attachment, or valve on the subject auxiliary steam lines. Subsequent analysis shows that the sections of auxiliary steam piping in the RWST valve room are able to withstand safe shutdown earthquake (SSE) loadings and rupture loadings. For piping of this qualification, breaks at all intermediate fittings, welded attachments, and valves do not need to be postulated. Instead, line breaks are only required to be assumed at the terminal ends of the lines and at the locations specified for ASME Class 2 and 3 piping. None of these postulated break locations are located inside the RWST valve room, and a postulated auxiliary steam line break outside of the room would not adversely affect the RWST level transmitters. "Since none of the postulated break locations are located inside the RWST valve room, there exists reasonable assurance that the RWST level transmitters would have remained capable of performing their safe shutdown function following a postulated break of the subject auxiliary steam lines. Further, there is no adverse effect on the assumed response to a postulated design basis LOCA since a hazard (such as a break in an auxiliary steam line) is not assumed to occur concurrently with the LOCA. Therefore, this condition does not meet the reporting requirements for an unanalyzed condition that significantly degraded plant safety or a condition that could have prevented fulfillment of a safety function. "Event notification 46715 is hereby retracted. "The NRC Senior Resident Inspector has been notified." Notified R4DO (Haire). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-03-31
46714 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-30 14:05 | 2011-03-31 11:17 | 2011-03-31 | CONTRABAND FOUND INSIDE THE PROTECTED AREA "While cleaning out portable toilets being used at the site, the waste disposal vendor employee discovered a two ounce (shot sized) liquor bottle in one of the units. The unit had been on-site since 2/25/11 and was staged in the Protected Area. The waste disposal vendor indicated that it is unlikely the bottle was in the portable toilet prior to delivery to the site." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2011-03-31
46713 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-03-30 15:42 | 2011-03-30 19:57 | 2011-03-30 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN INITIATED "On March 30, 2011 at 1443 CDT, during a refueling outage, Browns Ferry Unit 2 received an invalid Common Accident Signal (CAS) as a result of maintenance activities. All four Unit 1/2 diesel [generators] auto started and all four Unit 3 diesel [generators] auto started. Unit 2 received a full Reactor SCRAM and Core Spray pumps A, B, C, and D auto started and injected into the reactor. Unit 2 Division I RHR [Residual Heat Removal] system was in Shutdown Cooling with only the C pump in service. The A RHR pump auto started and Shutdown Cooling flow increased, as expected. Unit 2 Division II RHR system was tagged out for maintenance. HPCI [High Pressure Coolant Injection] and RCIC [Reactor Core Isolation Cooling] received auto initiation signals, however the steam isolation valves were tagged closed and the systems did not start. MSIVs [Main Steam Isolation Valves] isolated as a result of the CAS signal. "Unit 1 was at 100% power when the CAS on Unit 2 occurred. This caused initiation of the Preferred Pump Logic which designates Division I CS [Core Spray] and LPCI [Low Pressure Coolant Injection] pumps on Unit 1 (1A and 1C) and the Division II pumps on Unit 2 (2B and 2D) and prevents Unit 1 Division II pumps from auto starting. This resulted in the Division II RHR and CS pumps [being] inoperable for Unit 1. Unit 1 subsequently entered Technical Specification 3.5.1, Condition H (two or more low pressure ECCS [Emergency Core Cooling System] injection/spray subsystems inoperable) which requires entering LCO 3.0.3 immediately. "Unit 1 entered LCO 3.0.3 at 1443, which requires that actions shall be initiated within one hour to place the unit in Mode 2 within 10 hours; Mode 3 within 13 hours; and Mode 4 within 37 hours. At 1542 Unit 1 began lowering power in order to comply with LCO 3.0.3. "CAS logic was reset at 1812 and Unit 1 exited LCOs 3.5.1.H and 3.0.3. "This condition requires a four hour report in accordance with 50.72(b)(2)(i) - 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector was notified. Service Request #346544 was initiated in the Corrective Action Program." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-03-30
46712 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-30 15:38 | 2011-03-30 17:00 | 2011-03-30 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "An extent of condition review of Braidwood Unit 2 unplanned loss of safety system annunciators Emergency Plan Unusual Event on March 24, 2011 (ENS number 46694) was performed for both Units of Braidwood Station. During this review it was identified that a previous unknown loss of annunciators had also occurred on August 10, 2010 from 1024 to 1136 CT on Unit 2. This condition occurred during planned maintenance on annunciator cabinet 2PA19J power supply capacitors. "The maintenance performed on August 10, 2010 would normally not cause a loss of all Unit 2 annunciators. During the work, it was expected to lose approximately one third of the annunciators. Latent annunciator system problems identified from the March 24, 2011 event caused a loss of all Unit 2 annunciators and contributed to this condition being unknown to Main Control Room operators. All Unit 2 indications and computer points to the sequence of events recorder remained available and Unit 2 was stable during this timeframe. "At 1538 CT on 3/30/11, it was determined that the August 10, 2010 condition met the threshold for Emergency Action Level MU6, UNPLANNED loss of most or all safety system annunciation or indication in the control room for greater than 15 minutes. This notification is being made as an undeclared Unusual Event Emergency Plan Classification per 10 CFR 50.72(a)(1)(ii). "Per NUREG 1022, a 1- hour notification is required when a condition existed which met the emergency plan criteria but no emergency was declared and the basis for the emergency class no longer exists at the time of the discovery." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | IL | POW | [5 empty] | 0 | 2011-03-30
46711 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-03-30 07:00 | 2011-03-30 16:24 | 2011-03-30 | EMERGENCY SIRENS OUT OF SERVICE DUE TO INADVERTENT SECURING OF POWER "City of San Clemente inadvertently secured power to 19 Community Alert Sirens. Trouble alarms were received at 0700 [PDT] but it is not known at what time specifically power was removed. All sirens were functional the day before when an inspection was performed on 3/29/2011 at 1213 [PDT]. Power was restored to the sirens at 1145 [PDT] 3/30/2011. This event resulted in 20 community sirens being non-functional for greater than 1 hour. "Siren State Parks 4 (SP-4) was also non-functional for unrelated reasons and remains out of service." Power was restored and all but the state park siren capabilities were declared operable. The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-03-30
46710 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-03-29 10:00 | 2011-03-30 09:07 | 2011-03-30 | COMPLETION OF ISA ACTION PLAN CONVERSION MILESTONE "In response to a Notice of Violation (NOV), Global Nuclear Fuels - America (GNFA) committed to perform a review of the existing Integrated Safety Analysis (ISA). An ISA Action Plan and schedule for performing the ISA review was described in GNF-A's response to the NOV and the first milestone (conversion) was scheduled for completion by January 31, 2011. This milestone was subsequently extended by approximately 60 days. "On 3/29/11, GNF-A completed the ISA review for the conversion area and has identified 87 existing safety controls that are now being designated as items relied on for safety (IROFS). Implementation of the revised safety basis, IROFS and application of management measures to the new IROFS will be completed within 90 days per the ISA Action Plan. "Because the revised ISA has designated existing safety controls as additional IROFS, GNF-A is making a report of this completion pursuant to the reporting requirements of 10CFR70 Appendix A(b)(1) within 24 hours. "Safety Significance of Events: There was no event or plant condition that resulted in a degraded safety condition. "Safety Equipment Status: Existing conversion area safety controls have now been designated as IROFS per ISA Action Plan. Controls are available to perform their safety function. "Status of Corrective Actions: Conversion Area milestone complete. ISA Action Plan continues." The licensee intends to discuss this issue further with the State of North Carolina, New Hanover County, and the NRC Region 2 office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2011-03-30
46709 | -1 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-30 00:10 | 2011-03-30 07:01 | 2011-04-26 | CONTROL ROD MALFUNCTION DURING ROD TESTING RESULTS IN OPERATORS MANUALLY OPENING TRIP BREAKERS "Rod L-13 did not function as expected during control rod movement test. This rod is in Shutdown Bank C. When withdrawing this bank, rod L-13 did not withdraw and when the bank was manually inserted, rod L-13 began to withdraw. The [operating] crew went to Enclosure 13.2 of the procedure to deal with the misaligned rods. This enclosure has procedural guidance to open the reactor trip breakers, if desired. The reactor trip breakers were opened and all 211 rods are fully inserted. The reactor was not critical. This activity was performed twice [at the request of reactor engineering]." The licensee will remain in Mode 5 (Cold Shutdown) until troubleshooting and repair is completed. The licensee will be notifying the NRC Resident Inspector. * * * RETRACTION AT 1528 ON 4/26/2011 FROM JAMES DAIN TO MARK ABRAMOVITZ * * * "This notification pertains to Event Number 46709. Based on further investigation, this event is being retracted. "The event described in Event Number 46709 involved a control rod malfunction on Unit 2 while in Mode 5, during RCCA movement testing. Specifically, Control Rod 'L-13' in Shutdown Bank 'c' did not move with the bank when the bank was withdrawn from the bottom of the core. When the bank was reinserted to the bottom of the core, L-13 was observed to be 12 steps withdrawn. This condition was corrected by opening the reactor trip breakers which placed L-13 at the bottom of the core. The subsequent troubleshooting plan involved further manipulation of Shutdown Bank 'C' with additional instrumentation on the rod control cabinets. The same anomaly occurred and the reactor trip breakers were again opened. "This event (both openings of the reactor trip breakers) was reported to the NRC on 3/30/11 as a valid RPS actuation (8-hour report; 10 CFR 50.72(b)(3)(iv)(A)). The event in question did not result in any consequences, given that the plant was in Mode 5 and not critical. NUREG-1022, Revision 2 states that actuations that need not be reported are those initiated for reasons other than to mitigate the consequences of an event (e.g., at the discretion of the licensee as part of a preplanned procedure). Notwithstanding the issue of whether opening the reactor trip breakers was to mitigate the consequences of an event, NUREG-1022 cites one valid example of actuations that need not be reported, namely if the actuation was 'at the discretion of the licensee as part of a preplanned procedure'. The purpose of the test being conducted was to identify issues with the control rod system. The malfunction that occurred is one of a host of possible issues that could reasonably be expected to occur. Although the test personnel did not go into the test expecting the need to open the reactor trip breakers, the malfunction that occurred resulted in a desire to open the reactor trip breakers in order to restore the plant to the desired configuration. This action was a choice as allowed by the test procedure, and the personnel involved were aware of the result of the action before it occurred. Therefore, the event constituted a 'pre-planned sequence during testing', and was 'at the discretion of the licensee as part of a preplanned procedure.' "Based upon the above considerations, the event does not meet the aforementioned criteria for an 8-hour report, and Event Number 46709 is therefore retracted. The licensee has notified the NRC Resident Inspector of this update." Notified the R2DO (Seymour). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-03-30
46708 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-29 20:00 | 2011-03-30 01:39 | 2011-03-30 | POTENTIAL VOIDING IN AUXILIARY FEEDWATER ALTERNATE SUCTION LINE "The design of the Auxiliary Feedwater (AF) system is for the AF pumps to normally take suction from the condensate storage tank. If the condensate storage tank is not available, the essential service water system provides the alternate supply. Due to the AF system suction piping and valve configuration, a voided section of pipe could exist in the portion that isolates the condensate storage tank supply from the essential service water supply. A preliminary vendor analysis has determined that the void fraction to reach the pump in a dynamic scenario exceeds the acceptance criteria for AF pump operability. Based on past operation in this configuration, the event is being reported as a unanalyzed condition that significantly degrades plant safety and a condition that could have prevented the fulfillment of a safety function (i.e., remove residual heat) under 10CFR50.72(b)(3)(ii) and 10CFR50.72(b)(3)(v). Further review of the void model and pump performance characteristics are planned. "In 2011, prior to the completion of this analysis. The void was refilled and verified full for both trains at Byron U1 and U2." Unit 1 is defueled. This condition affects both 'A' and 'B' trains of auxiliary feedwater for both Unit 1 and Unit 2. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2011-03-30
46707 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-29 20:00 | 2011-03-30 01:34 | 2011-03-30 | POTENTIAL VOIDING IN AUXILIARY FEEDWATER ALTERNATE SUCTION LINE "The design of the Auxiliary Feedwater (AF) system is for the AF pumps to normally take suction from the condensate storage tank. If the condensate storage tank is not available, the essential service water system provides the alternate supply. Due to the AF system suction piping and valve configuration, a voided section of pipe could exist in the portion that isolates the condensate storage tank supply from the essential service water supply. A preliminary vendor analysis has determined that the void fraction to reach the pump in a dynamic scenario exceeds the acceptance criteria for AF pump operability. Based on past operation in this configuration, the event is being reported as a unanalyzed condition that significantly degrades plant safety and a condition that could have prevented the fulfillment of a safety function (i.e., remove residual heat) under 10CFR50.72(b)(3)(ii) and 10CFR50.72(b)(3)(v). Further review of the void model and pump performance characteristics are planned. "In 2011, prior to the completion of this analysis, the void was refilled and verified full for the 'B' trains at Braidwood U1 and U2. Filling the voided piping of both 'A' trains at Braidwood U1 and U2 is in progress. Once filled, the AF systems are operable." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2011-03-30
46706 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2011-03-29 | 2011-03-29 20:02 | 2011-03-29 | AGREEMENT STATE REPORT - STOLEN NDC DRAIN PROFILE GAUGE An NDC Model 104-P drainage profile gauge, serial number 1282, was stolen from a licensee vehicle. The box containing the gauge was chained to the floor of the vehicle which was also locked. The gauge contains an 80 mCi Am-241 source. A report was filed with the Chapin, SC police department. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2011-04-01
46705 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2011-03-28 14:30 | 2011-03-29 13:58 | 2011-03-29 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following information was received via fax: "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation, and is basically all that is known by the Agency [Arizona Radiation Regulatory Agency] Staff at this time. "At approximately 1000 MDT, March 28, 2011, the Agency was informed that the Licensee had a Troxler Model 3241-C, SN 1884, asphalt content gauge stolen from the F & F construction trailer at the Casa Grande job site. The theft occurred over the weekend. The gauge was locked with a chain in the construction trailer which was parked in a locked, fenced construction job site. The gauge contains 100 mCi Am-241:Be. "Casa Grande PD is investigating. The Agency continues to look for the source. The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2011-04-01
46704 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2011-03-29 01:55 | 2011-03-29 02:48 | 2011-03-29 | ELECTRICAL FIRE IN THE DRYWELL ON A PIECE OF LIFTING EQUIPMENT "At approximately 0145 EDT, the Unit 1 control room was notified of elevated carbon monoxide (CO) levels in the Unit 1 Drywell. The cause of the elevated CO was a small fire on a 'Lift-A-Loft'. The fire was immediately extinguished followed by an evacuation of all personnel from the Drywell. "Follow up atmosphere samples indicated carbon monoxide levels above the OSHA Threshold of 50 PPM. Readings were as high as 79 PPM and have been slowly lowering since the initial response. These values are considered to affect the health of plant personnel or safe plant operation and an Unusual Event was declared at 0155 EDT. "As of 0225 EDT, all values within the Unit 1 Drywell have been confirmed to be below the 50 PPM threshold. "As of 0226 EDT, the Unusual Event has been terminated." There were no injuries, no offsite assistance required, and the NRC Senior Resident Inspector responded to the site. The licensee notified the NRC Senior Resident Inspector, the State Emergency Communication Center, and the Oswego County Warning Point. No press release is planned. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-03-29
46703 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-28 13:00 | 2011-03-28 14:48 | 2011-03-31 | ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BLAKE MITCHELL TO CHARLES TEAL AT 1216 ON 3/31/2011 * * * After review of the circumstances surrounding the event, Farley Nuclear Plant is retracting the event notification. Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes) and via email the Part 73.71 Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-03-28
46702 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2011-03-28 11:43 | 2011-03-28 12:38 | 2011-03-28 | UNUSUAL EVENT DECLARED DUE TO SMOKE COMING FROM AN ELEVATOR CONTROL CABINET At 1129 EDT on 03/28/11, smoke was detected coming from an elevator power supply transformer in the "B" Residual Heat Removal (RHR) vault. The licensee declared a Unusual Event at 1143 EDT. At 1146 EDT the fire brigade responded and found smoke only and no flame. The smoke stopped when the cabinet was de-energized. At 1158 EDT, the fire was proven to be out when the cabinet was opened. No fire fighting extinguishing agents were used. There was no damage to other plant equipment and no personnel injuries. At 1151 EDT, the licensee notified the States of New Hampshire and Massachusetts and at 1209 EDT, activated their Technical Support Center (TSC). The plant was operating at 100% power and remained stable during and after the event. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JEFF MCNALLY TO JOHN SHOEMAKER AT 1341 EDT ON 03/28/11 * * * "At 1243 EDT on 03/28/11, the Unusual Event was terminated. Subsequent investigation has revealed that no plant equipment damage beyond a power transformer that supplies an equipment elevator occurred. There was no indication of [visible] flame (smoke only) and no personnel injuries as a result of the event." The licensee notified the NRC Resident Inspector. Notified R1DO (Powell), NRR EO (Cheok), IRD (Morris). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-03-28
46701 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-26 14:49 | 2011-03-26 21:10 | 2011-03-26 | MANUAL REACTOR TRIP WHEN A LOSS OF THE 2-1 MAIN FEEDWATER PUMP OCCURRED "This notification provides the 4-hour non-emergency event report for the manual reactor trip of Diablo Canyon Power Plant Unit 2 in accordance with 10 CFR 50.72(b)(2)(iv)(B) 'RPS Actuation (scram)'. Additionally, this notification provides the 8-hour non-emergency event report of the automatic actuation of the auxiliary feedwater system as a result of the reactor trip in accordance with 10 CFR 50.72(b)(3)(iv)(A) 'Specified System Actuation'. "On March 26, 2011 at 1449 PDT operators at Diablo Canyon Power Plant Unit 2 manually initiated a reactor trip in response to loss of main feedwater pump 2-1. The main feedwater pump is believed to have tripped due to non-radioactive water spray on its control console. The water spray was caused by leakage from the flange of the relief valve on the feedwater heater 2-1A condenser dump valve line. Emergency plan activation was not required. The unit is stable in mode 3 (Hot Standby) with offsite power being supplied to all buses via the 230 kV startup circuit. Diesel generators 2-1 and 2-2 remain OPERABLE in standby. Diesel generator 2-3 remains unavailable due to pre-planned maintenance. All rods fully inserted on the reactor trip. The reactor is being cooled by the auxiliary feedwater system with the condenser in service. All systems performed as designed with no unexpected pressure or level transients. ECCS actuation was not required. Automatic main feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown isolation occurred as expected. "Unit 1 was unaffected by this event and remains at 100% power." The licensee has notified the NRC Resident Inspector, San Luis Obispo County, and the State of California. | 0 | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-03-26
46700 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-25 14:00 | 2011-03-25 21:35 | 2011-03-27 | BOTH TRAINS OF EMERGENCY DIESEL GENERATORS ARE INOPERABLE "On March 25, 2011, the Train B emergency diesel generator (2EGS-EG2-2) was inoperable and unavailable due to being out of service for scheduled maintenance. At 1400 hours, the Train A emergency diesel generator (2EGS-EG2-1) was declared inoperable, but available, after questions were raised about the adequacy of the assembly method for fuel injection line compression fittings by the manufacturer. Without assurance that the fittings meet full qualification requirements, the Train A emergency diesel generator was declared inoperable. "The Unit is currently in Mode 6 with fuel loaded and the upper internals installed in the reactor vessel. The reactor vessel head is removed with 23 feet of water in the cavity, two Operable Residual Heat Removal trains one of which is in operation. With both emergency diesels inoperable, the safety functions needed for accident mitigation could be impaired in the event of a loss of off-site power. Actions are currently in progress to restore one emergency diesel generator to an Operable status. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D) due to both emergency diesel generators being inoperable. This event will be evaluated for 10 CFR Part 21 applicability." The licensee is in Technical Specification 3.8.2. With both diesels declared inoperable, they have to suspend all core alterations and possible reactivity additions and return an EDG to service. The licensee plans to return the B train EDG an available status (but not Operable per Technical Specification) by tomorrow. The licensee will then replace the discrepant fuel injector line compression fittings on the A train and return it to Technical Specification Operable status. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0226 ON 3/27/11 FROM DANIEL SCHWER TO MARK ABRAMOVITZ * * * "Following replacement of the questionable fuel injection line compression fittings and successful surveillance and post maintenance testing, the Train A emergency Diesel Generator (2EGS-EG2-1) was declared OPERABLE at 0058 hours on 3/27/2011. One Diesel Generator was maintained available at all times while the issue was being addressed." The licensee notified the NRC Resident Inspector. Notified the R1DO (Rogge). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-25
46699 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2011-03-25 10:53 | 2011-03-25 17:27 | 2011-03-29 | POTENTIAL UNANALYZED CONDITION DUE TO POWER LEVEL GREATER THAN LIMIT "During performance of maintenance to troubleshoot the B feedwater regulating bypass valve, the Thermal Power Monitor (TPM) indication exceeded the maximum thermal power assumed in the Safety Analysis Report. Operators were maintaining 12 Steam Generator (SG) water level in a band from 40 to 48 percent by controlling the B Feed Regulating Valve (FRV) in manual from the Control Room. Operators noted a power increase; adjustments were made via the FRV to reduce SG water level, however the valve response was sluggish and thermal power exceeded 100%. Immediate steps were taken to reduce power to below 100% by reducing 1st stage turbine pressure and inserting Bank D control rods 7 steps. "The TPM indication was above the maximum thermal power limit of 100.36% for 1.68 minutes. The TPM indication peak was 100.39%. No concurrent increase in power was observed by the nuclear indication system. "NRC Resident had been informed." * * * RETRACTION FROM JOHN KEMPKES TO JOHN SHOEMAKER AT 1350 EDT ON 03/29/11 * * * "An eight hour report (EN #46699) per 10 CFR 50.72(b)(3)(ii)(B) was conservatively reported on March 25, 2011 for Thermal Power Monitor indication above the maximum thermal power limit of 100.36% for 1.68 minutes. "Subsequent engineering investigation has determined that this specific transient had been previously analyzed. The transient was within the bounds of the safety analysis. "The 10 CFR 50.72(b)(3)(ii)(8) report (EN #46699) is retracted. "NRC Resident has been informed." Notified R3DO (Peterson). | 98 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-03-25
46698 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-25 | 2011-03-25 11:40 | 2011-03-25 | NON-COMPLIANCE WITH NUHOMS TECHNICAL SPECIFICATION "This 24-hour report is being issued in accordance with the requirements of NRC Certificate of Compliance 1030, Amendment 0, for the NUHOMS Storage System, Technical Specification (TS) 2.2, Functional Operating Limit Violations. "During a review of historical Surry NUHOMS Dry Storage Canister (DSC) loading certification documents, a discrepancy was identified. The NUHOMS Certificate of Compliance 1030 Amendment 0 Technical Specifications include a Figure 2, 'Heat Load Zones' which specifies the maximum decay heat load for each of the 32 assembly locations in a DSC. The figure includes limits for two zone '1b' locations and two zone '1a' locations in the four center locations of the DSC. The zone '1b' decay heat limit of 0.800 kw is specified for the two 'upper compartments' and zone '1a' decay heat limit of 1.05 kw is specified for the two 'lower compartments' on the figure. Contrary to this, the loading certifications for 6 of 12 DSCs already loaded at Surry were not developed to maintain this orientation when loaded in the horizontal storage module (HSM). As a result, the DSC zone '1b' heat load limits were exceeded in some cases for these 4 DSCs. "The heat load limit for all other zones in the DSCs are symmetric, and those assemblies were verified to the correct limit and are unaffected by this error. In addition the total heat load limit for the sum of the center assemblies was met for all DSCs. The maximum heat load of any zone '1b' assembly at the time of loading was 0.806 kw, which is slightly higher than the 0.800 kw limit. The lower heat load of assemblies in the other compartments offset the slightly higher heat load effects, and it is expected that the thermal analysis acceptance criteria would still have been met at the time of loading. "The decay heat of the assemblies has continued to decrease since their initial loading and all assemblies currently meet the upper central compartment limits. The affected fuel assemblies are in a safe condition as required by NUHOMS TS 2.2.1. "The NRC Resident Inspector has been notified of this event." | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2011-03-25
46697 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-24 14:00 | 2011-03-25 11:14 | 2011-03-25 | NON-COMPLIANCE WITH NUHOMS TECHNICAL SPECIFICATION "This 24-hour report is being issued in accordance with the requirements of NRC Certificate of Compliance 1030, Amendment 0, for the NUHOMS Storage System, Technical Specification (TS) 2.2, Functional Operating Limit Violations. "During a review of historical North Anna NUHOMS dry storage canister (DSC) loading certification documents, a discrepancy was identified. The NUHOMS Certificate of Compliance 1030 Amendment 0 Technical Specifications include a Figure 2, "Heat Load Zones" which specifies the maximum decay heat load for each of the 32 assembly locations in a DSC. The figure includes limits for two zone '1b' locations and two zone '1a' locations in the four center locations of the DSC. The zone '1b' decay heat limit of 0.8 kw is specified for the two 'upper compartments' and zone '1a' decay heat limit of 1.05 kw is specified for the two 'lower compartments' on the figure. Contrary to this, the loading certifications for 7 of 10 DSCs already loaded at NAPS (North Anna Power Station) were not developed to maintain this orientation when loaded in the horizontal storage module (HSM). As a result, the DSC zone '1b' heat load limits were exceeded in some cases for these 7 DSCs. "The heat load limit for all other zones in the DSCs are symmetric, and those assemblies were verified to the correct limit and are unaffected by this error. In addition the total heat load limit for the sum of the center assemblies was met for all DSCs. The maximum heat load of any zone '1b' assembly at the time of loading was 0.859 kw, which is slightly higher than the 0.8 kw limit. The lower heat load of assemblies in the other compartments offset the slightly higher heat load effects, and it is expected that the thermal analysis acceptance criteria would still have been met at the time of loading. "The decay heat of the assemblies has continued to decrease since their initial loading and it was confirmed that 12 of the 13 assemblies that initially exceeded the 0.8 kw limit currently meet the zone '1b' heat load limits. The current decay heat of the remaining assembly is slightly above the 0.8 kw limit. Based on the offsetting margins identified above all of the affected DSCs are currently in a safe condition as loaded in the HSMs." The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2011-03-25
46696 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2011-01-28 | 2011-03-24 19:02 | 2011-03-24 | TURNBUCKLE COLLAR THREADS OUT OF TOLERANCE "Name of firm constructing or supplying the basic component which fails to comply or contains a defect: OFI Fabrication, Richmond, VA. "Safety Hazard: Failure of turnbuckles could ultimately cause a failure of IROFS41 (i.e. breach of UF6 piping) during a seismic event resulting in release of licensed material, but this release would not exceed 10 CFR 70.61 requirements for the public or workers. "The date on which the information or such defect or failure to comply was obtained: January 28, 2011. "In a case of a basic component which contains a defect or a failure to comply, the number and location of all such components in use at or supplied for the URENCO USA Facility: Currently there are 164 non-defective components installed and 96 non-defective components in storage. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: Replacement NQA-1 turnbuckles were installed; and the Receipt Inspection Plan (RIP) for turnbuckles (collar as well as paddle assembly) was revised to include 100 percent verification of thread tolerances. All out of tolerance turnbuckle collars were returned to the vendor. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: Implement 100 percent verification of turnbuckle collar thread tolerances using appropriate 'Go-No Go' thread gauges." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 21.21 |  |  |  | 0 | 2011-03-24
46695 | 0 | GRADY MEMORIAL HOSPITAL |  |  |  |  | 2011-03-23 03:00 | 2011-03-24 16:20 | 2011-03-24 | EMERGENCY RETRACT MECHANISM FAILURE The Varian equipment representative provided notification of the following event that occurred at the Grady Memorial Hospital in Atlanta, GA. A technician was installing a Varisource IX high-dose afterloader when the active wire composed of a 10 Ci Ir-192 source failed to extend. After troubleshooting it was discovered that the wire was stuck on the wedge block which is part of the emergency retract mechanism. The active wire was removed and the emergency retract mechanism was replaced. The technician received 0.2 mrem during the repair work. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-03-24
46694 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-24 10:18 | 2011-03-24 11:39 | 2011-03-24 | UNEXPECTED LOSS OF ANNUCIATORS DURING PLANNED MAINTENANCE "During a planned maintenance activity on the Unit 2 main control room alarm cabinets, it was identified that all Unit 2 safety system annunciators were lost. This was identified at 1006 [CDT]. Main Control Board indicators remained functional. At 1018 [CDT], the Shift Manager declared an Unusual Event under Emergency Action Level MU6. This was due to an unplanned loss of most (approximately 75%) safety system annunciators for > 15 minutes. The planned maintenance activity was not expected to affect the amount of annunciators that were lost. "At 1030 [CST], the [planned maintenance] clearance order was cleared and power was restored to the Unit 2 annunciators." There was not transient on other plant equipment and the plant remained stable before and after this event. The cause for the unexpected loss of annunciators is not clearly understood and is still under investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM SCOTT BUTLER TO JOHN SHOEMAKER AT 1216 EDT ON 03/24/11 * * * The Unusual Event was terminated at 1047 CDT on 03/24/11. All annunciators have been restored and an investigation will be conducted to determine the cause. Notified R3DO (Cameron) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-03-24
46693 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-03-23 23:54 | 2011-03-24 06:02 | 2011-05-19 | PRESSURE TRANSMITTERS NEEDED FOR AUXILIARY FEEDWATER SUCTION PATH NOT ANALYZED FOR POTENTIAL HIGH ENERGY LINE BREAK "While performing an extent of condition review of high energy line break (HELB) analyses, a detailed review of the auxiliary steam system was being performed. During this review, sections of pipe that run through rooms 1206/1207 in the Auxiliary Building were identified that have design ratings indicating that they could possibly be classified as high energy lines. "The pipes were verified to have not been considered in the current HELB analyses. This condition affects pressure transmitters ALPT0037, 38, & 39 which are not qualified for operation in a harsh environment. These pressure transmitters provide the Auxiliary Feedwater Pump [AFW] Suction Transfer signal on low suction pressure from the non safety Condensate Storage Tank to the Safety Related supply (Essential Service Water). "Technical Specification [TS] 3.3.2-6.h bases state: "since these detectors are in an area not affected by HELBs or high radiation, they will not experience any adverse environmental conditions and the Trip Setpoint reflects only steady state instrument uncertainties." "Based upon the above bases, with the identified aux steam lines in service, the pressure transmitter's operability could not be assured. This represented an unanalyzed condition and had the potential to affect equipment used for accident mitigation. TS 3.0.3 was entered at time 2354 [CST] on 3/23/2011. At 0009 [CST] on 3/24/2011, Aux Steam valves FBV0158, FBV0I48, FAV0002, and FAV0003 were isolated, removing the HELB concern [TS 3.0.3 was exited at this time]. These are the active feed [isolation valves] to the lines passing through the Aux Building Rooms 1206/1207." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1525 ON 5/19/2011 FROM DAVID BONVILLIAM TO MARK ABRAMOVITZ * * * "On March 23, 2011, event notification EN 46693 documented that a harsh environment from a postulated High Energy Line Break (HELB) could affect pressure transmitter ALPT0037, 38 and 39. These pressure transmitters provide the Auxiliary Feedwater Pump suction transfer signal on low suction pressure from the Condensate Storage Tank to the safety-related water supply (Essential Service Water). This break was postulated to occur on auxiliary steam lines in Auxiliary Building rooms 1206 And 1207. This condition was initially reported both as an unanalyzed condition that significantly degraded plant safety and as a condition that could have prevented fulfillment of a safety function. "When EN 46693 was reported, it was assumed that breaks were required to be postulated at any intermediate fitting, welded attachment, or valve on the subject auxiliary steam lines. Subsequent analysis shows that these sections of auxiliary steam piping are able to withstand safe shutdown earthquake (SSE) loadings and rupture loadings. For piping of this qualification, breaks at all intermediate fittings, welded attachments, and valves do not need to be postulated. Instead, line breaks are only required to be assumed at the terminal ends of the lines and at the locations specified for ASME Class 2 and 3 piping. None of these postulated break locations are located inside rooms 1206 and 1207. "Analysis has been performed on these auxiliary steam lines for the remaining break locations that are required to be postulated. This analysis demonstrates reasonable assurance that safety related equipment, including pressure transmitters ALPT0037, 38 and 39, would have performed their safety functions following a postulated break of these auxiliary steam lines. Therefore, this condition does not meet the reporting requirements for an unanalyzed condition that significantly degraded plant safety or a condition that could have prevented fulfillment of a safety function. "Event notification 46693 is hereby retracted. "The NRC Resident Inspectors have been notified." Notified the R4DO (Shannon). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-03-24
46692 | 0 | AUTOMATIC VALVE |  |  |  |  | 2011-03-22 | 2011-03-23 16:24 | 2011-03-23 | VALVE PLUNGER GUIDE MALFUNCTION "Initial Concern: Valve, serial number 73386, does not consistently return to the closed position." "Nature of the Defect: A dent in the plunger guide may prevent the valve from changing state. "Number and Location of Components: "Model: U0204GBBR-AA Quantity: 32 Customer: EXELON LIMERICK, "Model: U0204GBBR-DEEL Quantity: 30 Customer: ALABAMA POWER FARLEY "Model: U0204GBBR-DE Quantity: 4 Customer: ALABAMA POWER FARLEY "Model: U0204FBBR-DE Quantity: 8 Customer: RALPH A. HILLER "Model: U0204GBBR-DEL Quantity: 4 Customer: DRESSER MASONEILAN "Model: U0204GBBR-DEP Quantity: 3 Customer: DRESSER MASONEILAN "Advice to Purchasers: "Any of the valves identified above may be inspected by removing the coil and checking the plunger guide for any defects. A dent which will prevent plunger movement is noticeable without magnification. It typically occurs approximately 0.10 inches from the base of the valve. Any valves thought to contain defects will be rebuilt or replaced by Automatic Valve." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | OTH | PAR | 21.21 |  |  |  | 0 | 2011-03-23
46691 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2011-03-22 17:35 | 2011-03-22 20:45 | 2011-03-22 | MOISTURE DENSITY GAUGE STOLEN AND RECOVERED "A Troxler Electronic Laboratories, Inc. Model 3430, portable gauging device [serial number 22936, containing approximately 8.0 millicuries of cesium-137, and approximately 40 millicuries of americium-241/beryllium] was stolen from the licensee's vehicle while parked at the Home Depot in Lindon, Utah. The Cs-137 source was in the safe shielded position when it was stolen and the transportation case was also secured. The device had been secured by two independent physical barriers, but both barriers were breached. The device was recovered at approximately 5:55 p.m. MST by licensee personnel. The transportation case had been opened, but the source rod was still secured in the shielded position. "The licensee's vehicle was an open bed pickup truck with a mechanism to secure the device as required." Utah Report: UT110001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2011-03-25
46690 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-22 13:08 | 2011-03-22 17:11 | 2011-03-22 | POTENTIAL FLOODING OF RAW WATER PUMP "During ongoing investigations of flood barrier penetrations at the station, a weakness in the flood protection strategy that would prevent protection of the raw water pumps for floods above 1007'-6" Mean Sea Level (MSL) was discovered. Cell in-leakage through penetrations at 997' 10" MSL would be beyond the capacity of the raw water pumps. During the preparation of a calculation to demonstrate the validity of this method it was determined that the grid backwash pipe for each grid and the surface sluice penetrate the east wall of the intake structure through an unsealed penetration (a total of 7 penetrations). The grid backwash line is an 18" pipe passing through a 24" sleeve. Flooding through the penetrations could have impacted the ability of the station's raw water pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). "The penetration is at an elevation of 997'10" MSL. The design flood for the station is at 1014' MSL. The raw water pumps would not be affected until a river level of 1007'6" MSL was reached. The river level is currently approximately 993.5' MSL and has been less than 995'MSL since prior to December 1, 2010. The raw water pumps are currently operable. The National Weather Service Weather Forecast Office is predicting a rise in river level of 2 feet over the next 5 days. Actions are in progress to seal the penetration." The licensee has instituted a temporary plug contingency plan dependant on river level. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-22
46689 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-22 10:58 | 2011-03-22 14:22 | 2011-03-22 | CONTAINMENT COOLERS DECLARED INOPERABLE "At 10:58 CDT, today during the performance of IC-ST-IA-3010B, I&C found NG-HCV-400A-A3, CCW INLET VALVE HCV-400A NITROGEN SUPPLY ISOLATION VALVE, closed which is required to remain open for VA-3A to remain operable. This valve supplies backup nitrogen to VA-3A CCW cooler isolation valve HCV-400A on loss of instrument air to maintain cooling flow to the ventilation during an accident condition. While the nitrogen valve NG-HCV-400A-A3 was closed, performance of IC-ST-IA-3010B on VA-3B, CONTAINMENT AIR RECIR FAN, placed the containment cooler in an inoperable status. This led to Technical Specification 2.0.1 entry due to both trains of cooling being inoperable. The cause for the mispositioning of NG-HCV-400A-A3 is unknown at this time. The inoperability of VA-3A along with VA-3B rendered the containment cooling trains unavailable to perform their safety function during an accident condition. This condition is being reported pursuant to 10 CFR 50.72(b)(3)(V)(D) for mitigating the consequences of an accident. FCS entered into Technical Specification at 10:58 CDT and exited Technical Specification at 11:14 CDT." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-22
46688 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-18 | 2011-03-21 13:19 | 2011-03-21 | DEFECTIVE KPR-14DG-125 RELAYS DISCOVERED DURING BENCH TESTING "The following event description is based on information currently available. The condition is reported under 10 CFR 21.21(d)(3)(i). "Part 21 Report - Potter Brumfield KRP-14DG-125 Relays, supplied by Southern Testing Services (STS) division of Argo Turboserve Corporation (ATC). "On March 17, 2011, during bench testing of the KRP-14DG-125 Relays, Fort Calhoun Station (FCS) discovered that some of these relays were defective in that one of the contacts would not close properly after energizing and de-energizing the relay coils. If installed in the plant, the improper closure of this contact could defeat the safety function of the relays that provide a signal to the component supported by that contact. This deviation from the design specifications is reportable per 10 CFR 21. FCS does not have any of the affected relays installed in the plant. "FCS returned the batch of relays to the vendor for further failure modes and effects evaluation and reporting. "FCS has not provided any of these relays from our stock to any other licensee. "The vendor and the [NRC] Resident Inspector have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 21.21 |  |  |  | 0 | 2011-03-21
46687 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2011-03-19 22:36 | 2011-03-20 07:08 | 2011-03-20 | HIGH PRESSURE CORE SPRAY VALVE BREAKER OVERCURRENT TRIP SETPOINT OUT OF TOLERANCE "During testing of the High Pressure Core Spray [HPCS] system minimum flow valve breaker, it was discovered that the overcurrent trip setpoint was out of tolerance. This testing was being performed as a result of a breaker trip that occurred during a surveillance. The discovery occurred while the system was inoperable for maintenance and no TS [Technical Specification] limits or action times were exceeded." The overcurrent trip setpoint was placed within tolerance and HPCS is in operable status. The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-20
46686 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-03-19 08:00 | 2011-03-19 16:21 | 2011-03-30 | ULTRASONIC EXAMINATION RESULTS IN INDICATIONS ON TWO REACTOR HEAD PENETRATIONS "On March 19, 2011, during the Byron Station Unit 1 refueling outage, it was determined that the results of planned ultrasonic (UT) examinations performed on two penetrations of the reactor vessel head would not meet the applicable acceptance criteria. Both require repair prior to returning the vessel head to service. These indications are not in the reactor coolant pressure boundary; however they are very near the toe of the J-groove weld. The examinations were being performed to meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to ensure the structural integrity of the reactor vessel head pressure boundary. The UT examinations continue for the remaining head penetrations. All of the penetrations will be examined during the current refueling outage. Repairs are currently being planned and will be competed prior to startup. "This is reportable pursuant to 10CFR50.72(b)(3)(ii)(A) since the as found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BLAINE PETERS TO JOHN SHOEMAKER AT 0910 EDT ON 03/30/11 * * * "Ultrasonic examination [made on March 19, 2011] resulted in indications on two reactor head penetrations. "As mentioned in Event Notification 46686, reactor vessel head penetrations [In-service inspection] ISI examinations were still in progress. On Wednesday, March 30, 2011, two additional Unit 1 reactor head penetrations were found to contain indications that will require repair prior to returning the reactor head to service. The indications on these two penetrations are within the reactor vessel head pressure boundary." The NRC Resident Inspector has been notified by the licensee. Notified the R3DO (Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2011-03-19
46685 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-03-19 04:04 | 2011-03-19 06:54 | 2011-03-19 | SAFETY INJECTION DISCHARGE TO THE REACTOR "Following a scheduled plant shutdown for refueling the operators were forced to close the Main Steam Isolation Valves (MSIV's) to limit plant cooldown. While opening MSIV's to restore steam to the secondary, a Reactor Trip and Safety Injection (SI) occurred. The MSIV bypass valves were opened to equalize pressure across the MSIV's. Steam header pressure dipped when the MSIV for 'C' Steam Generator (S/G) was opened. The low steamline pressure bistables are rate sensitive and actuated to cause the SI when steam pressure dipped. Lowest steamline pressure was 1040 psig, the low steam line pressure SI actuates at 615 psig. "During the SI the PZR [Pressurizer] PORV's cycled approximately 10 times to limit RCS pressure. When the PORV's opened the 'B' PZR Code Safety Main Control Board (MCB) and plant computer alarm actuated but the actual MCB indication did not change nor does plant response indicate that a PZR Code Safety opened. This appears to be an indication problem related to the PORV's cycling." "All equipment functioned as required." The station electric buses are aligned to normal offsite power. Decay heat removal is being discharged to the atmospheric relief valves with no indication of primary to secondary leakage. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MARCY BLOW TO DONALD NORWOOD AT 1221 EDT ON 3/19/2011 * * * "1. The expected system actuations that occurred when the plant experienced a Safety Injection (SI) 03/19/11 at 04:04 CDT, previously reported on EN 46685 for 10CFR50.72(b)(2)(iv)(A), is also reportable under 10CFR50.72(b)(3)(iv)(A) for Specified System Actuation. "2. During the recovery of the Safety Injection (SI) actuation that occurred 03/19/11 at 04:04 CDT and previously reported on EN 46685, the Safety Injection Signal was reset which blocked any further automatic actuation. This was directed per the appropriate procedure step. There is no Technical Specifications allowed condition for both trains of ECCS to be inoperable, therefore the unit entered Tech. Spec. 3.0.3 due to the Auto SI feature being blocked. LCO 3.5.2 action C.1. directs immediate entry into LCO 3.0.3. The entry into TS 3.0.3 was made at 0411 CDT and exited at 0639 CDT when the Reactor Trip Breakers were reclosed which re-enabled the automatic SI signal. This is reportable under 10CFR50.72(b)(3)(v)(D) for Accident Mitigation. "NRC Resident was notified of the update." Notified R4DO(Cain). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2011-03-19
46684 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2011-03-18 | 2011-03-18 17:34 | 2011-03-18 | AGREEMENT STATE REPORT - DENSITY GAUGE STUCK SHUTTER "The licensee Radiation Safety Officer (RSO) was performing a routine shutter check on a density gauge (Berthold model LB7440); the shutter was difficult to turn so the RSO used pliers to move the shutter to the indicated closed position. The shutter did not close. The detector on the gauge was still reading the same as when the shutter was indicated open. The RSO contacted the manufacturer and is in the process of scheduling them to service the device. The RSO tagged the gauge with a do not operate tag warning people of the problem." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2011-03-23
46683 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2011-03-17 | 2011-03-18 16:13 | 2011-03-18 | AGREEMENT STATE REPORT - YTTRIUM-90 MICROSPSHERES ADMINISTERED AT 150% OF PRESCRIBED DOSE "A medical event took place at Abbott-Northwestern Hospital involving a Yttrium-90 (Y-90) SIR microsphere therapy patient treated on 3/17/2011. It was discovered on 3/18/11, by the radiation oncologist covering the SIRS procedure from the day before, that the delivered amount of Y-90 SIRS wasn't 105% above the prescribed dose as intended, but actually 150% above the prescribed dose. She then brought this error to the attention of the lead medical physicist who was the attending medical physicist responsible for this treatment delivery, for further clarification. Upon investigation, it was deduced that the medical physicist had not read the patient's SIRS therapy (utilizing Y-90 radioactive isotope) written directive prescription correctly. A higher than intended dosage was administered to the patient (1.66 GBq). The correct dosage that was intended to be administered per the written directive was 1.11 GBq. After calculation was made after the incident it was determined that the intended dose to the liver was 30.72 Gy and the actual dose to the liver was 45.93 Gy. "Contributing factors to the above error identified by the licensee are as follows: "1. The amount of information presented in the SIRS written directive and the prescribed amount of isotope is hard to discern and is not set apart from all the other numbers presented. "2. The prescribed activity is manually transferred to a secondary worksheet used in Nuclear Medicine to draw the dose to be administered and this secondary activity worksheet is not verified by a secondary party. "The licensee stated that to prevent such an event from occurring in the future, the SIRS written directive document will be modified to display the prescribed activity more predominantly on the form as well as a space for initializing by a secondary party that the prescribed dose has been transferred/entered properly on the secondary activity worksheet that is used in Nuclear Medicine to draw the dose to be administered. "The referring physicians as well as the patient have been or are in the process of being notified of this event. "According to the licensee's Radiation Oncologist and Interventional Radiologist that were asked to consult, this higher dose would slightly increase the patient's risk of radiation-induced liver disease. The patient, as is standard for all SIRS (Y-90) patients, will receive liver function follow-up testing to track her status." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2011-03-24
46682 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2011-03-08 12:30 | 2011-03-18 16:30 | 2011-03-18 | UNPLANNED MEDICAL TREATMENT OF POTENTIALLY CONTAMINATED INDIVIDUAL "A contract employee entered the onsite medical facility with a laceration on his right arm. First aid was administered in preparation for transferring to an offsite medical facility. The employee had spreadable contamination on his clothing (60dpm/100cm2). The employee was decontaminated before leaving the site. The employee received 8 stitches at the offsite medical facility." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2011-03-18
46681 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-18 | 2011-03-18 14:40 | 2011-03-18 | PAINT CHIPS DISCOVERED IN WOODWARD GOVERNORS Woodward governors purchased as nuclear safety related items for use in turbine driven auxiliary feedwater pumps and emergency diesel generators, were found to have paint chips on internal surfaces. These governors were manufactured by Woodward Governor Company, Loveland, CO for use at the McGuire Nuclear Station. The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 21.21 |  |  |  | 0 | 2011-03-18
46680 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2011-03-18 01:45 | 2011-03-18 05:32 | 2011-03-30 | CONTROL ROOM BOUNDARY RENDERED INOPERABLE "On March 17, 2011 during a control room walk-down, it was discovered that a halon bottle located in the control room was removed from its associated piping for scheduled work. The open piping penetrates the control room boundary rendering it inoperable. "Technical Specification 3.7.6.1 'Control Room Emergency Ventilation System' is applicable in Modes 1, 2, 3, 4, 5 and 6 was entered. Since control room boundary was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to mitigate the consequences of an accident. Upon discovery the piping was capped re-establishing the control room boundary. "Further engineering review will be conducted to more fully evaluate the impact on the control room boundary. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D)." Offsite power is normal and all emergency diesel generators are operable. There was no increase in plant risk. The NRC Senior Resident Inspector has been notified. * * * UPDATE AT 1002 EDT ON 03/30/11 FROM WAYNE WOOLERY TO S. SANDIN * * * The Licensee is retracting this report based on the following: "On March 17, 2011 during a control room walk down at Millstone Power Station Unit 2, it was discovered that a halon bottle located in the control room was removed from its associated piping for scheduled work. Since the associated piping penetrates the control room boundary, operators declared the control room boundary inoperable. Upon discovery, the piping was capped re-establishing the control room boundary. "Operators made a report in accordance with 10CFR50.72(b)(3)(v)(D). "Subsequently, an engineering evaluation has been completed that concludes that the piping opening created by the removal of the halon bottle would not have prevented the fulfillment of the safety function to mitigate the consequences of an accident. Therefore, the condition reported in event report 46680 is being retracted. "The NRC Resident Inspector has been notified." Notified R1DO (Powell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-18
46679 | 0 | LIBERTY HOSPITAL |  |  |  |  | 2007-07-01 | 2011-03-17 16:21 | 2011-03-17 | TEN TRITIUM EXIT SIGNS DISCOVERED MISSING On 6/5/2007 during an NRC Inspection, ten (10) tritium exit signs were verified in storage. Approximately one month later in July 2007, the RSO noticed that the signs were gone and assumed that his Director had dispositioned them, i.e., returned them to the manufacturer for disposal. On 3/17/2011 at 0800 CDT, in response to a followup question from an NRC Inspector onsite 3/16/2011, it was determined there was no documentation associated with the transfer or disposal of these signs. The licensee contacted the NRC Inspector who was still in the area and informed her of this situation. The licensee has no information on the manufacturer, activity or serial numbers of the missing exit signs. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-03-17
46678 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-17 12:50 | 2011-03-17 13:58 | 2011-03-17 | OFFSITE NOTIFICATION DUE TO VEHICLE FIRE "Vehicle fire outside the protected area in the owner controlled area. Offsite fire department contacted and responded to site. Fire has been extinguished. Fire was limited to vehicle and no plant equipment was affected. Event had no affect on plant operation." The licensee notified the State of North Carolina, the State of South Carolina, York county, Gaston county, and Mecklenburg county. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-03-17
46677 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2011-03-16 16:47 | 2011-03-17 00:01 | 2011-03-17 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "On 03/16/11, at 1647 [EST], Peach Bottom Atomic Power Station Unit 2 declared the High Pressure Coolant Injection system inoperable for a condition found during testing which could cause the system to malfunction when swapping suction sources. While lined up to the suppression pool suction flow path, unsatisfactory results were obtained while venting for system fill verification, indicating potential voiding of a portion of the pump discharge piping. Unit 2 HPCI remains available while aligned to its normal suction, the condensate storage tank. "This report is being submitted pursuant to 10CFR 50.72(b)(3)(v)(D). "The NRC resident has been informed of this notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-22
46676 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-03-15 11:31 | 2011-03-15 17:38 | 2011-03-15 | LOSS OF POWER TO TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "On 03/15/2011 at 1131 EDT, the Technical Support Center (TSC) ventilation system was rendered nonfunctional as a result of loss of power to the system. System power was lost approximately one hour after returning the normal power supply to service following maintenance. This condition has the potential to render the TSC unavailable due to the inability of the ventilation and filtration system to maintain a habitable atmosphere. Compensatory measures exist to relocate the TSC to alternate locations. "On 03/15/2011 at 1545 EDT, after verifying the bus supplying the TSC ventilation was satisfactory for return to service, power was restored using an alternate feed. This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility. "The NRC Senior Resident Inspector was notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-03-15
46675 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2011-01-10 | 2011-03-15 16:43 | 2011-03-15 | DAMAGED FIXED GAUGE SAMPLE WHEEL The following report was received via fax. "Licensee's RSO contacted DRH [Mississippi Department of Radiological Health] by letter to report a malfunction of the sample wheel mechanism in their basis weight fixed gauge (Model No. BWM-H Beta Gauge, Gauge Serial No. 25630138, Source Model No. Amersham Corporation Model SIC.L5, Source Serial No. HW338). The device manufacturer was contacted and a representative removed the original faulty basis weight source head and replaced it with a refurbished unit. The replacement did not function, so the original source head was repaired and reattached. A leak test, survey and inspection were all conducted. As a precaution, the licensee ordered a refurbished source head and the manufacturer's representative came out to replace the original faulty source head. A leak test, survey and inspection were conducted. Leak tests revealed no contamination and surveys were normal." Source: Sr-90, 15 mCi Mississippi Tracking Number: MS-11002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-03-18
46674 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-15 14:56 | 2011-03-15 16:25 | 2011-05-13 | FLOOD BARRIER PENETRATION NOT SEALED "During investigations of flood barrier penetrations, a 4 inch conduit has been identified that is not sealed. This conduit penetrates the South wall of the auxiliary building near the transformers into room 19. Flooding through the penetrations could have impacted the ability of the station's auxiliary feedwater (AFW) pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). "The penetration is at an elevation of 1007'-8". The river level has been less than 995 feet Mean Sea Level (MSL) since prior to December 1, 2010. The AFW pumps are operable. There are not any indications of conditions that might result in a flood. Actions are in progress to plug the penetration." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ERICK MATZKE TO DONG PARK ON 5/13/11 AT 1709 EDT* * * Further investigation has determined that the penetration is adequately sealed inside of the affected structure. Therefore this notification is being retracted. The licensee will notify the NRC Resident Inspector. Notified R4DO (Walker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-03-15
46673 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2011-03-14 13:11 | 2011-03-15 15:16 | 2011-03-15 | ADDITIONAL DELAMINATED CONTAINMENT CONCRETE DISCOVERED "Crystal River Unit 3 is currently shutdown. Final tendon re-tensioning activities were being conducted following repair of delaminated (separated) concrete at the periphery of the containment wall. At approximately 1311 [EDT] on March 14, 2011, an indication was received from acoustic monitoring instrumentation located on the containment wall outside the previously repaired area. Re-tensioning activities were stopped and Plant Operations verified that there were no changes in plant parameters. Non-destructive examinations were initiated and preliminary indications are that there is delaminated concrete in the area identified by the acoustic monitoring. An assessment concluded that the containment continues to maintain the closure-pressure retaining capability required for Mode 5. There continues to be no threat to the public heath and safety. "Delaminated concrete at the periphery of the containment wall was created in late 2009 during the process of creating an opening in the structure to remove and replace the steam generators inside (Reference Event Report 45416). The unit was already shut down for refueling and maintenance at the time the damage was found and has remained shut down." The extent of newly discovered delaminated has not yet been determined. The licensee plans to make a press release. The licensee has notified the NRC Resident Inspector and the Florida Public Service Commission. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2011-03-15
46672 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2011-03-13 | 2011-03-14 23:01 | 2011-03-15 | AGREEMENT STATE REPORT - NUCLEAR GAUGES RECOVERED FROM OIL RIG FIRE North Dakota Department of Health (NDDH) notified the NRC of two nuclear gauges affected by a fire at an oil rig in Mckenzie County, North Dakota. The fire is out and one gauge has been retrieved with the shield intact with no unusual radiation readings. The second gauge has also been retrieved. There is no damage apparent to the second gauge except for some shifting of the lead shielding around the gauge. There was no unusual radiation levels, exposure or contamination impact to personnel. The gauges are Thermo-Fisher Scientific, model 5192. Arrangements are being made to ship both gauges to the manufacture for inspection and repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2011-03-17
46671 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-03-14 14:30 | 2011-03-14 16:09 | 2011-03-14 | EXTENT OF CONDITION REVIEW REVEALS A POTENTIAL VULNERABILITY Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures were not employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-03-14
46670 | 0 | STATE OF FLORIDA |  |  |  |  | 2011-03-09 | 2011-03-14 10:53 | 2011-03-14 | AGREEMENT STATE - DOSE MORE THAN PRESCRIBED "This information was provided by Danny Ray Jisha, Incident Investigator, Texas Department of State Health Services (DSHS). Two patients identified to have been over dosed with Phosporus-32 (P-32). The first patient received 565 Gy where 300 Gy was prescribed, and the second patient received 507 Gy where 200 Gy was prescribed. It is suspected that Anazaohealth Corporation [Florida] supplied incorrect concentrations/doses of P-32. The Tampa, Florida Inspection Office will investigate." The over dose took place at the University of Texas Southwestern Medical Center, Dallas, Texas, however the cause appears to be due to improper labeling of the dose material at Anazaohealth Corporation in Tampa, Florida. This event is being investigated by the State of Florida, Florida Incident # FL11-020, and the State of Texas. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | HOS | [5 empty] | 0 | 2011-03-20
46669 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-03-10 09:15 | 2011-03-11 08:15 | 2011-03-11 | MALFUNCTIONING VALVE LEADS TO A LOSS OF DEFENSE IN DEPTH "During a performance of temporary operating procedure on a laser optical device, it was identified that one of two valves used to isolate the device failed to operate. The valves are operated as a pair and the valves are redundant to provide defense in depth. One valve shut as expected. The second valve did not shut. "The valves are identified as an Item Relied on For Safety (IROFS). The system was not operating and one of the valves operated as designed. No unsafe condition existed. "Operability of both valves is required to meet the performance requirements of 10CFR70.61. "This event is being reported pursuant to the requirements of 10CFR70 Appendix A(b)(2) within 24 hours. The affected device will remain shutdown pending further investigation and implementation of associated corrective actions. "[This event is of] low safety significance - the discovery did not result in an unsafe condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2011-03-11
46668 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-11 01:23 | 2011-03-11 04:40 | 2011-03-11 | NOTICE OF UNUSUAL EVENT AS A RESULT OF A TSUNAMI WARNING IN THE AREA The licensee declared a notice of unusual event as a result of a tsunami warning issued for the coastal areas of California. The tsunami warning is a result of a 8.9 magnitude earthquake off the coast of Japan. The licensee is in EAL HU1.5, 'Tsunami Affecting the Protected Area.' The NRC remains in the normal response mode. The NRC Resident Inspector has been notified. * * * UPDATE AT 1134 EST ON 3/11/2011 FROM MIKE QUITTER TO JOE O'HARA * * * "A classification of unusual event was declared at 0123 PST on March 11, 2011 due to a tsunami warning issued by the NOAA for the California West Coast. Diablo Canyon Power Plant [DCPP] has implemented the requirements of Casualty Procedure M-5, 'Response to Tsunami Warning.' Plant personnel were evacuated from the DCPP intake structure at 0742 PST. Evacuation of personnel from the intake structure constitutes a deviation from DCPP license condition '2.E' and authorized pursuant to 10CFR50.54(x). "No damage or injuries has been observed as a result of this tsunami event and there is no impact on the health and safety of the general public." Notified the R4DO (Farnholtz), R4RA (Collins), IRD (Marshall), and NRR (Grobe). * * * UPDATE AT 1843 EST ON 3/11/2011 FROM JOHN BECERRA TO MARK ABRAMOVITZ * * * Diablo Canyon has terminated their Unusual Event at 1528 PST because the tsunami warning has been reduced to a tsunami advisory. No damage occurred during this event. Notified the R4DO (Farnholtz), IRD (Gott), NRR (Galloway), DHS (Gates), and FEMA (O'Connell) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-03-11
46667 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-03-10 20:15 | 2011-03-11 02:32 | 2011-03-11 | LOSS OF PRIMARY AND BACKUP METEROLOGICAL MONITORING EQUIPMENT ON BOTH TOWERS "Loss of power to radiological monitoring equipment (primary and backup). This constitutes a major loss of emergency assessment capability per Nine Mile Point procedures. The cause of the loss of monitoring equipment is a downed 13.2 kV power line. Monitoring capability was restored at 0100." The loss of power was caused by high winds, and the grid operator was able to restore power at 0100 EST. The NRC Resident Inspector has been notified. | 91 | 100 | 0 | 91 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-03-11
46666 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-03-10 15:49 | 2011-03-10 18:29 | 2011-03-10 | INADVERTANT OPENING A SUBSTATION BREAKER CAUSING LOSS OF STATION POWER "At 1549 on 03/10/2011 with the plant shut down and the reactor defueled, power was lost to Safeguards 4160 Volt Bus 6. Diesel Generator B started and re-energized Bus 6. "At the time of the event, Bus 6 was energized from the Main Auxiliary Transformer (MAT) on backfeed. The event was caused by opening of substation breaker TA2066 as the result of an error by technicians working In the substation. "All equipment operated as expected for the voltage restoration to Safeguards Bus 6. Safeguards Bus 5 remained energized from offsite power through the Tertiary Auxiliary Transformer during the event. "Spent Fuel Pool Cooling Train A remained In operation during the event. Spent Fuel Cooling Train B was restarted following restoration of power to Bus 6. "The loss of the MAT also resulted in the loss of non-safeguards 4160 V Buses 1-4. In response to the loss of power to Bus 4, the Technical Support Center (TSC) / Station Blackout (SBO) Diesel started and failed to load onto 480 Volt Bus 46. This resulted in a loss of power to the Technical Support Center. The loss of power to the TSC is being reported as a loss of Emergency Assessment Capability. At 1632, the TSC/SBO Diesel Generator tripped due to the failure of the output breaker to close and provide power to its support equipment. The cause of the failure of the TSC/SBO output breaker to close is unknown at this time." The licensee is investigating the cause of the breaker being opened and failure of the TSC/SBO diesel to load. One Spent Fuel Pool cooling train was in service throughout the event and no pool heatup occurred. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  |  | 0 | 2011-03-10
46665 | 0 | UNIVERSITY OF MICHIGAN HOSPITAL |  |  |  |  | 2011-03-09 10:00 | 2011-03-10 11:15 | 2011-03-10 | MEDICAL EVENT INVOLVING ADMINISTRATION OF GREATER THAN ORDERED DOSE "An Authorized User physician from the University of Michigan Department of Radiation Oncology planned two liver infusion treatments for a patient with unresectable hepatocellular carcinoma using Y-90 Theraspheres. As part of treatment preparation, an MRI was performed on the patient to determine the patient's liver segment volumes. Liver segment volumes are used in calculating the Y-90 activity needed to deliver the prescribed radiation dose to particular segments of the liver. The first treatment was to the right lobe and medial segment of the patient's liver and was performed on 12/15/2010. It proceeded without incident and in accordance with the written directive. "The Authorized User physician scheduled a second separate treatment to the patient's left lobe to be performed on 3/9/2011. The Authorized User ordered a 74.4 Gy dose to the left lobe of the liver. The medical physicist calculated a corresponding dosage of 60.5 mCi of Y-90 to be infused into the left lobe of the liver. "However, in arriving at the Y-90 activity needed, a medical physicist used the liver segment volumes for the right lobe and medial segment combined instead of that for the left lobe. The volume of the right lobe and medial segment is much larger than that for the left lobe. As a result, the Y-90 dosage of 60.5 mCi exceeded what was actually needed to deliver the prescribed dose of 74.4 Gy. The Y-90 was infused into to the left lobe on 3/9/2011 at approximately 10 [EST]. Based on the Authorized User's reassessment of the left lobe volume, the dose to the left lobe is calculated, post-administration, to be 159.4 Gy. "The patient was notified of the event on 3/9/2011. The referring physician was also notified on the morning of 3/10/2011. The Authorized User physician has concluded that the elevated radiation dose to the patient's liver will not result in permanent medical damage or loss of function. Upon initial investigation this event appears to possibly be due to a problem in transcription however causes and corrective actions are still being evaluated." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2011-03-16
46664 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-09 10:55 | 2011-03-09 11:20 | 2011-03-14 | FITNESS FOR DUTY A non-licensed employee failed to meet fitness-for-duty criteria. The employee's access to the plant has been terminated. Contact the NRC Headquarters Operations Officer for additional details. * * * UPDATE FROM MARK S. MCNEELY TO JOHN SHOEMAKER AT 1025 EST ON 03/14/11 * * * An update to this report has been provided by the licensee. Contact the NRC Headquarters Operations Officer for additional details. Notified R2DO Nease) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2011-03-09
46663 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-03-08 | 2011-03-08 10:18 | 2011-03-08 | GNF PROCEDURE 40-32 LOSS OF A SINGLE MATERIAL CONTROL TRANSACTION "At approximately 7:00 a.m. on Monday, March 7th, it was reported that a can of powder was present on a conveyor in the UO2 press feed area without the required material control transaction. At approximately 10:10 a.m. it was discovered that the can contained three vacuum bags of powder. The transaction is one criticality control for the conveyor to ensure only authorized dry materials are stored. "The second controlled parameter (mass of uranium in each can) was maintained at all times. As a result, no unsafe condition existed. The total amount of UO2 powder in the improperly stored can was approximately 13.6 kg. The material control transactions have been properly performed and the can has been transferred to an approved storage location. "As a result, SNM movements have been ceased pending investigation and implementation of additional corrective actions." The licensee has notified the NRC Resident (Thomas), New Hanover County Emergency Management, and North Carolina of Environment and Natural Resources. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2011-03-08
46662 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-03-08 03:57 | 2011-03-08 07:28 | 2011-03-08 | ONSITE FATALITY "At 0357 [EST on 3/8/11] the licensee received a call for medical assistance. The caller reported an individual [contract employee] had passed out but was still breathing. Our [McGuire] onsite medical response team reported the person was not breathing and in cardiac arrest. The person was transported offsite via ambulance [Gileade Volunteer Fire and Rescue] to the local hospital. At 0602 EST, the licensee received word that the individual had passed away at the hospital." The licensee will notify the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-03-08
46661 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2011-03-07 01:40 | 2011-03-07 10:31 | 2011-03-09 | INADVERTANT AUTO-START SIGNAL TO THE 1B DIESEL GENERATOR DURING TESTING "Farley Unit One was conducting FNP-1-STP-80.8, [test procedure for] 1B DG [Diesel Generator] 1000 KW load rejection. After successfully completing the load rejection portion of the procedure, the control room staff was restoring the 1B diesel to a normal auto start alignment. With the 1B diesel running, the plant operator was required to reset the 1B DG loading sequencer. He incorrectly pressed the Emergency Start reset push-button instead of the Sequencer reset push-button. As a result, the Emergency Diesel generator stop light illuminated for a brief few seconds and then extinguished. Subsequently due to the test configuration, the 1B diesel received an auto-start signal and returned to the running condition prior to the Emergency Start reset. Although further investigation is continuing, this report is being made due to an apparent valid actuation of ESF equipment." This event had no impact on other equipment or the plant electrical alignment. The Sequencer reset push-button and the Emergency Start reset push-button are not in close proximity to each other. The plant operator was assessed for fatigue and it was determined that fatigue was not a factor. The plant operator was removed from duties pending remedial training and assessment. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM STEVE GATES TO JOE O'HARA AT 1342 ON 03/09/11 * * * "The 8-hour non-emergency report (EN #46661) per 10CFR50.72(b)(3)(iv)(A) was conservatively reported based on the potential for a valid actuation of an Emergency Diesel Generator (EDG) during a 1000 KW load rejection surveillance test. "During the restoration phase of the load rejection test to align the 1B EDG to a normal shutdown configuration, a plant operator incorrectly pressed the Emergency Start Reset (ESR) push-button instead of the Sequencer Reset push-button. As a result, the 1B EDG stop light illuminated momentarily and then extinguished. The 1B EDG received a momentary shutdown signal, but remained in a running condition. "Upon completion of the 1B EDG circuit analysis, It was determined that the 1B EDG did not receive a valid actuation of the EDG safety function. Depressing the ESR push-button caused the emergency start relays to deenergize and remain de-energized. The emergency start relays energize on receipt of valid signals in response to actual plant conditions or parameters satisfying the requirements for the initiation of the safety function of the EDG. Therefore per section 3.2.6 of NUREG-1022, the 1B EDG did not receive a valid actuation signal." The NRC Resident Inspector has been notified. Notified R2DO(Musser) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-03-07
46660 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2011-03-06 16:44 | 2011-03-06 19:38 | 2011-03-06 | MANUAL REACTOR TRIP DUE TO SECONDARY SODIUM CONCENTRATIONS EXCEEDING CHEMISTRY LIMITS "This is a 4-hr Non-Emergency notification to the NRCOC [Nuclear Regulatory Commission Operations Center] for an event that results in actuation of the Reactor Protection System (RPS) when the reactor is critical in accordance with 10CFR50.72(b)(2)(iv)(B). "On 3/6/11 at approx 16:20 [EST], Steam Generator sodium concentrations started to rise and exceeded 3-ONOP-071.1 (Secondary Chemistry Deviation from limits) Action Level 3 criteria (250 ppb Sodium). The plant power was reduced to 25% per 3-ONOP-100, Fast Load Reduction, and a manual plant trip [was] initiated per procedure at 16:44 [EST]. Unit [3] is stabilized in Mode 3, and [the licensee] is performing secondary clean-up." All rods fully inserted. All safety systems functioned as required. The reactor trip was uncomplicated. Unit 4 was unaffected by this event. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-03-06
46659 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-03-05 23:15 | 2011-03-06 01:51 | 2011-03-06 | SPURIOUS SIREN ACTIVIATION "The purpose of this report is to provide a telephone notification under 10 CFR 50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of one Oswego County emergency notification siren at approximately 2315 EST on 3/5/11. Initial notification to the JFA [James A. Fitzpatrick] Control Room of the siren activation was via on-site security personnel and verified with Oswego County 911 Center. The faulted siren was alarming intermittently and repair personnel were dispatched to correct the problem. At 0107 EST, power to the affected siren was de-energized by off-site repair personnel. "Sirens affected provide coverage to Oswego County. The sirens are utility owned and shared with the Nine Mile Point site. "In the event the sirens are needed the county has it's Hyper-Reach (911 call back system) on standby. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-03-06
46658 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-03-05 23:15 | 2011-03-06 01:37 | 2011-03-06 | SPURIOUS SIREN ACTIVATION "One of the 37 Prompt Notification System sirens surrounding the James A. Fitzpatrick (JAF)/Nine Mile Point (NMP) sites spuriously activated at 2315 EST. "The Oswego County 911 Center notified the Nine Mile Point Emergency Preparedness Department of the inadvertent siren activation. "Repair technicians have de-activated and silenced the faulty siren as of 0107 EST. "The cause of the inadvertent siren activation is not understood at this time. The issue has been entered into the site's Corrective Action Program." The licensee has notified the NRC Resident Inspector, the Oswego County 911 Center, and the Public Service Commission. | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-03-06
46657 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-03-05 10:45 | 2011-03-05 13:04 | 2011-03-05 | OFFSITE NOTIFICATION RELATED TO FISH KILL "At 1045 the Monticello Nuclear Generating Plant (MNGP) control room was notified by an Xcel Energy environmental specialist that a fish kill count was conducted on the morning of 3/5/11 following reactor shutdown. In accordance with the MNGP water appropriations permit for fish kill in the Mississippi river, the environmental specialist will be notifying the State of Minnesota Department of Natural Resources and Minnesota Pollution Control Agency. "Notifications made to above government agencies meet the reporting criteria established in 10CFR50.72(b)(2)(xi) as an event or situation related to the protection of the environment for which a notification to government agencies has been or will be made. "Total fish kill was determined to be approximately 100 fish downstream of the plant's discharge canal. Fish kill was the result of cooldown of water being discharged to the river from the plant's discharge canal. All temperature limits specified in the plant's water appropriation permit were met throughout the shutdown. There was no release of any chemical or radioactive materials to the environment." The licensee has notified the NRC Resident Inspector and will be notifying appropriate state and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-03-05
46656 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2011-01-03 15:15 | 2011-03-04 16:24 | 2011-03-04 | 60 DAY TELEPHONE NOTIFICATON CONCERNING INVALID CONTAINMENT ISOLATION SYSTEM ACTUATIONS "This 60-day telephone notification is being made under the reporting requirements specified by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50. 73(a)(1) to report four closely-spaced invalid actuations of general containment isolation signals affecting more than one system. "Four events of unplanned actuations of general containment isolation signals affecting containment Isolation valves in more than one system occurred during planned transfers of power between the normal and alternate power supply for the 3A 480V Shutdown Board. The first event occurred on January 3, 2011, at 1515 hours Central Standard Time (CST), with Unit 3 in a forced outage and at 0 percent power (0 MWT). The electrical power to the 3A Reactor Protection System (RPS) was interrupted during the planned transfer of the 3A 480V Shutdown Board from its normal supply to its alternate power supply. During the transfer, the alternate feeder breaker did not close. An attempt was made to return to the normal power supply; however, the normal feeder breaker did not initially close but did close on re-attempt. This resulted in the interruption of power to the 3A 480V Shutdown Board, which caused the 3A RPS to de-energize, resulting in a half scram and the actuation of Primary Containment Isolation System (PCIS) logic Groups 2, 3, 6, and 8, and the initiation of Trains A, B, and C Standby Gas Treatment and Train A Control Room Emergency Ventilation. "Plant conditions, which require PCIS actuations and the associated system initiations (e.g., low reactor water level, high drywell pressure, abnormal area radiation level, or high area temperature), did not exist; therefore, the actuation was invalid. The affected equipment responded as designed. "On January 3, 2011, at approximately 1620 hours CST, Unit 3 Operations personnel restored 3A RPS power and re-aligned affected equipment, as appropriate. This event was entered in the Corrective Action Program as Problem Evaluation Report (PER) 305070. "Subsequent related failure to transfer events of the 3A 480V Shutdown Board occurred on January 4, 2011, at 2321 hours, on January 5, 2011, at 0448 hours, and on January 5, 2011, at 0841 hours. In each event the plant conditions which require PCIS actuations and the associated system initiation did not exist; therefore, the actuations were invalid. In each of the three subsequent events the affected equipment started and functioned successfully with one exception. During the last event, Main Control Room indication of a Secondary Containment outboard isolation damper closure was indeterminate (i.e., double-lit). The damper was declared inoperable, and the associated Technical Specification LCO 3.6.4.2 Action was taken. [A} work order [was] issued to investigate the problem repaired a damper limit switch. This problem was entered in the Corrective Action Program as PER 305062. "PERs were generated for each of these events (PER 305865, PER 305421, and PER 305893). All of these events were consolidated into PER 305070. "The Browns Ferry NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-03-04
46655 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2011-02-25 | 2011-03-04 12:53 | 2011-03-04 | PART 21 - ERROR IN VALVE BODY DRAWING The purpose of this Fisher Information Notice (FIN) is to alert Duke Energy that as of February 25, 2011, Fisher Controls International LLC became aware of the possibility of a situation which may affect the performance of the applicable equipment provided to McGuire Nuclear Station. Specifically, an error was discovered on valve body drawing V112298, when, during a revision process on Revision B of the drawing, a dimension was omitted that set the depth of the valve shaft bearing bore. This error resulted in a greater possible variation of bearing position in the valve shaft bore. If the error was large, the valve could not be assembled which was not the case for these valves. The valves assembled without incident and passed the operational testing, including a seat leakage test, with no anomalies. In the case that the bearing position error was slight, it is possible that the seal and disc could experience more wear than normal and increased leakage would result. Because these valves are equipped with manual operators, Fisher expects that these valves will not be cycled enough to experience any of the potential problems described above. This equipment included NPS 4, Class 150, Fisher Type A11 Butterfly Valve Assemblies equipped with Fisher Leverlock Manual Actuators. The NPS 4, A11 is a butterfly valve that uses internal bearings (located on either side of the disc) to provide a radial wear surface for shaft rotation and also serve as a centering system for the disc in the waterway. Centering of the disc is accomplished with a wear surface on the end of the bearings adjacent to the side of the disc. Lateral positioning of the disc is accomplished by controlling the length of the bearings and the depth of the bored holes in the body that accept the bearings. Fisher has revised the drawings to ensure that this issue is corrected. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2011-03-04
46654 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-03-03 22:59 | 2011-03-03 23:27 | 2011-03-03 | TECHNCIAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE HPCI At 2259 EST, Susquehanna Unit 1 commenced a TS Required shutdown for High Pressure Coolant Injection (HPCI) T.S. 3.5.1. Due to a suspected steam leak, the HPCI Inboard Steam Supply Valve HV155F002 was closed to attempt to identify and isolate an unknown drywell leakage condition. After closing the HV155F002, a detectable change in drywell leak rate occurred, therefore, HV155F002 was left closed. Closing HV155F002 makes HPCI INOP and UNAVAILABLE. TS 3.5.1 was entered for this condition on 2/25/2011 at 2136 EST. LCO completion time for T.S. 3.5.1 entry is 3/11/2011 at 2136 EST. The licensee has notified the NRC Resident Inspector and State authorities. The licensee also anticipates issuing a press release. | 86 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-03-03
46653 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2011-03-03 13:53 | 2011-03-03 20:11 | 2011-03-03 | TEMPORARY LOSS OF EMERGENCY FEEDWATER TRAINS "While testing fire detection systems, a radio was keyed in the vicinity of the Auxiliary Shutdown Panel. Control Room alarms that occurred at the same time led to a review of plant data. This review revealed two momentary events (approximately 8 and 19 seconds) over an approximate two minute period that caused momentary reductions in the control signals to the Auxiliary Feedwater Pump and Motor-Driven Feedwater Pump discharge control valves. These momentary signal reductions resulted in all trains of Emergency Feedwater being inoperable for approximately two minutes, pending further evaluation. "With all trains of Emergency Feedwater inoperable, this event is being reported in accordance with 10 CFR 50.72(b)(3)(v) as a momentary loss of safety function for equipment needed to (A) shut down the reactor and maintain it in a safe shutdown condition and to (B) remove residual heat. "Fire detection testing has been completed, and a sign placed on the Auxiliary Shutdown Panel Room door stating that no radio usage is permitted inside the room." All trains of Emergency Feedwater are now operable. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2011-03-03
46652 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-03-03 | 2011-03-03 16:35 | 2011-04-28 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS INTO PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1400 EDT ON 4/28/11 FROM GEORGE ROBERTSON TO S. SANDIN * * * The licensee is retracting this report after further assessment and has informed the NRC Resident Inspector. Notified R2DO (Seymour) and 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-03-03
46651 | -1 | DEFENSE LOGISTICS AGENCY |  |  |  |  | 2011-03-01 | 2011-03-02 15:20 | 2011-03-07 | LOST CHEMICAL DETECTION EQUIPMENT CONTAINING NI-63 SOURCES "As part of a mass turn in of Chemical Detection Equipment (CDE) containing radioactive sources, an Air Force (AF) unit located in Fort Leonard Wood, MO. reported that it had shipped 52 CDE systems, each containing Ni-63 with 20 milli Curie sources, to the Defense Logistics Agency (DLA) Distribution Center at Red River Texas. The CDE systems were shipped in 7 separate packages and confirmation of 7 separate packages was provided which showed the receipt by DLA on 21 May 2010. An inventory, conducted on 2 February 2011, of the 7 packages at the DLA Distribution Center could only account for 40 of the 52 CDE systems. The AF Radiation Safety Office contacted the DLA Radiation Safety Office indicating that there was a discrepancy in the number of items receipted compared to the number of items identified as shipped by the unit. The AF Radiation Safety Office provided the list of serial numbers for the 52 items reportedly shipped which were compared to the current inventory on hand. It was confirmed that there were 12 serial numbers identified on the shipping list that were not in the current inventory. An initial search of the designated Radioactive Material Storage area did not locate the items. "It has been identified that a major issue with the turn-in process was the lack of prior notification of transfer of the CDE from the AF units to the DLA Distribution Site at Red River. A global instruction was provided by the AF PM to ship the material, without the PM providing the turn-in documents. Had the AF PM directed all of the shipment, a document would have been generated and the number of items to be shipped would have been provided to the depot. In the current process, the depot could only act reactively based on available material and paperwork. "The transfer of CDE systems to the DLA Distribution Centers has been suspended until a more accountable process can be determined. Additionally the AF will, in the future, direct all shipments directly to Wright Patterson AFB for demilitarization and disposal. A continued effort to search the hazardous material warehouses for these items will continue." * * * RETRACTION FROM DAVID COLLINS TO JOE O'HARA AT 1642 ON 03/07/11 * * * "DLA Distribution is retracting the initial report of potential loss (Event # 46651) as the 12 Chemical Agent Detectors have been accounted for at Pine Bluff Arsenal, another Department of Defense facility and the ultimate destruction site. The materiel was shipped from DLA Distribution Red River to Pine Bluff Arsenal on October 8, 2010, under a different NSN [National Stock Number] than the one originally sent to DLA. The Chemical Agent Detection (CDE) Equipment can be in multiple configurations, each with their own NSN. In this case they shipped from the AF unit under one NSN (entire detection system) and we subsequently shipped under a corrected NSN (detector component only)." Notified R1DO(Hansell), R4DO(Farnholtz), FSME(Reis), Mexico, and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-03-02
46650 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2011-03-01 15:00 | 2011-03-02 11:10 | 2011-03-02 | FAILURE TO MAINTAIN MASS CONTROL OF UO2 POWDER "At approximately 3:00 pm [EST] on Tuesday, March 1st, it was reported that 15.3kg of UO2 powder was removed from the UO2 Sinter Test Grinding Station [High Efficiency Particulate Air] HEPA filter housing transition. This clean-out was performed as a response to routine radiological surveys that indicated the presence of uranium. It was determined that this material was present during prior filter replacement in early February in which 30.9 kg of UO2 powder was removed. The total amount of UO2 powder present in the housing was therefore approximately 46 kg, which is greater than a safe mass. "The Sinter Test Grinding Station and associated equipment was already shut down because of the HEPA filter housing clean-out and remained down pending investigation and implementation of corrective actions. "Failure to maintain mass control resulted in a loss of double contingency for the filter housing. The double contingency controls required include (1) mass control and (2) moderation control. Moderation control, the 2nd leg of double contingency remained in place, was effective, and was not challenged. As a result, no unsafe condition existed. "The UO2 in the HEPA housing was transferred into [a] favorable geometry [of] 3-gallon cans per procedure. An investigation is ongoing. "At no time did an unsafe condition exist as the moderation control was in place, was effective, and was not challenged. Immediate corrective actions [are] complete [transfer of material into 3-gallons cans]. Investigation of [the] event and implementation of long term corrective actions [are] pending. The licensee will be notifying the NRC Region II, State, and Local Authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2011-03-02
46649 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2011-03-01 11:00 | 2011-03-01 12:54 | 2011-03-01 | EMERGENCY DIESEL GENERATORS START ON A LOSS OF POWER FROM 138 KV CIRCUIT "At 1100 EST, Indian Point Unit 2 experienced a loss of offsite power from the 138 Kv circuit. All three Emergency Diesel Generators automatically started as required. All other plant systems functioned as required. Restoration of offsite power from the 13.8 Kv offsite circuit is in progress. Investigation into the loss of the 138 Kv circuit is ongoing. Indian Point, Unit 2 continues in Mode 1 at 100 % power." Indian Point, Unit 2 is in a 72 hour LCO due to a loss of 1 of 2 offsite circuits. Unit 3 was not affected. The licensee has notified the NRC Resident Inspector and will be notifying the Public Service Commission of the State of New York. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-03-01
46648 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-02-22 | 2011-02-28 12:14 | 2011-02-28 | AGREEMENT STATE REPORT - STATIC ELIMINATOR SOURCE SEAL INTEGRITY LOST "The following report was received by the Iowa Department of Public Health (IDPH) on February 23, 2011. On February 22, 2011, the University of Iowa Environmental Health and Safety (EHS) staff discovered evidence that a Nickel-63 foil in a custom made static eliminator had lost its seal integrity. The source in question consists of two 8.951 mCi Ni-63 foils that are housed in a custom built static eliminator (2 inch diameter steel pipe with the foils glued to the walls of the pipe). The static eliminator is attached to a chamber apparatus located in a fume hood within a principal investigator's lab. The results of the leak test indicated approximately 40,203 dpm (0.0181 uCi's) of activity on a wipe taken of several areas in the apparatus housing the Ni-63 foils. EHS personnel bagged the static eliminator and returned it to EHS for disposal. The two Ni-63 sources were purchased from DuPont/Merck in March of 1995. The Principle Investigator (PI) had been conducting research using these sources since that time. The University RSO reports that the PI does not have any more of these custom devices and will be pursuing other options for research. A previous leaking Ni-63 foil was reported as NMED Item Number 100592." Iowa Incident No. 110002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-03-03
46647 | 0 | TYCO ELECTRONICS |  |  |  |  | 2011-02-28 | 2011-02-28 10:00 | 2011-02-28 | PART 21 REPORT - SPECIFIED RELAYS WITH DEGRADED COILS During the dedication process of nuclear E7000 relays, Tyco Electronics experienced an issue with a component. This component, a coil internal to the relay, failed to operate during quality assurance testing. Tyco purged this lot of coils from their inventory and also from all "work in process." Tyco was able to account for all the coils in this lot of E7000 relays with serial numbers beginning with 1046. Tyco records indicate that some relays shipped to the Exelon/Quad Cities facility were made using this specific coil lot. Tyco sold this safety-related item for specified and unspecified applications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-02-28
46646 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2011-02-27 21:59 | 2011-02-28 03:45 | 2011-02-28 | DEGRADED ACCIDENT MITIGATION DUE TO SAFETY INJECTION OUT OF SERVICE "At 2159 CST on 2/27/2011, during the testing of the 'A' Train Safety Injection System, an Auxiliary Operator in the field identified that the oiler for 2P-15B, 'B' Train Safety Injection Pump, had rotated and the oil had drained out of the oiler. The Auxiliary Operator immediately reported this condition to control room personnel. The 'B' train safety injection pump was declared inoperable and LCO 3.0.3 was entered based upon the condition of both trains of safety injection being out of service. The Unit 2 'A' Train Safety Injection System was being tested in accordance with inservice testing procedure IT-535C, Leakage Reduction and Preventive Maintenance Program Train 'A' HHSI and RHR Piggyback Test Mode 1,5,6 (Refueling) Unit 2, which placed the Unit 2 ECCS in TSAC [Technical Specification Action Condition] 3.5.2.A, One ECCS Train Inoperable. "Unit 2 exited LCO 3.0.3 at 2211 CST, upon completion of the 'A' train inservice test. The 2P-151B safety injection pump remains inoperable in accordance with TSAC 3.5.2.A, One ECCS Train Inoperable for troubleshooting and repair. This condition is reported in accordance with 10 CFR 50.72(b)(3)(v)(D) Accident Mitigation." There was no impact on Unit 1 and the licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-28
46645 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-02-26 09:48 | 2011-02-26 12:16 | 2011-04-21 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "High Pressure Coolant Injection (HPCI) system declared inoperable due to Flow Indicating Controller process value indicating 542 gpm while in standby readiness condition. This condition could impact the system response time in developing flow for events it was credited in mitigating. "HPCI declared inoperable per TS 3.5.1 Condition F which allows 14 days to restore to operable status. "Preliminary cause is air intrusion into instrument sensing lines following pre-planned maintenance where system draining was performed. Troubleshooting is in progress. "All remaining ECCS and RCIC are operable and available. Grid stability has been verified." The NRC senior resident has been notified. * * * RETRACTION AT 1216 ON 4/21/2011 FROM BOB MURRELL TO MARK ABRAMOVITZ * * * "The purpose of this notification is to retract a previous report made on 2/26/2011 at 1216 (EDT) (EN 46645). Notification of the event to the NRC was initially made as a result of declaring High Pressure Coolant Injection (HPCI) system inoperable due to Flow Indicating Controller process value indicating 542 gpm while in standby readiness condition. This condition could have impacted the system response time in developing flow for events it was credited to mitigate. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the HPCI system was capable of performing its safety function. "NextEra concluded that the erroneous Flow Indicator Controller indication was due to air entrainment in the instrument sensing line. A detailed engineering analysis has concluded that the HPCI system was capable of providing design required flow rates with the flow offset. "This event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Senior Resident Inspector has been notified." Tech spec required flow is 2700 gpm. Calculations show that a margin of 600 gpm exists between the tech spec flow rate, and the HPCI automatic flow setpoint, therefore, with an error of 542 gpm, the required flow is met. Notified the R3DO (Phillips). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-26
46644 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-02-25 20:27 | 2011-02-25 23:12 | 2011-02-25 | UNIT 1 HPCI INOPERABLE DUE TO STEAM LEAK "At 2027 EST, Unit 1 HPCI system was declared inoperable due to a steam leak on HV155F002, HPCI Steam Supply Inboard Isolation Valve. Engineering evaluation determined that the valve actuator will not close the valve fully under design basis conditions, due to the impingement of steam from the valve packing region on the valve stem. The penetration flow path has been isolated and the outboard isolation valve has been deactivated. "HPCI is a single train ECCS safety system, This event results in the loss of an entire safety function which requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v) and the guidance provided under NUREG-1022, rev. 2. "There are no other ECCS systems presently out of service." Unit 1 is in a 14 day LCO 3.5.1. EDG's are operable, and offsite power is normal. There is no increase in plant risk, and the licensee will notify the Pennsylvania Emergency Management Agency (PEMA). The NRC Resident Inspector has been notified. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-25
46643 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-02-25 16:15 | 2011-02-25 19:03 | 2011-02-25 | MISSING SHUTTER HANDLE ON BERTHOLD MODEL LB 8010 PORTABLE DENSITY GAUGE On 2/22/11, Trican Well Service was preparing to use the portable gauge at a well jobsite in De Soto Parish, Louisiana when they discovered the gauge was missing its shutter handle. The crew stopped work, took surveys to ensure the shutter was fully closed, and placed the gauge out of service until a repair can be performed. The device is a Berthold Model LB 8010 serial number 10074 portable density gauge used in well servicing operations. The device contains 20 milliCuries of Cs-137, serial number 014808. The crew does not know when the handle became detached. They searched the jobsite for the handle but were unsuccessful in recovering it. The device is in the custody of the licensee. Berthold has been contacted and plans to repair the gauge on March 1, 2011. Texas Incident No. I-8825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-03-02
46642 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-02-19 11:35 | 2011-02-25 16:05 | 2011-02-25 | EMERGENCY OPERATIONS FACILITY (EOF) WITHOUT POWER "Recently obtained information determined that on Saturday February 19, 2011, there was a power loss to the Emergency Operations Facility (EOF) at North Omaha. The power loss lasted from 1135 to 1220 CST. The EOF Building was without power for that time period. The backup generator did not start. There was an electrical line down in the area. "While performing preventive maintenance on the EOF Generator on Wednesday February 23, 2011, the technician determined that the EOF generator would not function. Maintenance personnel were contacted to troubleshoot the generator problem. The battery was determined to be defective and was replaced. The EOF generator was tested satisfactory. "The EOF is required to be activated within one hour when required. The emergency plan does have provisions for an alternate to the EOF if required." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-25
46641 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2011-02-25 09:10 | 2011-02-25 11:48 | 2011-02-25 | MANUAL SCRAM DUE TO RECIRCULATION PUMP TRIP "Limerick Unit 2 was manually scrammed from 100% power on 2/25/11 at 0910 EST in accordance with plant procedure OT-112 'Recirculation Pump Trip', when both the '2A' and '2B' recirculation pumps tripped. Preliminary indication of why the recirculation pumps tripped is due to main generator stator water coolant runback. The cause of the stator water coolant runback is currently under investigation at this time. "All control rods inserted as required. No ECCS or RCIC initiations occurred. No primary or secondary containment isolations occurred. The plant is currently in HOT SHUTDOWN maintaining normal Reactor Water Level with Feedwater in service." Primary plant pressure and temperature is 600 psia and approximately 485 degrees F. All unit safety related equipment is operable and available, if needed. The decay heat path is via turbine bypass valves. There is no affect on Unit 1. The licensee informed Montgomery, Chester, Burks Counties and the Pennsylvania Emergency Management Agency (PEMA). The licensee intends to issue a press release. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-02-25
46640 | 0 | ASCO VALVE |  |  |  |  | 2010-03-18 | 2011-02-25 08:59 | 2011-02-25 | FAILURE OF ACTUATORS DUE TO UNDERSIZED OUTPUT SHAFTS The following is a synopsis of information received via facsimile: On March 18, 2010, Samkwange returned an NH90 Hydramotor to ASCO because the motor was not operating when power was applied. ASCO tested the actuator and found all recorded electrical values to be within specifications, however the output shaft did not have any movement. With the mounting plate removed and the pump activated, it was observed that the shaft was not turning with the rotor. On November 24, 2010, Diablo Canyon Power Plant returned an NH90 Hydramotor to ASCO because the unit was not attaining its full stroke when a signal was applied. The output shaft would start to stroke, but intermittently stopped and the pumping sound ceased. However, normal operating current was noted which indicated that the motor was still running and that a locked rotor condition was not occurring. Further testing revealed that the rotor core was turning on the shaft. In both of the above cases, it was determined that the output shaft was undersized. Corrective Action: All rotor-shaft assemblies in ASCO's inventory as of April 22, 2010 were returned to the supplier to confirm that they met specifications. In addition, a static torque test has been implemented for all rotor-shaft assemblies of all pump assemblies manufactured by ASCO since December 10, 2010. Also, all rotor-shaft assemblies that were in ASCO's inventory as of December 10, 2010 successfully completed the static torque test. Finally a static torque test will be performed on all pump kits in AREVA's inventory before they are supplied to customers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-02-25
46639 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-02-15 16:22 | 2011-02-24 17:25 | 2011-02-24 | PART 21 REPORT - MISALIGNED BELL ALARM SWITCH BRACKETS ON 480 VAC CLASS 1E CIRCUIT BREAKERS "The following event description is based on information currently available. The condition is being reported under 10 CFR 21.21(d)(1). "On February 15, 2011, Palo Verde Nuclear Generating Station (PVNGS) completed an evaluation of prior deviations related to the alignment of bell alarm switches that were installed by the manufacturer Asea Brown Boveri / ITE Imperial Company (ABB) on K-600S 480 VAC Class 1E circuit breakers. Had the breakers been placed into service as received, the misaligned bell alarm switch brackets could have prevented the automatic or remote closure of the breakers installed in safety-related applications. The station concluded the deviations were defects that are reportable per 10 CFR 21. The discussion below provides the technical details that were discovered for the bracket misalignments and the circumstances for the breakers in which this condition was identified. "The ABB K-600S breakers contain a protective indication feature related to the overcurrent trip. An overcurrent trip actuates a reset indicator which moves an armature roller away from the bell alarm switch (ABB part number 706747-T07/BBC) to open the alarm switch contact. The alignment of the bell alarm switch bracket affects the range of contact between the bell alarm switch and the reset indicator armature. This alignment is critical because the vibration of breaker closure can cause the switch and the armature to lose contact momentarily to create an unintended 86 lockout and trip the breaker open during the closure sequence. The breaker will not be able to be reclosed until the 86 lockout and the bell alarm switch have been manually reset. This defeats the safety function of the breaker to provide power to the supported component. "When the condition was identified, the station adjusted the bell alarm switch brackets (ABB part number 709827A00) on the breakers to correct the condition. The breakers were inserted into the intended breaker enclosures after further testing. The breakers were not returned to ABB. "The first condition that was known to have been documented in the corrective action program was discovered during pre-service testing that occurred on November 5, 2009 . The breaker had been refurbished by ABB and was accepted by PVNGS Quality Control Receiving on October 2, 2009. A similar condition occurred on October 21, 2010, on a new breaker that was accepted on June 3, 2010. The untimely evaluation and defect reporting have been entered into PVNGS's corrective action program. "This condition has not resulted in any reportable failures of in-service safety-related breakers under 10 CFR 50.73. The extent of this condition has been evaluated under an operability assessment and corrective actions to inspect potentially affected in-service breakers are in progress . "The manufacturer and refurbisher, ABB, has been notified and since has provided tolerance information and instructions for inspection and adjustment of the bracket alignment . "The use of ABB / ITE K600S breakers is common throughout the industry in nuclear safety-related applications. The station is unaware of which other licensee's use the bell alarm switch to actuate an 86 lockout feature. The station has not provided any of these breakers from its own stock to any other licensee. "The PVNGS reporting officer was notified on February 22, 2011." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 21.21 |  |  |  | 0 | 2011-02-24
46638 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2011-02-24 01:40 | 2011-02-24 15:00 | 2011-02-24 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED CONTRACTOR SUPERVISOR "A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. "The licensee informed the NRC Resident Inspector and Don Funk of NRC Region III." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2011-02-24
46637 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-02-22 14:25 | 2011-02-22 17:10 | 2011-02-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO SERVICE WATER PIPING LEAK "At approximately 1030 hours, the Control Room received notification of a leak in the Unit 3 West Service Water (SW) valve pit of approximately 150 gpm on the SW piping downstream of SW valves SWN-6 and SWN-7. The piping supplies conventional essential SW loads. Abnormal operating procedure 3-AOP-SW-1 (SW Malfunction) was entered due to a report of approximately 3 feet of water in the West valve pit in the area of SW valves SWN-6/SWN-7 and SWN-1111/SWN-1112. Adjustments were made to equipment to reduce the leak and pumps placed in the pit to reduce the pit water level. At 1203 hours, Technical Specification 3.7.9, 'Service Water System' (SWS), Condition E, 'SWS piping and valves inoperable for reasons other than Condition A, B, C or D with no loss of safety function' was entered. "After further assessment of the condition, it was determined at 1425 hours, that the condition would prevent the credited method of isolating the SW loads in the event of cold leg recirculation during a DBA due to inaccessibility to the valve pit for valve operation. This condition constituted a loss of safety function, and the plant entered TS 3.0.3. In accordance with TS 3.0.3, the unit initiated actions to shut down the plant at 1524 hours. This condition meets the reporting criteria of 10 CFR 50.72(b)(2)(i), 'The initiation of any plant shutdown required by the plants TS,' and an event or condition that could have prevented fulfillment of the safety function of structures, or systems that are needed to (D) mitigate the consequences of an accident which is reportable under 10 CFR 50.72(b)(3)(v). Investigations of the condition are in progress." The licensee notified the NRC Resident Inspector. | 0 | 57 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-02-22
46636 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-02-22 11:20 | 2011-02-22 16:10 | 2011-02-22 | OFFSITE NOTIFICATION DUE TO NONCOMPLIANT PARTIAL LAKE BYPASS OPERATION "At 1120 [CST] on February 22, 2011, Dresden Station transitioned to indirect open cycle (Partial Lake Bypass). This was done to control level in the Hot Discharge Canal, which was rising due to a failure of the 2/3 'E' Lift Pump on neutral over current earlier in the day. This is a noncompliance of the NPDES [National Pollution Discharge Elimination System] permit, which does not allow operation in lake bypass except when both units are shutdown. This noncompliance is reportable to the Illinois Environmental Protection Agency. The site representative for the Illinois Emergency Management Agency was also notified." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-22
46635 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2011-02-21 | 2011-02-22 15:09 | 2011-02-22 | AGREEMENT STATE REPORT - PHARMACOLOGICAL PACKAGE WITH SURFACE CONTAMINATION IN EXCESS OF LIMITS The state of Colorado submitted the following information via e-mail: "On 2/21/11, a medical licensee, St. Mary's Hospital in Grand Junction, Colorado (CO License # 14-03), notified the Department that they received a package containing medical isotopes that was externally contaminated in excess of reporting limits. The package originated from NuQuest Pharmacy (CO License # 1022-01) also located in Grand Junction, Colorado. Hospital staff reported that the package, which contained about 50 millicuries of I-131, was intact but had about 1 microcurie of external contamination present. "Hospital staff immediately notified the RSO at NuQuest who was able to contact their driver and perform contamination surveys, which were negative. NuQuest's RSO conducted an investigation and reported that the driver, who also works at the pharmacy as a helper, is a new employee. The RSO believes that the new employee must have forgotten to change his gloves after handling some I-131 waste, and touched the package before it was loaded into the vehicle. "The RSO stated that he provided additional training to the new employee as a corrective action. Also, as a precaution, the RSO plans to perform a thyroid scan to verify that there was no uptake of I-131 by the new employee. No other details are available at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2011-02-25
46634 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2011-02-22 09:09 | 2011-02-22 14:29 | 2011-02-22 | OFFSITE NOTIFICATION DUE TO LOSS OF POTABLE WATER SUPPLY "Arizona Public Service Co. made an offsite notification to the Maricopa County Environmental Services Division at 0909 MST on February 22, 2011, to report a loss of power to the Palo Verde Nuclear Generating Station drinking water supply pumps which resulted in the depressurization of the site domestic water supply header. The pumps were out of service on February 21, 2011, between the hours of 2001 and 2300 MST. Full service has been restored. "The loss of power was related to the loss of Startup Transformer A-E-NAN-X02 as reported in ENS #46633 at 0023 on February 21, 2011. "The NRC Resident Inspectors have been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-22
46633 | 0 | PALO VERDE | 1 |  | 3 | [1] CE,[2] CE,[3] CE | 2011-02-21 20:01 | 2011-02-22 02:23 | 2011-02-22 | AUTO START AND LOAD OF EDGs ON UNITS 1&3 FOLLOWING LOSS OF START-UP TRANSFORMER "On February 21, 2011, at approximately 2001 Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 1 Train 'B' Emergency Diesel Generator (EDG) and Unit 3 Train 'A' Emergency Diesel Generator occurred as a result of undervoltage on their respective safety buses. Both EDGs started and loaded as designed to energize the respective safety buses. No Emergency Plan declaration was made and none was required. "The loss of power to the Unit 1 and Unit 3 safety buses was the result of protective relay actuations on the A-E-NANX02 Startup Transformer which deenergized the transformer and the Unit 1 13.8KV Intermediate Bus 1-E-NAN-S06 and the Unit 3 13.8KV Intermediate Bus 3-E-NAN-SOS. The affected intermediate buses provide power to the Unit 1 safety bus 1-E-PBB-S04 and the Unit 3 safety bus 3-E-PBA-S03 respectively. The Auxiliary Operators responded to inspect the Startup Transformer and affected buses and determined that there was no fire or smoke and no obvious equipment damage to transformers or associated 13.8 KV Buses. At the time of the actuations, the Unit 1 Control Room received alarms for Startup Transformer A-E-NAN-X02 'Phase, Winding Ground Differential Trip'. "Subsequent inspection by the Electricians identified damage to the cabling from the 'Y' winding of A-E-NAN-X02 Start-Up Transformer to the alternate supply breaker on Unit 2 Intermediate Bus 2-E-NAN-SOS. Unit 1 and Unit 3 entered Technical Specification LCO 3.8.1, Condition 'A', for one (of two) required offsite circuits inoperable. Unit 2 currently has the 'B' EDG out of service for a planned maintenance outage and the Unit 2 safety buses and required offsite circuits were unaffected by the Startup Transformer trip. Unit 2 safety buses are being supplied by Startup Transformers A-E-NAN-X01 and A-E-NAN-X03. "Both Unit 1 and Unit 3 were at approximately 100% power, at normal operating temperature and pressure prior to and following the EDG actuations. No other ESF actuations occurred and none were required. No major equipment was inoperable prior to the event that contributed to the event. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been notified of the ESF actuations and this ENS notification." The licensee is working to restore normal electrical power to the affected safety buses from alternate available sources on Startup Transformers X01 and X03. The licensee stated that no significant non-safety related equipment has been deenergized. The licensee noted that while the cause of the damaged cabling noted in the above report is still under investigation, water intrusion repairs were recently conducted near the location where the current damages were found. * * * UPDATE AT 0356 EST ON 2/22/11 FROM ROBINSON TO HUFFMAN * * * The licensee has restored offsite power to the affected safety buses. The Unit 3 safety bus was restored from Startup Transformer X03 at 0106 MST. The Unit 1 safety bus was restored from Startup Transformer X01 at 0153 MST. The EDGs are in the process of being shutdown and reset. The LCO for required offsite power source to the buses has been exited. R4DO (Gaddy) and NRR (Brown) notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation |  | Power Operation | Power Operation |  | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-02-22
46632 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2011-02-20 08:30 | 2011-02-20 22:30 | 2011-02-20 | AGREEMENT STATE REPORT - FLY ASH GAUGE SHUTTER FAILURE The licensee uses industrial fixed gauges for measuring densities in fly ash hoppers. The industrial fixed gauges contain a 50 milliCurie Cesium 137 sealed source. The sources were manufactured and installed by Kay Ray, Inc. While the licensee was performing maintenance on the gauges, the remote source closure mechanism on 3 of the gauges did not operate as designed and the shutter did not close when operated by the handle on the floor. The chain that operates the source shutter mechanism 20 feet above the floor was disconnected which allowed the spring loaded shutter to close. No personnel were exposed to radiation during this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2011-02-23
46631 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-02-20 10:34 | 2011-02-20 17:47 | 2011-02-20 | REACTOR PROTECTION SYSTEM ACTUATION WHILE SHUTDOWN "On Sunday, February 20, 2011, at 1034 EST with the reactor shutdown and all control rods fully inserted a valid Reactor Protection System (RPS) low reactor water initiation signal (+12 inch) was received. The RPS actuation signal resulted in reactor scram and actuation of the Primary Containment Isolation Systems for Group II - Primary Containment Isolation and Reactor Building Isolation System (RBIS), and Group VI - Reactor Water Cleanup System (RWCU). At the time of the event, a controlled reactor shutdown and cooldown was in progress. The Reactor Mode Selector Switch was in 'Startup' and a cooldown was being controlled using the Mechanical Hydraulic Control (MHC) System. Initial event review indicates that the turbine by-pass valve controlling the cooldown closed causing a 'shrink' on indicated reactor water level to briefly lower to +12 inches (lowest observed water level). "Reactor water level was immediately restored, the isolations (Group II and VI) were reset, and the RPS signal was reset at 1135 EST. All systems operated as expected, in accordance with design. "This event had no impact on the health and/or safety of the public. "The US NRC Senior Resident Inspector was in the Main Control Room at the time of the event." The licensee will be notifying the State. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2011-02-20
46630 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2011-02-20 08:53 | 2011-02-20 12:02 | 2011-02-20 | TONE ALERT RADIO EMERGENCY NOTIFICATION SYSTEM OUT OF SERVICE "On Sunday, February 20, 2011, at 1007 EST, James A. Fitzpatrick (JAF) Nuclear Station Shift Manager (SM), John Walkowiak, notified Nine Mile Point [NMP], and NYS Warning Point, via the RECS Line, of a loss of the Tone Alert System for greater than one hour from the National Weather Service as of 0853 [EST]. Site Emergency Procedures define a loss of Tone Alert System for greater than one hour, as a significant loss of Emergency Communications (EPIP-EPP-30). "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the NMP and JAF Nuclear Power Plants. This failure meets NRC 8-Hour reporting criteria 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens, which also function as part of the Public Prompt Notification System, remained operable. "The loss of the Tone Alert System constitutes a significant loss of Emergency Off-Site Communications capability. Compensatory measures were verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper-reach system, which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "As of 1124 hours on February 20, 2011, Nine Mile Point was notified by the Oswego County 911 Center that the Tone Alert System has been returned to service." The licensee has notified the NRC Resident Inspector. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-20
46629 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-02-20 08:53 | 2011-02-20 10:47 | 2011-02-20 | TONE ALERT RADIO EMERGENCY NOTIFICATION SYSTEM OUT OF SERVICE The licensee has been notified by Oswego County Emergency Management that the Tone Alert Radio Emergency Notification System had been out of service since 0853 EST and is still out of service at this time. The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. Compensatory measures have been verified to be available should the Prompt Notification System be needed. The licensee has notified the State and the NRC Resident Inspector. * * * UPDATE FROM JOHN WALKOWIAK TO VINCE KLCO ON 2/20/2011 @ 1228 * * * At 1129 [EST], Fitzpatrick was notified by Oswego County Emergency Management that the Tone Alert Radio Emergency Notification System was restored to service at 1124 [EST] on 2/20/2011. The licensee notified the State and the NRC Resident Inspector. Notified the R1DO (Ferdas). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-20
46628 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-02-20 | 2011-02-20 00:55 | 2011-02-20 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN-REACTOR BUILDING CLOSED COOLING WATER TRAIN INOPERABLE "At 0000 hours on Sunday, February 20, 2011, the Pilgrim Nuclear Power Station (PNPS) commenced a controlled shutdown of the reactor due to the 'B' train of Reactor Building Closed Cooling Water (RBCCW) being declared inoperable at 1250 hours on February 18, 2011 and expected to exceed its 72-hour Limiting Condition for Operability (LCO) as required by TS prior to return to operable status. "With the plant operating at 100% power, leakage of Salt Service Water (SSW) was detected in the RBCCW system due to high chloride levels and increased inventory in the system. An investigation into the event determined that the source of the SSW was isolated to the 'B' RBCCW heat exchanger which is designed to cool RBCCW under normal and post-accident conditions. The quantity of the leakage was determined to exceed the design limits established to ensure post-accident operation of the system and the 'B' train of RBCCW was subsequently declared inoperable. "The leak identification and repair activities are expected to exceed the TS LCO for the RBCCW system and therefore a controlled shutdown of the reactor was initiated. "This event had no impact on the health and/or safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This 4-hour notification is being made in accordance with 10 CFR 50.72 (b)(2)(i)." | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-02-20
46627 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-02-19 19:20 | 2011-02-19 22:24 | 2011-02-19 | OFFSITE NOTIFIECTION DUE TO INADVERTENT CHEMICAL DISCHARGE "At 1920 [EST] on 2-19-11, a chemistry technician notified the Shift Manager that more than the expected amount of Sodium Bisulfite was inadvertently added to the Circulating Water System discharge. The Spill Prevention Control & Countermeasures (SPCC) Plan was referenced for required actions. 17 additional gallons of Sodium Bisulfite was discharged to surface waters of Lake Michigan. This amount of Sodium Bisulfite is less than the reportable quantity of 417 gallons per the SPCC Plan. However, since it was released to surface water (Lake Michigan), a notification to the District Water Quality Division (DWQD) was made at 2020 [EST] by the site's Senior Environmental Specialist (SES). The DWQD requested that additional notifications be made to state (Pollution Emergency Alert System - PEAS) and local (911 operator) agencies. PEAS was notified at 2020 [EST] by the SES and Van Buren County dispatch (911) was notified by the Control Room staff at 2047 [EST]." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-19
46626 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2011-02-19 00:50 | 2011-02-19 06:10 | 2011-02-19 | SAFETY PARAMETER DISPLAY SYSTEM INOPERABLE DUE TO PLANT COMPUTER PROBLEM "At 1650 EST on Friday, February 18, 2011, the Unit 1 Plant Process Computer was taken out of service for a planned outage for pre-modification testing. The Process Computer was successfully restarted at 0040 on Saturday, February 19, and all Computer functions were operational. However, at 0058, the Unit 1 Control Room received the annunciator for the Process Computer trouble. At the same time, all Process Computer displays stopped updating, including Safety Parameter Display System SPDS. "All Control Room panel indicators and annunciators continued to respond properly providing operators with non-computer based emergency assessment capability. An additional Plant Operator was called out in accordance with Technical Specification 6.2.2.a for minimum shift complement with the process computer out of service. "Repairs were completed and the Plant Process Computer was returned to service at 0450 on February 19, 2011." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-19
46625 | -1 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-02-18 10:45 | 2011-02-18 12:16 | 2011-02-24 | UNUSUAL EVENT- EXCESSIVE LEAKAGE FROM A CHARGING SYSTEM At 1045 CST, on 2/18/11, Comanche Peak Unit 1 declared an Unusual Event related to excessive leakage from the charging system. The 40 GPM leakage was in excess of the specified limit of 25 GPM. At 1121 CST, the charging system leakage was verified isolated. Unit 1 is in stable condition and remains at 100% power. No offsite assistance is required at this time. * * * UPDATE FROM TERRY MARSH TO DONG PARK AT 1438 EST ON 2/18/11 * * * "At 1311 EST, Comanche Peak Nuclear Power Plant has terminated the Unusual Event. The leaking valve in the charging system has been isolated reducing the leakage to zero. Repairs to the valve are in planning." The licensee notified the NRC Resident Inspector. The licensee notified the Texas Department of Public Safety and will be making a press release to the local press. Notified R4DO (Gaddy), IRD (Gott), NRR EO (Thorp), DHS (McDonald) and FEMA (Via). * * * RETRACTION FROM RAY FISHENCORD TO JOHN SHOEMAKER AT 0810 EST ON 2/24/11 * * * "This is a follow-up notification to inform the NRC that Comanche Peak Nuclear Power Plant is retracting Event Number 46625, the Unusual Event declaration reported on February 18, 2011 at 10:45 Central Standard Time. "The declaration was made based on EAL SU8.1, [Reactor Coolant System] RCS Leakage, and was terminated on February 18, 2011 at 13:11 Central Standard Time. The declaration is retracted because the source of the leakage was from the Chemical and Volume Control System (CVCS) and not from the Reactor Coolant System." The licensee has notified the NRC Resident Inspector. Notified R4DO (Campbell) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-02-18
46624 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2010-12-29 | 2011-02-18 09:00 | 2011-02-18 | INVALID SYSTEM ACTUATION DUE TO OPERATOR ERROR "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of Emergency Diesel Generator 'A' on 12/29/10 while performing a Diesel Generator shutdown. Emergency AC Electrical Power system including Emergency Diesel Generators is a system named in 50.73(a)(2)(iv)(6). "Emergency Diesel Generator 'A' was coasting down following a normal shutdown in accordance with steps in a routine surveillance test procedure. A manual reset was performed prior to verification that the generator had stopped rolling causing it to return to idle speed and continue to run. A procedure compliance error occurred during the conduct of the test. The control room individual did not request verification that the diesel generator had stopped rolling prior to pushing the reset pushbuttons. This is considered an INVALID signal with respect to 50.73(a)(2)(iv)(A). However the system was not fully removed from service [i.e. the diesel was not considered to be in a testing mode at the time of the event]. The re-start only affected Emergency Diesel Generator 'A'. "Specific information required per NUREG-1022: "a. The specific train(s) and system(s) that were actuated: The specific train(s) .and system(s) was Emergency Diesel Generator 'A'. The 'B' train was not affected by this event. "b. Whether each train actuation was complete or partial: The actuation was considered complete (i.e. all necessary components responded to the reset signal as expected under the actual field conditions). "c. Whether or not the system started and functioned successfully: Emergency Diesel Generator 'A' started and operated successfully until secured by Operations personnel. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-02-18
46623 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2011-02-18 00:51 | 2011-02-18 02:31 | 2011-02-18 | INACTIVE LEAK IDENTIFIED ON PRESURIZER HEATER WELL "During a scheduled VT-2 boric acid examination on the Unit 2 Pressurizer lower level heater penetrations a boric acid leak was identified on heater penetration N-3." The licensee characterized the leak as inactive. The approximate sizes of the round boric acid deposits are 1/32 inch and 1/64 inch. The licensee continues to investigate and plan recovery actions. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2011-02-18
46622 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-02-16 | 2011-02-17 20:16 | 2011-02-17 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE SOURCE The following information was received by email: "On February 16, 2011, RHB [California Radiologic Health Branch] South RM [Radiologic Materials] was contacted by the [licensee] RSO [Radiation Safety Officer] of RMA Group, concerning a loss of the Cs-137 source from a Troxler model 3430 (S/N 25220) moisture density gauge (8 mCi Cs-137, SN 758021, 40 mCi Am:Be-241, SN 4721490). [The licensee RSO] stated that the Troxler gauge was in use at a construction site located at the on/off ramp of Interstate 10 at North Indian Canyon Drive, near Palm Springs in early February (sometime between Feb. 3 and Feb. 8, 2011). [The licensee RSO] stated that operator noticed that the readings taken had dropped significantly from his previous readings and thought that the computer in the gauge had malfunctioned and the gauge was returned to their facility and stored until it was taken in for service at Southwest Calibration and Training LN 7567 (SWCT) on February 14 or 15. On the afternoon of February 16, 2011, [The licensee RSO] was contacted by SWCT that the Cs-137 source pellets were missing due to the cap of the source capsule breaking off at the weld. [The licensee RSO] stated that Troxler service was consulted and that they were informed that this was an issue that had occurred twice previously in the past 6 years and that they had requested that the source rod be returned to them to allow them to determine how the break had occurred. "[The licensee RSO] stated that he had been given a survey meter to be used to attempt to find the source. [The licensee RSO] stated that a survey of the storage area of their Rancho Cucamonga facility (all of the other gauges were out being used at the time) and the vehicle used to transport the gauge when the incident was likely to have occurred and did not find the source. [The licensee RSO] stated that he would attempt to find the sources at the construction site in the morning when he had determined the area that the gauge was in use when the incident occurred. [The licensee RSO] stated that the source may have already been buried under 10 inches of fill (soil) and 8-10 inches of asphalt, but he was not absolutely sure. [The licensee RSO] was informed that a 30 day report was required to be submitted to [the RHB] office. "On February 17, 2011, [RHB] confirmed that the damaged gauge had never had any incidents or trauma that potentially could have resulted in damage to the source capsule and that the construction site was on N. Indian Canyon Drive at one of the on/off ramps to Interstate 10. The results of the search for the missing source and a confirmation of the exact location of the incident will be forwarded to NMED when the RSO has confirmed the information. An investigation into the cause of the damage of the source capsule and possible location of the source capsule is ongoing." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-02-22
46621 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-02-17 15:11 | 2011-02-17 19:07 | 2011-02-17 | OFFSITE NOTIFICATION DUE TO HYDRAZINE SPILL CONTAINED ONSITE "On February 17, 2011, at approximately 1200 PST, noted approximately 70 gallons of diluted 35% hydrazine had spilled fully contained in a bermed area from a chemical holding tank inside the Protected Area and subsequently removed to barrels. "Off-site notifications were made as follows: "National Response Center at 1536 [PST] [NRC REPORT #967808] "Cal-EMA at 1530 [PST] "San Diego Department of Health at 1526 [PST]" The licensee has notified the NRC Resident Inspector. | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-17
46620 | -1 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-02-17 17:46 | 2011-02-17 18:34 | 2011-03-30 | SAFEGUARDS REPORT - SECURITY EVENT POTENTIALLY REDUCING PHYSICAL SECURITY EFFECTIVENESS The licensee discovered a security event potentially reducing physical security effectiveness. Upon discovery, compensatory measures were immediately implemented. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BRAD BISHOP TO DONALD NORWOOD AT 1536 EDT ON 3/30/2011 * * * After review of the circumstances surrounding the 2/17/11 event, St. Lucie is retracting the event notification. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. Notified R2DO(Sykes) and via E-mail, the Part 73.71 Group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-02-17
46619 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-02-17 14:39 | 2011-02-17 17:12 | 2011-02-17 | OFFSITE NOITIFICATION DUE TO AN ALARMING EMERGENCY SIREN "At 1439 [CST], on 2/17/2011, the NextEra Energy Duane Arnold control room was informed that an emergency siren in the Cedar Rapids area was alarming. This information came via the Cedar Rapids Police Department and Linn County Emergency Management Agency who stated that they had been informed that a siren was alarming. "No emergency condition exists at NextEra Energy Duane Arnold and efforts are currently underway to determine if in fact an emergency siren is alarming." The licensee notified the NRC Resident Inspector and the local press. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-17
46618 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2011-02-16 11:25 | 2011-02-16 15:29 | 2011-02-16 | STEAM LEAK ON HIGH PRESSURE COOLANT INJECTION SYSTEM "During system startup of [High Pressure Coolant Injection] HPCI for quarterly surveillance, audible and visual indications of steam leakage were observed. The system was secured and subsequently isolated (with outboard valve de-energized for configuration control). As a result of the steam leakage, a local fire alarm was received in the Control Room. HPCI is currently isolated and will not perform its safety function. "Operators were dispatched to the Reactor Building fire panel to verify that the fire alarm was due solely to the steam leak. As a precautionary measure, personnel were evacuated from the Reactor Building. Operators entered [Off Normal Procedure] ON 3158, Reactor Building High Area Temperature/Water Level, and verified that room temperatures were decreasing after the steam line was isolated. No EOP-4, Secondary Containment Control, entry conditions were exceeded." The steam leak was isolated when HPCI was secured. Associated fire alarms were verified to be caused by the steam leak. There was no impact on other plant equipment or personnel safety. The source of the steam leak is suspected to be from a steam trap but this has not been confirmed. The licensee notified the NRC Resident Inspector and the State of Vermont Department of Public Service Nuclear Engineer. Notified R1DO (Ferdas) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-16
46617 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-02-15 16:30 | 2011-02-15 19:22 | 2011-02-15 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT DUE TO MISADMINISTRATION This is a preliminary report. Details will be provided at a later date. During a general chart review, the licensee discovered that two pediatric patients were administered doses of P-32 albumin that appear to be in excess of 100% of the prescribed doses. The first event occurred approximately four months ago. The second event occurred approximately two months ago. These events may have each provided 1000 Rads excess dose to target tissue. The events may or may not involve a dispensing error. The doses were administered to tissue surrounding extremity joints of the two pediatric patients. Physicians do not expect any patient impact or unfavorable outcome from these misadministration. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-02-21
46616 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-02-15 11:40 | 2011-02-15 17:40 | 2011-02-15 | OFF-SITE NOTIFICATION OF SEWAGE SPILL CONTAINED ON-SITE (<100 GALLONS) "On February 15, 2011, at about 0830 PST, approximately 65 gallons (calculated maximum of 98 gallons) of partially treated sewage spilled on the ground and into a concrete ditch at San Onofre Nuclear Generating Station (SONGS) at the Mesa area while cleaning up from the plant overflow on 2-11-11. The spill was contained, vacuumed up, and returned to the sewage treatment plant. At approximately 1140 PST, Southern California Edison notified the San Diego Regional Water Quality Control Board, and the San Diego County Department of Environmental Health was notified at 1220 PST. "Unit 2 is operating at approximately 100% power and Unit 3 is in Mode 3 after a steam generator replacement and refueling outage." The licensee will notify the Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-15
46615 | 0 | MALLINCKRODT INC. |  |  |  |  | 2011-02-15 10:20 | 2011-02-15 11:30 | 2011-02-15 | MISSING TC-99 GENERATOR The licensee was shipping a 16 Curie MO-99/TC-99 Generator inside a 49 lb depleted uranium cask with an activity level of 8.09 millicuries of U-238 to a customer in Port Huron, Michigan. Shipping documents indicate that the ground courier (Associated Couriers, Inc.) had taken custody of the shipment from the air courier (AirNet) and transported it to its warehouse near Detroit, Michigan. When the ground courier went to make delivery of the device to the customer, the shipment could not be located. The licensee has contacted both the ground courier and air courier as well as the customers along the delivery route in an attempt to find the device. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2011-02-15
46614 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-02-14 09:20 | 2011-02-14 15:12 | 2011-02-14 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2011-02-14
46613 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2011-02-14 07:00 | 2011-02-14 03:09 | 2011-02-14 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the James A. FitzPatrlck (JAF) Nuclear Power Plant will remove the Technical Support Center (TSC) ventilation system from service. Therefore, the TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately 13 hours from 0700 to 2000 today. "If an emergency Is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the station Emergency Plant Manager will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures giving first consideration to the Control Room. TSC facility leads have been made aware of this contingency. "This notification Is being made in accordance 10 CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility (ERF). An update will be provided once the TSC ventilation has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM DAVID RICHARDSON TO DONALD NORWOOD ON 2/14/2011 AT 1922 EST * * * "As of 1839 hours today, the planned maintenance activity on the Technical Support Center (TSC) ventilation system is complete. Post-work testing is complete and the system has been restored to fully functional." The NRC Resident Inspector has been notified. Notified R1DO (Ferdas). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-14
46612 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-02-11 16:15 | 2011-02-11 22:40 | 2011-02-11 | OFFSITE NOTIFICATION OF A SEWAGE SPILL CONTAINED ONSITE The site Environmental Protection (EP) group notified the control room of a 3000 gallon sewage spill from the Mesa Sewage Treatment Plant. The spill overflowed to the storm water catch basin. The EP group notified the San Diego Regional Water Quality Board and the San Diego Department of Environmental Health. All sewage has been contained within the storm water catch basin. EP is currently on station to remediate the sewage spill. No sewage has been discharged offsite. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-11
46611 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2011-02-11 15:07 | 2011-02-11 16:37 | 2011-02-11 | UNUSUAL EVENT DECLARED BASED ON FIRE ALARM IN DRYWELL "At 1438 CST on 02/11/2011 a fire detector alarm was received for Recirculation Pump B in the Reactor Building Drywall. At 1453 CST the main control room was unable to determine the alarm was invalid. At this time the condition was met for EAL HU4 for a Fire within the Protected Area boundary that is not extinguished within 15 minutes of detection. At 1507 CST a Notification of an Unusual Event was declared. The alarm was verified to be invalid following visual inspection at 1513 CST. All Drywall parameters and operation of Recirculation Pump B verified to be normal. " The licensee has notified State and local authorities as well as the NRC Resident Inspector. No media or press release is planned. * * * UPDATE AT 1734 EST ON 2/11/11 FROM POLAN TO HUFFMAN * * * At 1552 CST River Bend terminated the Notification of an Unusual Event following confirmation that no fire existed. The licensee has notified the NRC Resident Inspector. R4DO (Clark) and NRR EO (Hiland) notified. DHS (Inzer) and FEMA (Canupp) informed. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Startup; FMode1: Startup | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2011-02-11
46610 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-02-11 13:12 | 2011-02-11 14:53 | 2011-02-11 | HYDRAZINE SPILL ONSITE "On February 11, 2011 at 1312 hours, a notification was made to the New Jersey Department of Environmental Protection of a spill of approximately 5 gallons of steam/water solution containing hydrazine with a concentration of 30ppb which was not cleaned up within 24 hours of identification. The spill due to a steam leak on the Unit 2 Main Steam System, was identified on February 9, 2011. The solution was spilled onto a gravel substrate next to the Unit 2 Main Steam mixing bottle. The closest storm drain leading to the Delaware river was sampled and had no detectable levels of hydrazine. Leak isolation and spill containment/cleanup are in progress. "There was no out-of-service safety related equipment that contributed to this event. No one was injured as a result of this event." The licensee notified the NRC Resident Inspector and Lower Alloways Creek Township. * * * RETRACTION FROM JACK OSBORNE TO PETE SNYDER AT 1753 ON 2/11/11 * * * As a correction to the earlier information: the subject spill was cleaned up within 24 hours and is therefore not reportable. Notified R1DO (Bellamy). | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-02-11
46609 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2011-02-10 | 2011-02-11 13:39 | 2011-02-11 | AGREEMENT STATE REPORT - LEAKING MAMOSITE BALLOON CATHETER POSSIBLY AFFECTED DOSE The State of Iowa reported the following via email: "The licensee reported a potential medical event that had occurred on Thursday, February 10, 2011. "A patient was under going breast cancer treatment using a Nucletron Corporation Micro Selection High Dose Rate Afterloader (HDR). The HDR contained a 5.2 curie Iridium-192 sealed source. The patient was scheduled to receive a total dose of 3400 cGy in ten (10) fractions of 340 cGy each over a five day period. The licensee performs a CT scan on the patient before each fraction to confirm the positioning of the balloon catheter. "On the morning of Thursday, February 10, 2011 the patient arrived for the seventh fraction. The licensee's CT scanner was not operable at the time so the Authorized User (AU) (Radiation Oncologist) imaged the patient using ultrasound. The AU noticed at the time that the patient had some drainage from the surgical incision but the results of the ultrasound appeared [to show] that the balloon catheter was correctly placed. The patient then received the seventh fraction. When the patient returned for the eighth fraction in the afternoon of the 10th the licensee's CT scanner was operable. This scan showed that the balloon catheter had completely leaked out all of the fluid. The AU and Medical Physicist made the decision to not perform the eighth fraction due to the possibility that the patient may have received a double dose (680 cGy) during the previous fraction. "The patient, referring physician and surgeon were then notified. The surgeon removed the leaking balloon catheter and replaced it with a new catheter. The patient completed fraction nine on the morning of Friday, February 11, 2011 and is scheduled for fraction ten and treatment completion in the afternoon of the 11th. "The AU and Medical Physicist do not believe that this event will result in any adverse complications to the health of the patient. The licensee will continue to investigate this event and provide a written report to IDPH within 15 days of the occurrence." Iowa Item Number: IA110001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2011-02-17
46608 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-02-10 17:02 | 2011-02-11 13:42 | 2011-02-11 | MATERIAL CONTROL AND ACCOUNTABILITY (MC&A) ALARM RESOLUTION "10 CFR 74.57 (f) (2) requires notification within 24 hours that an MC&A alarm resolution procedure has been initiated. In the solvent extraction area of Building 333, the input minus output value exceeded the MC&A limit. Because the alarm investigation procedure has been initiated, this notification is being made. There is no indication that a material loss has occurred. "There were no actual or potential safety consequences to workers, the public, or the environment." The licensee has notified NRC Region 2 and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 74.57 |  |  |  | 0 | 2011-02-15
46607 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2011-02-11 08:45 | 2011-02-11 12:35 | 2011-03-21 | TEARS DISCOVERED IN FLEXIBLE PIPE SEALS "On February 11, 2011, during a plant walk down, it was discovered that two flexible boots sealing two piping penetrations in the secondary containment boundary had a total of three small tears rendering them inoperable. "Technical Specification 3.6.6.2, 'Secondary Containment,' is applicable in Modes 1, 2, 3, and 4 and was entered. Since Secondary Containment was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to control the release of radioactive material. Further engineering review will be conducted to more fully evaluate the impact on radiological controls." No actual release occurred as a result of this condition. The licensee notified the NRC Resident Inspector, the State of Connecticut and the Town of Waterford. * * * RETRACTION FROM ROBERT ACQUARO TO DONALD NORWOOD AT 1503 EDT ON 3/21/2011 * * * "On February 11, 2011, small tears were discovered on flexible boots sealing two piping penetrations in the secondary containment boundary on Millstone Power Station Unit 3. Operators made a report in accordance with 10CFR50.72(b)(3)(v)(C). "Subsequently, an engineering evaluation has been completed that concludes that the discovered tears would not have prevented the fulfillment of the safety function of the secondary containment boundary. Therefore, the condition reported in event report 46607 is being retracted. "The NRC Senior Resident Inspector has been notified." Notified R1DO (Rogge). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2011-02-11
46606 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2011-02-11 03:27 | 2011-02-11 10:48 | 2011-02-11 | INOPERABLE CONTAINMENT ISOLATION DAMPERS "On February 11, 2011 at 0327 [CST], Secondary Containment isolation damper V-D-61 (Reactor Building Outboard Isolation Damper) was discovered iced closed with the actuator broken. The corresponding inboard damper, V-D-62, was found blocked partially open due to icing. Technical Specification Condition 3.6.4.2.B was entered for one Secondary Containment penetration flow path with two isolation valves inoperable. This resulted in a condition which could have prevented the fulfillment of a safety function required to control the release of radioactive material and mitigate the consequences of an accident. The required action to isolate the flow path by use of one closed and de-activated valve was completed at 0354 [CST], within the four hour completion time. Repair activities are in progress." The licensee notified the NRC Resident Inspector and the State of Minnesota Duty Officer. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-02-11
46605 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2011-02-09 18:04 | 2011-02-09 19:59 | 2011-02-09 | PRESSURE BOUNDARY LEAKAGE "At 1830 CST on 02/09/11, LaSalle Unit 1 commenced a Technical Specification required plant shutdown, due to identification of pressure boundary leakage. At 1804 CST on 02/09/11, it was identified that 1E51-F076, Reactor Core Isolation Cooling System Steam Supply Inboard Isolation Bypass Warmup Valve, had a one inch crack in a weld on the pressure seal joint. This qualifies as pressure boundary leakage, which requires entry into Tech Spec 3.4.5, RCS Operational Leakage, Required Action C, to be in Mode 3, Hot Shutdown, by 0604 on 02/10/11, and Mode 4, Cold Shutdown, by 0604 on 02/11/11 . At the time of discovery, Unit 1 was in startup mode following a forced outage. A repair plan is being prepared at this time and the Unit will remain in cold shutdown until repairs are complete." This is an unisolable leak. Reactor pressure is 913 psig. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2011-02-09
46604 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2010-12-20 04:38 | 2011-02-08 20:55 | 2011-02-08 | FUSE FAILURE CAUSES LOW PRESSURE CORE SPRAY TO BE INOPERABLE "On December 20, 2010, the low pressure core spray (LPCS) system was declared inoperable due to loss of power to the LPCS minimum flow valve. The minimum flow valve supports operability by providing a flow path to prevent pump damage during situations where the LPCS pump has been started in response to a transient, but reactor vessel pressure is not low enough to allow LPCS injection. The power loss was caused by the clearing of all 3 line power fuses for the motor starter for the minimum flow valve. An apparent cause evaluation concluded that the most likely cause of the fuses clearing was a random fuse failure of one of the fuses at less than design amperage attributable to a defect in the fuse solder joint. "The Technical Specification (TS) Required Action for LCO 3.5.1 Condition A, one low pressure ECCS injection/spray subsystems inoperable, was complied with by restoring the LPCS system to operable within the allowed completion time. "The safety functions for LPCS are to provide inventory makeup and spray cooling during large breaks in the reactor coolant system that uncover the core. All remaining ECCS subsystems were operable and at no time did this event result in the loss of a safety function. The low pressure injection function was not challenged due to all three loops of the Residual Heat Removal (RHR) system Low Pressure Coolant Injection (LPCI) mode being operable while the core spray function was satisfied by the operable High Pressure Core Spray (HPCS) system. "This event is being reported under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident tor a single train system. "Historically, LPCS inoperabilities at Columbia (including initial review of this event) were not considered to be a single train system for reportability purposes. The basis for the historical consideration was assessment of LPCS inoperabilities consistent with the plant safety analysis and the associated system and safety function groupings which do not single out LPCS as a single train system. There are two pertinent groupings in the safety analyses which are aligned with the credited safety functions of LPCS. The two groupings are the low pressure injection system function (combined with LPCI), and a core spray system function (combined with HPCS). Industry precedent has been consistent with the historical position. However, recent NRC interpretations have considered safety function at the lowest system level which result in LPCS being considered as a single train performing a safety function in scope of the reportability rules in 10 CFR 50.72 and 50.73. A Licensee Event Report will be submitted for this event. "As a result of the recent interpretation with regard to LPCS, a review of prior LPCS inoperabilities within the past three years is being performed to determine if the reporting criteria were met during prior events. If necessary, additional 10 CFR 50.72 and 10 CPR 50.73 notifications/reports will be made on prior LPCS inoperabilities . The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-08
46603 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-02-08 08:00 | 2011-02-08 15:06 | 2011-02-08 | UNANALYZED EVENT COULD INITIATE HIGH PRESSURE CORE SPRAY AND OVERFILL THE REACTOR PRESSURE VESSEL "During the performance of a Fire Protection self assessment, it was discovered that a calculation for the safe shutdown analysis has an assumed action for an operator to locally depress the internal breaker trip plunger to trip the High Pressure Core Spray (HPCS) pump in response to a fire in the main control room. However, due to personnel safety concerns related to potential arc flashing events associated with this action, the remote shutdown procedure was revised to locally close the HPCS injection valve (1E22F004) in lieu of depressing the internal breaker trip plunger. "During engineering's review of this procedure and supporting calculation, it was determined that the HPCS system could be initiated due to concurrent fire induced hot short cable damage to the two automatic initiation logic instrument cables routed in the same raceway in the area. In this event, even if the HPCS breaker could be tripped or the HPCS injection valve could be closed locally, HPCS would continue to fill the reactor pressure vessel (RPV) and flood the main steam lines. Once pressure reaches the setpoint for the Main Steam Safety Relief Valves (MSSRVs), they would lift and discharge mixed-phase water through the discharge line to the suppression pool. This conservatively postulated scenario would place the MSSRVs and their associated tailpipes in an unanalyzed condition for the stresses expected during the two-phase flow event. "While it is not expected that a failure of the MSSRV discharge line will occur, a confirmatory analysis will be performed. Compensatory measures for Multiple Spurious Operations have been determined to be adequate until the analysis is complete." The licensee added additional fire zone surveillance to operator plant walk downs and will investigate to determine further corrective actions. The license has notified the NRC Senior Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-02-08
46602 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-02-08 | 2011-02-08 13:51 | 2011-02-08 | AGREEMENT STATE REPORT - UNDER DOSE RECEIVED DURING BRACHYTHERAPY PROCEDURE The following information was received from the State of North Carolina via email: "A patient undergoing a HDR [High Dose Rate] brachytherapy procedure received an under dose on three fractions. "The guide tubes were misaligned which resulted in a 5 cm displacement from the source plan. This misalignment resulted in a 59% difference in dose (under dose) to the intended site and an overexposure to other tissue. The patient has received three of ten exposures and the plan will be re-worked to mitigate the under dosage of the intended site. "The patient has been notified and they are trying to contact the prescribing physician to notify him." An investigation has been initiated to determine the cause of this event and corrective actions. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-02-14
46601 | 0 | CRITTENTON HOSPITAL MEDICAL CENTER |  |  |  |  | 2011-02-07 16:00 | 2011-02-08 12:05 | 2011-03-07 | MEDICAL EVENTS - ACTUAL DOSE LESS THAN PRESCRIBED DOSE Nine breast cancer patients were treated with a multi-channel high dose rate afterloader with the incorrect dwell positions input into the afterloader controller. The intended prescription was for 5 mm between dwell positions. The actual input was 2.5 mm between dwell positions. The prescribed dose was for 3400 cGy and the actual dose delivered was approximately 25% less. No adverse clinical effects are expected. The doctors and patients will be notified. * * * UPDATE FROM DR. VIVIAN ARTERBERY TO JOHN SHOEMAKER AT 1507 EST ON 03/07/11 * * * There were a total of eleven breast cancer patients involved. Seven of the eleven patients had small areas of unintended target that received unplanned dose. The doctors and patients have been notified. Notified R3DO (Riemer) and FSME (McIntosh) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2011-02-14
46600 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2011-02-08 | 2011-02-08 11:19 | 2011-02-08 | AGREEMENT STATE REPORT - LOST GAS CHROMATOGRAPH SOURCE The following information was received via facsimile: "On December 9, 2010, North Carolina Radiation Protection Section (NCRPS) received a phone call from the Radiation Safety Officer (RSO) of J. Leek Associates, Inc. (JLA). The RSO stated that he needed to register a new Ni-63 gas chromatograph (GC) source because the old Ni-63 source had been lost. The lost source was used in a model GC-14A PSE, Shimadzu GC. The serial number of the lost source was 608335. "NCRPS initiated an investigation and performed an inspection on December 14, 2010. The missing source could not be located during the inspection. Three violations were issued by NCRPS to JLA in a Notice of Violation (NOV) letter dated December 21, 2010. The three violations were: "1. Loss of Ni-63, activity-10 mCi, Serial Number 608335. "2. Failure to perform inventory every six months. "3. Failure to perform leak test every six months. "JLA responded to the NOV on January 20, 2011. NCRPS is currently reviewing the JLA file for escalated enforcement actions and penalty assessment. This incident has been closed." NCRPS believes the source may have been lost in the trash and not stolen. NCRPS Incident No.: 11-06. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-02-11
46599 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-02-07 22:25 | 2011-02-07 22:35 | 2011-02-08 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM OUT OF SERVICE DUE TO PLANNED MAINTENANCE "On February 07, 2011 at 2225 EST, the Control Room Emergency Ventilation system on St. Lucie Unit 1 was declared out of service due to pre-planned maintenance to upgrade the Emergency Response Data Acquisition and Display System. This maintenance renders the control room envelope out of service for a portion of the maintenance. The Technical Support Center (TSC) ventilation system is part of the Unit 1 Control Room Emergency Ventilation system, therefore, the TSC ventilation system has been rendered non-functional during the course of work activities. The TSC ventilation is expected to be returned to service in 4 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Should the TSC become uninhabitable, the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF). An update will be provided once the TSC ventilation system has been restored to normal operation. The NRC Resident Inspector has been notified." * * * UPDATE FROM LOURDES PORRO TO DONG PARK AT 0040 EST ON 2/7/11* * * "[As of 0013 EST, the] Control Room and TSC ventilation system has been restored to normal operation." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-07
46598 | 0 | FAIRBANKS MORSE |  |  |  |  | 2011-02-07 | 2011-02-07 17:50 | 2011-02-07 | POTENTIAL EMERGENCY DIESEL GENERATOR BEARING FAILURES The following information was received via e-mail: "Linear indications (hot tears) were observed on one main bearing by the FM [Fairbanks Morse] production inspector. The indications were only on one edge of the bearing. The indications went across the entire edge and extended about 1 inch deep into the bearing, being visible on the outside diameter and the inside diameter for about 1 inch. Subsequent 100% liquid penetrant inspection (PT) of all finished bearings in stock has found linear indications on 13 of 454 bearings (3% reject rate) made from permanent mold castings. "No bearing failures in engines have been linked to linear indications. The root cause of the problem occurs during the casting of the aluminum material in the permanent mold. The linear indications occur only on one edge of the casting, which has been identified as the bottom of the casting. During the cooling and solidification of the molten material poured into the permanent mold tool, the material shrinks and must be continuously replenished with molten material from the top of the casting. If the top of the casting solidifies before the bottom, there is no additional molten material available from the top to feed the bottom as it cools and shrinks, resulting in tears (hot tears) to the material on the bottom of the casting. It is suspected these hot tears are occurring due to improper cooling of the mold tool core. Because there are no cooling passages within the solid mold tool core, the core becomes progressively hotter throughout the production run until the core reaches a temperature hot enough to cause the hot tears." Affected plants are: Limerick, Peach Bottom and Prairie Island. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2011-02-07
46597 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-02-07 09:18 | 2011-02-07 17:18 | 2011-04-08 | HIGH ENERGY LINE BREAK ANALYSIS FOR AUX STEAM TO THE AUXILIARY BUILDING "On December 15, 2009, Callaway Plant reported a condition in which valve FBV0146, an isolation valve on an auxiliary steam line in the Auxiliary Building, was found to be kept normally open. With FBV0146 open, the auxiliary steam line downstream of FBV0146 must be considered a high energy line. This configuration was not consistent with the analysis of record for High Energy Line Break (HELB) events. Valve FBV0146 was closed upon discovery of the condition. "This condition was reported under EN # 45571 as an unanalyzed condition that significantly degrades plant safety. EN #45571 was then retracted on January 21, 2010 when analysis showed that no safety-related components would be rendered inoperable in a postulated HELB event due to the condition. Based on this analysis, FBV0146 was reopened. "Subsequent review of this condition now shows that, with FCV0146 open, a harsh environment from a postulated HELB downstream of FBV0146 could be transmitted to other areas of the Auxiliary Building. This would occur via a flow path through door gaps and an Auxiliary Building elevator shaft. This flow path had not been considered by the previous analysis. "The areas that could be affected by a postulated line break contain safe shutdown equipment (such as equipment for the Component Cooling Water system) that is not assumed to experience harsh conditions. Because of the potential impact on this equipment, this condition is considered to have met the criteria for reporting under 10 CFR 50.72(b)(3)(ii)(B). "FBV0146 is now closed. "This review was performed as part of the ongoing evaluation of HELB Program deficiencies described in Callaway Plant License Event Report (LER) 2010-009-00. "The NRC Resident Inspector has been notified." The auxiliary steam line in the Auxiliary Building feeds non-safety related components. * * * UPDATE AT 1519 EDT ON 4/8/11 FROM KEITH DUNCAN TO S. SANDIN * * * The licensee is retracting this report based on the following: "On 02/07/2011, EN #46597 documented that a harsh environment from a postulated High Energy Line Break (HELB) could be transmitted to areas of the Auxiliary Building not qualified for harsh environments. This break was postulated to occur on an Auxiliary Steam line downstream of valve FBV0146 when FBV0146 is open. This condition was initially reported as an unanalyzed condition that significantly degraded plant safety. "When EN #46597 was reported, the analysis of the Auxiliary Steam line included postulated break locations at any intermediate fitting, welded attachment, or valve. Subsequent analysis shows that this section of Auxiliary Steam piping is able to withstand safe shutdown earthquake (SSE) loadings and rupture loadings. For piping of this qualification, line breaks are only assumed to occur at terminal ends and at the locations specified for ASME Class 2 and 3 piping. Breaks at intermediate fittings, welded attachments, and valves are not required to be assumed. "Postulated breaks of this Auxiliary Steam line at the locations described above have been analyzed. This analysis demonstrates reasonable assurance that safety-related equipment would have performed their safety functions following a postulated break of this Auxiliary Steam line. Therefore, this condition is not an unanalyzed condition that significantly degrades plant safety and does not meet the reporting requirements of 10 CFR 50.72(b)(3)(ii)(B). Event notification #46597, made on 02/07/2011, is hereby retracted. "The NRC Resident Inspectors have been notified." Notified R4DO (O'Keefe). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2011-02-07
46596 | 0 | LUZENAC AMERICA INC |  |  |  |  | 2011-02-07 10:45 | 2011-02-07 13:00 | 2011-02-07 | SEVEN TRITIUM EXIT SIGNS LOST Luzenac America Inc. purchased their property from Cypress Minerals Corporation in February 1988. Seven Tritium exit signs were included in the transfer. However, these exit signs were not inventoried nor were their locations documented. These signs cannot be located and have been declared missing. Sign Manufacturer: Self Powered Lighting Model: 710 Activity: 25 Ci each at the time of manufacture THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-02-07
46595 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-02-05 22:17 | 2011-02-06 03:37 | 2011-02-06 | BOTH TRAINS OF AUXILIARY FEED WATER DISABLED "On February 5, 2011, both trains of the Auxiliary Feed Water system were disabled while transitioning from Auxiliary Feed Water to Main Feed Water during plant start up. While performing OI-AFW-4 attachment 3, FW-6 Electric Driven AFW Pump Operations, both Steam Generator Auxiliary Feed Water inlet valves (HCV-1107A and HCV-1108A) control switches were placed in 'CLOSE'. This action defeated the Auxiliary Feedwater Actuation Signal (AFAS) ability to open the valves, rendering both trains of Auxiliary Feed Water to the Steam Generators inoperable. The condition was subsequently recognized and the control switches were placed in 'AUTO' restoring both trains to operable. The duration of the condition was 3 minutes from start to finish. Reference Fort Calhoun Station Condition Report 2011-0839. "This eight-hour notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(B)." The NRC Resident Inspector has been notified. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2011-02-06
46594 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2009-09-09 08:02 | 2011-02-04 18:17 | 2011-02-04 | UNSEALED PENETRATIONS DISCOVERED IN THE INTAKE STRUCTURE "On September 9, 2009, the NRC Component Design Basis Inspection (CDBI) Team identified Fire Protection penetrations on the west side of the Intake Structure were not sealed and it has been determined that the penetrations were below the USAR [Updated Safety Analysis Report] credited flood level. Flooding through the penetrations could have impacted the ability of all the station Raw Water Pumps to perform their design accident mitigation functions. Reference Fort Calhoun Station Condition Report 2009-4166. "This eight-hour notification is being made pursuant to 10 CFR 50.72 (b)(3)(v). This report should have been made on September 9, 2009, and is late. Subsequent review of the issue determined this reportability." The penetrations have since been sealed. The licensee notified the NRC Resident Inspector. See EN #46590 dated 2/3/2011 for a similar event at Fort Calhoun. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-04
46593 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2011-02-04 16:00 | 2011-02-04 16:17 | 2011-04-11 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM DUE TO PLANNED REPLACEMENT OF PLANT PROCESS COMPUTER "The implementation of a planned replacement of the Unit 3 plant process computer, also known as the Critical Function Monitoring System (CFMS), with a new Plant Integrated Computer System (PICS), resulted in the loss of the Emergency Response Data System (ERDS). The Meteorological Radiological Plant Data Acquisition System (MRPDAS), and Meteorological Information and Dose Assessment System (MIDAS) is also impacted. MIDAS will function but the automatic download of Unit 3 plant parameters will not be available and the MIDAS Operator (SM or Dose Assessor) will have to manually input this data to perform dose assessment. Meteorological data will remain available. All Unit 2 functions remain available. Other systems such as the Safety Parameter Display System (SPDS), the Radiological Emergency Communication System (RECS), and the Emergency Notification System (ENS) remain available. As a compensatory measure, a proceduralized backup method is available to FAX applicable data for ERDS and MRPDAS. As discussed in a letter to the NRC data October 6, 2010, the plant process computer is being replaced due to obsolescence. The new Unit 3 computer processors will be located in the Unit 2 Computer Room which will become the Computer Room for both the Unit 2 and Unit 3 Plant Computers. The new Unit 3 plant process computer work stations will be located in the Unit 3 Control Room. The new PICS was previously installed in the Unit 3 plant simulation facility. The modification was initiated on February 4, 2011 and is scheduled to be completed by March 6, 2011. The new PICS will not affect the transmitted data points nor affect the transmission format and computer communication protocol to ERDS. In accordance with the site reporting procedure, a loss of ERDS is reportable as a major loss of emergency assessment capability." The licensee expects the duration of the ERDS outage to be from one to three weeks. The licensee notified the NRC Resident Inspector. The licensee also notified the following: New York State, Putnam County, Westchester County, Rockland County, and Orange County. * * * UPDATE AT 0935 EDT ON 4/11/11 FROM CHARLES ROKES TO MARK ABRAMOVITZ * * * "This notification is an update to the information previously provided on February 4, 2011. The replacement of the Unit 3 plant process computer with a new plant integrated computer system (PICS) has been completed. With the return of PICS to service the function of ERDS was also returned to service. A quarterly test with the NRC on April 5, 2011, verified ERDS is functional. The link to PICS for MRPDAS and MIDAS remains unavailable. The previously reported compensatory measure using a proceduralized backup method remains available to FAX applicable data for MRPDAS. Future upgrades will address the PICS data for MRPDAS and MIDAS." The licensee notified the NRC Resident Inspector and will notify the state and local authorities. Notified the R1DO (Henderson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-04
46592 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2011-02-03 09:30 | 2011-02-04 09:05 | 2011-02-04 | 24 HOUR NOTIFICATION UNDER BULLETIN 91-01 CONCERNING LEAKAGE OF MODERATING LIQUID "At 0930 CST on 02-03-11, the Plant Shift Superintendent (PSS) was notified that a steam condensate line broke above the C-310 withdrawal room and water leaked through the ceiling into the withdrawal room on the ground floor. Water accumulated greater than 0.5 inch in depth in the diked area above the withdrawal room in violation of NCSA [Nuclear Criticality Safety Approval] 310-004. NCSA 310-004 requires that open containers with volumes greater than 5.5 gallons shall not contain pre-existing moderator greater than 0.5 inches in depth. During the walk down, it was discovered that the sprinkler heads currently installed above the withdrawal room are rated at 160F in violation of the NCS [Nuclear Criticality Safety] limit. NCSE [Nuclear Criticality Safety Evaluation] 032 requires the minimum activation temperature to be no lower than 200F. The sprinkler system was taken out of service and drained at 2131 CST on 02-03-11 and the level of water accumulated in the diked area was verified to be less than 0.5 inches at 0426 CST on 02-04-11. "Since one leg of double contingency was lost, this is being reported to the NRC as a 24-hour Event Report in accordance with NRC BL 91-01 Supplement 1. "The NRC Senior Resident Inspector has been notified of this event. SAFETY SIGNIFICANCE OF EVENTS "The first leg of double contingency is based on preventing a release of fissile material greater than the safe mass of uranium. This event did not release fissile material greater than the safe mass of uranium. POTENTIAL CRITICALITY PATHWAYS (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) "In order for a criticality to be possible, a large UF6 release containing greater than a critical mass of uranium would have to occur and accumulate greater than the critical configuration. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.) "The two process conditions relied upon for double contingency are mass and geometry. ESTIMATED AMOUNT, ENRICHMENT, FORM OF MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS) "Product withdrawal assay at the time of the event was less than 4.95 wt% U235. However, no UF6 release occurred. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "The first leg of double contingency is based on preventing a release of fissile material greater than the safe mass of uranium. Since a UF6 release containing greater than the safe mass has not occurred, the mass parameter has maintained. The second leg of double contingency limiting moderating liquids in open containers to less than 0.5 inches and requiring the sprinkler head activation temperature to greater than 200F. Since the diked area above the withdrawal room did accumulate water level greater than 0.5 inches, the control was violated. Additionally, since the installed sprinkler heads activation temperature is less than 200F, a design feature of NCSE 032 was violated. Therefore, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED "Shiftly checks of the diked area above the withdrawal have been initiated to ensure water level is not accumulating. The condensate leak above the withdrawal room was repaired and solution level verified to be less than 0.5 inches (0426 [CST] on 2/4/11). The sprinkler systems associated with the sprinkler heads above the withdrawal room have been isolated until the sprinkler heads can be replaced with heads that comply with NCSE 032 (Systems isolated at 2131 [CST] on 2/3/11)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2011-02-04
46591 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-02-03 08:58 | 2011-02-03 17:54 | 2011-02-03 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2011-02-03
46590 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-01-27 16:23 | 2011-02-03 17:40 | 2011-02-03 | UNSEALED PENETRATIONS DISCOVERED IN THE INTAKE STRUCTURE "During a walkdown of the Intake Structure conducted on January 27, 2011, to identify any penetrations in the exterior envelope of the building, four unsealed conduit penetrations [each penetration was four inches in diameter] were identified. These penetrations are concealed within a junction box on the northwest corner of the building. The penetrations are at an elevation of approximately 1006 ft. - 1007 ft. mean sea level (MSL). Flooding through the penetrations could have impacted the ability of all the station raw water pumps to perform their design accident mitigation functions. "This eight-hour notification is being made pursuant to 10CFR50.72(b)(3)(v). This report should have been made on January 27, 2011, and is late. Subsequent review of the issue determined this reportability. "The river level has been less than 990 ft MSL since January 27, 2011. There have not been any indications of conditions that might result in a flood. The penetrations have been temporarily plugged. A permanent modification is in progress." The penetrations were sealed on February 2, 2011. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-02-03
46589 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2011-02-02 14:30 | 2011-02-03 14:22 | 2011-02-03 | DISCOVERY OF AN UNFAVORABLE VOLUME CONTAINER IN THE URANIUM RECOVERY CONTAINER CONTROLLED AREA "On February 2, 2011 at 1430 hrs [EST], an unfavorable volume container was found in the Uranium Recovery Container Controlled Area (CCA). The container was immediately removed from the area. At the time of the discovery, the facility was not processing SNM due to planned maintenance work. Also, there was no SNM found in the container. Based on interviews with area personnel, it is believed that the container had been in the area when SNM operations were in progress in the past. The control of container volume is an [Item Relied On For Safety] IROFS. Having this container in the CCA in the past constitutes a loss of an IROFS. "The as-found condition did not have any safety significance since no SNM was present in the area or in the container. There was no immediate risk or threat to the safety of workers or the public as a result of this event. "An evaluation is currently being performed [by the licensee]. "B&W NOG-Lynchburg is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(2) - Loss or degradation of items relied on for safety that results in failure to meet the performance requirement of º70.61. The container is used during maintenance and had been left in the area during previous maintenance activities. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2011-02-05
46588 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-02-02 08:30 | 2011-02-02 17:14 | 2011-02-02 | PARTIAL LOSS OF PROMPT NOTIFICATION SYSTEM (PNS) EMERGENCY SIRENS DUE TO A LOSS OF POWER "At approximately 0830 [CST] on 2/2/2011, eleven (11) of thirty-two (32) STP Prompt Notification System (PNS) sirens were not operable due to loss of power. The sirens were subsequently polled at approximately 0909 [CST] and all sirens except 3 were operable. The loss of power was caused by rolling outages due to unusually severe cold weather. ERCOT issued an order requiring load shedding to maintain a steady state system frequency of 59.8 Hertz (Hz) on the grid. The outages were suspended at 1400 hrs but rolling outages could continue through the end of the week potentially affecting the sirens. All 32 sirens were likely affected during the outages for some un-quantified period of time. Continuous polling of the sirens was not performed or advisable since polling depletes the batteries which could affect the operability of the sirens. "STPNOC [South Texas Project Nuclear Operating Company] has notified Matagorda County Sheriff Department. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of using Local Law Enforcement Personnel for 'Route Alerting' of the affected areas of the Emergency Planning Zone (EPZ). Matagorda County Emergency Management has verified that the Matagorda County Sheriffs Department is on standby for Route Alerting. "STPNOC is currently transitioning to new sirens. While the new sirens are not currently credited in the STP Emergency Plan, we have received final FEMA approval. All of the new battery-backed sirens were tested and verified to remain operable and capable of notifying the population in the EPZ. "This notification is being made under 10 CFR 50.72(b)(3)(xiii) due to a significant loss of the offsite Prompt Notification System. It is possible that rolling outages may recommence in the next several days." The licensee informed the NRC Resident Inspector and the offsite agencies identified above. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-02
46587 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-02-01 | 2011-02-02 16:07 | 2011-02-02 | AGREEMENT STATE REPORT - STUCK SHUTTER ON GAUGE This information was provided by the state via email: "On February 2, 2011, the Agency [State of Texas] was notified by the licensee that the shutter on a Ronan model SA1-F37 nuclear gauge was stuck in the open position. The gauge contained an original activity of 100 milliCuries of Cesium (Cs) - 137. The gauge is mounted on a vessel 100 feet above the ground and does not pose an exposure risk. "The licensee has contacted the manufacturer and expects the gauge to be repaired in the next few days. Additional information will be supplied in accordance with SA-300." Texas Incident Number: I-8817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-02-07
46586 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2010-12-23 | 2011-02-02 15:47 | 2011-02-04 | AGREEMENT STATE REPORT INVOLVING AN UNPLANNED FETAL EXPOSURE This information was provided by the state via email: "On 12/23/10, the patient was administered the radiopharmaceutical for a nuclear stress test. Notices were posted in English and Spanish to [advise the patient to] inform the staff if you [the patient] think you are or could be pregnant. The patient was scheduled to return for the resting portion of the study on 12/28/2010. At this time, the patient and the husband raised the possibility of the patient being pregnant. The resting test was canceled and a pregnancy test performed which was positive. "The Agency continues to investigate the actions of the licensee and timeliness of reporting of this event. The U.S. NRC and the Arizona Governor's office have been notified of this event. Press coverage is not anticipated. "Source: Tc99m; Activity: 30 milliCuries" Arizona First Notice: 11-001 * * UPDATE FROM AUBREY GODWIN TO DONG PARK AT 1046 EST ON 2/4/11 * * * This information was provided by the State via email: "Doses: The licensee estimates the fetus exposure is 1,300 mRem. "Corrective Actions: The licensee now requires a signed statement on pregnancy." Notified FSME EO (Villamar) and R4DO (Howell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2011-02-07
46585 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2011-02-02 07:00 | 2011-02-02 10:08 | 2011-02-03 | PARTIAL LOSS OF EMERGENCY SIRENS DUE TO SEVERE WINTER STORM "February 2, 2011, at approximately 0600 hours (CST), a Severe Winter Ice Storm was experienced causing a loss of 11 of 40 emergency sirens (approximately 28 percent) for Clinton Power Station. At 0700 hours (CST), since the sirens were not restored to operation within one hour, this event was determined to be a major loss of emergency assessment capability. Currently, 29 of 40 sirens are operational and no estimated return to service has been provided for the remaining sirens. "DeWitt County, Illinois Emergency Management Agency, and the NRC Resident Inspector have been informed of this information." Unit operation is not affected by the storm. No additional contingency actions have been planned. No press release is planned. Also notified R4DO (Howell) due to weather issue at Region 3. * * * UPDATE AT 1245 EST ON 2/3/11 FROM ALAN DARELIUS TO S. SANDIN * * * "At 0700 [CST] on February 3, 2011, 39 of 40 sirens are in service. Ten of the eleven sirens [that were out of service] have been restored to service following power restoration. The one siren remaining will sound, however it does not rotate as designed. Troubleshooting and repair continues on that siren. "The DeWitt County, Illinois Emergency Management Agency, and the NRC Resident have been informed of this updated information." Notified R3DO (Skokowski). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-02
46584 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-02-02 05:33 | 2011-02-02 08:52 | 2011-02-02 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF RCS COOLANT FLOW IN ONE LOOP "Unit 2 Reactor automatically tripped at 0533 EST. This was due to loss of coolant flow in the 'C' RCS Loop. The first indication of the reactor trip was the annunciator for 'Loss of Coolant Flow > P8.' The 'C' RCP is running with motor current indicating normal. 'C' LOOP RCS flow is approximately 25% on all three channels with 'A' & 'B' RCS LOOP FLOW approximately 104%. All three auxiliary feedwater [AFW] pumps automatically initiated as designed on low-low steam generator level following the trip. Currently, RCS temperature is being maintained stable at no load temperature. All systems responded as expected with the exception of the Intermediate Range Neutron Indication. N36 indication was undercompensated and Source Range indication did not automatically energize, but was subsequently manually energized. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of RPS Activation and 10 CFR 50.72(b)(3)(iv)(A) for 8-hour notification of actuation of AFW. Plant responded as expected. The NRC Resident Inspector has been notified of this event and is on site. "There were no radiation releases due this event, nor were there any personnel injuries or contamination events." This was an uncomplicated reactor trip and all control rods fully inserted. The plant is in a normal electrical alignment. AFW has been secured and the steam generators are being feed from main feedwater. Decay heat is being released through the main condenser steam dumps. Estimated time for repair and re-start is not known. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-02-02
46583 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-02-01 21:30 | 2011-02-01 22:57 | 2011-02-02 | SAFEGUARDS REPORT - COMPENSATORY MEASURES WERE CHANGED DUE TO SEVERE WEATHER Due to severe weather, changes in security's compensatory measures were taken. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM DAVID BONVILLIAN TO JOHN SHOEMAKER AT 12:46 EST ON 2/2/11 * * * All required compensatory security measures have been returned to normal and are being maintained. The licensee has notified the NRC Resident Inspector. R4DO (Howell) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-02-01
46582 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2011-02-01 19:18 | 2011-02-01 22:54 | 2011-02-01 | REACTOR SCRAM AFTER A MAIN TRANSFORMER TRIP "At 1918 CST on February 1st 2011, LaSalle Unit 1 automatically scrammed due to a MPT [Main Power Transformer] trip and subsequent load reject, both RFP [Reactor Feed Pumps] tripped and [the reactor] scrammed on TCV [Throttle Control Valve] fast closure. 'U' safety relief valve actuated in the relief mode on the turbine trip and has subsequently reset with tailpipe temp returning to normal. As a result of the electrical transient, U1 and U2 RWCU [Reactor Water Cleanup] isolated, and this is not reportable due to being a single train system and there was no isolation in multiple systems. The plant is stable with reactor pressure control to the main condenser via the main steam isolation valves. Unit 2 remained at 96% in coastdown throughout the event. The plant is planned to remain in hot shutdown pending investigation of the cause of the MPT trip and load reject." All control rods fully inserted on the reactor scram. The cause of the RFP trips was swelling of the reactor water level as expected after a scram. The first out alarm was "turbine control valve fast closure." The plant is experiencing severe weather which may have influenced the MPT trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2011-02-01
46581 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2011-02-01 14:30 | 2011-02-01 17:51 | 2011-02-02 | SEVERE WEATHER CONDITIONS "At 1430 on 2-1-2011, due to worsening road conditions from heavy snowfall, a determination was made that there is a loss of plant access for some individuals and some impairment of evacuation routes. This meets the criteria for an immediate notification (8 Hour) per 10 CFR 50.72 (b)(3)(xiii). There is no impact on plant operation, all T/S [Technical Specification] required minimum staffing requirements are satisfied. The weather is predicted to be hazardous until the evening of 2/2/2011. The Missouri Department of Transportation reported they have a plow truck running from Callaway Plant to Jefferson City, MO. They also reported visibility is extremely poor due to blowing snow. The Missouri State Emergency Management Agency duty officer has been notified of the degraded Callaway ERO [Emergency Response Organization] response time and evacuation route issues. "The NRC Resident Inspector was notified of this event by the licensee." Two shifts of personnel will be on site throughout this event. Diesel fuel, food, and water are above required minimums. * * * UPDATE FROM DAVID BONVILLIAN TO JOHN KNOKE AT 1821 EST ON 02/02/11 * * * "As of 1600 [CST] on 2/2/2011, road conditions have significantly improved. Primary evacuation routes have been reported to be passable. There is reasonable assurance of normal ERO response time. NRC Resident Inspector has been informed of the intent of this change and will be notified of this communication." Notified R4DO (Howell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-02-01
46580 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-02-01 | 2011-02-01 14:15 | 2011-02-02 | STOLEN LOGGING TOOL WITH CESIUM-137 SOURCE "On February 1, 2011, the Agency [Texas Department of State Health] was notified by the licensee operating with reciprocity in the State of Texas, that a well logging tool containing a 125 millicurie (original activity) Cesium (Cs) - 137 source was stolen from their vehicle. The source was manufactured by Gulf Nuclear. The tool was removed from its storage location without the shielding for the source. The tool is about ten feet in length and is less than four inches in diameter. The licensee stated that the dose from the source is collimated. The local sheriff was notified of the event. The licensee's representative was in Tyler, Texas and was driving to the location to search for the device. The Radiation Safety Officer stated that the source was approximately 30 years old and the current activity would be about 65 millicuries. The location where the source was stolen is rather remote and heavily wooded. The licensee does not believe that there is a health risk to members of the general public from the source. The source housing is marked with the trefoil symbol and has the words "Radioactive Materials" engraved in it. Additional information will be provided as it is received in accordance with SA-300." * * * UPDATE FROM ART TUCKER TO JOHN KNOKE AT 1522 EST ON 02/01/2011 * * * The following information was provided by the state in an email: "On February 1, 2011, at 1400 hours, the licensee reported that they had completed a visual search and radiological survey in the area the source had been stored and did not find it. He [licensee] stated that he was going to search the roads in the area and stated that he would notify the Agency [State of Texas] if the source was found. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Linda Howell), FSME (Jack Foster), ILTAB (Daryl Johnson), Mexico (Fax) * * * UPDATE FROM ART TUCKER TO S. SANDIN AT 1651 EST ON 02/02/2011 * * * The following information was provided by the state in an email: "On February 2, 2011 an Agency inspector [the State of Texas] contacted a scrap yard in Longview, Texas who [scrap yard employee] stated that he had received the source on February 1, 2011. The licensee was contacted and at 1515, confirmed the source was the one that was stolen and had not been damaged. The licensee has taken control of the source. Additional information will be provided as it is received." Notified R4DO (Howell), FSME (Foster), ILTAB (via email) and Mexico (via fax). Texas Incident # I-8816 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-02-04
46579 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-01-26 | 2011-02-01 10:07 | 2011-02-04 | AGREEMENT STATE REPORT - MISSING RADIOACTIVE MATERIAL SHIPMENT The following Agreement State Report was received via fax: "The Radiation Safety Officer of QSA Global, Inc. reported the following information on February 2, 2011, to the Massachusetts Radiation Control Program: "On Wednesday, January 26, 2011, QSA shipped a radioactive [High Dose Rate] HDR source to Memorial Hospital SW Cancer Center in Houston, TX. It was scheduled to deliver on Friday, January 28. On Monday, January 31, the [common carrier] tracking website still showed it as 'At destination sort facility' in Houston, TX. [The common carrier] was called to track the package, and we [QSA Global, Inc.] were told that it was actually still in Memphis, TN. A trace was requested. The [common carrier] trace number is [redacted]. [The common carrier] said they would inform us with any new information. As of this morning, Tuesday, February 1, there was no news, so [the common carrier] was called. We were informed that the package was indeed LOST. We gave [the common carrier] a physical description of the package, and informed them of the importance of locating this package due to the fact that it was radioactive. They will call with any results. "The specifics of the package are as follows: Isotope - Ir-192 Activity - 10.951 Ci / 405.2. GBq Container s/n - 81C6 Source s/n - D36C-6084 Surface reading - 26.0 mr/hr Transport Index - 0.4" * * * UPDATE VIA FAX FROM JOHN SUMARES TO DONALD NORWOOD AT 1417 EST ON 2/4/2011 * * * "On February 3, 2011, the licensee notified the Agency [Massachusetts Radiation Control Program] that the missing / lost shipment was found. The licensee reported that the shipment was never actually lost. It had been delivered to the hospital on 1/27/11 under a different air way bill number and the licensee was not aware of the new number. On February 4, 2011, the Agency asked the licensee for the new air way bill number, received the new number from the licensee, and used the [common carrier] tracking system to confirm the shipment was received on January 27, 2011." Notified R1DO (Dwyer) and FSME EO (Villamar). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-02-04
46578 | 0 | U.S. NAVY |  |  |  |  | 2011-01-12 | 2011-01-31 16:45 | 2011-01-31 | UNPLANNED IODINE-131 DOSE TO AN EMBRYO The following event description is from an email message: "On 12 Jan 2011, a Nuclear Medicine patient received a dose of I-131 of 100 milliCuries for a thyroid ablation. She received a pregnancy test just before the dose was administered and the result was negative. Two weeks after the dose she made an ER visit complaining about nausea and vomiting; she was then administered a serum pregnancy test. The result indicated she was roughly two weeks pregnant. On 27 Jan the doctor notified the Navy that the patient became pregnant very close to the therapy time. "On 28 Jan a dose calculation estimated the dose to the embryo to be 213 mGy (21.3 rads). On 31 January the Naval Radiation Safety Committee was notified that the patient was possibly pregnant prior to the therapy. "Pregnancy test performed immediately prior to therapy was negative. Patient was not trying to get pregnant prior, but did have unprotected intercourse in the few days before therapy. She denies intercourse in the week after therapy. Standard precautions were given to the patient during a visit several weeks prior to the therapy and included the following: 1). She could not be treated if she was pregnant, and 2). A pregnancy test would be performed immediately prior to therapy. "At a dose estimate of 213 mGy, there is a slight increased risk of failure to implant, but if the fetus survives, the outcome is expected to be good. This was discussed at length with the patient. The patient and the doctor communicated on 26 Jan after the patient discovered she was pregnant. Further follow up included a phone call the next day and a counseling visit 4 days later, after dose estimate calculations were completed. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3047(a) |  |  |  | 0 | 2011-02-06
46577 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2011-01-13 | 2011-01-31 13:59 | 2011-03-04 | AGREEMENT STATE REPORT - POTENTIAL DOSE EXCEEDING ANNUAL OCCUPATIONAL DOSE LIMIT FOR ADULTS The following was received via email: "On 1/13/11, the licensee reported to the agency [Massachusetts Radiation Control Program] a potential dose exceeding the adult occupational total effective dose equivalent limit of 5 rem. The situation causing this event occurred during late December 2010, when a number of emergency repairs within a cyclotron were conducted over several days. The potential for overexposure was suspected on 1/5/11. A dosimeter exposure readings report of the [Optically Stimulated Luminescence OSL] was received by the licensee from the dosimeter service, after quick read, on 1/13/11. Affected individual's annual TEDE reported at 5457 mrem. Exposure (1596 mrem) obtained by official [OSL] dosimeters worn during cyclotron repair operations differed significantly from exposure (620 mrem) obtained by electronic dosimeter worn simultaneously during cyclotron repair operations. Electronic dosimeters are used by individuals for real-time readings during the repair operations. The licensee removed affected individual from any potentially high exposure operations. "Investigation ongoing. Intermediate and draft reports have been received. Awaiting final written report by licensee. "The Agency considers this event to still be OPEN." Massachusetts Event # 01-9454. Notified R1DO (Dwyer) and FSME (McIntosh). * * * UPDATE FROM TONY CARPENITO TO JOHN SHOEMAKER AT 1441 EST ON 03/03/11 VIA EMAIL * * * "Subsequent on-site agency inspection performed. Licensee submitted follow-up report [on] 2/28/11. "Cause Description: Misinterpretation of licensee's pre-existing policy restricting workers when YTD [year-to-date] annual exposures approach in-house limits and over-reliance on real-time electronic dosimeters worn specifically during potentially high exposure operations. "Precipitating factor: Over-reliance on real-time electronic dosimeters worn specifically during potentially high exposure operations. "Corrective Action: Licensee to implement policy re-write to minimize subjective misinterpretations, change full-time dosimeter exchange frequency to obtain more current year-to-date exposure totals, replace current job-specific dosimeters with different type of dosimeter better suited to monitor type of work involved, apply administrative correction factors to readings of job-specific dosimeters to obtain more conservative real-time results. "The individual [involved in this event was] removed from potentially high exposure operations during investigation and re-instated several weeks later on 3/3/11. "Although the Agency considers this specific situation to be closed, it will be revisited during future inspections." The report did not state whether an over exposure actually occurred. Notified R1DO (Dimitriadis) and FSME (McIntosh). * * * UPDATE FROM TONY CARPENITO TO CHARLES TEAL AT 0832 EST ON 03/03/11 VIA TELEPHONE * * * The Massachusetts Radiation Control Program determined the individual received a dose of 5457 mrem. Notified R1DO (Dimitriadis) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2011-02-03
46576 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2011-01-31 08:49 | 2011-01-31 10:14 | 2011-01-31 | EMERGENCY NOTIFICATION SYSTEM SIRENS INADVERTANTLY ACTUATED FOR 3 MINUTES "At 0849 [EST] on 1/31/2011 the Emergency Notification System Sirens inadvertently actuated for 3 minutes. We [Davis Besse] have been informed by Ottawa county that the actuation signal appears to have originated from the Ottawa County Sherriff's dispatcher console. They also informed Davis Besse that Vendor Support is being requested to assist in the determination of the cause. The Ottawa County Emergency Management Agency is planning a news release for the inadvertent actuation." The Emergency Notification System sirens were secured and are considered to be operable. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-01-31
46575 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2011-01-28 10:09 | 2011-01-28 11:07 | 2011-01-28 | PLANNED PRIMARY COMMUNICATIONS MAINTENANCE "On Friday, Jan. 28, 2011, the local phone company will upgrade communications lines on the plant site. Telephone (calls coming in and going outside of the plant site) and internet will be out of service from approximately 1 to 3 p.m. (HPN, ERDS, and SPDS will be out of service during this time). "There will be four phone lines that remain operational during the upgrade: "[1.] Emergency notification/verification line in the Control Room, Technical Support Center and Emergency Operation Facility; "[2.] Control Room; "[3.] Main Security; and "[4.] Cell Phone in the Control Room. "Alternate means are available to notify the State of Kansas and the County. Also, alternate means are available to notify the emergency plan organization. "This work is anticipated to last no longer than two hours. If there are problems, the phone company will revert to the original configuration at the end of that time period. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1719 EST ON 1/28/2011 FROM BILL STUCKER TO MARK ABRAMOVITZ * * * Maintenance was completed and tested by 1348 CST. The licensee notified the NRC Resident Inspector. Notified the R4DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-28
46574 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-01-26 | 2011-01-27 15:43 | 2011-01-27 | AGREEMENT STATE REPORT - PROSTATE BRACHYTHERAPY MEDICAL UNDERDOSE The following report was received via fax: "On January 27, 2011, the licensee's Radiation Safety Officer reported the identification of three medical events that were discovered on January 26, 2011, involving permanent implants of Pd-103 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. During a recent routine inspection, DHS [Wisconsin Department of Health Services] inspectors determined that the licensee was not reviewing prostate brachytherapy cases against the medical event criteria. The licensee established dose based criteria used by post-operation CT, prostate D90 values < 80% or >160% for classifying medical events. The licensee has evaluated all prostate implants performed since April 24, 2008. The licensee has notified the referring physicians and the referring physicians will not be notifying the patients. "Case 1, November 2008: Prescribed dose 100 Gy. Prostate D90 was 77%. "Case 2, April 2009: Prescribed dose 100 Gy. Prostate D90 was 71%. "Case 3, October 2009: Prescribed dose 125 Gy. Prostate D90 was 78%. "DHS inspectors are investigating these medical events and will send a special inspection team following the receipt of the licensee's 15 day report." Wisconsin Report Number: WI110003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-02-02
46573 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2011-01-25 20:43 | 2011-01-26 17:08 | 2011-01-26 | FITNESS FOR DUTY REPORT INVOLVING A NON-LICENSED CONTRACT SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The subject individual has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspectors. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2011-01-26
46572 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-12-08 | 2011-01-26 10:14 | 2011-01-26 | AGREEMENT STATE REPORT - POTENTIAL UNDERDOSE TO PATIENT DUE TO ABORTED TREATMENT The following information was received from the State of Ohio by email: "Written directive called for Iodine-125 radioactive seed implant of the prostate with 142 seeds, 0.477 mCi each, total activity 67.7 mCi. Transperineal implantation of the needles were attempted on 12/8/10. After placement of four needles (8 sources) in the first (anterior-most) row, it was subsequently noted that patient's pelvic inlet was too narrow for adequate placement of the lateral two columns of seeds after repeated attempts. Authorized User Physician decided to abort procedure at this point. Patient was taken to the recovery room in satisfactory condition. Patient was notified at time of event. Radiation Safety Officer was not notified at time of event. "Licensee's RSO discovered event during QMP review on morning of 1/25/11 and notified ODH [Ohio Department of Health] by telephone and e-mail that afternoon. ODH inspector will visit licensee's location on 1/31/11. "Given: Radionuclide: I-125; Activity: 3.2 mCi (118.4 MBq); Dose: 81.1 rad (0.811 Gy). "Intended: Radionuclide: I-125; Activity: 67.7 mCi (2504.9 MBq); Dose: 14400 rad (144 Gy)." The source used was a Brachytherapy sealed source I-125; Model Number STM-1251; Serial Number 2357321SO; Activity .477 Ci (17.649 GBq). Ohio number: OH110001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2011-02-01
46571 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-01-26 08:30 | 2011-01-26 09:36 | 2011-01-26 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PLANNED MAINTENANCE "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on TSC support systems. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority. A 10CFR50.54 (q) evaluation has been performed for this planned maintenance activity. "The NRC Resident Inspector has been notified." * * * UPDATE AT 2245 EST ON 1/26/11 FROM WESLEY GRANT TO MARK ABRAMOVITZ * * * TSC maintenance has been completed and testing was performed. The TSC has been returned to service. The licensee will inform the NRC Resident Inspector. Notified the R2DO (Desai). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-26
46570 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2011-01-24 16:54 | 2011-01-25 15:10 | 2011-01-25 | FITNESS FOR DUTY A licensed employee had a confirmed positive for a controlled substance during a fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2011-01-25
46569 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2011-01-25 06:10 | 2011-01-25 08:12 | 2011-01-25 | MANUAL REACTOR SCRAM DUE TO AN UNISOLABLE EXTRACTION STEAM SYSTEM LEAK "At 0610 EST hours on January 25, 2011, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to an unisolable extraction steam system leak in the 1C Feed Water Heater Bay area. "At 0517 EST reactor operators commenced lowering reactor power from 98.4% to 65%. Attempts to isolate the source of the leakage were unsuccessful. Based on continued indications of unisolated steam leakage, operations decided to shut down the plant. The reactor operator placed the mode switch in shutdown. All control rods inserted. Reactor water level lowered to -31 inches causing Level 3 (+ 13 inches) isolation and RCIC initiation. The operations crew subsequently maintained reactor water level at the normal operating band using FW [feedwater]. No steam relief valves opened. All safety systems operated as expected. RCIC automatically initiated on a -30 inch level signal and was manually secured. "The reactor is currently stable in Mode 3. Investigation into the cause of the extraction steam system leakage is underway. "The NRC Resident Inspector was notified. A voluntary notification to PEMA and press release will occur." The steam leak was isolated after the turbine was tripped. The plant is stable at normal temperature and pressure. Decay heat is being removed via the condenser steam dumps to the main condenser. The electrical lineup is in a normal configuration. Estimated time to restart is not known. | 0 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-01-25
46568 | 0 | CATAWBA NUCLEAR SITE |  |  |  |  | 2010-06-05 | 2011-01-24 18:11 | 2011-01-24 | POTENTIAL PART 21 - BUS DISCONNECT STAB ASSEMBLY - 600V ESSENTIAL MOTOR CONTROL CENTERS "During 2004, 2006 and 2010, Duke Energy Corporation (Duke) ordered spare parts for the 600V Essential Auxiliary Power System (EPE) motor control center, installed at the McGuire and Catawba Nuclear Stations. The spare parts were ordered under Purchase Orders 15488, 38585, 132512 and 134626 from Electrical Power Systems, Inc. (EPSI). The specific part is a NEMA Size 1 stab (disconnect) assembly for connecting motor control center feeder circuits to the motor control center main bus. The McGuire and Catawba motor control centers were manufactured by Nelson Electric in Tulsa, OK. Spare stab assemblies were needed for QA-1 applications but they were no longer available to purchase from an approved vendor. The parts were evaluated and approved for Commercial Grade procurement. "When the stab assemblies were received they were dedicated on site at Duke for Commercial Grade application at McGuire and also at Catawba. Inspection of the parts and application of the commercial grade process did not identify that the parts were not manufactured to the specifications used in the commercial grade evaluation process. The manufacturer, who was different from the original parts manufacturer, had revised the detail drawing of the stab assembly. The revised drawing allowed a different method for soldering the lead wire to the stab. During parts dedication, the new stab assemblies passed basic electrical checks, but there was no visual inspection of the soldering because the connections had been inserted into the stab assembly molding. "Catawba Unit 1 experienced a failure of the Jacket Water Keep Warm Pump Motor circuit for Diesel Generator (D/G) 1B on June 05, 2010 due to failure of the soldered connection on a stab assembly that had just been installed. The pump motor is QA Condition 1 and it is powered from a QA Condition 1 motor control center. The failure of the Catawba Unit 1 D/G Keep Warm Pump Motor was not significant from a plant risk standpoint. "Of the 21 spare stab assemblies purchased and dedicated for use at Catawba and McGuire, only one was placed in service. That stab assembly was installed at Catawba on 6/3/2010 and failed on 6/5/2010. The remaining suspect stab assemblies at Catawba and McGuire were put on HOLD shortly after this failure. Other than the failed Catawba stab assembly, no other suspect stab assemblies were placed in service in the past or currently at McGuire or Catawba Nuclear Stations. None of these dedicated stab assemblies were sold or transferred to another nuclear utility. Following the failure of the stab assembly at Catawba, stab assemblies were tested, a failure investigation was performed, design information was requested from the vendor and the commercial grade program implications were investigated. It was not until January 2011 that the issue was determined to be reportable per 10 CFR Part 21." The licensee provided courtesy notifications to the North Carolina and South Carolina Warning Points and York, Gaston and Mecklenburg County agencies. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2011-01-24
46567 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2011-01-19 | 2011-01-24 17:03 | 2011-01-24 | AGREEMENT STATE REPORT - POTENTIAL DOSAGE DIFFERENT THAN INTENDED DOSE The following information was received from the state by facsimile: "The licensee called the PaDEP [Pennsylvania Department Bureau of Radiation Protection] South East Region at 1600 [EST] on January 20, 2011 to provide a 24-hour verbal notice of a medical event involving a dosage that differs from the intended dose by greater than 20%, consequently requiring a 24-hour report per 10 CFR 35.3045(a)(1)(i). PaDEP Central Office was notified on 1/21/2011. "During a formal review immediately following a second Yttrium-90 (Y90) TheraSphere radiation treatment on January 19, 2011, CTCA [Cancer Treatment Centers of America] noticed that the activity of microspheres delivered was different than the activity that was prescribed by the doctor. The patient was first treated with 10 GBq (about 0.27 Ci) of TheraSphere Y-90 beads for the right lobe of the liver. A second treatment of 3 GBq (about 0.081 Ci) was prescribed for the left lobe, however the activity ordered remained unchanged on the second order form, resulting in 10 GBq (about 0.27 Ci) being delivered to the patient. "Cause of the Event: Human Error. "The Department [Pennsylvania Department Bureau of Radiation Protection] has a call into the Radiation Safety Officer regarding the estimated organ dose to the liver, and will be obtaining more event details. At this time DEP plans to send regional staff to conduct a reactive inspection on 1/25/2011. Final event details will be communicated in a NMED and any other required report." Pennsylvania Event Report: PA110001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2011-01-30
46566 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-12-28 | 2011-01-24 15:55 | 2011-01-24 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT INVOLVING RADIOPHARMACEUTICALS The following information was received by email: "DRH [Mississippi State Department of Health] was notified at 0720 [CST], about a transportation accident in Jackson, MS, on Riverside Drive. Cardinal Health Nuclear Pharmacy Services was delivering radiopharmaceuticals to Baptist Hospital and Kings Daughters Hospital. The driver hit an icy patch on the road where a water main had broken. The driver lost control of the delivery vehicle. The vehicle turned over in the median and the driver was trapped. DRH responded at 0730 [CST]. The driver was not injured. Packages were dislodged from their protective security rack, that is required to prevent shifting and movement of packages. Radiopharmaceutical packages were surveyed and wiped for contamination. [No contamination was detected.] The packages were picked up by the Radiation Safety Officer so they could be delivered to the hospitals. The pharmacy's vehicle was then released to the wrecker service." DRH closed this case on 12/28/2010. MS Report No.: MS-10010. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-01-27
46565 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2011-01-24 09:00 | 2011-01-24 11:39 | 2011-01-25 | OFFSITE NOTIFICATION - SODIUM HYPOCHLORITE SPILL AND RELEASE "On 01/24/2011, at 0900 EST, Peach Bottom Atomic Power Station had a spill and release of Sodium Hypochlorite from our water treatment plant's Sodium Hypochlorite tank. The quantity [rate] of release has been estimated at approximately 1 gpm to the surrounding soil area. The leak was into a moat surrounding the tank but it appears it has subsequently leaked from the moat. The leak was identified on 01/24/11 and was quantified as reportable at approximately 0900 EST. The leak is currently in progress with actions being taken to mitigate and control leakage to the area storm drain. This is a release of CERCLA (Comprehensive Environmental Response Compensation and Liability Act) reportable quantity of substance. "The release impacted or potentially impacted the Susquehanna River due to release through a storm drain and additional impact to the surrounding soil. Additional measures being taken include installing additional barriers to release. Lewis Environmental Hazard Mat team has been contacted and is responding to the site. In addition a truck has been dispatched to the site to pump out the moat. "This report is being submitted pursuant to 10CFR 50.72(b)(2)(xi) as a result of a notification of other government agencies." The licensee has notified the NRC Resident Inspector, and state and local government agencies. * * * UPDATE FROM PHILIP PAUTLER TO VINCE KLCO ON 1/25/2011 AT 1340 EST * * * "As of 2200 [EST] last night, the leaking tank and moat area have been drained, and all standing liquid has been removed. "Hourly water samples were collected from the discharge canal and tested. These samples confirmed that no release in excess of the station's NPDES [National Pollutant Discharge Elimination System] permit occurred." Notified the R1DO (Newport). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-01-24
46564 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-01-22 17:35 | 2011-01-22 18:24 | 2011-01-22 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF GENERATOR LOAD The licensee reported a loss of main generator load at full power resulting in a generator trip, turbine trip, and reactor trip. All rods fully inserted. All safety systems functioned as required. The reactor is stable at no-load temperature and pressure in Hot Standby. Auxiliary feedwater started as expected and is currently supplying cooling water to the steam generators. Decay heat is being removed via the atmospheric steam dumps because the turbine bypass system did not respond as expected. There is no known primary to secondary generator leakage The grid is stable and the plant is in a normal post-trip electrical lineup. The reactor trip was characterized as uncomplicated. The cause of the loss of generator load is not yet known and under investigation. The licensee has notified the NRC Resident Inspector. The local County Sheriff was notified of the use of the atmospheric steam dumps to alleviate any concern from local population in the vicinity of the plant. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-01-22
46563 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2011-01-18 17:31 | 2011-01-21 23:00 | 2011-01-21 | BOTH LOOPS OF LOW PRESSURE COOLANT INJECTION INOPERABLE "This condition is being reported in accordance with 10CFR50.72(b)(3)(v) as a condition that could have prevented fulfillment of a safety function. "On 1/18/2011 at 1731 CST, it was discovered that the open position indication light for RR-MO-53A, Reactor Recirculation [RR] Pump A discharge valve operator, was de-energized. The RR-MO-53A operator is powered by a 250 VDC motor with 125VDC control power. Investigations revealed that the 125 VDC control power circuit fuses for the valve operator were open. RR-MO-53A must close at a reactor pressure of 199 to 221 psig to allow Residual Heat Removal [RHR] Loop A to inject to the reactor during a LOCA involving Reactor Recirculation Loop B. This condition rendered RHR Loop A Low Pressure Coolant Injection [LPCI] function inoperable. At the time of discovery, RHR Loop B LPCI function was inoperable for planned maintenance. This maintenance was being performed on the service water side of the RHR heat exchanger, RHR-MO-25B, RHR Loop B Injection Outboard Isolation valve operator, RHR pump B motor, and RHR-MO-39B, Suppression Chamber Cooling Loop B Outboard Isolation valve operator. As specified by the Required Action for LCO 3.5.1 Condition H, two or more low pressure ECCS injection/spray subsystems inoperable, LCO 3.0.3 was immediately entered. LCO 3.0.3 requires the plant to be shutdown to Mode 2 within 7 hours. Preparations to commence plant shutdown were initiated in parallel with investigations to determine the cause of the open control power fuses. Subsequent troubleshooting revealed a failed light socket caused the fuses to open. The fuses were replaced and the circuit tested satisfactorily. At 1915 CST on 1/18/2011, RHR Loop A LPCI was declared Operable and LCO 3.0.3 was exited. The plant shutdown procedure was terminated prior to any power reduction occurring. "Initial review of this condition for immediate reportability under 50.72(b)(3)(v), Condition that Prevents Fulfillment of a Safety Function, concluded the condition was not reportable based on the availability of Core Spray Pump A [CS-P-A], Core Spray Pump B [CS-P-B ], and RHR Pump D [RHR-P-D]. Procedure 2.0.11.1, Safety Function Determination Program, states that Emergency Core Cooling System [ECCS] Safety Function is maintained if three low pressure ECCS Injection/Spray pumps remain operable. CS-P-A, CS-P-B and RHR-P-D all were operable at the time of discovery of the condition. RHR Pump B was restored to available at 1510. The maintenance on RHR Loop B did not remove RHR-P-D from service and an injection path was available at time of discovery of LPCI Loop A inoperable as RHR-MO-25B, RHR Loop B Injection Outboard Isolation valve, post work testing had been completed and the injection capability restored at 1701. Subsequent review determined that the reportability decision under 50.72(b)(3)(v) as a Condition that Prevents Fulfillment of a Safety Function should be based on safety function at the system level, rather than at the ECCS function level. The decision to report the simultaneous inoperability of both RHR LPCI Loops under 50.72(b)(3)(v) was made at 1549 on 1/21/2011." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-01-21
46562 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-01-21 15:39 | 2011-01-21 22:25 | 2011-03-22 | STEAM EXCLUSION DOOR DECLARED INOPERABLE "On 1/21/2011 at 1539 CST, the NRC Resident Inspector informed the Control Room that the lower Cane bolt was disengaged on Steam Exclusion Door 3, between Emergency Diesel Generator Room B and the Cardox Room. While the Cane bolt was not engaged, the barrier was Non-Functional and, in accordance with TRM 3.0.9, all equipment supported by that steam exclusion barrier was immediately declared inoperable. This included both Emergency Diesel Generators A & 8, safety-related 4160 V Busses 5 & 6, Service Water Trains A & B, and safety-related 480 V Busses 51, 52, 61. & 62. In addition, with Service Water inoperable, the following equipment was also inoperable in accordance with TRM 3.3.1: Component Cooling Trains A & B, Safety Injection Trains A & B, Residual Heat Removal Trains A & B, Containment Spray and Cooling Trains A & B, Auxiliary Feedwater Pumps A & B, and the Turbine Driven Auxiliary Feedwater Pump. With all three AFW pumps inoperable. TS 3 A.b.2 was entered to immediately initiate action to restore one AFW Train to operable status and suspend all LCOs requiring mode changes until one AFW Train is restored to operable status. "Steam Exclusion Door 3 was properly secured at 1545 CST on 1/21/2011, and LCO 3.0.c and TS 3 A.b.2 were exited at that time. All equipment affected by the steam exclusion barrier is operable. "This is reportable under 10 CFR 50.72 (b)(3)(v)(B), 'Any event or condition that at the time of discovery could have prevented the fulfillment of a safety function,' and under 10 CFR 50.72(b)(3)(ii)(B) 'any event or condition that results in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety.'" The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM CRAIG J. NEUSER TO DONALD NORWOOD AT 1427 EDT ON 3/22/2011 * * * "Retraction of EN #46562 Non-Functional Steam Exclusion Door. "On January 21, 2011, EN #46562 provided notification that both trains of ESF equipment (e.g., SI, RHR, ICS, etc ) were inoperable following discovery that the lower cane bolt was disengaged on steam exclusion Door 3, between emergency diesel generator Room B and an adjacent equipment room in the turbine building. With the lower cane bolt disengaged, the steam exclusion barrier was considered non-functional. "A subsequent engineering evaluation determined that the Door 3 lower cane bolt was not required for Door 3 to fulfill its function as a steam exclusion barrier. The previously reported condition would not have resulted in an environment that would have adversely impacted the equipment protected by Door 3. Therefore, the door remained functional and the supported ESF equipment remained operable. Consequently, this condition did not meet the reportability criteria in 10CFR50.72. "As a result, the notification made on January 21, 2011, in EN #46562 is hereby retracted. "The NRC Senior Resident Inspector has been notified." Notified R3DO(Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2011-01-21
46561 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2011-01-18 | 2011-01-20 18:39 | 2011-01-20 | AGREEMENT STATE REPORT - DAMAGED SOIL MOISTURE DENSITY GAUGE The following information was provided by the State of California via email: "A CPN MC1DR soil moisture density gauge was run over by a piece of earth moving equipment at a jobsite in Bel Aire, CA on 1-18-2011. This gauge contained 10 mCi Cs-137 and 50 mCi Am-241 sealed sources. The source rod was retracted at the time. The work was immediately stopped, people were kept away, and the area was secured until a CDPH [California Department of Public Health] representative arrived. The sources were leak tested and analyzed on 1-19-2011. The leak test results were negative - less than 0.0005uCi of removable contamination. "GeoSoils Consultants, Inc. is arranging for proper disposal." CA Notification # 011811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2011-01-25
46560 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-01-20 | 2011-01-20 17:33 | 2011-01-20 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The following information was provided by the State of Texas via email: "On January 20, 2010, the Agency (State of Texas) was notified by the licensee that while performing radiography operations at a field location, a radiography camera containing 29 curies of Iridium 192 fell approximately six feet to a concrete surface. The radiographer attempted to retract the source, but it would not move out of the collimator. The locking device on the camera appeared to be damaged and was restricting movement of the drive cable. The radiographer worked on the locking device and was able to retract the source after a period of about 10 minutes. The front source stop was installed to prevent the source from moving from the shielded position. The maximum dose rate taken on contact of the camera was 32 millirem after the event. The survey done on the camera prior to starting work that day was 19 millirem. The radiographer could not disconnect the drive cable from the source pig-tail due to the damage to the locking device. The camera was transported to the licensee's facility for further action. The licensee contacted the manufacturer and with their assistance, was able to disconnect the drive cable from the source pig tail. The rear dust cover was placed on the camera, and both covers secured in place using tape. The camera will be returned to the manufacturer for inspection and repair. "The total exposure received in this event was less than three millirem. Additional information will be provided as it is received." Texas Incident #: I - 8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-01-25
46559 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-01-20 15:18 | 2011-01-20 16:12 | 2011-01-20 | MANUAL REACTOR TRIP DUE TO LOSS OF BOTH MAIN FEED PUMPS DURING SHUTDOWN "Unit 1 performed a manual reactor trip (from 28% power) due to the trip of the 1B main feedwater pump trip concurrent with the 1A main feedwater pump having been previously tripped per the shutdown procedure. Reactor power was below the setpoint for an automatic reactor trip from a turbine trip." All rods fully inserted, heat removal is from auxiliary feedwater and condenser steam dumps, and the electrical system is in a normal alignment. The plant has stabilized at normal RCS pressure and temperature. Both Units 1 and 2 are being shutdown as per Tech Spec 3.0.3 associated with an inoperable Nuclear Service Water System. Unit 2 is at 40% and decreasing power due to the Tech Spec action and was not effected by the Unit 1 reactor trip. Both units will be placed in Mode 5. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-01-20
46558 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2011-01-19 19:00 | 2011-01-20 15:25 | 2011-01-20 | FITNESS FOR DUTY REPORT INVOLVING FFD PROGRAM VULNERABILITY A discovered vulnerability in the Fitness-For-Duty (FFD) program has resulted in contractor personnel being granted unescorted access to Vogtle 3&4 construction site without meeting all the requirements of the FFD Program. Contact the Headquarters Operations Officer for more details. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Under Construction; FMode1: Under Construction | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2011-01-20
46557 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-01-20 11:10 | 2011-01-20 12:46 | 2011-01-24 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "The 1B and 2B trains of Nuclear Service Water Systems (Raw Water Nuclear RN) were declared inoperable on 1/18/11 at 0423 EST due to fouling of the respective suction strainers when aligned to the Standby Nuclear Service Water Pond (SNSWP). "Tech. Spec. 3.0.3 was entered at 1110 EST on 1/20/11 due to the lack of reasonable assurance of operability pertaining to 1A and 2A RN trains in the event of a potential realignment to the SNSWP due to a seismic event." The licensee plans to reduce power and place both Units in Mode 5. Unit 1 has been reduced to 90% and Unit 2 is holding at 100% and will begin reducing power later. The fouling is being caused by fish being sucked into the RN train suction strainers. The licensee has been back-flushing the strainers to clear the fouling. The pond was chemically treated approximately 1 year ago to eliminate the fish. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TERESA PUTNAM TO JOHN KNOKE AT 1313 EST ON 01/21/11 * * * McGuire Units 1 & 2 entered Technical Specification 3.0.3 with a requirement to be in Mode 5 in 37 hours. A Notification of Enforcement Discretion was verbally approved by the Nuclear Regulatory Commission on 1/20/11 at 2336 EST, therefore both Unit 1 & 2 will remain in Mode 3. The licensee notified the NRC Resident Inspector. Notified R2DO (Sykes), NRR EO (Thomas), and IRD MOC (Gott) * * * UPDATE FROM TERESA PUTNAM TO JOHN KNOKE AT 1313 EST ON 01/24/11 * * * This is an amendment to Event Notification #46557 to include the following 8 hour non-emergency notifications previously omitted by the NRC from the event report: 50.72(b)(3)(v)(A) POT UNABLE TO SAFE S/D 50.72(b)(3)(v)(B) POT RHR INOP 50.72(b)(3)(v)(D) ACCIDENT MITIGATION The licensee will notify the NRC Resident Inspector. | 90 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2011-01-20
46556 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2011-01-19 18:41 | 2011-01-20 00:08 | 2011-01-20 | REACTOR TRIP DUE TO MAIN FEEDWATER PUMP TRIP "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On January 19, 2011, at approximately 1840 Mountain Standard Time (MST), Palo Verde Unit 3 received a Reactor Power Cutback (RPCB) due to the 'B' Main Feedwater Pump (MFP) tripping on low suction pressure in response to the 'A' MFP mini-flow valve failing open. Reactor power lowered to approximately 60% in response to the RPCB. Steam Generator levels continued to decrease and a Reactor Trip occurred on Low Steam Generator #1 level at 18:41. Unit 3 was at normal operating temperature and pressure prior to the trip. Following the automatic reactor trip all CEAs [Control Element Assemblies] inserted fully into the reactor core. No emergency classification was required per the Emergency Plan. An AFAS-2 [Auxiliary Feedwater Actuation Signal] occurred at 1844 on low Steam Generator #2 level. Safety related busses remained energized during and following the reactor trip. The Emergency Diesel Generators started in response to the AFAS-2 actuation but did not energize the class 4.16kV buses as they remained energized from off-site power. The offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event. "Unit 3 is stable at normal operating temperature and pressure in Mode 3 feeding the steam generators with Auxiliary Feedwater pump 'B'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The [NRC] Senior Resident Inspector was informed of the Unit 3 reactor trip." Unit 3 is in a normal post-trip electrical lineup. Decay heat is being removed via the turbine bypass valves to the main condenser. No safety valves on the secondary or primary side opened. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2011-01-20
46555 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2011-01-19 20:58 | 2011-01-19 22:50 | 2011-01-19 | NOTICE OF UNUSUAL EVENT (NOUE) DUE TO A SECURITY EVENT The licensee declared an unusual event based upon a potential security incident at the site. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. The licensee terminated the NOUE at 2150 CST. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | AR | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-01-19
46554 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-01-06 17:02 | 2011-01-19 17:44 | 2011-01-19 | FOREIGN MATERIAL FOUND IN SPARE HEAT EXCHANGER "Part 21 reportable defect foreign material (FM) was discovered in a spare heat exchanger (HX) when visually inspected on 10/19/10 as part of contingency planning for potential installation of the HX during the 3EOCÀ25 refueling outage. Visual inspections with a video probe (fiberscope) were being performed on the inlet/outlet channels and the tubes of a spare HX to verify that no FM was present. However, when performing these inspections, a problem was encountered in that maintenance was unable to disassemble and remove the bonnet from the lower (inlet) pressure seal connector on the HX. "Subsequently, on 10/19/10 a fiberscope inspection was performed of the "back side" of the pressure seal bonnet by inserting a fiberscope thru the inlet nozzle access. A foreign object that appeared as a u-shaped piece of thin wire was seen just behind the pressure seal bonnet, laying in the bottom of the body. Due to the inability to disassemble the pressure seal connector, the affected HX was not installed, "The FM was retrieved from the spare HX on December 27,2010 and its size and material type confirmed. The "U-shaped" material is type 304 stainless steel and appears to be a metal shaving. It is about 1-1/2" in length if the "u" was stretched out, 3/32" wide and less than 1/64" thick. "The HX was intended for use as a Reactor Coolant System Letdown Cooler. It was ordered in 2006 and was supplied by Energy Steel Supply Company (ESSC), Catalog 10 350952, SIN N32389-1, Purchase Order No. DP 19279. "Initial Safety Significance: This event has no actual significance since the issue was discovered prior to installation of the component and the component was not installed. However, Part 21 requires evaluation based on the assumption that the component was installed in the as-found condition. On 1/6/2011, Oconee Engineering concluded that, in some low probability scenarios, this FM could constitute a Substantial safety hazard. Per the postulated scenarios, the FM would be flushed out of the cooler when placed in service. A low potential exists that the FM could be trapped in a downstream valve and damage the seat, resulting in leakage. The cooler outlet valve and the next valve in series are containment isolation valves. If the FM caused leakage in one of those valves and the other was affected by a postulated single failure, any resultant leakage would constitute containment leakage. Also, in some event scenarios, unacceptable leakage past the cooler outlet valve seat could render the Oconee Standby Shutdown Facility (SSF) Reactor Coolant Make-up System inoperable. Therefore, Oconee concludes this issue meets the Part 21 definition as a reportable defect. "Corrective Action(s): The affected spare cooler was not installed. Subsequently, the FM was removed. A second spare cooler was inspected, no similar FM was found, and the second cooler was installed." The NRC Resident Inspector will be notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2011-01-19
46553 | 0 | BOTSFORD CANCER CENTER |  |  |  |  | 2011-01-19 09:40 | 2011-01-19 17:25 | 2011-01-19 | DOSE TO NON-RADIATION WORKER DURING MEDICAL TREATMENT The licensee reported an event that occurred while using a HDR Afterloader brachytherapy device for prostate treatment with a 8.3 curie Ir-192 source. Following setup of the HDR Afterloader, the medical staff exited the treatment room and commenced the prostate irradiation. 1.8 minutes after the start of the treatment, the anesthesiologist technician was observed exiting the treatment room. The staff physicist completed the patient treatment and then conducted a review of the circumstances of the event. The anesthesiologist technician was unaware that the treatment was beginning and was crouched down and not visible when the rest of the staff left the treatment room. The technician was not wearing dosimetry (and not required to) so his exposure was estimated based on recreation of the event. His calculated exposure is believed to be approximately 5.6 millirem. The licensee is still evaluating corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MI | HOS | [5 empty] | 0 | 2011-01-19
46552 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2011-01-19 | 2011-01-19 10:29 | 2011-01-25 | AGREEMENT STATE REPORT - INDUSTRIAL GAUGES INADVERTENTLY SENT TO SCRAP MATERIAL RECYCLER General Mills Company in Moonachie, New Jersey notified Terrapin Recycling of Baltimore, Maryland that they inadvertently sent three industrial gauges to Terrapin in a load of scrap material. General Mills has contracted Clym Environmental Services, LLC of Frederick, MD to locate and recover the gauges. The gauges are Peco Controls Corporation Industrial gauges and each of them contain 100 mCi of Am-241. The State of Maryland has notified the State of New Jersey. * * * UPDATE BY ALAN JACOBSON TO VINCE KLCO ON 1/25/2011 AT 1138 EST * * * The following information was received from the State of Maryland by email: "After searching approximately 800 tons of scrap metal on Friday, January 21, 2011, two of the three devices were located and retrieved from compressed bails. Leak tests were conducted. Results revealed no contamination. The two sources remain secured at Terrapin, pending transportation to an authorized recipient. The search for the third device continues. The State of New Jersey was notified on January 19, 2011." Notified the R1DO (Newport) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2011-01-24
46551 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2011-01-19 02:32 | 2011-01-19 03:10 | 2011-01-19 | NOTIFICATION OF UNUSUAL EVENT DUE TO A FIRE AND EXPLOSIONS IN THE PROTECTED AREA "An electrical fire and explosions were reported near the Containment Access Facility construction area. An Unusual Event was declared based on HU4. Temporary electrical power at service disconnect DSLM3-3 was isolated. The fire was out at 0243 EST. The fire was extinguished using dry chemical. The fire was reported at 0232 EST on 1/19/11. The cause of the fire has not been determined at this time." The fire and explosions were initially reported by site security personnel. The licensee declared the NOUE at 0243 EST based on criteria HU4. The licensee initially called for offsite assistance in putting out the fire, however, the fire was extinguished by plant personnel and the offsite assistance was turned back. The licensee posted a reflash watch. The fire reportedly involved temporary cables and possibly a transformer supplying power to the construction area which is located inside the protected area outside the auxiliary building. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TOM PHILLIPS TO DONALD NORWOOD AT 0405 EST ON 1/19/2011 * * * The licensee terminated the Notification of Unusual Event at 0358 EST. No additional information is available at this time. Notified R3DO (Bloomer), NRR EO (Skeen), IRD (Gott), DHS (Stringfield), and FEMA (Casto). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-01-19
46550 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2011-01-18 09:45 | 2011-01-18 16:37 | 2011-01-18 | SIREN GROWL HEARD OFFSITE "On January 18, 2011, at about 0830 PST, a State Park Ranger notified SONGS [San Onofre Nuclear Generating Station] Security that a siren growl was heard in the San Clemente State Park. Security subsequently notified the Control Room. Site Emergency Planning initiated an investigation of the event and informed the City of San Clemente Emergency Planning at approximately 0945 PST of the park ranger's call. "SONGS investigation by its siren technicians into the potential SONGS siren growl resulted in absolutely no indication of activation of any of SONGS emergency sirens. It should be noted that quarterly growl tests have been scheduled during working hours January 18-20, 2011, and this information is posted on the City of San Clemente web site. However the tests had not been initiated at the time of the ranger report. "In compliance with 10CFR50.72(b)(2)(xi), requiring licensees to report any event that results in notification to other government agencies, SCE [Southern California Edison] is providing this notification to the NRC. "At the time of the State Park Ranger notification, Unit 2 was at approximately 100 percent power and Unit 3 was shutdown for a Steam Generator Replacement Outage. SCE will notify the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." * * * UPDATE FROM DENNIS MORRIS TO JOE O'HARA AT 1954 ON 1/18/11 * * * "SONGS telecommunications confirmed that the siren which was reported earlier was associated with Camp Pendleton and not associated with SONGS." Notified R4DO(O'Keefe) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-01-18
46549 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2011-01-18 06:00 | 2011-01-18 15:19 | 2011-01-18 | CONFIRMED POSITIVE TEST FOR ILLEGAL DRUG A non-licensed employee supervisor has a confirmed positive test for an illegal drug during a random fitness for duty test. The employees access to the plant has been cancelled. Contact the Headquarters Operations Officer for more details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2011-01-18
46548 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2011-01-19 02:00 | 2011-01-18 10:48 | 2011-03-24 | EMERGENCY RESPONSE DATA ACQUISITION AND DISPLAY SYSTEM (ERDADS) REMOVED FROM SERVICE FOR MAINTENANCE "On 1/19/11, St Lucie Unit 1 and Unit 2 will lose the computer trains associated with Emergency Response Data Acquisition and Display System (ERDADS). Unit 1 will be removed for corrective maintenance, and Unit 2 will be removed for system modification. It is expected that Unit 1 will be restored by 1/21/11, and Unit 2 will be returned to a functional status prior to core reload and fully operational by March 20, 2011. Further, neither Unit 1 nor Unit 2 ERDADS will be removed from service until Unit 2 has defueled (currently scheduled for 1/19/2011 at 0200). This is an advance notification of a planned loss of emergency assessment capability, which will be reportable under 10CFR50.72(b)(3)(xiii). Other means to monitor critical data exists. Notification will be made when each unit is restored to available status." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM REESE KILIAN TO HOWIE CROUCH @ 0952 EST ON 1/19/11 * * * "Unit 1 and 2 ERDADS have been removed from service at 0955 [EST]." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM TIMOTHY KUDO TO JOHN SHOEMAKER @ 1527 EST ON 01/20/11 * * * Unit 1 ERDADS has been returned to available status as of 1520 EST on 01/20/11. Unit 2 ERDADS remains out of service. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BISHOP TO HUFFMAN AT 2013 EDT ON 3/24/11 * * * Unit 1 and Unit 2 ERDADS have both been restored to service as of 1600 EDT on 3/24/11. The licensee has notified the NRC Resident Inspector. R2DO (Rich) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-18
46547 | 0 | ELI LILLY AND COMPANY |  |  |  |  | 2011-01-14 | 2011-01-17 10:48 | 2011-02-08 | LOST TRITIUM EXIT SIGNS A major renovation was performed in two floors of Building 22 on the Eli Lilly Campus. This renovation was completed in December, 2010. An inventory of tritium exit signs was performed and eight exit signs on the two floors were found missing and presumed disposed of during the renovation. The exit signs each contained approximately 10 Curies of tritium. The licensee will perform wipe tests but expects negative results since the concrete surfaces were all covered with carpet, tile, or wall coverings. Four Evenlite Model 201 serial numbers 57281, 59311, 57381, 57421 Four SRBT Model BX serial numbers C035796, C035795, C035790, C035789 * * * UPDATE AT 1555 ON 2/8/2011 FROM STAN HANPTON TO MARK ABRAMOVITZ * * * The inventory of tritium exit signs was extended and eight additional tritium exit signs were missing. These additional exit signs were assigned to building 31 on the Eli Lilly Campus. This building had also been recently renovated. Each sign contained approximately 10 Ci tritium. Wipe tests in building 22 and 31 were performed with no activity detected. Notified the R3DO (Duncan), ILTAB (Allston), and FSME (McConnell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2011-01-17
46546 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2011-01-15 09:33 | 2011-01-15 13:26 | 2011-01-15 | NOTIFICATION OF STATE OF LOUISIANA AGENCIES DUE TO OFFSITE TRANSPORT OF POTENTIALLY CONTAMINATED INJURED INDIVIDUAL "In response to a personnel injury, River Bend Station notified the State of Louisiana Governor's Office of Homeland Security and the Louisiana Department of Environmental Quality that a potentially contaminated employee was being transported offsite for medical attention. "Later, it was determined by River Bend Radiation Protection technicians that the employee was not contaminated. State of Louisiana agencies were notified that no contamination was found on the employee, the gurney, or the ambulance. "The NRC Senior Resident Inspector was notified." The injured individual was non-responsive when transported. At the time of this report, no other details concerning the injured individual's condition were available. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2011-01-15
46545 | 0 | ABB INC. |  |  |  |  | 2011-01-10 | 2011-01-14 18:52 | 2011-02-08 | PART 21 NOTIFICATION OF POTENTIAL DEFECT FOR OVERCURRENT RELAYS The following information was received by facsimile: "This letter is submitted in accordance with 10 C.F.R º 21.21(d)(3)(ii) with respect to a failure to comply with the specifications associated with the COM 5, COM 9, and COM 11 Overcurrent Relays. The style numbers for the COM 5 relay are 1326D81A07A. 1326D81A05A, 1326D81A01, 1326D81A02, 1329D12A02, 1329D12A01, 1329D12A06, 1326D81A08, 1329D12A07, 1329D12A05, 1329D12A06, 1329D12A08, 1329D12A09, 1326D81A08A, and 1326D81A09A. The style numbers for the COM 9 relay are 1326D81A10A and 1326D81A10. The style numbers for the COM 11 relay are 1329D12A03, 1326D81A03, and 1326D81A03A. "The notifying individual is Mr. Pat Wilkinson, General Manager, ABB Inc. (Distribution Automation), 4300 Coral Ridge Rd, Coral Springs FL, 33065. "Notification regarding the subject relays is as follows: The failure to comply centers around the seismic specification of the COM 5, COM 9, and COM 11 relays. The Zero Period Acceleration (ZPA) rating for the COM 5, COM 9 and COM 11 relays were incorrectly being certified to meet a ZPA rating of 5.6g. The relays only meet a ZPA rating of 3.6g. "On December 14th, 2010, ABB's Engineering Group, while performing a document review of the ABB's CTR-COM-5 Qualification Conclusion Report, discovered the incorrectly reported ZPA rating. The deviation was identified as a potential defect on January 10, 2011. "The COM family relays were originally seismically qualified by Westinghouse on July 11, 1977 with a ZPA rating of 5.7g. A second seismic qualification test was performed by an outside vendor on September 12, 2001 with a reported ZPA rating of 3.6g. ABB then transferred the vendor information to its own conclusion report: CTR-COM-5 signed December 14, 2001. The CTR-COM-5 conclusion report incorrectly transcribed the ZPA rating of 3.6g from the outside vendor. The CTR-COM-5 conclusion report is the basis for ABB's Relay Selection disk, used by ABB Marketing, and ABB's quality Certificate of Conformance. "The root cause of this issue was determined to be inadequate review and transfer of the outside vendor's seismic test data. "ABB is taking, or has taken, the following corrective actions: - Correct CTR-COM-5 conclusion report to 3.6g ZPA (Engineering completed request on January 11, 2011 ) - Contact all customers with potentially affected open Purchase Orders to ensure acceptance of the 3.6g ZPA rating. Orders on hold until acceptance. (Sales to complete by January 21, 2011) - Update Certificate of Conformance template for the affected style numbers to reflect 3.6g ZPA. (Quality Assurance completed request on January 13, 2011) - Perform a review of all qualification reports to ensure all ZPA ratings for all product families are correctly reported (Engineering to complete by February 14, 2011) - Identification of potentially affected customers (Marketing to complete by February 15, 2011) - Notification of potentially affected customers (Marketing to complete by February 28, 2011). - Correct ZPA rating on the Relay Selection Disk to 3.6g ZPA (Marketing to complete by October 30, 2011) "The customers and the quantity data are still being collected at this time. Depending upon a Licensee's specified ZPA requirements, the lower ZPA rating of relays could possibly create a substantial safety hazard. If a higher ZPA rating is required by the Licensee, please contact ABB Coral Springs Customer Support at 1-800-222-1946 or (954) 825-0606 on available solutions. "If you have any questions regarding this notice, please contact the Quality Manager, Mr. Chad Buchwalter, directly at (954) 825-0604." * * * UPDATE FROM CHAD BUCHWALTER TO HOWIE CROUCH VIA FAX ON 2/8/11 @ 0857 EST * * * ABB Inc. updated their initial report to state that they had previously made 10 CFR 21.21 notifications on ZPA deviations for the COM relays (see EN #30753). Additionally, they provided a list of customers who may have received the subject relays. No nuclear power plants were listed on the customer roster. Notified R1DO (Bellamy), R2DO (Hopper), R3DO (Duncan), R4DO (Clark) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2011-01-14
46544 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-11-18 02:45 | 2011-01-14 17:19 | 2011-01-14 | INVALID ACTUATION OF MOTOR DRIVEN EMERGENCY FEEDWATER SYSTEM "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of the Emergency Feedwater (EFW) System on Oconee Unit 3 on 11/18/10 while moving the 3A Motor Driven EFW Pump (MD EFWP) control switch from position 'Auto 1' to 'Auto 2.' EFW is a system named in 50.73(a)(2)(iv)(B). "The 3A MD EFWP was inadvertently started during operation of the control switch in the Oconee Unit 3 Control Room. The start signal was a manual start when the operator moved the control switch beyond the intended position. The functioning/behavior of the MD EFWP control switch and human error are being investigated in the site corrective action program. This is considered an INVALID signal with respect to 50.73(a)(2)(iv)(A). The manual start only affected the 3A MD EFWP. "On 11/18/10, a Unit 3 startup from a refueling outage was in progress. Unit 3 was in Mode 3. While performing a step in OP/3/A/1102/001 (Controlling Procedure for Unit Startup), the Operator inadvertently started 3A MD EFWP when positioning 3A MD EFWP control switch from position 'Auto 1' to 'Auto 2.' "Specific Information Required per NUREG 1022: (a) The specific train(s) and system(s) that were actuated: The specific train(s) and system(s) that were actuated was the 3A MD EFWP and the A train of EFW. The 3B MD EFWP and the Turbine Driven EFW Pump were not affected by this event. (b) Whether each train actuation was complete or partial: The manual actuation was considered complete (i.e. all necessary components responded to the start signal to provide EFW to the Steam Generator (SG). The A train control valve (3FDW-315) was open, as expected for the evolutions in progress. This allowed EFW to reach the SG. C) Whether or not the system started and functioned successfully: The 3A MD EFWP and train started and operated successfully until secured by Operations personnel. "Initial Safety Significance: None, there was no significant transient. "Corrective Action(s): EFDW was secured within approximately one minute by placing 3A MD EFWP control switch in the Auto 2 position. This event has been entered into the site corrective action program for resolution." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2011-01-14
46543 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2010-11-23 | 2011-01-14 15:49 | 2011-01-14 | AGREEMENT STATE REPORT INVOLVING A MEDICAL EVENT The following report was received from the State of Illinois via email: "On January 13 [2011], the licensee's Radiation Safety Officer contacted the Agency [Illinois Emergency Management] to report an apparent medical event that had been discovered during routine post surgery follow up. A patient had undergone treatment for prostate cancer utilizing permanent brachytherapy I-125 seed placement. A total of 102 seeds were inserted into the region in order to deliver a prescribed dose of 14,500 Rad. Manual insertion of the 0.4 milliCi I-125 seeds was done by ultrasound guided placement of the needle template. A C-arm x-ray scan was done post implant of the 0.4mm x 1mm seeds. Visualization of the seed placement was problematic in the post operation scan. Initial estimates were that the seeds may have been inferior to the ideal placement, but still acceptable. However, engorgement of the surrounding tissue and prostate due to the surgical procedure made visualization difficult and performance of additional dosimetry was deemed inappropriate and of little value. The patient was kept appraised of the situation beginning just prior to discharge and advised of the need for continued follow up. As the patient healed, additional scans were scheduled at the 4 week post treatment mark. Those scans suggested the seed placement to be 4-5 cm inferior of the treatment plan. Although the inferior placement of the seeds resulted in avoiding doses to the rectum and bladder as intended in the original treatment plan, as wells as the urethra, the dose to the prostate was suboptimal. Regions receiving elevated dose were the soft tissue at the base of the penis and the penile bulb. Dosimetry values for dose to the prostate provided by the licensee at this time are rough estimates, but are less than 80% of the intended dose. "Currently, the patient is asymptomatic. No prediction of long term effects has been made at this time. Physicians are considering the application of external x-ray beam to provide a more effective treatment to the tumor site. This matter remains under investigation by the licensee and the Illinois Emergency Management Agency. The licensee is obliged to file a written report [to the Illinois Emergency Management Agency] in compliance with the rules within 15 days. Given: Therapeutic Procedure: BRACHY, MANUAL IMPLANT Organ: ND Radiopharmaceutical: Radionuclide: I-125, Activity: 42.7 mCi 1579.9 MBq, Dose: 4400 rad 44 Gy Intended: Therapeutic Procedure: BRACHY, MANUAL IMPLANT Organ: PROSTATE Radiopharmaceutical: Radionuclide: I-125, Activity: 42.7 mCi 1579.9 MBq, Dose: 14500 rad 145 Gy % Dose Exceeds Prescribed: 0 % Dose is Less Than Prescribed: 70 Effect on Patient: UNKNOWN The patient was informed of the underdose. IL Report No.: IL11-004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2011-01-20
46542 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2011-01-14 08:40 | 2011-01-14 14:31 | 2011-01-21 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO MAINTENANCE "At 0840 [CST] on Friday, January 14, 2011, a portion of the Duane Arnold Energy Center (DAEC) Technical Support Center (TSC) ventilation was removed from service to conduct maintenance on the charcoal filter medium. The TSC Stand-by Filter Unit (TSC-SFU) was found with deluge water in the bottom of the charcoal filtration bed, and is therefore non-functional. "Under certain accident conditions the TSC may become unavailable due to the inability of the ventilation system to maintain a habitable atmosphere. "The licensee has notified the NRC Resident Inspector. This notification is being made in accordance with 10 CFR 50.72 (b) (3) (xiii) due to a loss of emergency response facility." * * * UPDATE AT 1105 ON 1/21/11 FROM ROB SPADING TO PETE SNYDER * * * Maintenance has been completed and the TSC is returned to service as of 1005 CST. Notified R3DO (Bloomer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-14
46541 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-01-14 12:30 | 2011-01-14 14:07 | 2011-02-07 | SAFEGUARDS REPORT Failure to adequately control security-related information. Compensatory measures in effect. The licensee informed the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1529 ON 2/7/2011 FROM ERICK MATZKE TO MARK ABRAMOVITZ * * * During the continuing review, additional security related information was found. The licensee informed the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified the R4DO (Clark) and 73.71 group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2011-01-14
46540 | 0 | INDIANA MICHIGAN POWER |  |  |  |  | 2011-01-14 10:00 | 2011-01-14 13:50 | 2011-01-14 | FIXED GAUGE SHUTTER UNABLE TO CLOSE DUE TO MECHANICAL FAILURE "On Friday, January 14, 2011 at approximately 1000 Hrs (EST) one of [the] facility Assistant RSOs was advised that one of our devices was inoperable. This was due to a failure in the cable handle bracket mechanism, not the source itself. The handle that operates the cable that opens and closes the level indicator is held in place by a bracket that is mounted (bolted) to the side of the equipment. The lower lever pivot (hinge) bracket failed, probably due to age, resulting in an inability to operate the mechanism as designed. The radiation source is located between two Gas Recirculation Hoppers approximately 10-15 feet away. "The equipment has been tagged pending repair, and affected employees were notified. "A manufacturer's authorized repair technician has been scheduled to make repairs on Thursday, January 20, 2011. Upon completion of repairs and after the device has been inspected and placed back in service [the licensee] shall notify [the NRC] in writing. "Location: Indiana Michigan Power A Division of American Electric Power Rockport Plant Spencer County 2791 North US Hwy 231 Rockport, IN 47635 "Isotopes: Cs-137 Quantities: 100mCi Chemical/Physical Form: Gas Recirculation Hopper Level Indicator Manufacturer: Texas Nuclear Device Model: 5197 Device Serial Number: LE/LX 5705 Source Serial Number: B2147 "No personnel exposure or injuries sustained." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-01-14
46539 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2011-01-14 11:25 | 2011-01-14 12:47 | 2011-01-14 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "The Technical Support Center HVAC unit has been removed from service for a planned maintenance outage with an expected duration of 8 hours. A 10 CFR 50.54(q) evaluation has been performed for this outage and the current level of effectiveness of the FNP [Farley Nuclear Plant] Emergency Plan is maintained. Alternate Technical Support Center capability has been verified in accordance with site procedure FNP-0-EIP-6.0, Technical Support Center Setup and Activation. Technical Support Center HVAC is expected to be returned to service at 1925 [CST] on 1/14/11." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-14
46538 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2011-01-14 04:26 | 2011-01-14 11:49 | 2011-01-14 | LOSS OF ENS AND ERDS CAPABILITY DUE TO A FAILURE OF THE PHONE SYSTEM UPS "On January 14, 2011 from 0426 to 0551 [EST] the NRC ENS phone line was lost for Hope Creek and Salem Units 1 and 2. The loss of the phone lines occurred during planned island ring bus switching and was caused by a failure of the phone system Uninterruptible Power Supply (UPS). The phone system UPS was manually restored by Information Technology personnel and the phone line was verified to be operational. The loss of the phone line had no effect on plant operations and all three units remain at 100% power. "Additionally, Emergency Response Data System (ERDS) capability was lost during this time period and has been restored. "The station has initiated a prompt investigation into the cause of the failure of the phone system UPS to properly transfer. "No personnel injuries resulted from the event. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-14
46537 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2011-01-12 15:00 | 2011-01-13 16:03 | 2011-01-13 | AGREEMENT STATE REPORT - THEFT OF A NUCLEAR DENSITY GAUGE The following information was received by e-mail: "The licensee's RSO [Radiation Safety Officer] contacted DRH [Mississippi Division of Radiological Health] to report the theft of their Troxler Model 3440 (S/N 26434) nuclear gauge that was secured in the back of their stolen white Ford F-150 pick-up truck parked in the licensee's fenced lot. The truck and gauge were estimated to have been stolen between 1500 [CST] and 1530 [CST]. The gauge was stored in the yellow plastic transport case with Radioactive Yellow II labels attached. "The licensee was instructed by DRH to send in a written report describing the incidents leading up to the event that occurred on January 12, 2011, and any corrective actions or follow up performed. Once the gauge is located, DRH will survey and retrieve the gauge. DRH will notify NRC Operations. Event is under investigation and enforcement action may be required by DRH. "Jackson City Police was notified by the licensee. Mississippi State Department of Health (MSDH) notified Mississippi Emergency Management and Mississippi Homeland Security. MSDH issued a press release January 13, 2011. DRH will notify NRC Operations." Gauge Isotopes: Cs-137(9 mCi) and Am/Be-241 (40 mCi). Mississippi Event Number: MS-11-001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2011-01-18
46536 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-09-18 20:30 | 2011-01-13 15:30 | 2011-01-18 | AGREEMENT STATE REPORT INVOLVING AN EXIT TRITIUM SIGN DESTROYED IN A FACILITY FIRE The following information was received by facsimile: "The RPS [North Carolina Radiation Protection Section] received a voice message on 1-6-2011 from the FMC Lithium RSO [Radiation Safety Officer]. The RSO wanted RPS to contact him concerning removing an Exit Sign from his current inventory of sources. [RPS] was able to get in touch with the RSO on Wednesday, January 12, 2011 and the RSO stated on the phone than he needed to remove the Exit Sign because there was a fire at the facility on September 18, 2010 that shut down the facility for two weeks and damage was around $500,000. RPS explained to the RSO that he should have responded and reported the incident/fire immediately to our office. "[RPS] received a call back from the RSO for FMC Lithium concerning which Exit Sign was affected by fire on September 18, 2010. The General License Number: 036-2384-0G has 6 Cs-137 gauges that are active and one Cs-137 gauge in storage. Also, they have 22 Tritium exit lights in service on and before the fire on September 18, 2010. The reason the RSO reported the Exit Sign on 1-12-2011 was he was going to order a replacement for the one that was destroyed in the fire and he was getting ready to perform a Radiation Training Session for their employees. The source that was destroyed was: Manufacturer: Shield, Model: SLX-60, Serial Number: 10-21664, Source: H-3, Activity: 0.230 mCi ea., Location: SO Building 1st floor. Installed: Aug/2010" North Carolina Event: 11-02 * * * UPDATE FROM WILLIAM JOHNSON TO JOE O'HARA AT 1246 EST ON 1/18/11 * * * The state called to clarify that the activity level is 6.21 Curies H-3 vice 0.230 mCuries, and the manufacturers full name is Shield/Isolite vice Shield as reported above for the exit sign which was destroyed. Notified R1DO(Jackson) and FSME(Villamar). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2011-01-18
46535 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2011-01-12 10:20 | 2011-01-12 15:16 | 2011-01-12 | LOSS OF UNIT 2 ESSENTIAL SERVICE 480V BUS "On January 12, 2011, at 1020 hours, Unit 2 480V Essential Service Bus 29 was inadvertently deenergized. The cause of the bus trip was inadvertent contact with a bus feed breaker by a station employee during unrelated work activities. Normal power to Bus 29 was restored at 1026 hours. While Bus 29 was deenergized Division II core and containment cooling systems were unavailable and inoperable. "The plant responded normally to the loss of Bus 29 with the exception of Bus 28/29-5 which should have automatically transferred from Bus 29 to the reserve feed from Bus 28. This condition renders both divisions of the Low Pressure Cooling Injection (LPCI) mode of the Residual Heat Removal (RHR) system inoperable. Technical Specifications 3.5.1.E has been entered, requiring restoration of LPCI in 72 hours. "Bus 28/29-5 was manually energized from Bus 28 at 1213 hours; however, LPCI remains inoperable pending investigation and restoration of Bus 28/29-5 auto-transfer function. "This event is reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function." LPCI mode of the RHR system is inoperable because the auto-transfer function for Bus 28/29-5 provides a back-up power supply to the LPCI injection motor operated valves from Bus 28. A swing diesel test was in progress during this bus loss, however the diesel was not loaded and had no impact on the bus failure. The diesel was subsequently secured. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-01-12
46534 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2011-01-10 19:00 | 2011-01-11 18:27 | 2011-01-14 | AGREEMENT STATE REPORT - SPOOL VALVE FAILURE ON IRRADIATOR "A pool type irradiator experienced a drive mechanism failure on one of the two racks. This caused the 1.2 M Curie of Co-60 to remain stuck in the retracted position. It remained there for one hour until the operators discovered that a spool valve was stuck. Once the valve was freed the source rack returned to the pool as normal. The licensee is investigating the equipment malfunction and will submit further information when available." There were no personnel injuries. TX Incident No: I- 8809 * * * UPDATE FROM BLANCHARD TO KLCO ON 1/14/11 AT 1355 EST * * * "At approximately 1900 [CST] on January 10, 2011, a licensee operating a pool-type irradiator in El Paso, TX, experienced a drive mechanism failure on one of two source racks. This caused the 1.2MCi of Cobalt-60 (Co-60) to fail to descend into the pool. The source rack remained in the lifted position for approximately one hour until the operators discovered that a spool valve was stuck. A piece of pipe was removed to allow the piston to vent, thus bypassing the valve. The source rack returned to the pool in a controlled, normal descent. The licensee is investigating the equipment malfunction and will submit further information when available. "The initial report stated that the source rack had remained in the retracted position. Wording has been changed to more clearly describe, and clarify, that the source rack was stuck outside the pool (unshielded) for approximately one hour. There were no problems with the rack or the sources, the only issue was the spool valve malfunction." Notified R4DO (Hagar) and FSME (Villamar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2011-01-14
46533 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2011-01-10 23:59 | 2011-01-11 10:29 | 2011-01-11 | LOCKING MECHANISM MALFUNCTION ON RADIOGRAPHY CAMERA "On January 10th, the radiography crew working the Kuparuk Oil Field on the North Slope of Alaska experienced a malfunctioning locking system on an INC IR-100 exposure device (serial number 6631). "During the shift the source was cranked in and the camera was surveyed per the proper procedure. There were no abnormal readings observed during the survey and the key was turned to the lock position. When the crank assembly was removed it was noted that the pigtail was not fully seated. "The 2 mR/Hr boundary was reconfirmed and the night foreman was notified. The camera was surveyed and noted as being safe to transport. The camera was tagged out and placed in the permanent storage facility. A trained radiographer removed and cleaned the locking system. The locking system was successfully reinstalled. The camera has been returned to service. "Exposure Device: Industrial Nuclear IR-100 Device SIN: 6631 Source SIN: 666928 Source Activity: 95 curies Source Type: Ir192 Source Model # QSA 87703 "There was no exposure to the crew or the general public during this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2011-01-11
46532 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2011-01-10 12:00 | 2011-01-10 21:47 | 2011-01-10 | FITNESS FOR DUTY - CONTRACTOR CUSTODIAN FOUND WITH ALCOHOL INSIDE THE PROTECTED AREA Alcohol was found in the possession of a contractor inside the protected area. The individuals access to the plant has been terminated. Contact the Headquarters Operations Officer for additional information. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2011-01-10
46531 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-01-10 13:21 | 2011-01-10 19:39 | 2011-01-14 | BOTH TRAINS OF AUXILIARY BUILDING VENTILATION BECAME INOPERABLE "On January 10, 2011, at 1321 PST, Diablo Canyon Power Plant, Unit 2, entered Technical Specification Limiting Condition of Operation (TS LCO) 3.0.3, when both trains of Auxiliary Building Ventilation System (ABVS) became inoperable following closure of damper M-4 and the ensuing loss of both exhaust fans E-1 and E-2. TS LCO 3.0.3 was exited on January 10, 2011, at 1342 following a status reset and selection of fan E-2. This provided a ventilation flowpath and use of both exhaust fans in the Safeguards mode. Both trains of Auxiliary Building Ventilation are operable. This 8-hour non-emergency report is made pursuant to 10 CFR 50.72(b)(3)(v)(D)." The unit is not in a TS LCO. All 3 unit EDG's are operable and offsite power is in the normal lineup. The NRC Resident Inspector has been notified. * * * UPDATE FROM WES FIANT TO DONALD NORWOOD AT 0021 EST ON 1/14/2011 * * * "On January 13, 2011, at 1603 PST, engineering determined that a single failure design vulnerability exists at Diablo Canyon Power Plant Units 1 and 2. "Engineering review of the control logic of the ABVS determined that while in Buildings Only (non-safeguards) alignment or during system realignment from Safeguards Only to Buildings Only alignment, failure of damper M-4A or M-4B (series dampers) could result in the control logic securing both ABVS exhaust fans. This would prevent ABVS actuation on receipt of a valid safeguards actuation signal. When this occurs, a control room alarm is actuated, which requires the operators to reset the control logic from the control room, thereby re-enabling the capability of the ABVS to respond to a safeguards actuation signal. The Unit 2 event on January 10, 2011, at 1321, occurred due to this single failure vulnerability when the control system attempted to restore the ABVS alignment from Safeguards Only to the Buildings Only alignment. This design vulnerability is currently mitigated by maintaining the ABVS in either of the two safeguards alignments (Safeguards Only or Buildings and Safeguards). "This single failure design vulnerability is an 8-hour non-emergency report made pursuant to 10CFR50.72(b)(3)(ii)(B) for an event that resulted in the nuclear power plant being in an unanalyzed condition for both Unit 1 and Unit 2." The licensee will notify the NRC Resident Inspector. Notified R4DO (Hagar). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | UNANALYZED CONDITION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2011-01-10
46530 | 0 | U.S. ARMY |  |  |  |  | 2011-01-04 09:00 | 2011-01-10 16:22 | 2011-01-10 | TRITIUM VIAL CRACKED DURING MAINTENANCE OF MORTAR SIGHT UNIT "On 4 January 2011 at 0900 hrs an Army National Guard employee was performing maintenance on a M64A1 sight unit in an attempt to remove the course elevation deflection scale on the sight unit which contained a 1 curie tritium lamp. The assembly is considered a module which is authorized by the licensee for replacement. During the removal of the scale assembly the tritium lamp was damaged. The worker immediately realized what had happened and called the local RSO to handle the incident. The State RSO was notified of the incident who in turn notified the US Army CECOM health physicist. The device was double bagged by the local RSO and placed in a designated LLRW storage area for future disposal. The local RSO performed contamination wipes of the device and surrounding works areas on Jan 4th. The arms room in the CSMS shop was immediately shut down and had limited access by authorized personnel. Wipe test results were received back from the Army lab on 6 Jan that indicated tritium contamination of 60 K dpm on the device itself and a few thousand dpm of the surrounding work bench. The RSO proceeded to decontaminated the affected contaminated areas and rewiped the work area to release it from radiological control. The second contamination survey (after decon) showed tritium contamination significantly reduced. At the time of this report the licensee does not have the final test results. The maintenance person involved in the incident was required by the licensee to have a tritium bioassay taken. Tritium bioassay results were not available at the time of the report. Investigation by the licensee is being conducted as to determine how the device was damaged during maintenance." The event occurred at the New York Army National Guard, Combined Support maintenance Shop - Arms Room in Rochester New York. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 30.50(b)(1) |  |  |  | 0 | 2011-01-10
46529 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-01-10 | 2011-01-10 14:29 | 2011-02-01 | AGREEMENT STATE REPORT - PROSTATE BRACHYTHERAPY MISDOSING The following information was received from the State of Wisconsin via fax: "On January 10, 2011, the licensee's Radiation Safety Officer reported the identification of ten medical events involving permanent implants of I-125 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. "During a recent routine inspection, Department of Health Services inspectors determined that the licensee was not reviewing prostate brachytherapy cases against medical event criteria. The licensee is identifying as a medical event any case where D90<135 Gy or D90>195 Gy for patients who receive seed implants only, and D90<100 Gy or D90>145 Gy for patients who receive seed implants in conjunction with external beam therapy (combined therapy). The licensee performed a comprehensive review of all 82 prostate implants performed since August 2003. The licensee's ten medical events include six overdoses to the prostate and four underdoses to the prostate. No medical events were identified involving doses to other organs or tissue above 0.50 Sv and 50% more than the expected dose. The licensee has notified the referring physicians and will not be notifying the affected patients per DHS 157.72(1). "Overdoses (medical event criteria used - D90>195 Gy): 12/23/2003: 204.95 Gy; 10/27/2004: 160.49 Gy {combined therapy, medical event criteria used - D90>145 Gy}; 1/20/2006: 211.23 Gy; 6/14/2006: 207.03 Gy; 9/5/2007: 205.7 Gy; and 10/17/2007: 210.47 Gy. "Underdoses (medical event criteria used - D90<135 Gy): 9/26/2003: 123.03 Gy; 10/31/2003: 116.78 Gy; 1/14/2004: 126.73 Gy; and 3/31/2009: 123.74 Gy. "DHS will send a special inspection team to determine the root cause(s) of these medical events on February 2, 2011." * * * UPDATE FROM CHRIS TIMMERMAN TO JOHN KNOKE AT 1212 EST ON 2/1/11 * * * "This is an update to Event Notification 46529. On January 31, 2011, the licensee retracted one medical event for a prostate brachytherapy patient treated on 3/31/2009 based on refined post-implant dosimetry. Further updates will be made through NMED. "DHS will send a special inspection team on February 3 2011. " WI Event Report ID No.: WI 110001 Update Notified FSME (Angela McIntosh) and R3DO (Richard Skokowski) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-01-16
46528 | -1 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2011-01-10 | 2011-01-10 14:29 | 2011-03-01 | AGREEMENT STATE REPORT - NUMEROUS MEDICAL EVENTS FROM PROSTATE BRACHYTHERAPY The following was received from the state via fax; "In July 2010, the Wisconsin Department of Health Services (DHS) sent out an Information Notice to all licensees who perform prostate brachytherapy and asked them to perform a comprehensive review of all prostate brachytherapy cases to determine whether any medical events had occurred. On January 10, 2011, the licensee's Radiation Safely Officer reported the identification of five medical events involving permanent implants of I-125 for prostate brachytherapy where the total dose delivered differs from the prescribed dose by 20% or more. The licensee is identifying a medical event of any case where D90<135 Gy or D90>195 Gy for patients who receive seed implants only. [D90 is a recognized value in the regulatory guidelines and means a dose of 90% to the prostate. Anything outside of the D90 value is considered to be a medical event.] The licensee performed a comprehensive review of all 44 prostate implants performed since August 2003. The licensee's five medical events include one overdose to the prostate and four underdoses to the prostate. All were patients who received seed implants only. No medical events were identified involving doses to other organs or tissue above 0.50 Sv and 50% more than the expected dose. The licensee has notified the referring physicians and will not be notifying the affected patients per DHS 157.72(1)(e). "Overdoses (medical event criteria used: D90>195 Gy): 11/13/2008: 199.15 Gy "Underdoses (medical event criteria used: D90<135 Gy): 2/9/2007: 100.20 Gy; 11/12/2007: 127.34 Gy; 6/16/2008: 130.12 Gy; and 7/13/2010: 116.16 Gy" * * * UPDATE FROM CHRIS TIMMERMAN TO JOHN KNOKE AT 1212 EST ON 2/1/11 * * * "This is an update to Event Notification 46528. The licensee recently performed post-implant dosimetry on seven prostate brachytherapy patients whose post-implant dosimetry had never been performed. Evaluation of these seven implants prompted the licensee to report two additional medical events. The medical events involved permanent implants of l-125 for prostate brachytherapy where the total dose delivered to the prostate differs from the prescribed dose by 20% or more. The licensee is in the process of notifying the affected patients and referring physicians. "Underdoses (medical event criteria used: D90<135 Gy): 8/22/2005: 102.89 Gy; and 5/8/2006: 126.24 Gy; "DHS will send a special inspection team to determine the root cause(s) of these medical events." WI Event Report ID No.: WI 110001 Update Notified FSME(Angela McIntire) and R3DO (Richard Skokowski) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * RETRACTION FROM MEGAN SHOBER TO JOHN SHOEMAKER VIA FACSIMLE AT 1355 EST ON 3/1/11 * "This is a second update to Event Notification 46528. The licensee is retracting an overdose previously reported for a patient who received a permanent prostate implant on November 13, 2008. During a reactive inspection conducted on February 18, 2011, DHS inspectors identified that post-implant dosimetry of prostate brachytherapy implants had not been performed appropriately. Specifically, the licensee's former physics consultant generated post-plans that were not based on the number of I-125 seeds actually implanted in the patients. For the patient in question, the original post-plan was based on an implant of 98 seeds; however, only 76 seeds were actually implanted. The licensee's current physicist generated a new post-plan using the correct number of I-125 seeds and observed a corresponding reduction in dose delivered. The new D90 value for this patient does not meet the licensee's medical event criteria." WI Event Report ID No.: WI 110002, 2nd Update Notified FSME(McIntosh) and R3DO (Dickson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2011-01-16
46527 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2011-01-10 09:21 | 2011-01-10 11:51 | 2011-01-10 | UNAVAILABILITY OF TSC AND EOF FUNCTIONS DUE TO SCHEDULED MAINTENANCE "At 0921 CST on Monday January 10, 2011, the Kewaunee Power Station (KPS) disabled electrical power to the KPS Technical Support Center (TSC) to perform motor control center maintenance. The major TSC components that were disabled include plant process control system (PPCS) workstations, primary lighting, and ventilation. In the Emergency Operations Facility (EOF), PPCS workstations have been disabled. Additionally, the dose projection program (MIDAS) does not have the capability to automatically populate with plant data. The safety parameter display system (SPDS) and emergency response data system (ERDS) remain operational. This activity has been evaluated in accordance with 10 CFR 50.54(q) to ensure that KPS will be able to deal with an accident or emergency should one occur. If required, existing procedural guidance will be utilized to relocate TSC personnel to predetermined alternate locations. A copy of emergency procedures and emergency telephone directories are staged in the alternate locations. "The maintenance is scheduled to be completed by 1400 CST on January 10, 2011." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM GARY AHRENS TO PETE SNYDER AT 1701 EST ON 1/10/11 * * * At 1545 CST all of the functionality that was removed from service per the above notification was restored to service. Notified R3DO (Kunowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-10
46526 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2011-01-08 14:00 | 2011-01-08 17:06 | 2011-01-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO PARTIAL CLOSURE OF LETDOWN LINE ISOLATION VALVE 1HP-5 "At 1400 on Saturday, January 8, 2011, Oconee Unit 1 initiated a shutdown required by Technical Specification (TS) 3.6.3, 'Containment Isolation Valves.' Unit 1 experienced an unexpected partial closure of letdown line containment isolation valve 1HP-5 during Engineered Safeguards (ES) Channel 2 on-line testing. 1HP-5 reopened when power was restored. Unit 1 entered TS 3.6.3, CONDITION A at 0148 on 1/8/11. Unit 1 entered TS 3.6.3, CONDITION D at 0548 on 1/8/11. TS 3.6.3, CONDITION D requires Unit 1 to be in mode 3 by 1748 on 1/8/11, and in mode 5 by 1748 on 1/9/11. An updated notification will be provided if the TS CONDITION is exited prior to Unit 1 reaching mode 5. An investigation is in progress to determine the cause of the unexpected partial closure of 1HP-5." All safety systems required for safe shutdown are operable and the electrical lineup is normal. The licensee is evaluating any potential impact of this event on Unit 2 and Unit 3. There is no estimate for the completion of the investigation at this time. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2011-01-08
46525 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-01-08 14:38 | 2011-01-08 15:29 | 2011-01-09 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "A condition is being reported per Technical Requirements Manual 13.13.1, Emergency Response Facilities, Action B.2. The functionality of the Technical Support Center (TSC) has been lost due to planned maintenance being performed on the 480V Motor Control Switchgear ANBL. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to functional status with a high priority. A 10CFR50.54(q) evaluation has been performed for this planned maintenance activity. Normal power is still available but may be lost during a loss of offsite power. Contingency plans are in place to restore backup power if necessary. Expected return to service is Tuesday, January 11, 2011. The NRC Resident Inspector has been notified. * * * UPDATE FROM CARL GRANT TO JOE O'HARA AT 1505 ON 1/9/11 * * * TSC returned to service at 1430 EST. Normal power supply is aligned and the temporary modifications have been removed. The NRC Resident Inspector has been notified. Notified R2DO(Vias) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-08
46524 | 0 | PALISADES | 1 |  |  | [1] CE | 2011-01-08 13:03 | 2011-01-08 13:21 | 2011-01-09 | UNUSUAL EVENT DECLARED DUE TO CATASTROPHIC FAILURE OF NON-SAFETY RELATED BUS BREAKER A notice of unusual event was declared for 'Hazards and other conditions affecting plant safety' at 1303 EST for Emergency Action Level (EAL) HU1 as a result of a breaker/bus fault in a non-safety related feeder bus 'F'. The loss of the bus resulted in loss of cooling water tower pumps and fans and subsequently a loss of one cooling tower. There is indication of a pressure transient on the breaker panel and smoke but no fire. There is no indication of sabotage or terrorism, and no offsite assistance requested. There is no radiological release in progress. The NRC remains in the normal mode. NRC Resident staff are enroute to the site. Plant is stable at 55 % reactor power following a down-power maneuver from 100% reactor power with all safety related equipment operable. * * * UPDATE FROM CARYLIN MCCOY TO JOHN KNOKE AT 0102 EST ON 01/09/11 * * * At 0043 Palisades terminated from their Unusual Event for 'Hazards and Other Conditions Affecting Plant Safety'. The faulted bus has been isolated, and licensee started their investigation into the cause of this incident. The licensee has tagged out and racked out the breaker, and has isolated the startup power to the 'F' bus. The associated Startup Transformer has also been isolated. The 'F' bus and associated Startup Transformer will not be energized until the situation is better understood, and repaired if necessary. Power level will be maintained at 53% due to the loss of associated equipment supporting one cooling tower. The licensee is in a 72 hour LCO. The licensee has notified the NRC Resident Inspector. Notified the R3DO (Christine Lipa), IRD MOC (Bill Gott), NRR EO (Mike Cheok), DHS (Gates), FEMA (Casto) | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2011-01-08
46523 | 0 | FAIRBANKS MORSE ENGINE |  |  |  |  | 2010-11-16 | 2011-01-07 17:13 | 2011-01-07 | PART 21 REPORT FOR POTENTIAL SAFETY HAZARD ON SPEED SWITCH INSTALLED ON EMERGENCY DIESEL GENERATOR (EDG) The following was received via fax: "[Fairbanks Morse (FM) determined] that when the speed switch assembly was mounted on a conductive surface, the voltage regulator grounded out the 24 volt direct current power through the heat sink preventing the speed switch from operating. "This condition was not detected prior to the first speed switch being shipped to Hope Creek in September, 2010. It was never installed on the EDG prior to being recalled. The unit was returned to FM and has since been reworked and verified to be in compliance with the latest design to eliminate the deficiency." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2011-01-07
46522 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2010-07-13 | 2011-01-05 16:51 | 2011-01-05 | KENTUCKY AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following information was obtained from the State of Kentucky via email: "The event timetable began on 12 July 2010 when the Medical Physicist entered the pre-treatment information into the facilities brachytherapy software package (VariSeed«, Varian Inc). The information included patient demographics, treatment date and radioisotope information; in this case I-125 encased in titanium for a treatment date of 13 July 2010. The medical procedure was carried out successfully and 97 seeds were implanted. This number of seeds is within the expected limit of what is normally encountered during these procedures and thus did not stand out as a triggering event for a double check. "During a routine post-procedure review, conducted on 14 July 2010, the medical physicist identified a potential issue and began the chain of notification as required by the radiation safety office; medical, administrative and safety. "The discrepancy arose from the identification of source activity, as indicated on the written directive versus the information printed on the post-procedure information sheet. The information had inadvertently been entered into the pre-procedure planning software in units of milliCurie while the units of measure were identified as units of 'U' [Air-Kerma], leading to a discrepancy in the delivered dose of approximately +27%. The specific information in this case indicated the strength was 0.410 U (0.323 mCi) while in reality the actual source strength was 0.521 U (0.410 mCi). "The facility conducted a root-cause analysis that indicated two areas of concern for a root cause. The initial identified area of concern is the ability to enter information into an automated system in either of two separate units; 'U' or milliCurie. This was followed closely by the lack of a documented double verify means; which although always important to any therapeutic intervention, would have negated the incident in this case. Since the software does not allow for the exclusion of one unit in favor of the other, the root-cause is the failure to have in place a procedure that included the documented double-verification of the dose strength used in the calculations. "In order to negate the recurrence of this type of error, the oncology physics section has implemented the following procedure. The therapeutic seeds will be ordered and received as is currently performed. The medical physicist will enter the information into the software package using the vendor supplied source strength of the implantable seeds; using the 'U' [Air-Kerma] value only. The Air-Kerma value has been chosen as the unit of preference because this is rapidly becoming the professional unit of choice by the medical physics community and is the default unit of the VariSeed« software package. Once in the operating room a time-out will be conducted between the medical physicist and the medical dosimetrist. The dosimetrist will observe the software settings while the medical physicist reads aloud the information contained in the 'Seed Count and Strength Verification' form including the seed strength; in 'U' [Air-Kerma], and procedure date. Both persons will then sign the form. The remainder of the process will remain unchanged. "The patient was contacted by the radiation oncologist the morning of 15 July 2010 and returned for immediate CT imaging of the pelvis on 16 July 2010. The error was explained to the patient, as well as the urologist who assisted in the procedure, and additional monitoring of the prostate, rectum and urethra are to be conducted to better determine a dose distribution. At this point a general dose estimate is that the patient received 3,800 Rem greater than was intended. Although this estimate may be decreased or otherwise adjusted based on the serial monitoring to be conducted over the six months post-procedure. "The procedure has been implemented and the physics section, including the radiation oncologist, have been in-serviced as of 26 July 2010." The State of Kentucky received the above notification from the licensee on July 28, 2010. According to the State of Kentucky, the licensee did not originally report this event (via telephone on July 15, 2010) as a medical event therefore the State did not report the event to the NRC Operations Center. During an interoffice review, the State determined that a miscommunication had occurred and they should have reported this event to the NRC. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2011-01-11
46521 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2011-01-05 01:20 | 2011-01-05 09:03 | 2011-03-04 | REACTOR CORE ISOLATION COOLING DECLARED INOPERABLE "On January 5, 2011, at 0120 hours, with the reactor at 100% thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNSP) declared the Reactor Core Isolation Cooling (RCIC) system inoperable due to the RCIC suction isolation valve from the Torus/Suppression Pool (RCIC-26) failing to go fully closed during planned surveillance testing. The RCIC-26 is a motor-operated valve (MOV) and its normal position is closed. The RClC-26 valve is redundant to the RCIC-25 valve, and is not the credited containment isolation valve. The RCIC-26 valve has a safety function to be (manually) opened during certain event mitigation scenarios requiring a transfer of suction sources from the Condensate Storage Tank (CST) to the Torus. "Based on the valve failing to fully close during MOV stroke time testing per PNPS Procedure 8.5.5.4, the RCIC system was declared inoperable at 0120 hours and the appropriate LCO was entered. The RCIC-26 was subsequently returned to a full open position, caution tagged and the RCIC system was declared operable. The LCO was exited at 0200 hours. An investigation of the event is underway and continuing. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector is on-site and has been notified. "This is an 8-hour notification made in accordance with 50.72(b)(3)(v)(D)." The licensee will notify the State of Massachusetts. * * * RETRACTION FROM JOSEPH LYNCH TO JOHN KNOKE AT 1946 EST ON 3/4/11 * * * "Event Notification 46521 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were satisfied pending the evaluation of RCIC System operability. "On 01/05/11, at 0120 hours the RCIC System was declared inoperable due to uncertainty of RCIC System Operability when the Torus/Suppression Pool Suction Valve (RCIC-26) failed to go fully closed during planned surveillance testing. The valve was restored to the full open position and the valve was declared operable based on capability to meet the required safety function to fully open when RCIC pump suction from the suppression pool is required. "The apparent cause evaluation concluded that valve failure was the result of high relay contact resistance in the closing control circuit components of the valve breaker. This failure prevented the valve from fully closing but had no affect on capability to open the valve. Surveillance testing verified that capability to open the valve was not affected. "Corrective action was completed to clean or replace the control circuit relay contacts. Post work testing confirmed capability to open and close the valve. An extent of condition for similar breaker control circuit components was also performed. All relevant technical information is documented in the corrective action system. "The failure observed did not affect the valve's required safety function and did not impact RCIC System operability. Thus there was no impact on nuclear safety. This event is not reportable pursuant to 10 CFR 50.72(b)(3)(v)(D) . "Event Number 46521, made on 01/05/2011, is being retracted." The licensee has notified the NRC Resident Inspector. Notified R1DO (Anthony Dimitriadis) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2011-01-05
46520 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2011-01-04 08:00 | 2011-01-04 08:15 | 2011-01-04 | UNAVAILABILITY OF TSC VENTILATION SYSTEM DUE TO SCHEDULED MAINTENANCE "At 0800 EST on Tuesday, January 4, 2011, the Cook Nuclear Plant (CNP) Technical Support Center (TSC) air conditioning and charcoal filtration systems were removed from service for scheduled maintenance. "Under certain accident conditions the TSC may become unavailable due to the inability of the air conditioning and charcoal filtration systems to maintain a habitable atmosphere. Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary . "TSC ventilation system maintenance is scheduled to be completed by 1600 EST on Tuesday, January 4, 2011. "The licensee has notified the NRC Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the loss of an emergency response facility," * * * UPDATE FROM BUD HINCKLEY TO DONALD NORWOOD AT 1709 EST ON 01/04/2011 * * * "The TSC ventilation system maintenance was completed satisfactorily and the system was restored to service at 1705 EST." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Lipa) via e-mail. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2011-01-04
46519 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2011-01-03 13:44 | 2011-01-03 21:09 | 2011-06-07 | SINGLE POINT OF FAILURE VULNERABILITY DISCOVERED WHICH COULD POTENTIALLY AFFECT ACCIDENT RESPONSE "On Monday, January 3, 2011, at 1344 EST, it was discovered by engineering that a single point of vulnerability exists at Susquehanna Steam Electric Station affecting both Unit 1 and Unit 2. "A potential single HVAC control component has been discovered whose failure could result in a spurious Steam Leak Detection (SLD) isolation causing a loss of generation, loss of the normal heat sink (main condenser) and a loss of HPCI and RCIC. The SLD delta temperature (delta T) instrumentation is dependent on proper operation of the Unit 1 and Unit 2 RB [Reactor Building] HVAC heater temperature controller during cold weather operation. The Unit 1 and Unit 2 RB HVAC heaters are controlled by a single temperature controller which sends a signal to multiple step controllers. Failure of the temperature controller could cause the heaters to turn off. This would cause a significant decrease in RB HVAC supply temperature which results in a significant increase in measured SLD delta T during cold winter months. This could cause an isolation of the MSIVs, HPCI, RCIC and RWCU within a short period of time. "This is reportable pursuant to 10CFR50.72(b)(3)(v) for a condition that at discovery could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident and 10CFR50.72(b)(3)(ii) for and event that resulted in the nuclear power plant being in an unanalyzed condition." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TODD CREASY TO JOE O'HARA AT 1310 ON 2/28/11 * * * "On January 3, 2011, SSES reported the discovery of a single point vulnerability that affected both Unit 1 and Unit 2 (EN # 46519). The vulnerability involved failure of a temperature controller that had the potential to result in a Steam Leak Detection (SLD) isolation causing a loss of generation, loss of the normal heat sink (main condenser), and a loss of HPCI and RCIC. The condition was reported pursuant to 10CFR50.72(b)(3)(v) as a condition that at discovery could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident and pursuant to 10CFR50.72(b)(3)(ii) as an event that resulted in the nuclear power plant being in an unanalyzed condition. "SSES has further evaluated the condition and determined that the condition did not meet reporting criterion 10CFR50.72(b)(3)(v) for a condition that at discovery could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "The level of judgment in reporting under this criterion Is a reasonable expectation of preventing fulfillment of a safety function. Alternately stated, the condition is reportable if there was reasonable doubt that the safety function would have been fulfilled if the system had been called upon to perform it. Technical evaluation of the condition concluded the following: there is reasonable assurance (high degree of confidence) that the HPCI, RCIC, Main Steam Isolation and RWCU systems will remain operable. The identified condition does not adversely affect the operability of the affected systems. The identified condition increases the probability that a failure of the Reactor Building HVAC temperature controller TC-17589 or TC-27589 could cause the MSIV's, HPCI and RCIC to isolate during cold weather operation. However, this increase in probability is very small and is not sufficient to erode the confidence in the reasonable expectation of operability. For a system isolation to occur, the heater controller had to fail and concurrently the outside air temperature had to be below approximately 10?F. The Reactor Building HVAC temperature controllers are highly reliable and the outside air temperatures required for this event occur infrequently (there have only been 11 instances of temperatures at Susquehanna dropping below 10 deg F in the past two years). Since both infrequent conditions have to occur concurrently, it is unlikely that this postulated failure would occur. "As a result, reporting pursuant to 10CFR50.72(b)(3)(v) is retracted; however, the condition remains reportable pursuant to 10CFR50.72(b)b)(3)(ii) as an event that resulted in the nuclear power plant being in an unanalyzed condition." The NRC Resident Inspector has been notified. Notified R1DO (T.Dimitriadis) * * * UPDATE FROM DAVE BORGER TO HOWIE CROUCH AT 1220 EDT ON 6/7/2011 * * * "On January 3, 2011, SSES reported the discovery of a single point vulnerability that affected both Unit 1 and Unit 2 (EN #46519). The vulnerability involved failure of a temperature controller that had the potential to result in a Steam Leak Detection (SLD) isolation causing a loss of generation, loss of the normal heat sink (main condenser), and a loss of HPCI and RCIC. The condition was reported pursuant to 10CFR50.72(b)(3)(v) as a condition that at discovery could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident and pursuant to 10CFR50.72(b)(3)(ii) as an event that resulted in the nuclear power plant being in an unanalyzed condition. "On February 28, 2011, SSES retracted the 10CFR50.72(b)(3)(v) portion of the report on the basis that there was reasonable assurance that the HPCI, RCIC, Main Steam Isolation and RWCU systems would remain operable. The reasonable assurance was based on the very small probability of system isolation that required failure of the highly reliable heater controller had to fail concurrent with outside air temperature below approximately 10?F. "This notification is intended to revise the basis for retraction of the 10CFR50.72(b)(3)(v) portion of the report. The revised basis is that the conditions required to prevent fulfillment of a safety function did not exist at the time of discovery." The licensee has notified the NRC Resident Inspector. Notified R1DO (Rogge). | 98 | 94 | 0 | 98 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2011-01-03
46518 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2011-01-03 09:59 | 2011-01-03 14:28 | 2011-01-03 | SUPERVISOR FAILS RANDOM FITNESS FOR DUTY CHECK A non-licensed employee supervisor had a confirmed positive for alcohol on a random fitness-for-duty test. The individual did not and does not have access to the protected area. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2011-01-03
46517 | 0 | MT OPERATING OF NJ, LLC |  |  |  |  | 2010-12-29 21:30 | 2010-12-30 09:19 | 2010-12-30 | STOLEN TROXLER MOISTER DENSITY GAUGE A company employee was robbed, at gunpoint, of his car which contained a Troxler moisture density gauge in the trunk. The employee works for MT Operating of NJ, LLC, and was unable to return the gauge to the normal company storage area in Wallingford, CT., at the end of the day. The employee began working a second job in Bloomfield, CT, where the robbery took place. The employee was also robbed of his cell phone and wallet, in addition to his car containing the gauge. The nuclear gauge is a Troxler Model 3411B, S/N 4783, which contains two radioactive sources. One source is 40 mCi of Am-241/Be and the other source is 8 mCi of Cs-137. The licensee has notified the Bloomfield Connecticut Police Department to investigate the theft (case # 10-26288). The licensee has other company employees searching the area in an attempt to locate the missing vehicle. The licensee plans to make a press release and offer a cash reward. * * * UPDATE ON 12/30/10 AT 2200 EST FROM PENNISI TO HUFFMAN * * * The licensee states the Bloomfield Police Department has recovered the Troxler gauge. The circumstances of the recovery are not yet known, however, the gauge appears to be undamaged. Officials from the State of Connecticut have surveyed the gauge and determined found no evidence of unusual radiation levels. The gauge is in Police custody. R1DO (Hansell), FSME (Watson) and ILTAB (Johnson via email) notified. * * * UPDATE ON 12/30/10 AT 2300 EST FROM PENNISI TO SNYDER * * * State of Connecticut informed the NRC Operations Center that the Troxler has been turned over to the licensee's RSO. R1DO (Hansell), FSME (Watson) and ILTAB (Johnson via email) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-12-30
46516 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-12-29 08:15 | 2010-12-29 09:06 | 2010-12-29 | SCHEDULED MICROWAVE RADIO MAINTENANCE IMPACT TO THE CCNPP CONTROL ROOM AND EMERGENCY OPERATIONS FACILITY "This is an eight hour report per 10 CFR 50.72 (b)(3)(xiii). Calvert Cliffs Nuclear Power Plant (CCNPP) will be implementing a scheduled maintenance to the microwave radio system to improve reliability of the system at the Emergency Operations Facility (EOF), State and County facilities. "This work will require that the microwave radio system at the EOF be removed for a period of approximately 6 to 8 hours. During this time, the following systems will be impacted for the duration of maintenance: 1. The plant's (e.g., Control Room, Technical Support Center (TSC), Simulator) Dedicated Offsite Agency telephones will be out of service. (EOF's system will continue to function) 2. 800 MHz desk set radios at the EOF only will be out of service. 3. 153.44 MHz frequency at the EOF only will be out of service. (backup for MEMA and MDE) 4. MIDAS Terminal (Meteorological Data) located in the Dose Assessment Office at the EOF will be out of service. 5. TSC Computer data transfer to the EOF only will be out of service. "Once the scheduled maintenance starts the systems (listed above) can be returned to service within 1 hour. "Should an emergency be declared during this period, the Control Room will continue to have the capability to make the notification to the offsite agencies using the direct line for the appropriate agencies. The Emergency Preparedness communications procedure provides a chart listing the communication devices available and the order in which the process is to be implemented. MIDAS (Meteorological Data) will continue to be operational at the site and can be obtained by contacting the Control Room or TSC. The ERPIPs also provide a backup process and the instructions necessary for the EOF Dose Assessment Office to obtain Meteorological Data. Plant data can be obtain from the CR or TSC and will continue to be downloaded from the plant computer to the ERO SharePoint site. "All work associated with this microwave radio maintenance will be performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. A test of all systems will be performed at the completion of the maintenance. "All EOF responders and Control Room personnel have been briefed on this work and expected contingent actions. "This job will start on Wednesday, December 29, 2010 at approximately 8:00 am. We anticipate that all work will be completed by 4:00 pm on the same day, including testing of the system. We will provide a notification update upon completion of the job." The licensee informed the NRC Resident Inspector. Licensee will also notify state and local governments. * * * UPDATE FROM DAN GENEVA TO JOE O'HARA AT 1405 ON 12/29/10 * * * Communications are back in full service as of 1220 on 12/29/10. Notified R1DO(Hansell) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-29
46515 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-12-28 12:20 | 2010-12-28 16:27 | 2010-12-28 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO INOPERABLE MINIMUM FLOW VALVE "On December 28, 2010 at approximately 1220 hours, during surveillance testing of the High Pressure Coolant Injection (HPCI) system, abnormal control room position indication was observed on the HPCI Minimum Flow Valve, E4150F012 as the valve was stroking closed. HPCI had been removed from service for quarterly surveillance testing at 0950 hours. The unplanned inoperability condition began at 1220 hours when position indication was lost on the minimum flow valve. The valve was manually closed to comply with the action of LCO 3.6.1.3 to isolate the penetration. A 14 day LCO was entered and back dated to the time that HPCI was removed from service per LCO 3.5.1. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on loss of a single train safety system. RCIC was and has remained operable. The failure is currently under investigation." The licensee notified the NRC Resident Inspector. | 75 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-12-28
46514 | 0 | PALISADES | 1 |  |  | [1] CE | 2010-12-27 19:45 | 2010-12-27 20:13 | 2010-12-27 | SAFEGUARDS REPORT - SAFEGUARDS VULNERABILITY FOR WHICH COMPENSATORY MEASURES WERE NOT TAKEN "Discovered vulnerability in a safeguards system for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-12-27
46513 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-12-27 15:37 | 2010-12-27 16:18 | 2010-12-27 | OFFSITE NOTIFICATIONS - EXCEEDED DISCHARGE PERMIT "On December 27, 2010, at 1537, a report was made to the Michigan Department of Natural Resources and Environment for exceeding the National Pollutant Discharge Elimination System (NPDES) permit limits to outfall 011A. The limits were exceeded due to the General Service Water (GSW) traveling screens being in continuous operation and the back wash being aligned to outfall 011A which resulted in exceeding the maximum discharge limit of 1.8 million gallons per calendar day as a result of a fish intrusion event occurring at the GSW intake. The GSW traveling screens have been in continuous operation since 2100 on December 25 and the daily discharge limit was reached at 1700 on December 26. The condition was necessary to maintain safe and reliable operations of the plant in response to the fish intrusion. The GSW traveling screens are being continuously monitored in order to limit unnecessary discharge into outfall 011A and restore full compliance with the NPDES permit as conditions improve. This report is being made in accordance with 10CFR50.72(b)(2)(xi) 'Any event or situation. Related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' " The NRC Resident Inspector has been notified. | 75 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-27
46512 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2010-12-22 12:30 | 2010-12-27 11:13 | 2010-12-27 | AGREEMENT STATE REPORT INVOLVING AN HDR MISADMINISTRATION The following report was received from the State of Arizona via fax: "At approximately 12:30 PM December 22, 2010, the Licensee phoned the Agency [Arizona Radiation Regulatory Agency] to report an HDR [High Dose Radiation] misadministration. A breast cancer patient was undergoing treatment with a Nucletron MicroSelectron-HDR. A Savi-8 Accelerated Partial Breast Irradiation Device was connected to the HDR. This is manufactured by Cianno. The source apparently punched through the catheter and moved along the skin surface during the treatment. The patient did not notice the source was outside the tube. The source retracted normally to the shielded position. The physicist estimates that the patient's skin received 5 Gray if the source moved along the skins surface but if the source stuck in one position the patient's skin received 50 Gray. According to the licensee the catheter is easily kinked which can cause this failure. This has happened before but is the first time that this has resulted in an exposure. In the past, the licensee would repair the catheter with heat shrink tubing. "The Agency continues to investigate the actions of the licensee. "The U.S. NRC and the Arizona Governor's office have been notified of this event. "Press coverage is not anticipated." Arizona First Notice: 10-016 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2011-01-02
46511 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2010-12-26 16:20 | 2010-12-26 20:53 | 2010-12-26 | MANUAL REACTOR SCRAM DUE TO HIGH VIBRATION ON MAIN GENERATOR EXCITER "On 12/26/2010 at 1620 CST, Browns Ferry Unit 3 initiated a manual reactor SCRAM due to high vibration on the Unit 3 Generator Exciter inboard and outboard journal bearings. All plant systems responded as required to the manual SCRAM signal. No Emergency Core Cooling System (ECCS) initiations occurred as a result of the manual SCRAM signal. Reactor water level lowered below Level 3 (+2") as a result of the SCRAM and was recovered to the normal water level band by the Reactor Feed Pumps (RFPs). The expected Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations were received due to reactor water level lowering below Level 3 (+2") with all systems isolating as required. There were no indications of main steam relief valves (MSRVs) opening. "The manual scram from critical is reportable within four hours under 10CFR50.72(b)(2)(iv)(B), 'Any event or condition that results in a valid actuation of the Reactor Protection System' and within eight hours under 10CFR50.72(b)(3)(iv)(A), 'Any event that results in an actuation of the specified systems.' The manual scram from critical also requires a 60-day written report in accordance with 10CFR50.73(a)(2)(iv)(A). "The event was entered into the licensee corrective action program as Problem Evaluation Report 301505. "The NRC Resident Inspector was informed." All control rods fully inserted. Plant is in a normal post-scram electrical alignment. Decay heat is being removed through the turbine bypass valves to the main condenser. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-12-26
46510 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2010-12-26 06:50 | 2010-12-26 07:41 | 2010-12-30 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. Compensatory measures were taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM WEATHERSBY TO HUFFMAN ON 12/30/10 AT 1418 EST * * * Upon further review, the licensee determined that the event was not reportable based on lack of malevolent intent and that the contraband was interdicted prior to the reaching the protected area. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. R2DO (Bartley) notified. Part 73.71 group notified by e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-12-26
46509 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-12-25 16:25 | 2010-12-25 19:40 | 2011-01-28 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO HIGH WINDS Notification of Unusual Event declared due to high winds. EAL HU 1.2 condition of peak wind in excess of 80 miles per hour have been met. Sustained winds at the present time are 53.5 miles per hour. Wind direction (from) 38.8 degrees. There has been no damage on-site. There are no plans to reduce reactor power on either unit at the present time. The Emergency Operations Center has not been activated. The storm front causing the high winds is expected to exit the area within the next three to four hours. The licensee notified the NRC Resident Inspector. The licensee notified the San Luis Obispo Sheriff and the State of California Office of Emergency Services. * * * UPDATE FROM JAMES EWART TO DONALD NORWOOD AT 2018 EST ON 12/25/2010 * * * Current wind speed is 3.7 miles per hour. Wind direction (from) 134.7 degrees. There has been no damage on-site. The access roads to the site are open and passable. * * * UPDATE FROM JAMES EWART TO DONALD NORWOOD AT 2057 EST ON 12/25/2010 * * * Current wind speed 9.2 miles per hour. Wind direction (from) 101.6 degrees. The NRC Senior Resident Inspector is on-site. * * * UPDATE AT 2333 EST ON 12/25/2010 FROM JEFF PORTNEY TO MARK ABRAMOVITZ * * * The licensee terminated the NOUE at 2021 PST. Winds are less than 2 mph gusting to 2.8 mph from 63.9 degrees. The storm has passed and no damage has been detected. The NRC Resident Inspector will be notified. Notified the R4DO (Werner), IRD (Gott), NRR EO (Howe), DHS (Knox), and FEMA (Fuller). * * * RETRACTION ON 12/28/2011 AT 1159 FROM ROB KLEIN TO DONG PARK * * * "During a rain storm on December 25, 2010, PG&E declared an Unusual Event at the Diablo Canyon Power Plant due to indicated peak wind speed of 42.6 meters per second (m/s), (95.3 miles per hour (mph)), at the 10m elevation on the Primary Meteorological Tower, in excess of 80 mph indicated. After analyzing other wind speed instrumentation from the same time period, PG&E concluded that this reading did not accurately reflect meteorological conditions at that time. The next highest reading was taken at the 76m elevation on the Primary Meteorological Tower and indicated peak wind speeds of 23.7 m/s (53.0 mph). The Backup Meteorological Tower mechanical anemometers indicated a wind speed of 16.1 m/s (36.0 mph) for the 10m elevation, and 18.2 m/s (40.7 mph) for the 60m elevation. The Primary Meteorological Tower sonic sensors read both wind speed and wind direction with a single sensor. Concurrent with the Primary Meteorological Tower 10m wind speed spike, the 10m Primary Meteorological Tower wind-direction made a step-change from 153 degrees to 39 degrees. This step change indicated a value approximately 180 degrees opposite all other wind direction instrumentation indications. "PG&E made the initial reporting of this event assuming the wind speed indicator at the 10m elevation on the Primary Meteorological Tower was functioning correctly. Analysis determined that this instrument was not functioning correctly. PG&E troubleshooting found the sonic wind speed and direction sensors are vulnerable to moisture intrusion. Moisture was found in the body of a wind speed and direction sensor after it had spiked in the rain. The vendor confirmed that moisture on the circuit board could cause an interruption of measurement, which would cause the sensor outputs to read high. PG&E identified moisture intrusion as the presumptive cause of the wind speed spiking . PG&E has sealed all sensors to eliminate the vulnerability. Given the above, PG&E retracts this event report." Notified the R4DO (Miller). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-12-25
46508 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-10-22 18:49 | 2010-12-23 18:37 | 2010-12-23 | UNANALYZED CONDITION - BATTERY CHARGERS MAY LOCKUP DURING A DESIGN BASIS EVENT "On October 22, 2010, the station confirmed the following: "On a safety injection (SI) event with no loss of offsite power (LOOP), calculations show that at various points in the load sequence, the voltage at the charger Motor Control Center will dip low enough on the SI unit to lockup both of the chargers. Additionally, when considering out of sequence loads, such as the containment spray pump, starting on the emergency diesel generator during normal load sequencing, the potential exists that the voltage for any of the chargers on an SI event with a LOOP may drop to the point that would cause the chargers to lockup. "On October 22, 2010, the station completed an operability evaluation of the 11, 12, 21, and 22 battery chargers, implemented compensatory measures to restore battery chargers in the event of an SI to maintain operability (a simple manual action to restart the charger), and determined that the battery chargers were operable but non-conforming. "The NRC Resident [Inspector] has been informed." The licensee is planning on correcting this issue during the next refueling outage. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-12-23
46507 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-12-23 14:07 | 2010-12-23 16:40 | 2010-12-23 | REACTOR SCRAM DURING STARTUP "At 1407 EST, during reactor startup at a RCS [Reactor Coolant System] pressure of 570 psig and with the turbine off-line, a Low Condenser Vacuum trip signal from both RPS [Reactor Protection System] channels resulted in an automatic reactor scram. All control rods fully inserted and plant response was as expected. This notification is in accordance with 10CFR50.72(b)(2)(iv)(B). The reactor is currently subcritical." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-12-23
46506 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-12-23 10:50 | 2010-12-23 12:40 | 2010-12-23 | UNCOMPLICATED REACTOR TRIP FROM 100% POWER "At 1050 CST on 12/23/2010, Fort Calhoun Station experienced a reactor trip due to an unknown cause. No abnormal indications were present at the time of the trip. [Procedure] "EOP-00, Standard Post Trip Actions, was performed. "At 1054 CST, transitioned to [procedure] EOP-01, Reactor Trip Recovery. All Safety Functions of EOP-01 are being satisfied. "At 1207 CST, 345KV Backfeed was established to all 4160V buses. "The plant is currently stable in Mode 3, and the station continues efforts to determine the cause of the reactor trip." All tripable control rods fully inserted during the reactor trip. No PORVs or safety valves lifted. The steam generators are being fed from the Main Feed Pumps and decay heat is being removed to the main condenser. No Emergency Safety Features actuated during the trip except for the reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-12-23
46505 | 0 | PALISADES | 1 |  |  | [1] CE | 2010-12-22 20:00 | 2010-12-22 22:12 | 2010-12-22 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISOR A licensed operator had a confirmed positive for a Controlled Substance during a random fitness-for-duty test. The employee's unescorted access has been suspended. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2010-12-22
46504 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-11-14 05:09 | 2010-12-22 21:33 | 2010-12-22 | INVALID ACTUATION OF TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "This report is a 60-day telephone notification in lieu of written LER being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1). The event was an invalid actuation of the Unit 1 turbine driven auxiliary feedwater (TDAFW) pump. "At 0509 EST on 11/14/2010, during testing of the 1B main feedwater pump (MFP), the TDAFW pump started and the motor driven auxiliary feedwater (MDAFW) valves received a signal to go to automatic control. An investigation determined that during previous testing of the 1A MFP, the 1A MFP trip relay (RTT-1) remained stuck in the trip condition. The stuck relay on the 1A MFP and the trip test on 1B MFP made up the logic for a TDAFW and MDAFW start from both MFPs tripped signal. The 1A MFP trip relay was replaced. "The Unit 1A and B train MDAFW and TDAFW system received the actuation signal. The 1A and 1B MDAFW pumps were already in service at the time for Mode 3 operation. Actual plant conditions did not exist that required an automatic start of the auxiliary feedwater system. Therefore, this actuation was invalid. A complete train actuation occurred and the auxiliary feedwater system functioned successfully." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-12-22
46503 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-12-21 19:32 | 2010-12-21 23:52 | 2010-12-22 | ACCESS TO PRIMARY EMERGENCY OPERATIONS FACILITY NOT POSSIBLE DUE TO ROAD FLOODING "Notified by the Security Shift Commander at 1932 [PST] that access to the primary EOF is not possible due to flooding. San Onofre will activate the alternate EOF if an event is declared. There are no other affected systems or loss to emergency response capabilities due to this flooding." Access to the site has not been impacted due to the flooding. The NRC Resident Inspector has been notified. See similar report #46499. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-22
46502 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-12-21 10:07 | 2010-12-21 15:32 | 2010-12-21 | PROHIBITIVE SUBSTANCE LOCATED INSIDE THE PROTECTED AREA "At 1007 EST a prohibitive substance (un-opened alcohol container) was discovered in the protected area. The non-supervisory individual involved is being evaluated under the behavior observation program and the prohibitive substance (alcohol) has been confiscated. "This report is being made in accordance Significant Fitness-For-Duty Events SEC 1.10, 10 CFR 26.719 (b) Significant FFD policy violations or programmatic failures. The following significant FFD policy violations and programmatic failures must be reported to the NRC Operations Center by telephone within 24 hours after the licensee or other entity discovers the violation: "(1) The use, sale, distribution, possession, or presence of illegal drugs, or the consumption or presence of alcohol within a protected area; "The following are considered significant fitness-for-duty events and must be reported by nuclear stations to the NRC Operations Center by telephone within 24 hours of discovery of the event by the licensee; "Alcoholic beverages and illegal drugs within the protected area, even if no person is in possession of the items." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2010-12-21
46501 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-08-12 | 2010-12-21 12:30 | 2010-12-21 | AGREEMENT STATE REPORT - MEDICAL EVENT- PROSTATE BRACHYTHERAPY TREATMENT UNDERDOSE This information was emailed by the state as follows: "In July 2010, the Wisconsin Department of Health Services (DHS) sent out an Information Notice to all licensees who perform prostate brachytherapy and asked them to perform a retrospective review of all prostate brachytherapy cases to determine whether any medical events had occurred. On December 20, 2010, the licensee's Radiation Safety Officer notified DHS that on August 12, 2008 a patient received only 75.4 % of the prescribed dose during prostate brachytherapy using I-125 seeds. The patient was prescribed 145 Gy to the prostate, and based on a CT scan performed thirty days post-surgery, the licensee determined that the treatment delivered only 109.3 Gy to the prostate. "The authorized user who treated this patient is no longer at the licensee's facility. The licensee is complying with the reporting criteria in DHS 157.72(1)(e) concerning notifications to the patient and referring physician. The licensee has already made process improvements (i.e. planning to higher D90 values) which have resulted in improved dosimetric coverage. DHS inspectors will follow up on the next routine inspection." Event Report ID # WI100019 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-12-27
46500 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2010-11-30 | 2010-12-21 12:30 | 2010-12-21 | AGREEMENT STATE REPORT - MEDICAL EVENT- PROSTATE BRACHYTHERAPY TREATMENT UNDERDOSES This information was emailed by the state as follows: "In July 2010, the Wisconsin Department of Health Services (DHS) sent out an Information Notice to all licensees who perform prostate brachytherapy and asked them to perform a retrospective review of all prostate brachytherapy cases to determine whether any medical events had occurred. During a recent routine inspection, DHS determined that in response to the Information Notice, this licensee was reviewing medical records of several patients who may have received doses during prostate brachytherapy that were less than intended. On November 30, 2010, the licensee's Radiation Safety Officer reported the preliminary identification of one medical event. On December 20, 2010, the licensee's 15-day written report included information on this event, plus an additional two medical events. The doses delivered are D90 values based on CT scans performed thirty days post-surgery. Treatment Date Isotope Prescription Dose Delivered Percentage 6/17/2008 Pd-103 125 Gy to prostate 97.4 Gy to prostate 77.9% 8/24/2009 I-125 145 Gy to prostate 107.9 Gy to prostate 74.4% 9/02/2009 I-125 145 Gy t0 prostate 93.05 Gy to prostate 64.2% "The licensee is complying with the reporting criteria in DHS 157.72(1)(e) concerning notifications to the patients and referring physicians. The licensee stated that the events occurred due to clinical limitations of the interstitial prostate brachytherapy implant technique. The licensee made process improvements (i.e. planning to D90 of 115% of the prescribed dose) which have resulted in unproved dosimetric coverage. DHS inspectors performed a reactive inspection and will follow up on the next inspection." Event Report ID No.: WI100018 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2010-12-27
46499 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-12-20 20:20 | 2010-12-21 01:40 | 2010-12-21 | ACCESS TO PRIMARY EMERGENCY OPERATIONS FACILITY NOT POSSIBLE DUE TO FLOODING "Notified by the Security Shift Commander at 2020 [PST] that access to the primary EOF is not possible due to flooding. San Onofre will activate the alternate EOF if an event is declared. There are no other affected systems or loss to emergency response capabilities due to this flooding." Access to the site has not been impacted due to the flooding. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-21
46498 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2010-12-20 | 2010-12-20 15:10 | 2010-12-20 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The State of Arizona emailed the following information: "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation, and is basically all that is known by the Agency Staff [Arizona Radiation Regulatory Agency] at this time. "At approximately 8:00 AM December 20, 2010, the licensee phoned the Agency [state] to report of a stolen Troxler Laboratories Model # 3430, serial # 36977. The truck from which the gauge was stolen was located at 3330 West Greenway Road Bld. #7, Phoenix, AZ. The gauge contained 8 milliCuries of Cesium-137 and [40 milliCuries (typical) Americium-241: Beryllium]. Phoenix Police were notified at 6:00 AM by the employee. The employee stated that his keys were stolen out of his apartment. The thief then took the gauge out of its agency required lockbox from the bed of a company truck. Phoenix PD is also investigating this event. "The Agency continues to investigate the actions of the licensee and timeliness of reporting the theft. Mexico, the States of CA, CO, NE, NM, UT, and TX as well as the U.S. NRC and the Arizona Governor's office have been notified of this event. Press coverage is not anticipated." First Notice: 10-014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2010-12-23
46497 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-12-19 | 2010-12-20 10:34 | 2010-12-23 | AGREEMENT STATE REPORT - DELAYED MEDICAL SHIPMENT The following was received via email from the Commonwealth of Massachusetts: "Licensee reported not receiving 400 Ci Mo-99/Tc-99m shipment from supplier on schedule (arrival originally expected for 12/18/10). Licensee is in communication with supplier and carrier(s) in ongoing effort to locate missing package. "Last known location, per IRE (shipper), was Frankfurt, Germany. At 12/20/10, 8:30 AM ET, licensee received verbal confirmation confirming the shipment is still on the ground in Germany. Licensee has requested more definitive confirmation from its source(s). "The Agency [Commonwealth] considers this event still OPEN." * * * UPDATE AT 1330 EST ON 12/21/2010 FROM THE COMMONWEALTH OF MASSACHUSETTS TO JOHN SHOEMAKER * * * "The licensee stated that photographic evidence has been received confirming the shipment is still on the ground in Germany. The shipment will be returned to the supplier. "The Commonwealth of Massachusetts considers the event to be closed." Notified R1DO (Perry), FSME (Burgess), and ILTAB (Whitney) * * * UPDATE AT 1137 EST ON 12/23/2010 FROM ANTHONY CARPENITO TO DONALD NORWOOD * * * The Massachusetts Event Docket Number for this event is 12-9422. Notified R1DO (Perry), FSME (Villamar), FSME (Lewis) and ILTAB (Johnson) all via E-mail. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-12-23
46496 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-12-20 03:57 | 2010-12-20 12:26 | 2010-12-20 | FUEL POOL/REACTOR BUILDING EXHAUST PLENUM PRIMARY POWER SUPPLY FAILED "At 0357 December 20, 2010 the 'A' division Fuel Pool/Reactor Building Exhaust Plenum Primary Power Supply failed, resulting in upscale readings on both the Fuel Pool and Reactor Building Ventilation Plenum radiation monitors. This condition resulted in closure of the Group II Primary Containment Isolation Valves (PCIV), isolation of Secondary Containment (SCT), initiation of the Standby Gas Treatment System (SBGT), and a transfer of the Control Room Ventilation (CRV) and Control Room Emergency Filtration (CREF) systems to the High Radiation Mode. Conditions and Required Actions were entered for Technical Specification 3.3.6.2 (SCT Instrumentation), 3.3.7.1 (CREF Instrumentation), and 3.4.5 (RCS Leakage Detection - CAM). Radiation levels were verified to be normal in the affected areas. Isolations signals were reset and Secondary Containment ventilation systems were restored to a normal lineup. "Repairs are currently in progress to replace the high voltage power supply to the affected radiation monitors and are expected to complete within the required action time limits of the applicable technical specifications." The licensee is in a 24 hour LCO. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-12-20
46495 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-12-20 08:05 | 2010-12-20 11:01 | 2010-12-20 | FISH KILL CAUSED BY RATE OF TEMPERATURE CHANGE IN DISCHARGE CANAL "At 0938 hours (EST), the New Jersey Department of Environmental Protection (NJDEP) was notified of a fish kill. The fish kill is due to the rate of temperature change in the discharge canal, associated with an unscheduled and non-routine plant shutdown for a reactor recirculation pump repair. As of 0930 hours, seven (7) Speckled Sea Trout and two (2) Black Drums were reported dead west of the route 9 bridge in the stations discharge canal. "The [New Jersey Pollutant Discharge Elimination System] NJPDES discharge to surface water permit No. 0005550 part IV-B/C item 11, rate of temperature change states, "The rate of temperature change shall not cause mortality of fish or shellfish." "This report is being made in accordance with 10 CFR 50.72(b)(2)(xi) for the occurrence of any event or situation related to protection of the environment, for which a news release is planned or notification to other government agencies has been made." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-20
46494 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-12-20 06:24 | 2010-12-20 10:48 | 2010-12-20 | EVENT REQUIRING OFFSITE NOTIFICATION WITH POTENTIAL MEDIA INTEREST "On 12/20/10 at approximately 0624 CST, the control room received notification that a vehicle/pedestrian accident had occurred on plant property near the south office building complex outside of the protected area. An emergency medical technician from the station's security department immediately responded to the scene of the accident to render emergency medical treatment. A 911 call was placed to local authorities to obtain response by appropriate agencies. Local fire department and ambulance services responded to the site. The individual was transported via helicopter to a trauma center in Green Bay, Wisconsin. "The Senior Resident Inspector has been notified of this event. A press release is not planned at this time, however, the station will respond to media inquiries as needed. This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-20
46493 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-12-20 07:00 | 2010-12-20 05:15 | 2010-12-20 | TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "On 12/20/10, at 0700, planned maintenance is being performed on the Onsite Technical Support Center (TSC) Ventilation System. Air handling unit #1 for the TSC supply ventilation is undergoing its 5 year PM. The TSC ventilation system will be tested following maintenance and returned to normal in service lineup. The system is expected to be out of service for a total time of 8 hours. "This report is being submitted pursuant to 10CFR50.72(b)(3)(xiii) as a result of a reduction in the effectiveness of the Onsite Technical Support Center." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-20
46492 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-20 00:50 | 2010-12-20 03:47 | 2010-12-20 | MANUAL REACTOR TRIP DUE TO A FIRE IN THE MAIN GENERATOR BUS DUCT "At 0050 EST on 12/20/2010, Unit 1 reactor was manually tripped due to a reported fire inside the Unit 1 main generator bus duct. "A fire was reported at 0045 EST in the Unit 1 bus duct which is located inside the turbine building. The Unit 1 reactor was tripped to remove power from the generator bus. After the reactor trip, the fire was extinguished by the application of water to the bus duct by the fire brigade. The fire was reported extinguished at 0100 EST. "Method of decay heat removal is via steam dumps. Current temperature and pressure: Temp. 548 degrees and stable; Pressure 2239 psig and stable. No indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from off-site power. No impact to Unit 2, [and] Unit 2 is operating at 100% power [in] Mode 1." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-12-20
46491 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-20 00:21 | 2010-12-20 01:09 | 2010-12-20 | FIRE IN FUEL HANDLING BUILDING HVAC PANEL "Smoke and sparks were identified as coming from a level 4 Control Building Normal Fuel Handling Building HVAC Heater Control Panel. The heater control panel was deenergized. The fire team was dispatched. The fire was contained in the heater control panel. Smoke removal is in progress." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM HANS BISHOP TO PETE SNYDER AT 0219 EST ON 12/20/10 * * * At 0218 the licensee terminated the Notice of Unusual Event. Notified R2DO (Henson), NRR EO (Evans), DHS (Strangfeld), and FEMA (Hollis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-12-20
46490 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2010-12-19 00:08 | 2010-12-19 01:39 | 2010-12-19 | QUICKLY CONCLUDED NOTICE OF UNUSUAL EVENT DUE TO A LOSS OF COMMUNICATIONS "At 2355 CST, on 12/18/2010, the Control Room was notified by security of the inability of offsite personnel to call into the plant. [At] 0008 CST, on 12/19/2010, the control room verified that the ENS Phone, Conference Operation Network (COP), Security Building, Training Center, and Blair Phone Lines were not functional. At 0011 CST, a Notice of Unusual Event (NOUE) was declared per IC SU6 EAL 2. This also meets the criteria for a Major Loss of Communications Capability under 10 CFR 50.72(b)(3)(xiii). "At 0028 CST, the control room was notified by security that Huntel Communications was attempting to correct the communications issue. At 0030 CST, the COP phone was restored. At 0046 CST, the ENS phone was verified to be functional. "At 0050 [CST], the criteria to exit the NOUE [was met] and the event was terminated. At 0059 [CST], the NRC Senior Resident Inspector was notified." The state and local agencies were notified. The NRC Operations Center conducted a satisfactory test of the ENS line. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(xiii) |  |  | 0 | 2010-12-19
46489 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-12-10 | 2010-12-17 19:16 | 2011-02-01 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA LOCKING DEVICE FAILURE RESULTING IN PERSONNEL EXPOSURE "On December 17, 2010, the Agency [Texas Department of Health Services] was notified by the licensee that on December 10, 2010, the locking device on QSA model 880 camera containing 97 curies of Iridium (Ir) 192 failed to activate. The radiography crew (group A) had completed operations at one site near Lufkin, Texas, and was moving to a new location at the same site. The radiography camera with the cranking device and guide tube still attached were placed in the dark room of the radiographers' truck. The licensee stated that a survey was conducted to verify the source was in the fully shielded, locked position. As the radiographer was driving to the new location, he passed about 5 feet from another group of radiographers (group B) from the same licensee. As group A passed by group B, group B's dosimeters alarmed. Group B stopped group A and told them that their alarms had gone off. Group A went to the camera, picked up the crank for the camera, and found that the source had moved from the locked position approximately one quarter of a turn. The radiographer cranked the source back to the fully shielded position and secured the camera for transportation. "The radiographers did not inform the licensee of the event until December 16, 2010. At that time, the licensee began an investigation of the event, including reenactments of the event to determine how much dose the radiographers had received. During the investigation, it was discovered that both radiographer's self reading pocket dosimeters had been read after the camera was secured and were reading off scale. The licensee determined that radiographers 'A' were eight feet from the source while they were driving and would have been exposed to the source for approximately 10 minutes. A dose estimate of 1,700 millirem was made for both individuals. The thermoluminescent dosimeters for radiographers 'A' have been sent to the processor for reading. The licensee stated they expected the readings by late Monday December 20. The licensee stated that several pieces of radiography film were lying on the seat of the truck when the event occurred. The film was developed and indicated that it had been exposed to approximately 1,700 millirem. The licensee stated that neither radiographer would have received enough exposure to exceed any limit. The licensee stated that no member of the general public was exposed to any radiation as a result of this event. "The licensee has not inspected the camera. The licensee stated that the camera is out of service and is currently stored in their storage facility. Additional information has been requested of the licensee. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #I-8803 * * * UPDATE FROM ART TUCKER TO JOE O'HARA VIA E-MAIL AT 1203 EST ON 1/18/11 * * * "On December 23, 2010, the Agency [Texas Department of Health Services] performed an on-site investigation at the licensee's facility. The investigation determined that the camera did not fail to operate properly, but that the operator failed to fully retract and lock the source in place." * * * RETRACTION RECEIVED VIA EMAIL FROM A. TUCKER TO J. SHOEMAKER AT 0856 EST ON 2/1/11 * * * "This event was initially reported as a failure of the locking device on a radiography camera. The investigation into the event determined that it was caused by operator error and not a failure of the equipment to operate as designed." Notified R4DO(Howell) and FSME(McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-12-22
46488 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-12-17 15:35 | 2010-12-17 17:38 | 2010-12-17 | UNANALYZED CONDITION - POTENTIAL EQUIPMENT ACTUATIONS DUE TO ELECTRICAL SHORT CIRCUITS "A post-fire safe shutdown (PFSSD) circuit analysis identified the potential for a fire in the Control Room to cause multiple proper polarity hot shorts causing the Pressurizer Power Operated Relief Valves (PORV) to open. This postulated failure would require at least three separate 'smart' hot shorts including 1) a positive external hot short, 2) a negative external hot short, and 3) a short across the control room hand switch to cause each PORV to open. This could result in a loss of coolant accident inside the containment building. "This circuit analysis also identified that a fire in the control room could cause the recirculation dampers associated with the 'B' Essential Service Water Pump Room and 'B' Emergency Diesel Generator Room to fail open, closed, or anywhere in between. This could cause the room temperatures to drop below the minimum or rise above maximum design temperatures depending on ambient conditions. "Compensatory measures are established for early detection and extinguishment of a fire associated with these circuits in the Control Room. Procedure changes are also being developed for Control Room Evacuation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-12-17
46487 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-12-17 09:37 | 2010-12-17 14:12 | 2010-12-17 | DIESEL FUEL OIL SPILL CONTAINED ON SITE - FEDERAL AND STATE OFFICIALS NOTIFIED "At 0937 CST, 12/17/2010, the Kentucky Emergency Response Team (Report Number 2321984), the Kentucky Department for Environmental Protection, and the National Response Center (Report Number 962502) were notified of the following issue: a diesel fuel oil leak occurred from a pressure indicating line from storage tank located at [Bldg] C-600. The amount of diesel fuel that leaked from the storage tank is greater than the reportable quantity of 75 gallons. The secondary containment drain valve leaked which allowed the diesel fuel to reach the oil containment underflow dam at outfall 008. The diesel fuel is currently contained in the oil containment underflow dam. The effluent from outfall 008 has been tested and does not contain any detectable diesel fuel. Additionally, no visible sheen was observed from the effluent from outfall 008. Cleanup of the diesel fuel is in progress. "This event is reportable as 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.' "The NRC Resident Inspector has been notified of this event. "PGDP Event Report No. PAD-2010-13." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2010-12-17
46486 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2010-12-16 10:44 | 2010-12-17 09:04 | 2010-12-17 | BOTH HF DETECTORS IN GHS TEST LOOP FAILED TO BE AVAILABLE AND OPERABLE "During a performance of internal procedure to verify functionality of installed HF detectors in the Test Loop (TL) Gas Handling System (GHS) room, it was discovered at about 1044 [EST on] 12/16/10, that both IROFS TL-HF-01 and IROFS TL-HF-02 failed to pass internal test requirements. At least one of these HF detector IROFS is required to be available and operable to meet 10 CFR 70.61 performance requirements. "The installed HF detector electrochemical sensors performance appears to have been degraded as a result of low room 'relative humidity' as a result of unusually cold outdoor conditions. The independent IROFS TL-HF-04 (an administrative control) remained intact, thus no unsafe condition existed. While one documented IROFS remained functional (TL-HF-04) to assure the consequence of chemical and radiological exposure is maintained low, TL-HF-04 could not alone meet 10 CFR 70.61 performance requirements. "No loss of UF6 containment occurred in affected process equipment. The degradation of TL-HF-01 and TL-HF-02 was observed as part of the IROFS' periodic surveillance. This event is therefore being reported pursuant to the requirements of 10 CFR 70 Appendix A(b)(2) within 24 hours. The affected TL bench scale experiment equipment will remain shutdown pending further investigation and implementation of associated corrective actions. "SAFETY SIGNIFICANCE OF EVENTS - Low safety significance - the discovery did not result in an unsafe condition. "SAFETY EQUIPMENT STATUS - Required IROFS TL-HF-01 and TL-HF-02 functionality being re-established. "STATUS OF CORRECTIVE ACTIONS - The affected TL process operation remains shutdown pending investigation and implementation of corrective actions." The licensee will be contacting NRC Region 2, state and local government agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-12-17
46485 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2010-12-16 08:00 | 2010-12-16 06:04 | 2010-12-16 | PLANNED MAINTENANCE TO MICROWAVE RADIO SYSTEM AFFECTING EOF, STATE AND COUNTY FACILITIES "This is an eight hour report per 10 CFR 50.72 (b)(3)(xiii). Calvert Cliffs will be implementing scheduled maintenance to the microwave radio system to improve reliability of the system at the Emergency Operations Facility (EOF), State and County facilities. "This work will require that the microwave radio system at the EOF be removed for a period of approximately 4 to 6 hours. During this time, the following systems will be impacted for the duration of maintenance: 1. The plant's (e.g., Control Room, Technical Support Center (TSC), Simulator) Dedicated Offsite Agency telephones will be out of service. (EOF's system will continue to function) 2. 800 MHz desk set radios at the EOF only will be out of service. 3. 153.44 MHz frequency at the EOF only will be out of service. (backup for MEMA and MDE) 4. MIDAS Terminal (Meteorological Data) located in the Dose Assessment Office at the EOF will be out of service. 5. TSC Computer data transfer to the EOF only will be out of service. "Once the scheduled maintenance starts, the systems (listed above) can be returned to service within 1 hour. "Should an emergency be declared during this period, the Control Room will continue to have the capability to make the event notification to the offsite agencies within 15 minutes using either commercial telephone lines or the 800 MHz radio console (includes the 153.44 MHz frequency). The Emergency Preparedness communications procedure provides a chart listing the communication devices available and the order in which the process is to be implemented. MIDAS (Meteorological Data) will continue to be operational at the site and can be obtained by contacting the Control Room or TSC. The ERPIPs also provide a backup process and the instructions necessary for the EOF Dose Assessment Office to obtain Meteorological Data. Plant data can be obtained from the CR or TSC and will continue to be downloaded from the plant computer to the ERO SharePoint site. "All work associated with this microwave radio maintenance will be performed in an expeditious manner consistent with the goal of minimizing unavailability of the systems listed above. A test of the offsite agency notification devices in the Control Room will be made prior to the commencement of the maintenance. A test of all systems will be performed at the completion of the maintenance. "All EOF responders and Control Room personnel have been briefed on this work and expected contingent actions. "This job will start on Thursday, December 16, 2010 at approximately 8:00 am. We anticipate that all work will be completed by 2:00 pm on the same day, including testing of the system. We will provide a notification update upon completion of the job." The licensee informed the NRC Resident Inspector and the affected State and County Agencies. * * * UPDATE AT 1248 ON 12/16/2010 FROM TOM JONES TO MARK ABRAMOVITZ * * * The maintenance and testing was completed satisfactorily at 1130 EST. The licensee notified the NRC Resident Inspector. Notified the R1DO (Holody). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-16
46484 | 0 | NORTH CAROLINA STATE UNIVERSITY |  |  |  | 1000 KW PULSTAR POOL TYPE | 2010-12-13 15:00 | 2010-12-15 16:24 | 2010-12-15 | RESEARCH REACTOR RADIOGRAPHY INCIDENT On 12/13/10 at 1500 EST, North Carolina State University [NCSU] was conducting routine radiography with the reactor at 1MW when unknown to the technician, the shutter stuck open. The technician entered the shielded room and noticed the shutter wasn't closed and immediately left the exposure room. After the technician left the room and secured the area, he notified other personnel including the control room. NCSU reports that the reactor was shut down by the operator because of this event. After the reactor was shut down, personnel entered the room and closed the shutter. The shutter door interlock had malfunctioned due to a mechanical interference. It was noted that the technician was not wearing personal dosimetry. NCSU estimates (based on cameras and a re-enactment conducted with the technician) that the technician was exposed for a maximum of 18 seconds with a resulting dose rate of about 150 mRem. NCSU corrective actions include a research reactor shutdown, closing of the radiography shutter, installing interlocks to prevent shielded room access with the shutter not fully closed, and safety training of personnel related to use of the radiography facility. NCSU is making this report in accordance with their research reactor technical specifications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 2 | NC | NPR | [5 empty] | 0 | 2010-12-15
46483 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-15 13:20 | 2010-12-15 16:37 | 2010-12-15 | OFFSITE NOTIFICATION OF AN AMMONIA SPILL INTO THE DELAWARE RIVER "A notification was made to the New Jersey Department of Environmental Protection of a discharge of approximately 500 gallons of water containing ammonia with a concentration of 1 ppm. The discharge occurred due to the U-1 FHB [Fuel Handling Building] Supply Fan HW coil rupture. The solution was discharged into the storm drain outside of the FHB Annex door. That storm drain leads to a permitted outfall that communicates with the Delaware River. The leak has been isolated and the downstream catch basin plugged. The remaining water in the discharge line upstream of the plugged catch basin will be removed by a contractor. "There was no out-of service safely related equipment that contributed to this event. No one was injured as a result of this event." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-15
46482 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-12-15 01:48 | 2010-12-15 05:40 | 2010-12-15 | UNIT 2 MANUAL REACTOR TRIP DURING STARTUP "On 12/15/10 at 0148 [CST] Control room personnel initiated a manual reactor trip in order to abort a startup in progress with the Unit 2 Reactor subcritical. "During the performance of OP-1B, Reactor Startup for Unit 2 both Rod Control System Urgent and Non-Urgent alarms were received. Shortly after receiving the alarms multiple groups of control rods fell into the core as indicated by Individual Rod Position Indicators (IRPl's) and rod bottom lights. Based on these indications a manual reactor trip was initiated. All systems functioned as expected, with all control rods fully inserting. The plant is currently in Mode 3 and operating in accordance with normal plant procedures." The cause of the control rod alarms is under investigation. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-12-15
46481 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-12-14 17:40 | 2010-12-14 22:35 | 2010-12-14 | ENS PHONE LINES OUT OF SERVICE DUE TO A FAILED RECTIFIER "At 1740 CST the control room was notified by a commercial phone provider that they had received alarms indicating the ENS communications lines were out of service. Attempts to use the ENS lines confirmed that the ENS system is not functioning at the site. Commercial lines with an 899 prefix are also not functioning. Alternate commercial lines are available and have been verified functional. The vendor has determined that the loss of the ENS lines are the result of a failed rectifier. It is currently not known when the ENS lines will be returned to service. Farley Nuclear Plant may be contacted via commercial line." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM ARENS TO KLCO ON 12/14/10 AT 2318 * * * ENS line at Farley was repaired and successfully tested. The licensee will notify the NRC Resident Inspector. Notified R2DO (Henson) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-14
46480 | 0 | HIRSCHFELD INDUSTRIES |  |  |  |  | 2010-12-10 | 2010-12-14 16:43 | 2010-12-14 | STRUCTURAL STEEL BEAM FAULTS The following information was received by facsimile: "Several W16 x 67 [structural steel] beams have been discovered with a longitudinal crack in the web of the beam. The crack appears to run intermittently down the entire length of the beam. Each of the beams were found to be from the same heat (22536130). "Procurement was notified and indicated that [Hirschfeld] purchased 15- 50 feet beams with this heat number. The location of all pieces of this heat were located. It was determined that some were in [the Hirschfeld] shop, some were at the fireproofer and three pieces had been delivered to the site [Eunice, NM] but were not erected. Arrangements have been [made] to have all pieces returned to [the Hirschfeld] facility. Customer, Baker Concrete Construction (National Enrichment Facility, Eunice, NM) has been notified as has the supplier of the steel, Gerdau Ameristeel, Midlothian, TX." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2010-12-14
46479 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2010-12-14 | 2010-12-14 16:15 | 2010-12-29 | AGREEMENT STATE REPORT - STOLEN TROXLER SOIL MOISTURE DENSITY GAUGE The following report was received via facsimile: At 1545 EST on 12/14/10, the Florida Bureau of Radiation Control received an initial report from the licensee concerning a stolen soil moisture density gauge. The gauge was stolen from a truck at either the employee's residence [Branford, FL] or the licensee's place of business. A chain was cut from the truck securing the case with the gauge inside. Both the case and gauge were discovered stolen. The licensee still has keys to the gauge and will offer a reward for its recovery. Jacksonville Inspection Office will investigate. The Soil Moisture Density Gauge is a Troxler Model 3430, serial #27858, containing 40 mCi of Am/Be and 8 mCi of Cs-137 sources. FL Incident No.: FL10-120 * * * UPDATE FROM STEVE FURNACE TO JOE O'HARA AT 1614 AT 12/29/10 * * * On December 15, 2010, the gauge was discovered by a private citizen in Suwannee County, Florida and placed in the custody of the police department. The gauge was locked and undamaged. The incident has been referred to the state licensing and materials office for further investigation. Notified R1DO(Hansell), FSME(Watson), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2010-12-17
46478 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-12-14 12:45 | 2010-12-14 14:29 | 2010-12-14 | SAFEGUARDS REPORT - POTENTIAL DISCOVERED VULNERABILITY Discovered vulnerability in a safeguard system that could potentially allow access to a controlled access area for which compensatory measures had not been employed. Upon discovery, compensatory measures were established. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-12-14
46477 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-13 21:19 | 2010-12-14 02:02 | 2010-12-14 | MANUAL ACTUATION OF AUXILIARY FEEDWATER SYSTEM IN RESPONSE TO LOSS OF ONE MAIN FEEDWATER PUMP "At 2119 EST on December 13, 2010, operators manually started all Auxiliary Feedwater (AFW) pumps in response to a loss of the Unit 1 East Main Feedwater Pump. "Operators were responding to decreasing condenser vacuum on the East Main Feedwater Pump and reducing turbine load when the East Main Feedwater Pump was manually tripped at approximately 21 inches of vacuum Hg. Operators entered the abnormal operating procedure for Loss of One Main Feedwater Pump, which directs starting all three AFW pumps. "Plant power was stabilized at approximately 49%. "The licensee will be notifying the NRC Senior Resident Inspector. "This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A) due to the valid actuation of the AFW system in response to equipment failure." No maintenance was in progress, and the cause of the decreasing condenser vacuum in the MFP was due to debris in the traveling water screen. | 49 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-12-14
46476 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2008-03-10 | 2010-12-13 15:51 | 2011-07-01 | AGREEMENT STATE REPORT - MEDICAL EVENT - PATIENT RECEIVED LESS THAN THE PRESCRIBED DOSE "The Kentucky Radiation Health Branch was notified by the U.S. NRC by email on October 4, 2010 of a possible medical event occurring in the Commonwealth. There was no identification of the licensee involved. After extensive research, the Radiation Health Branch identified the licensee where the alleged medical event occurred. During an inspection of the facility, a review of medical documents identified a medical event involving the therapeutic treatment of prostate cancer with Pd-103 seeds. "The treatment plan called for 100 Pd-103 seeds with an activity of 1.237 mCi per seed. The pretreatment plan of D90=132.78 Gy. The post treatment plan indicated the prostate received a D90=5.18 Gy. The licensee has not acknowledged a medical event. The patient involved has never been notified by the licensee. He was advised of the misadministration by another physician during a second opinion medical evaluation. "Violations have been issued to the licensee. [An] evaluation [by the state] is ongoing." * * * UPDATE FROM MICHELE GREENWELL TO JOE O'HARA AT 0841 ON 12/15/10 * * * The following update was received from the Commonwealth via fax: "The written directive had a prescribed dose for Pd-103, 100 Gy, act/seed 1.6 U, number of seeds 100." Notified R1DO(Holody) and FSME(Villamar). * * * UPDATE FROM MICHELE GREENWELL TO MARK ABRAMOVITZ ON 7/1/2011 AT 1353 EDT * * * The Commonwealth of Kentucky performed an inspection of Our Lady of Bellefonte Hospital on 11/30/2010 and found 35 additional cases of medical misadministration during prostate seed implantation by one doctor. The date of the misadministration occurred from 10/3/2001 to 2/24/2009. No written directive for the dose prescribed or delivered was found for 14 of the cases with the remainder of the cases not having the post implant dose recorded. There was no post CT scan on 17 cases, and D90 doses ranged from 0% to 162% of the prescribed dose. The physician was notified on all of these cases however, none of the patients were notified. Notified the R1DO (Welling) and FSME (Jackson). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2010-12-19
46475 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-12-13 12:10 | 2010-12-13 15:07 | 2010-12-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO NOT MEETING ROD GROUP ALLIGNMENT LIMITS "On 12/13/10 at 1210 CST a Technical Specification (TS) required shutdown was initiated on Unit 2. TS Limiting Condition for Operation (LCO) 3.1.4, Rod Group Alignment Limits, was not met as a result of Surveillance Requirement (SR) 3.1.4.2 not being met. TS Action Condition (TSAC) 3.1.4.A was entered which requires the shutdown margin to be within the limits of the Core Operating Limits Report (COLR) or boration be initiated to restore shutdown margin to within the limits within one hour and that the reactor to be in MODE 3 within 6 hours. Shutdown margin has been verified to be within the limits specified in the COLR and a reactor shutdown has been initiated. "On 12/10/10 at 1350 [CST], during performance of Technical Specification surveillance procedure TS-06 Rod Exercise Test, rod control urgent and non-urgent failure alarms occurred while stepping Control Bank B rods out. These alarms were verified locally in the Unit 2 rod drive room. On 12/10/10 at 2212 [CST], the test recommenced and control bank B was stepped out one step as procedurally required with no alarms. When control bank B was subsequently stepped inward one step, both rod control urgent and non-urgent failure alarms were received. Both of the times that Control Bank B rods failed to move, the movable gripper coil power supply fuse blew for control rod F-6. On 12/12/10 at 2143 CST, the surveillance procedure for Control Banks A, C, and D and Shutdown Banks A and B were completed satisfactorily, however, the failure of the Control Bank B rods to step in correctly resulted in the inability to satisfy SR 3.1.4.2, and entry into TSAC 3.1.4.A being required. During continuation of the surveillance on 12/12/10, it was not recognized that troubleshooting and repairs could not be conducted satisfactorily prior to the expiration of the surveillance interval. Therefore, a TS-required shutdown in accordance was not initiated. "The likely cause of the failure is a damaged cable in the movable gripper circuitry for control rod FÀ6. Troubleshooting is continuing and a repair plan has been developed. "The NRC Senior Resident Inspector and Region III have been notified." * * * UPDATE FROM PLESSAS TO KLCO ON 12/15/10 AT 1736 * * * "On 12/13/10 at 1210 CST, a Technical Specifications (TS) required shutdown was initiated on the Unit 2 reactor. TS Limiting Condition for Operation (LCO) 3.1.4 Rod Group Alignment Limits was not met due to exceeding the specified Frequency and Grace Period for Surveillance Requirement (SR) 3.1.4.2, which required a verification of the freedom of movement (trippability) of each control rod not fully inserted into the core. TS LCO 3.1.4 is not met, and TS Action Condition 3.1.4.A was entered which requires the shutdown margin to be within the limits of the Core Operating Limits Report or boration be initiated to restore shutdown margin to within the limits within one hour as well as requiring that the reactor to be in Mode 3 within 6 hours. Shutdown margin has been verified to be within the limits specified in the Core Operating Limits Report and a reactor shutdown has been initiated. "On 12/10/10 at 1350 CST, during performance of TS Surveillance-6 (TS-6) Rod Exercise Test, Rod Control Urgent and Non-Urgent failure alarms occurred while stepping Control Bank B rods out. These alarms were verified locally in the Unit 2 rod drive room. On 12/10/10 at 2212 CST, TS-6 recommenced and Control Bank B was stepped out one step as procedurally required with no alarms. When control bank B was subsequently stepped inward one step, both Rod Control Urgent and Non-Urgent failure alarms were received again. Both of the times that the Control Bank B rods failed to move, the movable gripper coil power supply fuse blew for control rod F-6. On 12/12/10 at 2143 CST, TS-6 for control banks A, C, & D and Shutdown Banks A & B was completed satisfactorily. "Troubleshooting is continuing and a repair plan has been developed. "The NRC Resident Inspector has been notified." Notified R3DO (Kozak), IRD (Grant), NRR (Evans) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-12-13
46474 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2010-12-12 11:28 | 2010-12-12 16:44 | 2010-12-12 | HIGH PRESSURE COOLANT INJECTION SYSTEM UNAVAILABLE "During quarterly operability verification of the HPCI Turbine Overspeed Trip Assembly, the Trip/Reset knob was manually lifted and released to time the automatic reset function. Upon release of the knob, the Trip Assembly failed to automatically reset (the HPCI Turbine Stop and Control Valves remained closed). Adjustment of the Trip/Reset needle valve was unsuccessful. The HPCI Turbine Stop and Control Valves remain in the tripped condition, rendering HPCI unavailable. "Engineering and Maintenance have been dispatched to troubleshoot and repair the Overspeed Trip Assembly and restore HPCI to operable status. "All other required systems are available, operable, and protected." The licensee is in the 14 day LCO 3.5.1. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-12-12
46473 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-12-09 23:04 | 2010-12-10 15:54 | 2010-12-12 | OFFSITE NOTIFICATION - AGENCIES NOTIFIED OF ONSITE TRITIUM LEAK "On December 9, 2010, elevated levels of tritium were identified in water samples taken from in-leakage into the below ground elevation of the diesel generator building (i.e., through underground conduit penetrations). The tritium levels were determined to be in excess of the Nuclear Energy Institute (NEI) voluntary reporting criteria (i.e., 30,000 pCi/L for onsite groundwater, as specified in the Offsite Dose Calculation Manual). Further investigation determined that the likely source of the tritiated water is buried piping located west of the diesel generator building. The area of the leak is inside the plant protected area, well inside the site's property boundary. There is no indication that tritium has migrated into drinking water sources or has migrated off plant property. The leakage has not impacted plant reliability or the operability of any safety-related equipment. "Corrective actions taken were to capture the in-leakage of water into the diesel generator building and route it through our normal permitted discharge paths. Additional water samples will continue to be obtained from site monitoring wells until the source of the leak is isolated. Efforts to identify and isolate the source of the leakage, and plans for excavation of the suspected area, are in-progress. "The Brunswick plant has had an extensive groundwater protection monitoring program in place since 2007. This environmental sampling program consists of more than 100 monitoring wells which are routinely sampled. "The following agencies will be updated on the status of the onsite tritium samples: City of Southport, Brunswick County, State Officials, NEI, INPO, and ANI. "The Licensee has notified the NRC Resident Inspector." * * * UPDATE ON 6/12/10 AT 1610 EST FROM GRZECK TO HUFFMAN * * * "On December 10, 2010, at 2124 hours (EST), the buried piping leak was stopped after isolating the Unit 1 Condensate Make-up line to the Main Condenser (i.e., from the Condensate Storage Tank (CST)). The elevated levels of tritium are confined to the area in close proximity to the identified buried pipe location, west of the diesel generator building, well within the site's property boundary. The perimeter monitoring wells to the plant's protected area and site boundary continue to be analyzed with no increase in tritium levels identified. Preparations for the excavation and repair of the Condensate Make-up line are in-progress. "The following agencies will be provided an update of this event: City of Southport, Brunswick County, State Officials, NEI, INPO, and ANI. "The initial safety significance of this event is minimal. The Brunswick Steam Electric Plant has not identified any health or safety risk to the public or onsite personnel. There is no impact to plant reliability or safety. "The Licensee has notified the NRC Resident Inspector." R2DO (Moorman) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-10
46472 | 0 | HENRY FORD MACOMB |  |  |  |  | 2010-12-10 09:00 | 2010-12-10 14:57 | 2010-12-15 | MEDICAL EVENT - TREATMENT AREA DIFFERENT FROM THE PRESCRIBED AREA A High Dose Rate brachytherapy treatment with a 5.11 Ci source of Ir-192 was performed on a patient for vaginal cancer. The prescribed procedure was for a tube be inserted into the vaginal area for 120 cm, however, the treatment length of insertion was 132 cm. This was an out-patient procedure, so the patient went home after her treatment. The physician will be notifying the patient of the 12 cm insertion error. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1610 EST ON 12/15/2010 FROM BRETT MILLER TO MARK ABRAMOVITZ * * * The brachytherapy exposure was received by four patients with the 12 cm insertion error. Three patients received three fractions each and the fourth received five fractions. The physicians have been notified except for the fourth patient's physician who will be notified. Notified the R3DO (Kazak) and FSME (O'Sullivan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-12-16
46471 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-12-09 22:58 | 2010-12-10 01:25 | 2010-12-10 | MANUAL REACTOR TRIP AFTER INDICATIONS OF A CONDENSER TUBE LEAK "At 2200 [EST] 12/09/2010, Unit 4 had indication of a condenser tube leak. A power reduction was commenced in accordance with plant procedures to allow isolation of the leaking waterbox. Sodium levels in the Steam Generators increased and a unit shutdown was required. Power was reduced to 20% and a manual reactor trip was initiated at 2258 [EST] 12/09/10, in accordance with plant procedures. All systems operated as required and the unit is stable in mode 3." The reactor trip was not complicated. All control rods inserted fully and decay heat is being removed by the atmospheric steam dumps. There is no indications of primary to secondary leakage. Normal offsite power is available and Unit 3 is unaffected. 3 of 3 steam generators are affected by the increase in sodium levels. The licensee is in progress of conducting steam generator blowdowns. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-12-10
46470 | -1 | PIPE COUNTY MEMORIAL HOSPITAL |  |  |  |  | 2010-12-09 12:00 | 2010-12-09 18:05 | 2010-12-10 | TWO DIFFERENT PATIENTS RECEIVED INCORRECT DIAGNOSIC DOSES DUE TO VIAL MIX-UP A representative of the licensee (the hospital rad tech) reported that two patients were administered doses of diagnostic Technetium-99m (Tc-99m) for the wrong organs due to a mixed-up of the dose vials. Specifically: Patient #1 received a 25 millicurie Tc-99m dose for a bone scan instead of the prescribed 10 millicurie Tc-99m dose for a Hida scan (to the gall bladder). Shortly thereafter, Patient #2 received the 10 millicurie Tc-99m dose for a Hida scan instead of the prescribed 25 millicurie Tc-99m dose for a bone scan. Both errors were discovered when the actual diagnostic scans were performed. The patients, their physicians, and the RSO have been notified of this event. The licensee representative stated that there should be no harm to the patient from the incorrect administration. The cause of this event was reported to be insufficient verification that the proper vial had been selected for injection. Both vials were reported to be identical in appearance. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM JOEL HASSIEN TO HUFFMAN AT 1549 EST ON 12/10/10 * * * After further review of the event described above, the licensee determined that the event was not reportable to the NRC Operations Center. The retraction is based on a determination that the dose to the organs involved did not exceed the reportability limits. The licensee will log the details of this event. R3DO (Daley) and FSME (Diaz-Torro) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2010-12-15
46469 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-06 08:15 | 2010-12-09 12:53 | 2010-12-09 | OFFSITE NOTIFICATION - OSHA CONTACTED DUE TO FATALITY OF CONTRACTOR EMPLOYEE "At 0815 Eastern Standard Time on December 6, 2010, TVA Construction Contractor, Bechtel, notified the Occupational Safety and Health Administration (OSHA), in accordance with 29 CFR 1904.39, that a Bechtel employee had suffered a fatality from an apparent heart attack, while working on the Watts Bar Unit 2 Construction completion project. This information was also provided to Tennessee Department of Labor and Workforce Development, Division of Occupational Safety and Health (TOSHA). "This event had no consequences to the health and safety of the public, other onsite workers, or the environment. "The NRC Resident Inspector has been notified of this event." The employee's heart attack happened while he was operating a fork lift at the Parts/Receiving area. Offsite responders were called to the scene, however, the employee was unresponsive to their actions. Employee was transported to the Rhea County Hospital where he was pronounced dead. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-09
46468 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-12-08 10:45 | 2010-12-09 09:33 | 2010-12-09 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR MOISTURE/DENSITY GAUGE The following report was received via facsimile: "Event date and time: December 8, 2010 - Time: 10:45 am "Event location: 91st & Heritage Lake Drive, Lincoln, Nebraska, 685 "Event description: The licensee possesses a Humboldt Scientific, Inc. Model 5001-EZ 122 Nuclear Moisture/Density Gauge Serial Number 2027. On December 8, 2010, the gauge was being used at a construction site just east of Lincoln, NE. The operator of the gauge had started a test when he was distracted by another worker asking questions. During that time a front end loader backed into the gauge and broke the stationary guide rod. No other damage was observed to the gauge. The area was secured and radiation surveys as well as a leak test were performed. No unusual readings were observed. The source rod was secured in to safe position in the gauge housing and the gauge was place in the transport case for return to the licensee's office. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-12-14
46467 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2010-10-28 15:04 | 2010-12-08 16:51 | 2010-12-08 | INVALID ACTUATION OF THE "B" EMERGENCY SERVICE WATER (ESW) PUMP Text provided by the licensee. Quotations omitted for readability. Report Type: This 60-day telephone notification is being made under 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1). Description: On October 28, 2010, during the performance of MST I0073, "Train 'B' 18 Month Manual Reactor Trip, Solid State Protection System Actuation Logic & Master Relay Test", two sequential errors resulted in the inappropriate activation of the 'B' ESW pump. During night shift on October 27/28th, the Master Relay Selector Switch was not returned to the required OFF position. This caused day shift to find one of the two general warning lights to be lit. During the troubleshooting for the light, a technician discovered the Master Relay Selector Switch out of the expected OFF position as required by the procedure. A technician moved the switch to the OFF position outside of procedural guidance, resulting in the partial activation of the Reactor Protection System, including the 'B' ESW pump. The plant was in Mode 6 due to refueling outage 16 during the event. Actual plant conditions and parameters did not exist that required an automatic start of the 'B' ESW Pump. Therefore, this actuation is classified as invalid. The system started and functioned successfully. This invalid actuation was entered into the corrective action program as NCR 430289. Cause: Poor performance of task by the individual. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-12-08
46466 | 0 | RIO TINTO MINERALS |  |  |  |  | 2010-12-02 | 2010-12-08 15:44 | 2010-12-08 | FIXED NUCLEAR GAUGE RECOVERED IN LOAD OF SCRAP STEEL A 50mCi Cs-137 Kay-Ray Model 7062B (S/N 17573) Gauge was recovered in a pile of scrap steel at the Pacific Steel & Recycling Company in Bozeman, MT. The U.S. NRC Region IV contacted the device manufacturer to identify the owner of the general licensed source and dispatched an NRC Inspector on 12/3/10 to initiate a reactive inspection (PNO-RIV-2010-006). The owner, Cyprus Industrial Minerals in Ennis, Montana, had purchased the gauge in June 1984 for use in their Yellowstone mine. The company was subsequently sold to Rio Tinto Minerals located in Three Forks, MT. The representative from Rio Tinto Minerals is currently arranging for removal and disposal of the gauge in safe storage at the Pacific Steel & Recycling Company. A conference call was held on 12/2/10 at 1800 EST with R4 (Vivian Campbell, Tony Gaines) and FSME (James Danna). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-12-08
46465 | 0 | CONTINENTAL CEMENT |  |  |  |  | 2010-12-08 13:00 | 2010-12-08 14:17 | 2010-12-08 | STUCK SHUTTER ON BERTHOLD MODEL P2608-100 DUE TO CEMENT DUST BUILDUP While performing semi-annual shutter checks on a Berthold Waybelt Scale Process Gauge Model P2608-100 containing 5 milliCuries of Cobalt 60, a technician found the shutter partially open and was not able to fully close the shutter due to cement dust buildup on the shutter mechanism. The gauge is located in a secure guarded location not readily accessible to personnel, and does not present a hazard to personnel. The company will shut down the process line on 12/21/10 and perform repairs to the process gauge at that time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-12-08
46464 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-12-08 08:07 | 2010-12-08 10:50 | 2010-12-08 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF EMERGENCY SIRENS "At approximately 0807 CST on December 8, 2010, Pierce County [Wisconsin] Dispatch inadvertently activated the Pierce County sirens during the conduct of the silent siren test. The sirens were deactivated within 30 seconds." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-08
46463 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-12-07 15:32 | 2010-12-07 18:19 | 2010-12-07 | OFFSITE NOTIFICATION DUE TO SEWAGE SPILL "An approximate 14,000 gallon sewage spill was identified outside the plant protected area [coming] from a sewage manhole. The spill was suspected to have begun on 12/6/10. Site personnel have responded and the upstream lift station has been secured which has stopped the spill. The manhole is presently being pumped down at this time. It appears at this time that the spill occurred from a severely corroded clean-out pipe cap. This sewage spill has no effect on safe operation of McGuire Units 1 and 2." The licensee will notify the NRC Resident Inspector and the North Carolina Department of Environment and Natural Resources in Mooresville, NC. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-07
46462 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-12-07 13:30 | 2010-12-07 15:01 | 2010-12-24 | AGREEMENT STATE REPORT - LEAKING ECKERT & ZIEGLER MODEL NER-004 NI-63 SOURCE "Excellims Corporation in Acton, MA, (license # 55-0588) telephoned to inform the Agency [Commonwealth of Massachusetts, Radiation Control Program] that a 6 month wipe test of a stored Ni-63 source foil yielded 0.0061 uCi. The Eckert & Ziegler model NER-004 source is stored in the container in which the manufacturer sent the source. The RSO stated that a previous wipe test of the same Ni-63 source yielded higher results and he concluded that he had wiped the 'hot' side. This wipe test (0.0061 uCi) was a wipe of the 'inactive' side, however, he thought that he may have spread contamination to the inactive side during the previous inadvertent wipe test of the 'hot' side. "ACTION REQUESTED: The RSO will send to the Agency an initial written notification of this wipe test result and the technical data sheet of the NER-004 source that he received from the manufacturer. He stated that he could complete this request in a few days. "ACTION TAKEN: Document this telephone notification; inform Agency supervision; submit a report to US NRC." The source has been secured in the original container and stored in a secure location. A Eckert & Ziegler model NER-004 is used in a Gas Chromatograph and has a Ni-63 source of less that 50 milliCuries. * * * UPDATE FROM JOHN SUMARES TO VINCE KLCO ON 12/24/10 AT 1004 EST * * * The following information was received by facsimile: "Analysis results of a Ni-63 source foil wipe test indicated 0.0061 uCi, which is above 0.005 uCi limit. "The original wipe test sample registered a high reading because the swab test was accidentally performed incorrectly when the active side and inactive side were swabbed. The leak test procedure was reviewed and the test was repeated using the correct procedure. The repeat test indicated 0.0061 uCi and the licensee concluded that some of the Ni-63 from the active side had been transferred to the inactive side during the initial wipe test. The licensee reported this wipe test result to the Agency. The source foil was kept in storage. To address the issue, the leak test procedures for the Ni-63 foil provided by the manufacturer and testing facility was reviewed again, and the leak test instructions were incorporated into the licensee's radiation safety manual. The foil was decontaminated using appropriate safety and control measures and all decontamination materials were placed in waste storage. After decontamination of the inactive side of the foil, the wipe test was repeated using the correct procedure, and the results were <0.00005 uCi. The Ni-63 source was considered ready for use. "The Agency was provided written notification of this event, initial wipe test results, the technical data sheet for the source involved, and the final wipe test results after foil decontamination. "The Agency considers this event to be closed." Notified R1DO (Perry) and FSME (Lewis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-12-10
46461 | 0 | ULTRA ELECTRONICS |  |  |  |  | 2010-12-06 | 2010-12-07 09:58 | 2010-12-07 | FAIL SAFE FUNCTION OF THE N7000 SERIES TEMPERATURE TRANSMITTER DOES NOT OPERATE CORRECTLY UNDER CERTAIN CONDITIONS "The functional issue is limited to N7000 transmitters where the field selectable jumper is set for downscale indication upon loss of input (open circuit, over range RTD, or short circuit). The transmitter may indicate a mid-range output upon open circuit or over range RTD input instead of going downscale (4 mA) as intended. Short circuit detection operates correctly in all cases. "This issue does not affect temperature transmitters during normal operating conditions, only the downscale input sensor failure indication function. N7000 transmitters that have been set for upscale sensor failure indication are not affected; however, this notification is applicable to all N7000 customers because the sensor failure indication is field selectable." The following sites are affected: Oconee, Calvert Cliffs, Perry, North Anna, Surry, Framatome ANP, Kewaunee, Diablo Canyon, and Hope Creek. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2010-12-07
46460 | 0 | OAKWOOD ANNAPOLIS HOSPITAL |  |  |  |  | 2010-12-04 10:30 | 2010-12-06 14:49 | 2010-12-06 | DELIVERED DOSE GREATER THAN PRESCRIBED DOSE "A patient was scheduled for a Tc-99m Myoview diagnostic cardiac resting perfusion study on 12/04/2010. Prescribed dosage was 10 mCi as noted on the departmental Prescribed Dosage List. These dosages are delivered as unit dose quantities along with Tc-99m in bulk quantity. "Technetium-99m was delivered in bulk quantity in a syringe at approximately 0600 [EST] as 150 mCi calibrated for 1200 [EST]. At approximately 0900 [EST] a MAA kit was made by withdrawing 64 mCi from the bulk allotment. "The nuclear medicine technologist inadvertently picked up the syringe at approximately 1030 [EST] containing Tc-99m as pertechnetate in bulk quantity (124.5 mCi) and without confirmatory assay in the dose calibrator injected the patient. "As per 10 CFR 35.3045 (a)(1), the dose delivered differs from the prescribed dose by greater than 5 rem effective dose equivalent (EDE). However the upper large intestine (ULI) dose does not differ by more than 50 rads from the dose to be delivered from the prescribed dosage as follows: Prescribed Dosage (10 mCi) EDE: 0.481 rem Administered Dosage (31.4 mCi) EDE: 5.988 rem (Difference = 5.507 rem) ULI Dose from Prescribed Dosage (10 mCi) 2.109 rads ULI Dose From Administered Dosage (124.5 mCi) 26.257 rads (Difference = 24.148 rads) "As per 10 CFR 35.3045 (a)(1)(ii), the administered dosage (124.5 mCi) differs from the prescribed dosage (10 mCi) by greater than the limit of 20%." The physician determined there was no adverse impact on the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-12-12
46459 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-12-06 | 2010-12-06 14:03 | 2010-12-06 | AGREEMENT STATE INVOLVING A LOST TRITIUM EXIT SIGN The following information was received from the State of North Carolina via fax: "Brief Description of Incident: General License: 011-2650-0G, was issued on August 2, 2010 to HB Haynes for one Exit Light, Serial Number: 421564, from Safety Light. "Model Number: SLX-60 for 7.5 Curies of H-3 (Tritium), Date Shipped; 7-20-2007. In August 2007, Haynes Electric installed the sign at Memorial Mission Hospital in Asheville, NC in the Stairwell at the new Dogwood Building and completed [work at] the temporary site in the fall at 2009. "The General License was issued on August 2, 2010 and [the President of Haynes Electric] called to confirm that they had gone back to the site and could not locate the sign. [The] RSO for Mission Memorial Hospital was contacted and confirmed the sign was lost and that they did not possess any radioactive material with exit signs. Also, on December 6, 2010 [the representative] with Safety Light also listed as Isolite confirmed that they had not received the light. The light was considered lost on December 6, 2010 and the NRC was notified." NC Incident No.: 10-51 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-12-09
46458 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-11-29 | 2010-12-06 10:56 | 2010-12-06 | AGREEMENT STATE REPORT - LEAKING SOURCE IN A STATIC ELIMINATOR The following report was received via e-mail: "The following report was received by the Iowa Department of Public Health (IDPH) on December 3, 2010. On November 29, 2010, the University of Iowa Environmental Health and Safety (EHS) staff discovered evidence that a Nickel-63 foil in a custom made static eliminator had lost its seal integrity. The source in question consists of two 10 mCi Ni-63 foils that are housed in a custom built static eliminator (2 inch diameter steel pipe with the foils glued to the walls of the pipe). The static eliminator is attached to a chamber apparatus located in a fume hood within a principal investigator's lab. The results of the leak test indicated approximately 11,500 dpm (0.0052 microCuries) of activity on a wipe taken of several areas in the apparatus housing the Ni-63 foils. EHS personnel bagged the static eliminator and returned it to EHS for disposal." Iowa Report Number: IA100008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-12-09
46457 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-12-06 04:18 | 2010-12-06 05:42 | 2010-12-06 | TECH SPEC REQUIRED SHUTDOWN DUE TO EXCEEDING ALLOWED OUTAGE TIME ON THE 'A' EMERGENCY DIESEL GENERATOR "(KKJ01A) 'A' Emergency Diesel Generator (EDG) was removed from service and declared inoperable [on] 11/29/2010 at 0500 (CST) for a scheduled 7 day Technical Specification equipment outage to perform various scheduled maintenance items. Technical Specification 3.8.1 Condition B was entered for one Diesel Generator inoperable, utilizing Action B.4.2.2, 'Restore the Diesel Generator to OPERABLE within 7 days AND 10 days from discovery of failure to meet LCO'. "On 12/06/2010, it was discovered during the Operability Run Surveillance, STS KJ-015A, utilized to restore the EDG to service, the Engine Analyzer Data Acquisition [software] indicated the No. 12 cylinder is 'out of balance' and will require a clearance order and maintenance repair. On 12/06/2010 [at] 0350 hrs., it was determined that the work required to restore the EDG to service would cause the Tech Spec 3.8.1 Action B.4.2.2 Completion Time requirement of 7 days to be exceeded, requiring a Plant Shutdown per TS 3.8.1 Condition H, with Action H.1, 'Be in Mode 3 within 6 hours', and Action H.2, 'Be in Mode 5 within 36 hours'. "Plant Shutdown to Mode 3 was commenced [on] 12/06/2010 at 0418 (CST). "The [NRC] Resident Inspector has been contacted." The licensee indicated that required repairs should be completed within 8 hours and expects restart to occur on 12/06/2010. | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2010-12-06
46456 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2010-12-04 11:42 | 2010-12-04 14:37 | 2010-12-04 | TONE ALERT EMERGENCY NOTIFICATION SYSTEM INOPERABLE "On Saturday, December 04, 2010 at 1142 [EST], the NYS Warning Point informed NMP [Nine Mile Point] via the RECS [Radiological Emergency Communications System] line that the EAS/Tone system was out of service for greater than one hour as of 1128 [EST]. "10CFR 50.72(b)(3)(xiii) requires reporting within 8 hours when a significant portion of the emergency communications system has been lost. Site Emergency Procedures define a loss of EAS/Tone for greater than 1 hour as a significant loss of emergency communications. "The EAS/Tone Alert system was returned to service on December 4, 2010 at 1255 [EST]. "The event has been entered into the corrective action program," The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-04
46455 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-12-04 11:28 | 2010-12-04 14:13 | 2010-12-04 | TONE ALERT EMERGENCY NOTIFICATION SYSTEM INOPERABLE "At 1142 (EST) on December 4, 2010, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 1028 (EST). "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The County Alert Sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement Personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the resident inspector has been briefed . "At 1258 (EST) on December 4, 2010, Oswego County Emergency Management notified JAF that the Tone Alert Radio System has been restored effective at 1255 (EST) ." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-12-04
46454 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-10-14 | 2010-12-03 19:20 | 2010-12-03 | AGREEMENT STATE REPORT - TROXER DENSITY GAUGE LOST AND THEN RECOVERED The following information was received by e-mail: "On 10/14/10, a soil density gauge possessed by Cal Trans District 6 (Troxler Model 3440, S/N 30696, containing 8 mCi of Cs-137 and 40 mCi of Am-241), fell from the tail gate of a pick-up truck in which it was being transported from the job site on State Highway 198 near Visalia, CA. The soil gauge was subsequently recovered by the operator and his ARSO [Assistant Radiation Safety Officer]. The soil gauge was damaged. The damaged gauge was returned to its permanent storage area in Visalia, CA. The RSO was notified, investigated the incident and reported the incident to RHB [California Radiation Health Branch] on the date it occurred. The gauge was surveyed by the RSO using a Radiation Alert Inspector PGM survey meter at the Visalia Field Site on the date of the incident. The maximum radiation level identified was 0.3 mR/hr at 1 meter from the gauge. The gauge was leak tested by the RSO with negative [satisfactory] results. The dosimeters for the gauge operator and ARSO were processed, and no radiation exposures were recorded. The Cal Trans District 6 facility in Fresno was visited by RHB on 10/28/10, and three items of noncompliance were identified. "Until December 2, 2010, RHB was working under the assumption that the gauge was not lost, but was only damaged when it fell from the back of the truck and was never out of sight of the operator and/or ARSO. On December 2, 2010, RHB determined that the gauge was lost for a period of time between it falling from the truck and being recovered. Therefore, RHB now consider it as having been lost and are reporting it as such." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-12-08
46453 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-12-02 16:00 | 2010-12-03 15:39 | 2010-12-03 | AGREEMENT STATE REPORT - DELIVERED DOSE GREATER THAN PRESCRIBED DOSE The following information was received via email from the State of Colorado: "At approximately 1600 MST, 12/2/10, the Colorado Department of Public Health and Environment received a report of a possible misadministration at the Prostate Seed Center, a Colorado radioactive materials licensee. "Additional information was received on 12/3/10 that there was indeed a misadministration of I-125 in seed form. An excess dose of 27 to 32% was administered above the prescribed dose. "There was an apparent miscommunication between the supplier and the Prostate Seed Center about the units of dose the seeds were to contain. Apparently, Air Kerma units were ordered and milliCuries were delivered. "An investigation as to the cause of the misadministration is being performed. A written report on the incident is required by the Department within 30 days." The excess dose was delivered to the patient's prostate. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-12-09
46452 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-12-02 12:30 | 2010-12-03 11:18 | 2011-09-06 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The following was received via email from the State of Arkansas: "The Arkansas Department of Health, Radioactive Materials Program, was notified at 1315 CST on December 2, 2010 by licensee Grubbs, Hoskyn, Barton, and Wyatt, Inc. (ARK-0456-03121) of a missing Troxler moisture/density gauge. The gauge was being transported between their office in Little Rock, Arkansas and a job-site in Bryant, Arkansas. The authorized user observed the gauge was missing at approximately 1230 CST. The gauge had apparently fallen from the transport vehicle. "The Troxler gauge is a Model 3430 (SN 63492) containing 40 mCi Am-241:Be and 8 mCi Cs-137. "It appears that the gauge was not properly secured in the vehicle. The Arkansas Department of Health is investigating the circumstances surrounding this event. "The Arkansas Department of Health prepared a press release concerning this event. Arkansas Department of Health also notified the Police Departments of Little Rock and Bryant, the Sheriff's Offices of Saline and Pulaski Counties, the Arkansas State Police, and the Arkansas Department of Emergency Management. "Arkansas has assigned event report ID number AR-12-10-02." * * * UPDATE AT 1147 EDT ON 9/6/11 FROM PEMBERTON TO HUFFMAN VIA E-MAIL * * * "On August 30, 2011, the Arkansas Department of Health, Radioactive Material Division was informed by [the] Radiation Safety Officer for Grubbs, Hoskyn, Barton and Wyatt, that the Troxler 3430 Moisture/Density Gauge, SN#63492, lost on December 2, 2010, had been recovered. "A Departmental investigation confirmed that the gauge recovered on August 30, 2011, was in fact the device lost on December 2, 2010. The Department considers this incident to be closed." The State Department of Health Representative indicated that the gauge was returned to the licensee by a private citizen who wished to remain anonymous. R4DO (Drake) and FSME (McIntosh) notified. ILTAB notified via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2010-12-08
46451 | -1 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-12-02 03:20 | 2010-12-02 20:45 | 2010-12-03 | AGREEMENT STATE REPORT - EMPLOYEE CONTAMINATIONS DURING CYCLOTRON OPERATION The following information was received by e-mail: The state reported that three employees of Cardinal Health were contaminated by Fluorine 18 (F-18) from operation of a cyclotron. Initial contamination of the employees was 1600 cpm. Soap and water was used to decontaminate the personnel and at 1130 PST the contamination was reported to be 1300 dpm. The licensee believes the cause of the contamination to be faulty delivery lines. The cyclotron device is a General Electric Accelerator PETrace. Nevada Incident Number: NV100022 * * * RETRACTION FROM SNEHA RAVIKUMAR TO ERIC SIMPSON AT 1507 EST ON 12/3/10 * * * The following information was received by email from the State of Nevada: The State of Nevada is retracting the Event Report sent on December 2, 2010, regarding Cardinal Health. This event does not need to be reported based on the fact that a contamination events must restrict access to the area for more than 24 hours or cause doses to workers that exceed regulatory limits in order to be reportable. Due to the short half life of the material involved and the fact that it was limited to the transfer tube, it is unlikely that anyone received a dose >1 ALI (24 hr notification) or >5 ALI (immediate notification). Notified R4DO (Powers) and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-12-07
46450 | 0 | ACUREN |  |  |  |  | 2010-12-02 10:00 | 2010-12-02 20:19 | 2010-12-02 | SOURCE FAILED TO RETRACT DUE TO ICE BUILD-UP A radiography crew working on the Prudhoe Bay North Slope experienced a malfunction of the source retraction portion of their Sentinel Delta 880 radiography device due to ice intrusion. The device source is Ir-192 with a 99 Curie activity. The radiography crew was able to retract the source into the shielded position using the device crank. Based on pocket dosimetry readings, there were no personnel over-exposures during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-12-02
46449 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2010-11-22 | 2010-12-02 20:15 | 2010-12-02 | ANOLMALY DISCOVERED ON ROSEMOUNT MODEL 1152 DIFFERENTIAL PRESSURE TRANSMITTERS WITH OUTPUT CODE "L" 10-50 mA ELECTRONICS The following was received via fax: Rosemount Nuclear discovered an anomaly in Model 1152 differential pressure transmitters while troubleshooting a separate, unrelated issue. The anomaly is related to the pressure transmitters response during a overpressure condition. Normally, under a low side overpressure condition, the output will go off-scale and remain off scale for conditions less than 10 mA. Rosemount has discovered that some detectors may go off-scale and then return to on-scale between 10mA and 50 mA, rather than remain off scale under 10mA. This is caused by a change made to operational amplifier components in March 2001. Rosemount recommends all customers evaluate the safety impact of this anomaly on their plants. No field failures have been reported to date. The following sites are affected: Browns Ferry, Brunswick, Cook, Dresden, Duane Arnold, Fermi, Fort Calhoun, Ginna, Hatch, Indian Point, Kewaunee, Millstone, Nine Mile Point, Oyster Creek, Palisades, Pilgrim, Quad Cities, Sequoyah, Vermont Yankee, and Watts Bar. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2010-12-02
46448 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-12-02 16:10 | 2010-12-02 18:32 | 2010-12-02 | OFFSITE NOTIFICATION DUE TO AN INDIVIDUAL CONTAMINATION "TVA notified TN Dept of Environment and Conservation [TDEC] of an incident at Watts Bar as follows: "On December 2, 2010, a contractor employee of PAR-Westinghouse was processing in through Watts Bar Nuclear Plant Radiological Protection Program for his first day of work. He was discovered to have been previously contaminated with radioactive material from another worksite. It is clear that the radioactive contamination did not come from any TVA source and was found before he entered the rad control area. "The contamination was discovered during required in-processing activities for workers by TVA's radiation monitoring and detection equipment. The contamination was found to be a particle on the individual's shoe. "The individual's clothing was also found to contain measurable contamination and was confiscated. The radioactive contamination found on the individual has been safely contained. "TDEC Division of Radiological Health was notified of this event as of 1610 Eastern Time and this notification under 10 CFR 50.72(b)(2)(xi) is for that Government Agency notification. TVA has notified the NRC Resident Inspector and Regional Administrator of this incident." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-02
46447 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2010-12-02 07:15 | 2010-12-02 17:39 | 2010-12-02 | URANIUM CONCENTRATION GREATER THAN EXPECTED IN GAS STRIPPER SYSTEM FOLLOWING AN ACID WASH "Background: The purpose of the Ammonia Recovery Facility (ARF) facility is to recover ammonia from the ammonium diuranante (ADU) process effluent by use of a stripper column. The feed of effluent to ARF has a uranium concentration is typically less than 1 ppm. Two uranium analyzers provide assurance that the effluent uranium concentration is less than 100 ppm prior to discharge to the Ammonia Recovery process feed tank V-621. "The ISA Summary for this process states that only minute quantities of radioactive material are present in the feed to the ARF and that there are no credible accident sequences that result in intermediate or high consequences. "Event Description: On 12/02/2010 at 0715, a Process Engineer informed Nuclear Criticality Safety (NCS) that he had confirmed that an acid wash of ARF stripper column had recovered 8 kg of Uranium (U). The acid wash is expected to have removed all significant amounts of Uranium from the system. This resulted in a review of the adequacy of the ISA treatment for the ARF stripper column. "Safety Significance of Event: The safety significance is low. The amount of Uranium recovered, approximately 8 kg, is less than 25% of a minimum critical mass in spherical geometry. The concentration of the liquid is about 1 g U/liter. The 8 kg constitutes an approximate ten year accumulation since the last column acid wash in 2001. Based on the accumulation rate over the past 10-years, another 40 years of accumulation would be required without any removal during maintenance before achieving a critical mass. "The system was down for maintenance at the time of discovery. Maintenance activities were suspended and will remain suspended until an appropriate processing path is identified to process this material and appropriate controls are established. The system will not be restarted until the system has been reanalyzed and appropriate controls are verified to be in place to meet 10CFR70.62 performance criteria. "Potential Criticality Pathways Involved (Brief Scenarios of how criticality could occur): Criticality is possible if material in the ARF equipment exceeds a minimum critical concentration and a minimum critical mass for a given geometry. "Controlled Parameters: The controlled parameters are upstream of the ARF process and are based on concentration of the feed material. The uranium concentration in ARF feed is typically less than 1 ppm. Two uranium analyzers provide assurance that the ADU effluent uranium concentration is less than 100 ppm prior to discharge to the Ammonia Recovery process. "Estimated Amount, Enrichment, Form of Licensed Material and % of worst case Critical Mass: The facility is only licensed to 5 wt.% U-235. The material present in the stripper column prior to being dissolved was likely ammonium diuranate. Once dissolved, the material is uranyl nitrate. The mass in the system is expected to have been less than 25% of a minimum critical mass in spherical geometry. "When equipment geometry is taken into account, much higher masses are required to obtain a critical condition. For example, the ARF feed tank with a uniform slab of U02-H20 would require an areal density exceeding 10 kg U/ft2 (more than 500 kg U). "Nuclear Criticality Controls) or Control System(s)) and Description of the Failure Deficiencies: The upstream controls on concentration performed as required. The material plate-out within the stripper column was greater than anticipated. "Corrective Actions to Restore Safety Systems and When Each Was Implemented: The system was down for maintenance at the time of discovery. Maintenance activities were suspended and will remain suspended until an appropriate processing path is identified to process this material and appropriate controls are established. The system will not be restarted until the system has been reanalyzed and appropriate controls are verified to be in place." The licensee initiated the acid wash of the gas stripper as a result of concerns over the differences in the inlet and outlet pressures of the system, which indicated that the system was becoming less efficient. The licensee briefed Region 2 management and Region 2 fuel cycle facility inspectors about this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2010-12-02
46446 | 0 | GEOCONCEPTS ENGINEERING, INC |  |  |  |  | 2010-12-02 14:00 | 2010-12-02 16:25 | 2010-12-14 | THEFT OF TROXLER MOISTURE DENSITY GAUGE A Troxler moisture density gauge being used at Fort Meade (Maryland) was found to be stolen along with other industrial equipment at 1400 on 12/2/10. The Troxler gauge was last seen on Monday afternoon, 11/29/10, when it was secured in a temporary storage location inside a lock-box and chained to a sea container. Other items stolen included crane mats, a generator and miscellaneous tools. The nuclear gauge is a Troxler Model 3430, S/N 37672, which contains two radioactive sources. One source is 44 mCi of Am-241/Be (S/N 78-2430). The other source is 9 mCi of Cs-137 (S/N 77-4907). The licensee will notify base police to begin an investigation into the theft. The licensee has notified the State of Maryland of the theft. * * * UPDATE FROM DREW THOMAS TO JOE O'HARA AT 0948 ON 12/14/10 * * * On 12/10/10, FT. Meade U.S. Army base police officers informed the licensee that the stolen container had been "dumped" back onto the jobsite. The licensee responded to the site and discovered the missing gauge inside the container. The source was in the locked and shielded position inside the gauge and the gauge doesn't appear to have been damaged. The gauge has been recovered and is now in the custody of the licensee. A leak test of the gauge is scheduled to be performed. Notified R1DO(Holody), FSME(Reis) and ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-12-02
46445 | -1 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-12-01 13:59 | 2010-12-01 17:40 | 2010-12-02 | OFFSITE NOTIFICATION OF PETROLEUM SPILL INTO THE SUSQUEHANA RIVER "On 12/01/10, at 1359 EST, Peach Bottom Atomic Power Station reported a petroleum product spill in the discharge canal. Total quantity of substance is less than 1 quart. Lewis Environmental agency has been contacted to aid in containment and cleanup of the spill. "This report is being submitted pursuant to 10 CFR 50.72(b)(2)(xi) and 10 CFR 72.75(b)(2)." The spill did not reach Comprehensive Environmental Response Compensation and Liability Act (CERCLA) reportable quantities. The licensee notified the Pennsylvania Department of Environmental Protection, United States Coast Guard, and EPA Region 3. The NRC Resident Inspector has been notified. * * * RETRACTION FROM E. WRIGHT TO V. KLCO ON 12/2/10 AT 1354 EST * * * The licensee is retracting the event due to the quantity of substance released to the environment is less than the reportable quantity. The licensee will notify the NRC Resident Inspector. Notified R1DO (Schmidt). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-12-01
46444 | -1 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2010-11-30 05:00 | 2010-12-01 15:20 | 2010-12-20 | LOSS OF POWER TO INSTRUMENTATION IN THE OPERATING UNITS OF THE FEED MATERIALS BUILDING "Description of the Event: This report is performed pursuant to 10 CFR 40.60(b)(2) reporting requirements. "On Tuesday, November 30, 2010, at approximately 0500, the failure of F-Substation caused a loss of instrumentation in operating units in the Feed Materials Building. At 0505, various weight, temperature and pressure indications were not available. "Due to the loss of power to a load cell component, the UF6 Vaporizer weight exceeded the administrative limit. During the power loss the vessel's weight measurement was not available to the operator. "At 0538, power was restored and instrumentation readings returned to normal. The loss of the Vaporizer weight control did not have any safety consequences. "Isotope, Quantities and Chemical Form: No material release. "Personnel Radiation Exposure Date (if applicable): No additional exposure to radiation or radioactive materials." The licensee will inform the NRC Region II Office. * * * RETRACTION FROM MICHAEL GREENO TO JOE O'HARA AT 1659 ON 12/20/10 * * * "On December 1, 2010, Honeywell Metropolis Works made notification of Event #46444 to the NRC Operations Center. This November 30, 2010 incident occurred due to the loss of power to a load cell component. During the power loss the weight measurement was not available to the operator, and the UF6 Vaporizer weight exceeded the administrative limit. "This twenty-four hour report was made following 10 CFR 40.60(b)(2) reporting requirements: "Each licensee shall notify the NRC within 24 hours after the discovery of any of the following events involving licensed material: ... "(2) An event in which equipment is disabled or fails to function as designed when: (i) The equipment is required by regulation or license condition to prevent releases exceeding regulatory limits, to prevent exposures to radiation and radioactive materials exceeding regulatory limits, or to mitigate the consequences of an accident; (ii) The equipment is required to be available and operable when it is disabled or fails to function; and (iii) No redundant equipment is available and operable to perform the required safety function. "As determined by Honeywell's safety analysis, potential UF6 release may occur due to failure to control process resulting in process vessel failure. UF6 Vaporizer load cells, which are identified in the safety analysis as a safety feature to control the total weight in this vessel, were not operable during the incident. However, load cells are not the only component designed to perform the equivalent safety function - to prevent UF6 Vaporizer failure. Thus, UF6 Vaporizer failure due to over-pressurization is prevented by the existing relief system which is designed to relieve at a pressure below the maximum allowable working pressure. This Vaporizer relief system was available and operable during the event. "As a result of these additional considerations, Honeywell determined that the redundant equipment (Vaporizer relief system) was available and operable to perform the required safety function (Vaporizer failure prevention), and therefore the initially reported incident (# 46444) does not meet the reporting requirement (iii). Since this incident does not constitute a reportable event, Honeywell requests to withdraw its event notification #46444." Notified R2DO(Henson) and NMSS EO(Davis) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2010-12-01
46443 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2010-12-01 14:55 | 2010-12-01 15:14 | 2010-12-01 | UNUSUAL EVENT DECLARED DUE TO EXCESSIVE RCS LEAKAGE FROM "B" RECIRC PUMP SEAL "Oyster Creek has declared an Unusual Event (MU7) due to Reactor Coolant System leakage greater than 10 gpm. Leakage has been determined to be from the 'B' reactor recirculation pump seals. The 'B' Reactor Recirculation Loop was isolated and leakage stopped." The plant remained in the normal electrical lineup and no safety systems actuated during this evolution. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ERIC SWAIN TO ERIC SIMPSON AT 1548 ON 12/1/10 * * * At 1537 EST, "Oyster Creek has terminated from an Unusual Event. Event terminated due to isolating leakage from the 'B' Reactor Coolant Loop." The licensee notified the NRC Resident Inspector. Notified R1DO (Schmidt), IRD (Gott), NRR EO (Nelson), DHS and FEMA. | 25 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2010-12-01
46442 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-29 16:12 | 2010-11-29 19:20 | 2010-11-29 | PLANT COMPUTER MAINTENANCE OUTAGE "At 1612 today, November 29, 2010 Unit 2 Integrated Plant Computer (IPC) was shutdown for upgrade work. This includes the SPDS [Safety Parameter Display] system which is a function of the IPC. The IPC will be returned to service in approximately two weeks and SPDS function will be restored at that time. In addition, the ERDS [Emergency Response Data System] is out of service and will be restored in the same time frame. "Per the 50.54.Q that was prepared by our Emergency Preparedness group, notification has been made to the NRC ERDS group (Roger Chow) of the unavailability of the ERDS. While the IPC is out of service, control board indications are being utilized by the control room crew. In addition, the safety-related Plant Safety Monitoring System (PSMS) is operable. Restoration of SPDS and ERDS functions have been given the highest priority during restoration of the system. Both the NRC Ops Center and the NRC ERDS group will be notified when SPDS and ERDS capability have been restored." The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-11-29
46441 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2010-11-28 15:15 | 2010-11-28 17:27 | 2010-11-28 | AUTOMATIC REACTOR TRIP AFTER TURBINE TRIP DUE TO LOSS OF CONDENSER VACUUM "Loss of two circulating water pumps in one condenser caused a high main condenser backpressure. The high main condenser back pressure caused an automatic main turbine and reactor trip while critical >15%. "Low steam generator water level following the trip caused an automatic Auxiliary Feedwater actuation. The low water level condition has cleared. Normal post-trip response has been verified and the plant is stable." The licensee removed one circulating water pump from service in preparation of performing scheduled maintenance when the other circulator unexpectedly tripped. The cause of the pump trip is under investigation. During the trip, all rods inserted into the core. There were no primary safety valves that lifted during the transient but main steam safeties "chattered" during the transient and have fully reseated. There is no known primary to secondary leakage. The electrical grid is stable and supplying plant loads in a normal shutdown electrical lineup. The reactor is stable at normal operating pressure and temperature with decay heat being removed via the steam dumps to condenser. The licensee has notified the State of Connecticut Department of Environmental Protection, the town of Waterford, CT, and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-11-28
46440 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-11-26 17:34 | 2010-11-26 23:36 | 2010-11-26 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE DUE TO A STEAM LEAK "While performing the High Pressure Coolant Injection (HPCI) high pressure run required by SR 3.5.1.6 following Unit 3 refueling outage D3R21, a steam leak developed from the HPCI turbine. The steam leak resulted in a HPCI room high temperature alarm and the HPCI turbine was manually tripped. The U3 HPCI system was declared inoperable and Tech Spec LCO 3.5.1 condition G.1 and G.2 were entered. "The condition is being reported in accordance with 10 CFR 50.72 (b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. "Maintenance activities are currently in progress to restore system to operable status." The failure resulted in the licensee entering a 14-day LCO action statement for restoration. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-11-26
46439 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-11-26 | 2010-11-26 12:33 | 2010-12-01 | AGREEMENT STATE REPORT - VEHICLE TRANSPORTING WELL LOGGING SOURCES INVOLVED IN ACCIDENT WITH FATALITY The Texas Department of Health, Radiation Branch, received notification from the licensee that their truck, transporting well logging sources, was involved in a rollover accident in which the driver was killed. During the accident, the overpack carrying the sources was torn loose from the vehicle but remained intact. The overpack did sustain some damage but the source boxes appear to be intact and accounted for. A U.S. Border Patrol officer was on scene and performed surveys of the overpack and surrounding area and did not detect any abnormal background readings. The sources are currently under the control of the Texas Department of Public Safety officers (Texas State Troopers) at the scene awaiting recovery and transport by the licensee. Due to the nature of the accident, all paperwork pertaining to the sources is scattered around the accident scene. Paperwork recovered at the scene indicate that the truck was carrying Iridium-192, Scandium-46 and Antimony-124 with total activity of all packages at approximately 726 mCi. The accident occurred 4 miles outside of Encinal, TX on State Highway 44. * * * UPDATE AT 1708 EST ON 11/26/10 FROM KAREN BLANCHARD TO S. SANDIN * * * The licensee has arrived on-scene, confirmed that there was no release of radioactive material and taken possession of the following packages containing 240 mCi Iridium-192, 160 mCi Scandium-46 and 320 mCi Antimony-124 for return to their Alice, TX office. Notified R4DO (Andrews) and FSME (Piccone). * * * RETRACTION AT 1722 EST ON 12/1/10 FROM KAREN BLANCHARD TO P. SNYDER * * * The State of Texas provided the following information via e-mail: "It was determined after all information was collected that the incident does not meet any reporting requirement. "The Agency [Texas Department of Health] is requesting that this event be retracted." Notified R4DO (Powers) and FSME (Danna). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-12-01
46438 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-11-25 03:57 | 2010-11-25 09:01 | 2010-11-25 | INJURED PERSONNEL WITH SEVERED CONTAMINATED FINGERS TRANSPORTED OFFSITE "No reactor systems were impacted, no initiations of any safety systems or any plant events occurred. Report is for transportation of contaminated fingers with an injured non-contaminated person to a hospital for potential reattachment. "Fermi 2 is currently in a refueling outage. At 0300, the control room was informed that an individual, who was assisting in rigging of a Reactor Shield Block ([approximately] 100 tons), received an injury when his fingers were pinched between the Reactor Cavity wall and the Reactor Shield Block severing portions of two fingers. "The portions of the fingers remained in PC Clothing (gloves) and decontamination was unsuccessful. The fingers were treated as contaminated material and transported to the hospital by radiation protection personnel. This material [contaminated fingers] was deemed unusable and at 0540 all bio-hazard/contaminated material was returned to the Fermi site." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2010-11-25
46437 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2010-11-24 15:50 | 2010-11-24 17:43 | 2010-11-24 | OFFSITE NOTIFICATION DUE TO RELEASE OF AN OILY MIXTURE TO DISCHARGE CANAL "During maintenance activities at Crystal River Unit 3, approximately 25 to 30 gallons of an oily water mixture was pumped from a manway/vault. A small amount of this mixture was inadvertently discharged to a storm drain that leads to the Crystal River Unit 3 outfall (discharge canal). There was a slight sheen observed at the outfall as approximately 1/2 cup of the mixture entered the outfall area. This is reportable under 40CFR110 due to a light sheen observed on the site discharge canal. Crystal River Environmental Specialists responded to the spill with a combination of sand bags, floating sorbent boom, as well as sorbent pads. After deployment of the sand bags, floating sorbent booms, and securing the pumping activities, the spill status was confirmed as ceased and contained. Notifications will be made to the Florida Department of Environmental Protection State Warning Point and the National Response Center. This is 4-hour reportable per 10 CFR 50.72(b)(2)(xi) as a situation related to protection of environment, for which government agencies will be notified." The substance discharged appears to be some sort of motor oil. Prior to pumping, a sample of the liquid was analyzed and did not contain any radioactive nuclides. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-24
46436 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-11-24 15:15 | 2010-11-24 16:00 | 2010-11-26 | SAFETY PARAMETER DISPLAY SYSTEM AND EMERGENCY RESPONSE DATA SYSTEM OUT OF SERVICE FOR PLANNED MAINTENANCE "On 11/24/10 at 1515 EST, the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 48 hours. During this time, the majority of the Control Room indications remain available to the plant staff, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems, if needed. The plant is currently in Mode 4, and will remain in Mode 4, for the duration of the SPDS and ERDS unavailability. Since the unavailability will last greater than 8 hours, this is considered a Loss of Emergency Assessment Capability, and reportable under 10CFR50.72(b)(3)(xiii). "Followup notification will be made when SPDS and ERDS have been restored." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1850 EST ON 11/26/10 FROM JIM KONRAD TO S. SANDIN * * * "Update to Event #46436: On 11/26/10 at 1733 EST, regarding Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) systems removed from service to support planned maintenance on the UPS vital bus power supply. "Planned work which resulted in the loss of SPDS and ERDS is complete. All Emergency Assessment Capabilities have been restored." The licensee informed the NRC Resident Inspector. Notified R3DO (Dickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-11-24
46435 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2010-11-10 00:24 | 2010-11-23 15:35 | 2010-11-23 | TELEPHONE NOTIFICATION IN LIEU OF WRITTEN LER - INVALID ACTUATION OF MOTOR DRIVEN AUXILIARY FEEDWATER PUMP "Event: Invalid actuation of the 'B' Motor Driven Auxiliary Feedwater (MDAFW) pump. "Report Type: This 60-day telephone notification is being made under 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1). "Description: On November 10, 2010, the 'A' Main Feedwater Pump (MFP) was started per plant operating procedures. When the 'A' MFP was started, there was a partial activation of the Auxiliary Feedwater System with the start of the 'B' MDAFW. "The plant was in Mode 3 after completing refueling outage 16 during this event. Actual plant conditions and parameters did not exist that required an automatic start of the 'B' MDAFW pump. Therefore, this actuation is classified as invalid. The system started and functioned successfully. "This invalid actuation was entered into the corrective action program as NCR-432566." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-11-23
46434 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-10-26 23:56 | 2010-11-23 15:31 | 2010-11-23 | INVALID ACTUATION OF HIGH CONSEQUENCE LIMITING SAFEGUARDS AND SAFETY INJECTION SYSTEMS "This telephone notification is being made for an invalid actuation under 10 CFR 50.73(a)(2)(iv)(A) following the reporting guidance of 10 CFR 50.73(a)(1). "With Unit 1 at cold shutdown (about 105 degrees Fahrenheight and depressurized), an invalid actuation of the Unit 1 'A' train of the High Consequence Limiting Safeguards (HI CLS) system and Unit 1 'A' train of the Safety Injection (SI) system occurred at 23:56 during setup for 'H' Bus Logic Testing. Plant systems and components responding to the HI CLS and SI 'A' train signals started and functioned successfully as designed (with the exception of those systems and components procedurally rendered inoperable due to the RCS being below 350 degrees Fahrenheight and 450 psig). The HI CLS and SI 'A' trains were reset and the affected systems were restored to their pre-event configurations. "Specific trains and systems that actuated for the 'A' train of HI CLS and SI are described below: "- With the unit at cold shutdown, one high head pump was running (the two redundant pump controls were in the pull to lock position in compliance with Technical Specifications). The 'A' train High Head Safety Injection motor operated valves re-aligned such that the running high head pump provided flow to the RCS cold legs from the Refueling Water Storage Tank (RWST). During this time the pressurizer level increased from approximately 23 percent to about 42 percent. "- Auxiliary Feedwater (AFW) Pump motor operated valves opened but no flow was delivered to the steam generators since the AFW pumps were in pull to lock. "- The 'A' train containment isolation valves closed, isolating the 'A' Residual Heat Removal (RHR) heat exchanger. However, shutdown cooling was previously aligned to the 'B' train RHR and therefore shutdown cooling was uninterrupted. Containment isolation valves were later restored to a normal alignment. "- One train of Auxiliary Ventilation actuated and was restored to normal after the Safety Injection signal was reset. "- Emergency Diesel Generator (EDG) No. 1 started but did not load since its associated Emergency Bus remained energized by offsite power. The EDG was stopped and returned to automatic. "An apparent cause evaluation is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-11-23
46433 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-11-23 11:45 | 2010-11-23 14:53 | 2010-11-23 | OTHER GOVERNMENT AGENCY NOTIFICATION DUE TO SEWAGE LEAK "On 11/23/10 at 1145 EST, a verbal report to the Michigan Department of Natural Resources & Environment (MDNRE) was made relating to a sewage leak to the ground from the Training Building restrooms. The onsite Facilities Maintenance Journeyman discovered mud and stones while clearing a drain to relieve a blockage. An immediate repair of the broken drain is being implemented. The plant is currently in Mode 4, in Refueling Outage 14 (RF14). Since a verbal report was made to the MDNRE, this is considered a News Release / Notification of Other Government Agency, and is reportable under 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. The licensee also notified the Monroe County Health Department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-23
46432 | 0 | VA CARIBBEAN HEALTHCARE ADMIN. |  |  |  |  | 2010-10-31 | 2010-11-23 14:24 | 2010-11-23 | VA CARRABEAN HEALTH CARE SYSTEM IN SAN JUAN, PUERTO RICO - LOST TRITIUM EXIT SIGNS The Department of Veterans Affairs, Veterans Health Administration, National Health Physics Program reported the loss of generally licensed devices (self-illuminating tritium exit signs). "This report is required by 10 CFR 31.5(a)(10) and 10 CFR 20.2201(a)(1). Four (4) tritium exit signs are declared to be missing by the VA Caribbean Healthcare System, San Juan, Puerto Rico. The signs had been possessed under general licensing provisions of 10 CFR 31.5. "The signs were model number SLXTU1RB15 manufactured by Foreverlite, Inc., and contained about 9.5 curies of tritium each. The signs had been removed from use by the facility earlier this year [March 19, 2010] and placed into temporary storage at the facility pending transfer to an authorized recipient. There are no indications that the signs were damaged or that these circumstances have resulted in any radiation exposure to individuals. "A 30-day written report of the event will be provided to the NRC as required in 10 CFR 20.2201(a)(2)." It was not determined the signs were missing until October 2010. A thorough search was conducted but failed to locate the missing signs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2010-11-23
46431 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-11-22 17:47 | 2010-11-22 23:32 | 2010-11-22 | VALVES IDENTIFIED OPEN IN MODE 2 THAT SHOULD HAVE BEEN CLOSED "At 1547 CST, November 22, 2010, the reactor mode was changed from Mode 4 to Mode 2 with the main steam drain valves, which are primary containment isolation valves, tagged open with power removed from their respective breakers. The valves were tagged to comply with S/D [Shutdown] operating procedure requirements. The valves should have been restored prior to making the mode change. The main steam line drain isolation valves MO-2373 and MO-2374 were restored at 1747 CST and verified at 1755 CST. Startup was held for determination of further actions needed. Reactor startup recommenced at 2200 CST. Currently the reactor is not critical." The licensee notified the NRC Resident Inspector. The licensee notified the Minnesota State Duty Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-11-22
46430 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-11-21 12:00 | 2010-11-22 11:38 | 2010-11-22 | AGREEMENT STATE REPORT - SOURCE DISCONNECT AND RETRIEVAL The following information was provided by the State of Texas via email: "On November 22, 2010, the [Texas Department of Health Services] Agency received notification from the licensee that it had experienced a source disconnect yesterday, November 21, 2010 at approximately 1200 CST. The licensee stated that a two person radiography crew was working at a refinery near Alvin, Texas when they experienced a source disconnect. "The radiographers were using a QSA Global device (Model: 660-B) that housed a 67 curie, Selenium (Se) - 75 source. According to the licensee, the radiographers had made 24 exposures and on the 25th exposure, the source disconnected from the drive cable. The radiographers were able to crank the cable back into the camera, but the source remained out. The radiographers contacted their Site Radiation Safety Officer (SRSO). "The SRSO, who is authorized to retrieve sources, traveled to the site and returned the source to the camera at approximately 1700 CST. The radiographers at the site waited for the SRSO to arrive while verifying the 2 millirem per hour boundary, and keeping constant security on the radioactive material. According to the licensee, the highest exposure measured by the radiographers' pocket dosimeters was that of the SRSO, whose dose was measured to be 45 millirem for the event. "The licensee stated that they were unsure why the source disconnected from the drive cable. However, the licensee has contacted the manufacturer, and will send the entire set-up (camera, guide tube, drive cable, etc) to the manufacturer for inspection and repair." TX: I-8798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-11-25
46429 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2010-11-18 | 2010-11-19 08:33 | 2010-11-19 | POTENTIAL FOR REVERSE POLARITY ON HPCI TURBINE EG-R HYDRAULIC ACTUATORS "GE Hitachi Nuclear Energy (GEH) has completed an evaluation of the 'Reverse Polarity on HPCI EG-R Hydraulic Actuators,' and has concluded that this is a Reportable Condition in accordance with the requirements of 10 CFR 21.21 (d). "Discussion: "GEH provided a refurbished HPCI turbine EG-R Hydraulic Actuator, (GEH Part number DD213A8527P003), as a safety related component, to a domestic BWR/4. When the customer installed the EG-R Hydraulic Actuator at the plant, calibration and post maintenance testing found that the turbine governor valves went to the full open position when the proper response was a fully closed position. Troubleshooting of the newly installed component revealed that the polarity of the component was reversed. An improperly configured EG-R Hydraulic Actuator cannot be utilized in the system because the reversed polarity causes the turbine governor control valves to operate in a manner opposite to the expected response, and calibration of the component by plant personnel cannot be completed. "GEH contracted Engine Systems Incorporated (ESI) to perform the repair/refurbishment of this EG-R Hydraulic Actuator. This particular EG-R Hydraulic Actuator is identified as GEH part number DD213A8527P003. The specific EG-R Hydraulic Actuator that was identified with this defective condition was identified as serial number 2288717. "Conclusion: "This condition would change the operational characteristics of the HPCI system and would create a Substantial Safety Hazard or a violation of a Technical Specification Safety Limit. As such this condition has been determined to be a Reportable Condition within the context of 10 CFR Part 21.21 (d). "ABWR and ESBWR Design Certification Documentation Applicability: "The issues described above have been reviewed for applicability to documentation associated with 10CFR 52 and it has been determined that there is no affect on the technical information contained in either the ABWR certified design or the ESBWR design in certification. "Recommended Action: "GEH recommends that [the Hatch, Hope Creek and Peach Bottom] sites that have received EG-R Hydraulic Actuator(s) (GEH Part number DD213A8527P003), check warehouse inventory. If the EG-R Hydraulic Actuator remains 'in stock,' the potential exists that incorrect internal wiring could exist resulting in the EG-R Hydraulic Actuator not responding as expected. GEH recommends that if an EG-R Hydraulic Actuator (GEH Part number DD213A8527P003) is in warehouse stock, that the component be returned to GEH for verification of the internal wiring configuration." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-11-19
46428 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2010-11-18 16:26 | 2010-11-18 19:30 | 2010-11-18 | POTENTIAL POST FIRE SAFE SHUTDOWN UNANALYZED CONDITION "A Post Fire Safe Shutdown (PFSSD) circuit analysis identified that certain fuses installed within Train 'B' Exciter/Voltage Regulator cabinet NE106 are susceptible to failure in the event of postulated fire-induced hot shorts within the control room. Loss of power to this circuit will prevent operation of these functions. The emergency pre-positions and manual voltage adjustment circuits are not credited for PFSSD following a control room fire. However, field flashing is credited following a fire in the control room. Failure of field flashing after a postulated fire will prevent voltage generation on the 'B' diesel generator. This could result in the inability of the 'B' train EDG to supply its associated safety bus during the postulated fire. "Compensatory measures are established for early detection and extinguishment of a fire associated with this circuit in the Control Room. Additional compensatory measures are being developed." The licensee is not in any tech. spec LCO's as a result of this condition and has established fire watches as a compensatory measure. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-11-18
46427 | 0 | PORTSMOUTH LEAD CASCADE |  |  |  | URANIUM ENRICHMENT FACILITY | 2010-11-18 13:41 | 2010-11-18 16:40 | 2010-11-29 | OFFSITE NOTIFICATION TO OSHA DUE TO ONSITE FATALITY The American Centrifuge Plant reported an employee collapsed in the Centrifuge Test and Training Facility, was transported offsite to a medical facility, and subsequently died. Initial reports indicate that the employee died of natural causes. The licensee notified Region 2 (D. Hartland) of the event. * * * UPDATE FROM CRABTREE TO KLCO ON 11/19/2010 AT 1054 EST * * * On 11/18/2010, at 1551 EST, the licensee commenced notification of OSHA and completed notification at 1602 EST on the same day. Notified R2DO (Rich), NMSS-E(McCartin) and IRD (Grant). * * * UPDATE AT 1555 EST ON 11/29/10 FROM THOMAS MARTIN TO ERIC SIMPSON * * * The licensee called with administrative corrections (facility, docket and license numbers) to the original event notification. Notified R2DO (Schaffer), NMSS-E(Benner) and IRD (Grant). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2010-11-29
46426 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2010-11-18 03:00 | 2010-11-17 18:26 | 2010-11-18 | PLANNED TECHNICAL SUPPORT CENTER VENTILATION CORRECTIVE MAINTENANCE "This ENS is being issued in advance of a planned activity. "On November 18th 2010 at 0300, Limerick Generating Station [will apply] a clearance to perform corrective maintenance associated with MD-1 (Outside Air Damper). During the time that the block is applied, the TSC ventilation system will not be available to be restored in a time period required to staff and activate the TSC ERO [Emergency Response Organization]. "This work is expected to be complete on 11/18/10 at 1800. If an emergency is declared requiring TSC activation, the TSC will be staffed and activated using emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation becomes necessary the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10CFR50.72(b)(3) due to the loss of an emergency response facility (ERF) because of unavailability of the emergency ventilation system. "An update will be provided when the TSC ventilation has been restored to normal operation. The NRC resident has been notified." * * * UPDATE FROM PAUL MARVEL TO DONG PARK AT 1729 EST ON 11/18/10 * * * Planned work on the TSC ventilation system has been completed at 1700 on November 18, 2010. The TSC has been restored to normal status. The licensee will notify the NRC Resident Inspector. Notified R1DO (Gray). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-11-17
46425 | 0 | ABERDEEN TEST CENTER |  |  |  |  | 2010-11-16 11:00 | 2010-11-17 10:10 | 2010-11-17 | CONTAMINATION OUTSIDE BOUNDARY AREA DUE TO A PROJECTILE OFF FLIGHT PATH The licensee was conducting live fire exercises at the Ford Farms section of the Aberdeen Test Center when a depleted uranium (DU) projectile went off its flight path and struck metal causing the projectile to shatter and become friable. Ford Farms is an indoor hard target facility that is targeted from weapons outside of the facility. The projectile shattered outside of Ford Farms thus the contamination is outside the facility. Initial surveys indicate contamination levels as high as 400 cpm > background. The licensee has roped off the contaminated area and is sampling the air continuously while they formulate a cleanup plan. They estimate cleanup will take approximately two weeks with an additional week required for post-cleanup surveys. The licensee has made notification to the USNRC Region I office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 40.60(b)(1) |  |  |  | 0 | 2010-11-17
46424 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-11-16 22:10 | 2010-11-16 23:43 | 2010-11-16 | MANUAL REACTOR TRIP BASED ON DECREASING STEAM GENERATOR LEVEL "At 2210 EST on 11/16/2010, the Unit 1 reactor was manually tripped based on decreasing S/G level in Loop 4. Prior to the reactor trip power was at 26% and ascending following completion of a scheduled refueling outage. Moisture Separator Reheater 1C1 safety valve lifted and would not reseat. Turbine was tripped at 2206 EST to isolate steam leak. Following the Turbine trip, automatic S/G level control did not maintain S/G level. Manual control was taken however, S/G level could not be recovered. A manual reactor trip was initiated due to low narrow range S/G level. All other plant systems responded as expected." All rods fully inserted into the core during the trip. The reactor is at normal operating pressure and temperature and operators are removing decay heat via the steam dumps to condenser. As expected, the auxiliary feedwater system actuated during the transient. The grid is stable and the plant is in its normal shutdown electrical lineup. There is no known primary-to-secondary leakage. Plant response to the trip was considered normal and uncomplicated. Unit 2 was not affected by this event. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 26 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-11-16
46423 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-10-20 | 2010-11-16 17:21 | 2010-11-16 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received via facsimile: "On October 29, 2010, the licensee's RSO contacted DRH [Mississippi State Department of Health, Division of Radiological Health] about their inlet shutter/lock out device that would not close completely. The licensee had shutdown one of their Polymer lines for maintenance/turn around on October 20, 2010 and proceeded to the Disc Ring Reactor to lock out the rod source devices. The outlet rod source was retracted into the holder and shutter/lock out device was closed and locked. The inlet rod source was retracted into the holder but the shutter/lock out device would not close completely. "On October 22, 2010, Berthold Technologies USA, LLC was contacted by the licensee to assess the problem and make repairs. On October 27, 2010, Berthold Technologies USA, LLC came to inspect and perform repairs on the insertion rod source. The maintenance technician fully retracted the source which allowed the shutter/gate to turn further, but not to the fully indicated closed position. The maintenance technician then verified the source was fully retracted by knowledge of the device and survey readings (12 inches from device 2.6 mR/hr at one end, average along length of device, 0.5 mR/hr). The device was then removed for further inspection and maintenance. The device was then locked in the off/closed position and remounted in its original location. Installation surveys were performed, but readings were not obtained as plant maintenance was being done in the area. "The licensee was instructed by DRH to send in a written report describing the incidents leading up to the event that occurred on October 20, 2010, and any corrective actions or follow up performed. The requested report was received by [DRH] on November 5, 2010. DRH will notify NRC Operations and no other action is required by DRH." This device contains 7.41mCi of Co-60. The source serial number is 1772-10-02. The shield serial number is 005217. DRH considers the device to have been repaired successfully and fully operational at the present time. Mississippi Incident Report Number: MS-10007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-11-19
46422 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-11-13 | 2010-11-16 11:01 | 2010-12-02 | AGREEMENT STATE REPORT - PATIENT RECEIVED A THYROID IMAGING DOSE OF I-123 THAT WAS CONTAMINATED WITH I-131 The following report was received from the State of North Carolina via email: "This is to notify you about a medical event under the regulation .0364, i.e., within 24-hr notification requirement after discovery. The following summarizes the medical event. "Event: Contamination of I-123 thyroid imaging dose with I-131 (WRONG RADIONUCLIDE). "Dose: 380 rad (3.8 Gy) to the thyroid gland (EXCEEDS 50-RAD THRESHOLD FOR ORGAN DOSE) "Notification: Patient's parent and referring physician have been notified. "A detailed report will follow within 15 days." This event occurred sometime on Friday 11/13/10 and was discovered on Monday 11/15/10 at 1535 hrs. The patient was a child and potential adverse effects have not been determined at this time. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE RECEIVED FROM PAUL HUGGINS TO JOHN SHOEMAKER VIA EMAIL ON 11/22/10 @ 0954 * * * "DESCRIPTION OF THE EVENT: A patient was administered 0.389 mCi of iodine-123 orally for a thyroid uptake and scan procedure. Upon imaging at 4 hours, the technologist noted excessive background in the image. The acquisition computer showed an additional peak at 364 keV, consistent with presence of iodine-131 contamination. The iodine-131 thyroid burden at 21 hours was estimated to be about 43 microcuries. Based upon an iodine-123 uptake of 30%, the intake of iodine-131 was estimated to be about 143 microcuries. The absorbed dose to the thyroid, as estimated on 11/15/2010, was about 3.8 Gy (380 rad), or an equivalent dose of 3.8 Sv (380 rem), assuming age-specific reference values for thyroid mass and effective half-life. "An intake of 143 mCi of iodine-131 is comparable to activities that were administered in the past for diagnostic thyroid imaging, and no adverse effects are expected. "WHY THE EVENT OCCURRED: Interviews with staff and assaying the equipment used for the iodine-123 administration indicate that the screw-cap on the vial was the likely source of the contamination. It is unclear whether the screw-cap removal device, or improper handling of the cap, was the cause of the contamination. "STEPS BEING TAKEN TO PREVENT A RECURRENCE: The Authorized User and senior technical staff have educated staff about proper handling of radioiodine. To prevent a recurrence, we have changed our procedure as follows: 1) Only one radioiodine dose will be kept in the 'dosing hood' at any time. 2) The vial will be opened only when the patient and necessary staff are in the hot lab. 3) A separate cap remover will be used for each radionuclide. 4) Only one technologist will be involved with preparing dosing area, dosing the patient, cleaning up the dosing area and surveying post therapy." North Caroline Incident #: NC 10-50 Notified R1DO - R. Conte and FSME - G. Villamar * * * UPDATE FROM PAUL HUGGINS TO ERIC SIMPSON AT 0936 EST ON 12/2/10 * * * The I-131 intake is being corrected to 143 microcuries, instead of 143 millicuries, as reported previously. Notified the R1DO (Schmidt) and FSME (Villamar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-11-19
46421 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-11-16 00:01 | 2010-11-16 05:48 | 2010-11-17 | CONTROL ROOM ENVELOPE INOPERABLE DUE TO EXCESSIVE EMERGENCY CORE COOLING SYSTEM RELIEF VALVE LEAKAGE DURING ECCS PUMP SURVEILLANCE TESTING "The Licensee identified that Emergency Core Cooling System (ECCS) leakage exceeded the allowable limit as described in the Updated Final Safety Analysis Report (UFSAR). This is being reported as an Unanalyzed Condition in accordance with 10CFR50.72(b)(3)(ii)(B) and 10CFR50.72(b)(3)(v)® Control of Rad Release. "The leakage from the Low Head Safety Injection discharge relief valve occurred during Low Head Safety Injection Pump surveillance testing. Efforts to resolve the lifting of the Low Head Safety Injection discharge relief valve are in progress. "At 0001 [EST] on 11/16/10, Beaver Valley Power Station Unit 1 determined that leakage from the Low Head Safety Injection system in conjunction with a postulated Design Basis Accident (DBA) Loss Of Coolant Accident (LOCA) with transfer to Safety Injection Recirculation would result in dose exceeding the Dose Analysis for the Exclusion Area Boundary (EAB) and the Control Room. The projected dose would exceed the 10CFR50.67 EAB dose limit, and the 10CFR50 GDC 19 Control Room limit, assuming the leakage continued during the postulated DBA event. "Beaver Valley Units 1 & 2 share a common Control Room Envelope, which has been declared inoperable as a result of this condition. Technical Specification Limiting Condition for Operation 3.7.10, Condition B, has been applied. "The Senior NRC Resident has been informed of the condition [by the Licensee]." Notified R1DO (Harold Gray). * * * UPDATE FROM DAVID SHARBAUGH TO DONALD NORWOOD AT 1448 EST ON 11/17/2010 * * * "Actions have been completed to prevent leakage from the degraded Low Head Safety Injection System relief valve at BVPS Unit 1. Following successful completion of the post-maintenance test, the BVPS Unit 1 Low Safety Injection System was declared operable and applicable Technical Specification Actions at both BVPS Units were exited at 1545 hours on 11/16/1010. "The Senior NRC Resident Inspector has been notified." Notified R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) |  |  | 0 | 2010-11-16
46420 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-11-15 11:30 | 2010-11-15 18:37 | 2010-11-15 | AGREEMENT STATE REPORT - FLY ASH DENSITY GAUGE SHUTTER FAILS OPEN The following report was received via fax: "The licensee uses fixed industrial gauges for measuring densities in fly ash hoppers at the Stations precipitator building. The industrial fixed gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in April 1984 and at the time contained 50 milliCuries per source. The sources were manufactured and installed by Kay Ray, Inc. The gauge is Model No. 7080 and housing serial number 16785-G. The source capsule manufacturer was Amersham model no. CDC 800 and K-R ref. number serial number 15485 V. The Authorized User was performing the semi-annual 'Shutter Function Test' on Unit #3's precipitator sources. The 'external' source closure mechanism for the 3FA-1B & 2B hoppers did not operate as designed and the shutter did not close when the handle on the floor was operated. The external closure cable had detached from the shutter arms. In this condition, when the shutter closure mechanism was moved, the cable that operates the source shutter mechanism 20 feet above the floor did not move the shutter to the closed position. It should be noted that this cable is an older one which has been slated for replacement. This event happened at 11:30 am. The event was reported to the Lab Supervisor and the Radiation Safety Officer (RSO) at the Ft. Calhoun Power Station was notified. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-11-18
46419 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2010-11-15 06:03 | 2010-11-15 07:06 | 2010-11-15 | MANUAL REACTOR TRIP DUE TO LOSS OF A CIRCULATING WATER PUMP WITH ANOTHER PUMP OUT OF SERVICE FOR MAINTENANCE "On 11/15/10 at 0603 [hrs. EST], the Unit 3 reactor was manually tripped after receiving a report that there was an overheating packing gland on the 3A2 Circulating Water Pump. The 3A1 Circulating Water Pump was already tagged out for maintenance. This required Unit 3 to be tripped due to only two Circulating Water Pumps in operation. The Unit 3 reactor was stabilized in Mode 3. Auxiliary Feedwater automatically actuated. A train of normal feedwater remains available to feed Steam Generators. "During the Unit 3 reactor trip, the 3B Steam Dump to Atmosphere failed to close on operator demand per procedure. It was locally isolated with a manual isolation valve stopping the cooldown. The RCS was stabilized at 487.56?F and was borated as required by procedure. All boration systems operated as designed. The RCS returned to normal operating temperature and pressure." During the trip, all rods inserted into the core. Other than the steam dump to atmosphere valve lifting, no other relief valves lifted. There is no known primary to secondary leakage. The electrical grid is normal and the plant is in a normal shutdown electrical line-up. Decay heat is being removed via the 3A and 3C steam dumps to atmosphere since the Main Steam Isolation Valves were closed. The plant is heating up to normal operating temperature at which time auxiliary feedwater will be secured. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-11-15
46418 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-11-14 06:52 | 2010-11-14 09:05 | 2010-11-14 | MANUAL REACTOR TRIP DUE TO LOSS OF COOLING TO THE 'A' PHASE MAIN BANK TRANSFORMER "At 0617 [hrs. EST], Watts Bar experienced a failure of the cooling system to the 'A' phase Main Bank Transformer. Due to rising oil temperatures on the 'A' phase Main Bank Transformer, the reactor was manually tripped at 0652 hrs. All systems responded as designed with no issues." All rods inserted during the trip. There were no primary or secondary relief valves that lifted during the transient. The grid is stable and the plant is in a normal shutdown electrical line-up. The reactor is at normal pressure and temperature with decay heat being removed via the steam dumps to condenser with auxiliary feedwater providing steam generator make-up. The cause of the loss of cooling to the 'A' phase Main Bank Transformer was the failure of a control power transformer that supplies the Main Bank Transformer cooling system components. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-11-14
46417 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-11-12 12:10 | 2010-11-12 20:42 | 2010-11-12 | UNANALYZED 10CFR50 APPENDIX R SCENARIO "At approximately 1210 on November 12, 2010, a fire protection assessment identified a potentially unanalyzed condition in the plant's 10CFR50 Appendix R analysis. In the unlikely event of a fire in the main control room or cable spreading room, coincident with a fire induced loss of off site power, in which the control room must be evacuated, Operations personnel would proceed to the Alternate Shutdown System (ASDS) panel to perform required safe shutdown activities. During certain scenarios, High Pressure Coolant Injection (HPCI) may start on a reactor low-low water level signal or on high drywell pressure signal. Since HPCI is not controlled manually from the ASDS, a postulated fire induced short could prevent the HPCI system high reactor water level trip and possibly result in reactor vessel overfill. "Operation of the Safety Relief Valves in this condition has not been analyzed. For this scenario, the following unlikely sequence of events is required: 1. A fire would have to occur in the main control room or cable spreading room 2. The fire would have to be significant enough to require main control room evacuation 3. Offsite power would have to be lost 4. HPCI would have to initiate 5. A fire induced short preventing HPCI from tripping automatically would have to occur "Applicable safety systems remain operable, and Operations personnel are trained in procedures to handle complex fire scenarios, including fires in the main control room and cable spreading room. Additionally, the cable spreading room is protected by an automatic Halon fire suppression system. "As a precaution, a fire watch has been established as a compensatory measure. This event is being reported under 10CFR50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. | 47 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-11-12
46416 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-12 13:00 | 2010-11-12 16:33 | 2010-11-12 | INACCURATE INFORMATION PROVIDED IN LICENSE AMENDMENT REQUEST "At 1300, on November 12, 2010, Exelon Generation Company LLC concluded that inaccurate information contained in the PRA technical bases for a 1987 License Amendment Request (LAR) for Byron and Braidwood Stations would have potentially impacted the acceptability of the LAR by the NRC. The LAR was to extend Allowed Outage Times (AOT) from 72 hours to 7 days for several systems, to include the Component Cooling (CC) and Residual Heat Removal (RH) Systems. "The original design intent of the CC system was that each unit has two independent CC pumps and a fifth pump (U0) CC pump could be used as an operable spare for any of the unit specific pumps. This is how CC was modeled in the PRA technical justification for the 1987 LAR. However, a piping configuration design flaw was recently evaluated in that the U0 CC pump could not be considered an operable spare for either unit's B pumps was not modeled in the PRA. "During the evaluation to assess the potential significance of this CC design flaw on the PRA justification for the 1987 LAR, another potentially significant discrepancy was discovered in that it appears the operational practice to always split CC trains after a design basis LOCA was not modeled correctly in the RH analysis. "Administrative controls have been put in place to restrict the AOT for the CC pumps and RH trains to the pre-LAR timeframe of 72 hours pending the permanent corrective actions. In addition, administrative controls have been put in place to prohibit the U0 CC pump from being an operable spare for either unit's B trains. "This event is being reported as an unanalyzed condition that significantly degrades plant safety under 10 CFR 50.72(b)(3)(ii). "The NRC Resident Inspectors have been notified" | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-11-12
46415 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-12 13:00 | 2010-11-12 15:44 | 2010-11-12 | INACCURATE INFORMATION PROVIDED IN LICENSE AMENDMENT REQUEST "At 1300, on November 12, 2010, Exelon Generation Company LLC concluded that inaccurate information contained in the PRA technical bases for a 1987 License Amendment Request (LAR) for Byron and Braidwood Stations would have potentially impacted the acceptability of the LAR by the NRC. The LAR was to extend Allowed Outage Times (AOT) from 72 hours to 7 days for several systems, to include the Component Cooling (CC) and Residual Heat Removal (RH) Systems. "The original design intent of the CC system was that each unit has two independent CC pumps and a fifth pump (U0) CC pump could be used as an operable spare for any of the unit specific pumps. This is how CC was modeled in the PRA technical justification for the 1987 LAR. However, a piping configuration design flaw that was recently evaluated in that the U0 CC pump could not be considered an operable spare for either unit's B pumps was not correctly modeled in the PRA. "During the evaluation to assess the potential significance of this CC design flaw on the PRA justification for the 1987 LAR, another potentially significant discrepancy was discovered in that it appears the operational practice to always split CC trains after a design basis LOCA was not modeled correctly in the RH analysis. "Administrative controls have been put in place to restrict the AOT for the CC pumps and RH trains to the pre-LAR timeframe of 72 hours pending the permanent corrective actions. In addition, administrative controls have been put in place to prohibit the U0 CC pump from being an operable spare for either unit's B trains. "This event is being reported as an unanalyzed condition that significantly degrades plant safety under 10 CFR 50.72(b)(3)(ii). "The NRC Resident Inspectors have been notified" | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2010-11-12
46414 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-12 08:18 | 2010-11-12 15:44 | 2011-01-20 | CONTROL ROOM OUTSIDE AIR INTAKE NOBLE GAS CHANNEL SETPOINTS NON-CONSERVATIVE "At 0818 CST, 11/12/10, Radiation Protection determined that the setpoints for the Control Room Outside Air Intake Noble Gas channels are non-conservative. This affects Tech Spec 3.3.7 required monitors 0PR31B, 0PR32B, 0PR33B and 0PR34B (Noble gas channels). The current setpoints for 0PR31B, 0PR32B, 0PR33B and 0PR34B are High Alarm 9.55E-05 microCi/cc and Alert Alarm 9.55E-06 microCi/ml. The calculated required setpoints are High Alarm 6.61E-05 microCi/cc and Alert Alarm 6.61E-06 microCi/cc. This is approximately a 30% decrease in setpoints from the current setpoints. LCO 3.3.7 conditions A and B were entered at 0818, 11/12/10. LCO 3.3.7 conditions A and B required actions completion time is 1 hour. All required actions were complete at 0900 11/12/10, less than 1 hour. "This report is being made per 10 CFR 50.72(b)(3)(v), Event or condition that could have prevented fulfillment of a safety function, 8 hour non-emergency notification. "Both trains of radiation monitor setpoints were non-conservative and actuate control room ventilation in emergency mode. The margin available in the control room dose analysis will be reviewed to confirm impact on safety function. The setpoints have been non-conservative since 1999." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BART KELLER TO JOHN SHOEMAKER AT 1414 EST ON 01/20/11 * * * "At 0818 CST, 11/12/2010, Radiation Protection determined that the setpoints for the Control Room Outside Air Intake Noble Gas channels are non-conservative. This affects Tech Spec 3.3.7 required monitors 0PR31B, 0PR32B, 0PR33B, 0PR34B (Noble Gas channels). ENS notification was made under ENS 46414 under 10 CFR 50.72(b)(3)(v)(D). "The design basis accidents do not credit automatic actuation of the Control Room Outside Air Intake system to the Emergency mode from a high radiation signal. Therefore, the high radiation signal is not needed to mitigate the consequences of an accident and this event did not result in a safety system functional failure. "Therefore, ENS notification 46414 is being retracted." The licensee notified the NRC resident inspector. Notified R3DO (Bloomer) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-11-12
46413 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-11 09:30 | 2010-11-11 10:12 | 2010-11-11 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS INTO PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-11-11
46412 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-11-10 11:00 | 2010-11-10 18:02 | 2010-11-10 | AGREEMENT STATE REPORT - UNDERDOSAGE TO INTENDED TREATMENT AREA The following was received via e-mail: "At approximately 11:00 am on November 10, 2010, the Minnesota Department of Health was notified of a medical event that occurred at Mayo Clinic. Mayo Clinic reports during a biliary LDR treatment using Iridium-192, the catheter and guide wire moved and the radioactive sources moved out of position approximately 7 cm distal to the treatment location (still in the bile duct). The oncologist noticed the guide wire had moved at approximately 10:30 am on November 10, 2010, at that point the RSO was notified. It was determined that the intended treatment site received only 1.24 Gy of the intended dose of 20.0 Gy, making this a reportable event. "MDH will continue to investigate and will do an on-site visit during the week of November 15. More information to follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2010-11-16
46411 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2010-10-15 | 2010-11-10 15:31 | 2010-11-10 | AGREEMENT STATE REPORT - MISSING VARIAN GAS CHROMATOGRAPH CONTAINING TWO 15 MILLICURIE NICKEL - 63 SOURCES "The licensee's RSO notified Department of Radiological Health (DRH) about their missing Varian electron capture detectors on 10/15/10, while conducting their six (6) month sealed source inventory and leak tests. The licensee's Receiving and Property Control Office picked the Varian gas chromatograph, Serial No. 10734, up for disposal from one of the licensee's labs and boxed it for shipment to Creative Recycling Systems, Inc., in Palmetto, Georgia. Creative Recycling Systems received the licensee's recycle trailer on 10/12/10. On 10/15/10, the licensee's property control office contacted Creative Recycling Systems, Inc., and requested notification if the detectors were ever found." Creative Recycling Systems did not find the Varian electron capture detector containing two Ni-63 sources, serial numbers A2115 and T585, and it is assumed that it has been lost at the recycle facility. The licensee did survey a similar Varian device and found that survey readings were very close to background. MS Incident #: MS-10006. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2010-11-15
46410 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2010-11-10 05:18 | 2010-11-10 13:49 | 2010-11-10 | RHR PUMP TRIPPED WHILE OPERATING IN SHUTDOWN COOLING MODE "On November 10, 2010, at approximately 0518 hours, with the plant in Mode 5 during Refueling Outage (RFO) 22, the 'A' Residual Heat Removal (RHR) pump tripped while operating in the shutdown cooling mode resulting in an interruption of the primary means of decay heat removal for approximately 30 minutes. During this period the maximum increase in reactor temperature was approximately 2 degrees Fahrenheit with a calculated time to boil of approximately 33.9 hours. There was no loss of decay heat removal due to the fact that both trains of Fuel Pool Cooling system and the Reactor Water Cleanup system remained in service. At the time of this event, the plant was in the process of restoring motive power to MO-1909, Outboard Shutdown Cooling Isolation valve. Motive power had previously been isolated to the valve as part of a preplanned evolution of transferring the power supply to 'B' Reactor Protection System (RPS). Due to a failure to isolate the control power to MO-1909 when RPS power had been transferred, MO-1909 automatically closed when motive power had been restored due the existence of a Primary Containment Isolation System (PCIS) signal that was initiated when 'B' RPS power had been transferred. The closure of MO-1909 resulted in the isolation of the common shutdown cooling pathway, and therefore prevented both the 'A' and the 'B' RHR systems from removing decay heat. Preliminary investigations into this event indicate that the failure to isolate control power to MO-1909 occurred due to an existing procedure deficiency for transferring RPS power supplies. "As a result of the closure of MO-1909, Operations entered Abnormal Operating Procedure (AOP) 149, Loss of Decay Heat Removal, and Technical Specification (TS) Limiting Condition for Operations (LCO) 3.9.7 Condition A; Required RHR Shutdown Cooling Subsystem Inoperable and performed the required actions of the AOP and TS. At approximately 0547, shutdown cooling was restored when the 'C' RHR pump was placed in shutdown cooling. TS 3.9.7 and AOP 149 were subsequently exited at 0551. During the duration of this event adequate decay heat removal existed as part of the site's Shutdown Risk Management in that two loops of Fuel Pool Cooling were in-service and Feed and Bleed utilizing the Control Rod Drive pumps was available. Additionally, Reactor Water Cleanup was in service and remained in service for the duration of this event. Note that RHR shutdown cooling was considered available during this event due to the fact that there were no component failures associated with MO-1909 preventing it from being immediately re-opened. "This event is being reported as an event or condition that at the time of discovery could have prevented fulfillment of a safety function of structures or systems that are needed to remove residual heat under 10 CFR 50.72 (b)(3)(v)(B). "The [NRC] Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-11-10
46409 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2010-11-10 10:56 | 2010-11-10 13:00 | 2010-11-10 | UNPLANNED AUTOMATIC SCRAM AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION DURING TESTING "At 10:56 [EST] on Wednesday, November 10, 2010, Nine Mile Point Unit [1] One automatically scrammed from rated power. The cause of the scram was Main Steam Isolation Valve (MSIV) closure. The MSIV closure occurred during Instrument and Control Lo-Lo Level Surveillance Testing. The Lo-Lo Surveillance Test has been secured and all Reactor Protection System (RPS) Level Signals returned to normal. Two of four MSIVs went closed; troubleshooting to follow to determine the cause of the equipment malfunction [unexpected MSIV closure]. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated. At Nine Mile Point Unit One, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. At 10:58, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was initially established on the Emergency Condensers (ECS). The MSIVs have been re-opened and the normal heat removal capability has been re-established [to the Main Condensers]. "All off-site power sources remain available [with a normal electrical alignment]. "10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours when a valid actuation of the Reactor Protection System occurs. "10 CFR 50.72(b)(3)(iv)(A) requires reporting within 8 hours when a valid actuation of the High Pressure Coolant Injection System occurs. "There are no other adverse impacts to the station based on this event." All control rods inserted and the unit is stable in Mode 3 with reactor pressure and temperature approximately 600 psig and 480 degrees. All other safety systems operated as expected. The licensee notified the NRC Resident Inspector and the New York State Public Service Commission. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2010-11-10
46408 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2010-11-08 | 2010-11-09 15:42 | 2010-11-10 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL SHIPMENT FAILS TO ARRIVE "A shipment containing 88.7 Ci Ir-192 that was scheduled to be delivered on 11/8/2010 did not arrive as scheduled. A trace was requested today. Details are as follows: "On Friday 11/5/10, QSA Global, Inc (MA License 12-8361) shipped a CPIR100 to Kakivik Asset Management (NRC 50-27667-01) to be delivered C/O Northern Air Cargo in Anchorage, AK. It was shipped [by the carrier] P1 (Priority overnight) along with a small non-radioactive piece that contained a leak test kit. Both pieces were scheduled to be delivered to Northern Air Cargo on Monday 11/8/10. The leak test delivered without issue. However, the radioactive piece is still showing as arrived at [the carrier's] location in Newark, NJ. "Today, Tuesday, 11/9/10, [the carrier] was contacted to put a trace on the radioactive material. They believe that the address label must have somehow come off the package. QSA provided a complete physical description of the IR100 overpack." Source serial # - 66641B Source Activity - 88.7 Ci / 3281.9 GBq Surface reading - 18.0 mr/hr Transport Index - 0.4 * * * UPDATE FROM JOSH DAEHLER TO DONG PARK AT 1025 EST ON 11/10/10 * * * The following information was received via email: "QSA has been notified by the carrier this morning that the package referenced [above] was located overnight and has been forwarded to its destination on a new tracking [number]." Notified R1DO (Bellamy), FSME (Burgess), and ILTAB (Pearson). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2010-11-15
46407 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-11-09 11:39 | 2010-11-09 15:13 | 2010-11-09 | OFFSITE NOTIFICATION - VIOLATION OF THE DISCHARGE PERMIT "The Minnesota Pollution Control Agency was notified [on 11/9/10] at 1139 hours [CST] today that at Monticello, the Circulating Water and Service Water Streams were simultaneously chlorinated for a duration of approximately one (1) hour. Simultaneous chlorination of these two water streams is a violation of the National Pollutant Discharge Elimination System (NPDES) Permit. Chapter 4, Section 2.3, states, 'The condenser cooling water and the service water shall not be chlorinated simultaneously.' Upon discovery of this event, both the Service Water and the Circulating Water bleach injection skids were secured. "This event did not result in bleach discharge concentration in excess of the 0.038 ppm concentration set forth in the NPDES permit." The licensee notified NRC Resident Inspector. | 47 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-09
46406 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-10-19 | 2010-11-09 12:12 | 2010-11-09 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER NOT OPERATING PROPERLY The following information was reported via email by the State of Ohio: "A licensed service provider (AHP) visited the licensee's site on 10/19/10 and completed an inspection of six fixed level gauges with the following results: a) Four device shutters functioned as designed and were secured closed for maintenance activities. b) One shutter device was inoperable due to the fact that the shutter positioning pin was rusted and could not be removed. Through lubricating and gentle mechanical persuasion the pin was removed and the shutter cycled properly. c) The last device had a shutter operating handle that turned freely but did not rotate the shield block into the beam path. This device obviously did not function as designed and meets the reporting criteria. Through the use of more aggressive measures that did not include disassembly the shutter was eventually closed. "These activities were closely monitored by the service provider's representative and at no time were licensee personnel exposed to the direct beam. The shutter on this device is now seized in the closed position. Upon identification of the shutter hanging up the service provider contacted the Bureau by telephone and e-mail. "All six devices remain bolted in their fixed positions. The licensee intends to have the service provider unbolt and transfer all six devices to a secure storage location on licensee property where they will be properly packaged for transfer for disposal." The 2 sealed sources are both 50 milliCuries of Cs-137. The manufacturer of the fixed gauge is General Nucleonics, Model # 13250, serial # 114 & 116. Ohio Item Number: OH100027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-11-12
46405 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-11-09 02:00 | 2010-11-09 03:49 | 2010-11-09 | SECURITY EVENT POTENTIALLY REDUCING PHYSICAL SECURITY EFFECTIVENESS The licensee discovered a security event potentially reducing physical security effectiveness. Upon discovery, compensatory measures were immediately implemented. Contact the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RICK LULLING TO JOHN KNOKE AT 1406 ON 10/09/10 * * * "The Reg Guide clearly indicates this event to be loggable under section 2.3, and the appropriate compensatory measures were immediately taken, report EN #46405 is retracted." Contact the Headquarters Operations Officer for details. The licensee has notified the NRC Resident Inspector. Notified R2DO (Alan Blamey) 73.71 Group (email) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-11-09
46404 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2010-11-08 10:15 | 2010-11-08 17:59 | 2010-11-08 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER COULD NOT BE LOCKED CLOSED The following information was reported via fax by the State of Nebraska "The licensee uses fixed industrial gauges for measuring densities in flyash hoppers at the Stations precipitator building. The industrial fixed gauges contain a Cesium 137 sealed source. The Cesium 137 sources were originally installed in April, 1984 and at the time contained 50 milliCuries per source. The Sources were manufactured and installed by Kay Ray Inc. The gauge is Model No. 7062BP, and housing serial number 17666. The source capsule manufacture was Amersham model No. CDC 800 and K-R Ref. Number serial number 15607-V. "The maintenance group at North Omaha wanted to replace bags in the Unit 5 Transfer House Tertiary Collector. The Shift Supervisor and Operations was notified of the "Tag-out request" as well as the Laboratory. The first step of the "tag-out" is to secure the Transfer House level detectors, the sealed radiation sources. There are two sources in the Transfer House. Both source shutters closed properly, as indicated by surveys. The keys for the interlock Mechanism for the Primary Collector Tank could not be turned to lock the handle in the Closed Position. (Reference: Attachment 2 of Registry for the Kay-Ray Fixed Gauge Model 7062BP). The shutters for both sources remain operable, and can be opened and closed. This 'event' happened at 10:15 am. No personnel were exposed to radiation during this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2010-11-11
46403 | 0 | VELAN INC |  |  |  |  | 2010-09-15 | 2010-11-08 16:02 | 2011-02-08 | PART 21 REPORT - LIMITORQUE LIMIT SWITCH DEFECT The following report was received via fax: "During the performance testing of our valves equipped with Limitorque SMB-00 we found that the limit switch contacts proved to be defective. These tests took place in July 2010. Flowserve was advised and sent in replacement parts that were installed by their representatives. The valve-actuator assemblies were cycled and proper operation was assessed. These valves have been shipped to Dominion Virginia. At the time we considered the issue isolated and did not pursue an in-depth corrective action response from the Supplier. "Later in September when testing three valves equipped with Limitorque SMB-00 and two valves equipped with Limitorque SMB-2-06, we found again that the limit switch contacts were defective, exhibiting similar problems as found earlier in July. These valves are still at our factory, awaiting the response and corrective action from Flowserve. "The limit switch boxes (4 gear train limit switches, 16 sets of contacts) appear to be identical on the two types of actuators mentioned above. "Upon closer examination, we determined that construction and installation elements appear poorly controlled, resulting in unexpected failure to operate due to the contact blade (called finger base by the Manufacturer) not returning to a position where it can make contact again. This was documented internally on a Velan internal deviation report on September 3, 2010. "We advised Flowserve of our findings on September 15 and issued a formal Corrective Action Request (CAR 25500-73903) on September 16, 2010, with a deadline for responding that expired on October 26, 2010. After a number of follow-ups, we managed to make contact with responsible personnel at Flowserve on October 29. An evaluation report (electrical continuity test performed on sample switch assemblies cycled 2000 times) was submitted to our attention by Flowserve. However, we determined that the test did not answer all our concerns and requested Flowserve to provide additional information. Currently the supplier is engaged in retrieving the defective parts from our facilities and performing additional examinations and tests. The Manufacturer expects to have all necessary tests, examinations and evaluations completed on or before November 19, 2010. "Based on functional testing performed at Velan we determined that we have no record of similar defects on valve-actuator assemblies produced prior to these events, we therefore believe that the root cause is relatively recent but there is no way to know until Flowserve analyzes and evaluates the deficiency. "This type of defect has the potential to affect other valve manufacturers who may have installed Limitorque actuators equipped with this type of limit switch but we cannot say if such deviation could create a substantial safety hazard." * * * UPDATE FROM VICTOR APOSTOLESCU TO DONALD NORWOOD VIA FACSIMILE AT 0804 EST ON 1/24/2011 * * * On January 14, 2011, Velan received the final report from Flowserve concerning limit switches identified in this notification. Velan has accepted the conclusions in the report. The following is a synopsis of those conclusions: It was determined that producing a bend in the contact finger cannot occur during normal cyclic operation of the rotor. It is highly likely that the cause of the bent finger assemblies was due to the use of a flat blade screwdriver. A flat blade screwdriver can also exert enough force to damage the cotter pin hole in the spring stud. Based on testing and evaluations of all returned Velan switches and switches from Flowserve stock, a design deficiency has not been identified. Properly set switches will perform their intended functions. A maintenance update will be issued by Flowserve to guide the industry on any recommendations during their regularly scheduled maintenance outages. Notified R1DO (Newport), R2DO (Sykes), R3DO (Bloomer), and R4DO (O'Keefe). Notified Part 21 Group via E-mail. Notified NRR and NRO via facsimile. * * * UPDATE AT 1528 ON 2/8/2011 FROM VICTOR APOSTOLESCU TO MARK ABRAMOVITZ * * * Velan Inc. has issued the final report on this problem with no changes from the January 14, 2011 update. Notified R1DO (Bellamy), R2DO (McCoy), R3DO (Duncan), and R4DO (Clark). Notified Part 21 Group via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2010-11-08
46402 | 0 | INPO |  |  |  |  | 2010-11-02 | 2010-11-08 15:53 | 2010-11-08 | FITNESS FOR DUTY - SUPERVISOR AT INSTITUTE OF NUCLEAR POWER OPERATIONS TESTED POSITIVE FOR ALCOHOL A supervisor at the Institute of Nuclear Power Operations (INPO) had a confirmed positive for alcohol during a random fitness-for-duty test. The individual functioned as a supervisor at the Institute of Nuclear Power Operations. The employee's unescorted access has been suspended. Contact the Headquarters Operations Officer for further details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 26.719 |  |  |  | 0 | 2010-11-08
46401 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2010-09-16 | 2010-11-08 13:48 | 2010-11-08 | PART 21 REPORT - UPS MOTHERBOARD FAILED PRE-SERVICE INSPECTION The information below is a summary of a report received via facsimile from QualTech NP dated November 8, 2010. "This letter provides notification per regulation 10 CFR Part21 concerning the discovery through testing and evaluation of (4) four UPS System motherboards that reported to have failed pre-service inspection prior to installation into a UPS system at Southern Nuclear- Farley Station Unit 1 TDAFWP UPS 'B' Section. Trentec (now known as QualTech NP) provided these safety related motherboards for installation on a UPS system manufactured by (OEM) Dependable Power System. "The (4) four questionable motherboards were returned to QualTech NP for testing and evaluation to determine operability of their safety function including fit, form and function for use within the UPS System. Southern Nuclear Condition Report, CR2010109013, states 'Motherboard (DPS 20050061, SN 354, Trentec Tag # 7T55201 SN01) with different valued resistors and or different locations than original motherboard...' "QualTech NP developed a new dedication plan (DPS2010.0 Rev.1) to evaluate the returned motherboards for fit, form and function. The plan involves visual inspection verification - QualTech NP compared the returned boards to DPS BOM lists to identify any differences; and functional performance verification - the functionality of the items were verified by performance testing as factory Go/No Go board tests using a UPS system to the parameters defined in the existing referenced dedication plans. "Visual inspection of the motherboards found one resistor installed in the wrong location. Performance testing of motherboards found the resistor installed in the wrong location affected the safety function of the UPS system. "The motherboard with the resistor installed in the wrong location failed to operate during performance testing. The motherboard was reworked by original equipment manufacturer (OEM) who removed the resistor in question and re-installed it in the correct location. The repaired motherboard was performance tested and found acceptable for safety function for use within the UPS system. "QuaITech NP has reviewed its customer project / PO files and has determined the dedicated UPS system (2) and these motherboards with Date Code 2007 have only been provided to Southern Nuclear-Farley Station Unit 1 & 2 (total quantity- 4). Southern Nuclear- Farley Station Unit 1 & 2 has two (2) motherboards in service. QualTech NP has addressed the dedication and testing of motherboards by the developing a new dedication plan (DPS2010.0 Rev. 1). Southern Nuclear has reviewed and approved this new plan. "QuaITech NP's conclusion is that the resistor in the wrong location on the motherboard caused the UPS system not to operate during performance testing and established the equipment would not perform its intended safety function. After rework, relocation of the resistor, and retesting the UPS system became operable and was performing its safety related function. QualTech NP has completed testing, evaluation, and repair of motherboards, no further action is required." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2010-11-08
46400 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-11-07 18:39 | 2010-11-07 19:07 | 2010-11-08 | ALERT DECLARED DUE TO EXPLOSION IN THE 21 MAIN TRANSFORMER At 1849 EST, the licensee declared an Alert due to an explosion in the 21 Main Transformer. As a result of the loss of the transformer, Unit 2 experienced a reactor trip. Plant response to the trip was normal and the plant is stable in Mode 3. At 1839 hrs., the licensee activated their Emergency Response Organization. Additionally, there was a report of smoke issuing from a metering station at the site boundary. Offsite assistance has been requested to investigate the metering station. No injuries were reported and the licensee is investigating whether any other equipment damage occurred as a result of the transformer failure. * * * UPDATE FROM NICK LIZZO TO HOWIE CROUCH AT 2200 EST ON 11/07/10 * * * "On November 7, 2010, at 1839 hours, the Reactor Protection System automatically actuated at 100% Reactor Power when the 21 Main Transformer failed. The failure resulted in a turbine / reactor trip. All plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv). The transformer failure was characterized as an explosion that meets the IPEC [Indian Point Energy Center] EAL criteria 8.2.3. An Alert was declared at 1849 hours. The plant is stable in Mode 3 at this time. "The Auxiliary Feedwater System actuated following the manual trip, as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The Station Auxiliary Transformer tap changer has remained at the maximum tap changer position and is inoperable, however the unit remains on offsite power and all electrical loads are stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal temperature and pressure with residual heat removal using auxiliary feedwater and normal heat removal through the condenser via steam dumps. There was no radiation released. "Indian Point Unit Three was not affected by this event and remains at 100% power. "A post trip investigation is in progress. "A one hour notification of the Alert Declaration was made to the NRC Emergency Operations Duty Center officer Howie Crouch at 1907 [hrs. EST]." The licensee has notified the NRC Resident Inspector, the New York State Public Service Commission, New York State EMA and local county officials. Notified R1DO (White). * * * UPDATE FROM CHARLES LAVERDE TO HOWIE CROUCH AT 2230 EST ON 11/07/10 * * * At 2218 EST, the licensee exited the Alert emergency declaration. The exit criteria was that: 1) The plant was in or was proceeding to cold shutdown, 2) No radiation release was in progress or anticipated 3) All radiation levels in the plant were stable or decreasing, and 4) No limitation on access to all plant areas. The licensee has notified the NRC Resident Inspector. Notified IRD (Gott), R1DO (White), NRR EO (Bahadur), FEMA (Heyman), DHS (Doyle), HHS (Gruenspecht), USDA (John) and DOE (Turner). * * * UPDATE ON 11/8/2010 AT 1228 FROM MICHAEL McCARTHY TO MARK ABRAMOVITZ * * * Approximately 50-100 gallons of oil from the transformer reached the Hudson River. The licensee notified the National Response Center and the New York State Department of Environmental Conservation. The licensee notified the NRC Resident Inspector. Notified the R1DO (White). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2010-11-07
46399 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2010-11-07 10:23 | 2010-11-07 13:54 | 2010-11-07 | HIGH PRESSURE CORE SPRAY PUMP OIL LEAK "At 1023 CST on 11/07/2010, the HPCS System was declared inoperable due to a steady stream oil leak issuing from the lower motor bearing drain plug. The oil was being collected by an absorbent pad installed around the oil drain plug below the lower bearing sight glass. When the rag was removed from the drain plug, oil issued from the installed plug in a stream with the diameter of a number two pencil lead. River Bend personnel are currently making plans to repair the oil leak." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-11-07
46398 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2010-11-05 12:45 | 2010-11-05 16:19 | 2010-11-05 | SMALL PETROLEUM SPILL WITHIN SITE PROPERTY "This communication is intended to serve as a notification that the New York State Department of Environmental Conservation has been informed of a petroleum spill within the site property. A slight sheen and odor that indicated a petroleum product has been released to a local creek within the owner controlled property. A petroleum spill from an unknown vehicle was discovered along the length of an entrance driveway and in a parking lot, which due to the local rain entered the storm water system. Due to the area affected along the driveway spill location, Ginna's spill remediation vendor has been contacted to assist with the cleanup. Petroleum absorbent booms have been placed in the creek and along driveway runoff locations to minimize any further introduction of the spilled product and to further protect the waterway." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-05
46397 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-11-04 23:25 | 2010-11-05 12:41 | 2010-11-07 | FOUR AVERAGE POWER RANGE MONITORS OUTSIDE ALLOWABLE RANGE "Following a power reduction to 49 percent reactor thermal power at approximately 2312 [CDT] on November 4, 2010, 'B' high pressure feedwater heaters were isolated at approximately 2320 in preparation for repair of the 15B feedwater heater. Calculated core thermal power (CTP) rose by approximately 50 MWth. This resulted in all four average power range monitors (APRMs) failing to satisfy Technical Specification (TS) Surveillance Requirement SR 3.3.1.1.2 in that the absolute difference between the APRMs and the calculated power from the heat balance was greater than 2.0 percent rated thermal power (RTP). All four APRM channels were between approximately 3.5 and 4.0 percent lower than CTP. Since all four APRM channels were affected, the functions of the APRMs were inoperable and RPS trip capability had not been maintained. TS Conditions 3.3.1.1.A and 3.3.1.1.C were entered at 2325. All four APRM gains were adjusted and the TS Conditions were exited at 2349. "This event is reportable under 10CFR50.72(b)(3)(v) as an event that could have prevented the fulfillment of the safety function of a system needed to: (A) shutdown the reactor and (D) mitigate the consequences of an accident. "This event notification is being submitted outside the 8 hour reporting requirement." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RANDY SCHULTZ TO HOWIE CROUCH AT 1652 EST ON 11/7/10 * * * "The following is an update to Event Notification 46397 made on 5 November 2010 concerning Average Power Range Monitors (APRMs) inoperability due to >2% deviation from calculated Core Thermal Power (CTP). "During review of inputs to the CTP calculation, Operations staff determined that indicated power levels were not consistent with the indicated electrical output of the turbine generator. Subsequent investigation revealed an erroneous feedwater flow input from the isolated 'B' feedwater heater string. Actual CTP was less than indicated CTP by approximately 50 MWth. This was validated and verified through manual calculation. 50 MWth constitutes approximately 3% of rated thermal power. With the adjustments made to APRM on 4 November 2010, this resulted in all four APRMs being outside of the acceptable tech spec value. Following Operations review, at 1108 on November 7, 2010, all four APRMs were declared inoperable and tech. spec. 3.3.1.1.A and 3.3.1.1.C actions were initiated. "Values consistent with the actual plant configuration ('B' feedwater heater string isolated) were input to the CTP calculation with subsequent indicated CTP returning to actual CTP. All four APRM gains were adjusted and APRMs returned to operable status. Tech Spec 3,3.1.1.A and 3.3.1.1.C conditions were exited at 1207 on November 7, 2010." The licensee has notified the NRC Resident Inspector. Notified R3DO (Giessner). | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-11-05
46396 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2010-11-05 01:04 | 2010-11-05 06:50 | 2010-11-05 | VALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR FOLLOWING INADVERTENT DE-ENERGIZATION OF SAFETY BUS "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), an event or condition that resulted in a valid actuation of emergency AC electrical power systems. "At 0104 EDT on November 5, 2010, the plant was in Mode 5 Cold Shutdown in a refueling outage. Maintenance personnel were performing post maintenance testing on the main generator relay panel when the 'B-SB' Safety Bus was inadvertently de-energized, resulting in automatic starting of the 'B-SB' Emergency Diesel Generator. Safety systems responded as expected during the event, and the 'A-SA' Emergency Bus remained operable with power available from both offsite power and the 'A-SA' Emergency Diesel Generator throughout the event. The 'B-SB' Safety Bus was powering shutdown cooling, which was restored using 'B-SB' Residual Heat Removal system at 0107 EDT with the 'B-SB' Emergency Diesel Generator supplying the bus. The testing procedure was not intended to result in the safety bus being de-energized nor automatic start of the Emergency Diesel Generator. Although the specific cause of the safety bus being de-energized is not known at the present time, it appears that it was directly related to the testing being performed. "The licensee notified the NRC Resident Inspector." The 'B-SB' Safety Bus has been returned to its normal offsite power source and the 'B-SB' Emergency Diesel Generator secured and returned to standby status. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-11-05
46395 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-11-04 15:04 | 2010-11-04 22:22 | 2010-11-06 | PORTAL RADIATION MONITOR ALARM ON A SCRAP SHIPMENT "On November 4, 2010, at approximately 1504 PDT, San Onofre Nuclear Generating Station (SONGS) was notified that scrap circuit breakers salvaged from the SONGS warehouse had alarmed a portal radiation monitor at a metal recycling facility in Los Angeles County. The monitor indicated a reading approximately 40% above background levels. Naturally occurring isotopes in the circuit breakers are suspected to have alarmed the portal monitor. The metal recycling vendor (Alpert and Alpert) called the Los Angeles branch of the California Department of Health Services, Radiologic Health Branch to obtain a special permit authorizing the return shipment to SCE. "SCE is reporting this event in accordance with 10CFR50.72(b)(2)(xi). "At the time of this report, Unit 2 was operating at 100% power and Unit 3 is defueled." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0018 EDT ON 11/06/10 FROM SIMMON TO HUFFMAN * * "On November 5, 2010, employees of the San Onofre staff disassembled the scrap circuit breakers that had been sent from the San Onofre Warehouse to the Alpert and Alpert salvage yard on November 4. These high voltage circuit breakers contain arc chutes consisting of large ceramic plates that contain naturally occurring radioactive material. All ceramic materials were removed. Health Physics technicians then re-surveyed the circuit breaker casings by direct and indirect survey and verified that they did not contain any detectable levels of radioactive material. Indirect survey of the ceramic material demonstrated that they had no detectable levels of removable radioactive material. "The California Department of Health Services, Radiologic Health Branch will be notified of these results." The licensee has notified the NRC Resident Inspector. R4DO (Howell) and FSME (Chang) notified. | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-04
46394 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2010-11-04 | 2010-11-04 17:22 | 2010-11-04 | CONTAINMENT AIR LOCK DOORS NOT OPERATED PROPERLY "On November 4, 2010, at 11:28 AM both doors in airlock 124 from secondary containment to access control were simultaneously open for a period <5 seconds. The doors were immediately closed. This condition resulted in an unplanned entry into Technical Specification 3.6.4.1.A for secondary containment. The condition could have prevented the Standby Gas Treatment System from developing a negative pressure within secondary containment following a design basis accident. This negative pressure is required to prevent ground consequences following an accident. The Standby Gas Treatment System remained operable throughout the event." The licensee was decreasing power at the time of the report for a condition unrelated to the report. The licensee will notify the Minnesota Duty Officer. The licensee notified the NRC Resident Inspector. | 78 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-11-04
46393 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-11-04 | 2010-11-04 14:25 | 2010-11-04 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was reported via e-mail by the State of California: "On November 03, 2010, the RSO at UC Berkeley informed the [California] Radiologic Health Branch (RHB) that on 11/01/10 an Electron Capture Device (ECD), S/N F7737 containing 15 mCi of Ni-63, was determined to have leakage in excess of 0.005 microcurie criteria. The leaking source was installed in a Hewlett-Packard gas chromatography unit Mode 5890. Immediately after the leakage was found, the unit was taken out of service. Follow-up surveys performed did not show any area contamination. The maximum contamination found on the internal portion of the ECD outlet port was 0.007 microcuries. The extent of contamination was limited to the ECD and exhaust tubing. No personal contamination was expected since the leakage was limited to the internal parts of the gas chromatography unit and vent tubing. "The unit was used for routine analysis of organic materials. The leakage may have been due to the routine use over many years (@ 16 years). The University will pursue disposal of this ECD." California RHB 5010 - 110310. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-11-09
46392 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2010-11-04 01:23 | 2010-11-04 03:05 | 2010-12-20 | CHARGING PUMP '23' DECLARED INOPERABLE DURING SURVEILLANCE TESTING "On November 4, 2010 at 0123 [EDT], '23' Charging Pump was declared inoperable due to not meeting required test parameters during surveillance testing. '23' Charging Pump is required for remote shutdown per Technical Specification 3.3.4, Remote Shutdown, and is a single component system intended to perform the inventory control safety function. Since '23' Charging Pump has been declared inoperable, a loss of safely function has occurred and is reportable per 10CFR50.72 (b)(3)(v)(A). "The cause of the inoperability is under investigation. Per Technical Specification 3.3.4, Remote Shutdown, '23' Charging Pump must be restored to operable status within 30 days." The licensee will inform the NY State PSC (Public Service Commission) and the NRC Resident Inspector. * * * RETRACTION FROM CHARLES ROKES TO DONG PARK AT 1028 EST ON 12/20/10 * * * "Indian Point Unit 2 is withdrawing the 8-hour non-emergency notification made on November 4, 2010, at 0305 EST. The notification on November 4, 2010, reported a safety system functional failure (SSFF) as a result of declaring the 23 Charging Pump (CP) inoperable. The 23 CP failed to meet test parameters during testing. Because the 23 CP is credited in Technical Specification (TS) 3.3.4 for Remote Shutdown, the inoperable condition was determined to be a loss of safety function. The TS 3.3.4 Allowed Outage Time (AOT) for inoperable conditions is 30 days. The remote shutdown function is not credited in the accident analysis. "Subsequent investigations determined that during a two year comprehensive test (IST) the 23 CP failed the flow test due to low pump discharge flow (79.3 gpm) at the prescribed test speed (85% of rated speed). Troubleshooting determined that the 23 CP recirculation line valves 1279 and 4902 had leak-by of approximately 6.7 gpm. The leak-by results in a reduction of available discharge flow from the 23 CP to the Reactor Coolant System (RCS) due to a small amount of the pump discharge being diverted through the recirculation line. Engineering determined that the CP capacity for emergency boration with the recirculation line valves leak-by was within the capability of the 23 CP to maintain overall system function. The 23 CP is also credited for RCS inventory maintenance per TS 3.3.4 and Station Administrative Order (SAO) 703 for fire protection. Engineering concluded that with a normal CP output of approximately 87-90 gpm and a nominal rated capacity of 98 gpm, the reduction by approximately 6.7 gpm due to leak-by did not significantly impact normal operation of the CP. Therefore, the 23 CP continues to meet the established IST requirement when the 6.7 gpm recirculation line valve leak-by is accounted for. The degraded output is associated with the system rather than the 23 CP therefore the IST requirement for the 23 CP is satisfied. Additionally, the 23 CP test was performed at approximately 85% of rated speed in accordance with the IST requirements. At 100% rated speed, the remaining available capability to the RCS would be approximately 92 gpm. Engineering concludes that although degraded the 23 CP and system can perform their intended function and no SSFF occurred." The licensee will notify the NRC Resident Inspector. The R1DO (Perry) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-11-04
46391 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-11-03 08:13 | 2010-11-03 16:36 | 2010-11-03 | FUEL STORAGE TRANSFER CASK NEUTRON SHIELD PARTIAL DRAINDOWN "At 0813 [CDT], the Cooper Nuclear Station (CNS) Control Room (CR) received a report of a partial neutron water shield drain down on the Dry Fuel On-site Transfer Cask (TC). The TC, with a loaded Dry Storage Cask (DSC), was located in the Reactor Building (RB) Railroad Airlock area. Final preparations were being completed prior to transferring the DSC to Horizontal Storage Module (HSM) 2A. The RB and south side of the Administration Building were cleared of unnecessary personnel. No abnormally elevated RB area radiological readings were noted on CR indication. Local indication in the [Railroad] Airlock from portable radiation monitors indicated abnormally high readings due to the drain down. At 0819 [CDT], CNS entered Abnormal Procedure 5.1 RAD, Building Radiation Trouble. Surveys indicate the top of the TC had readings of about 130 mR/hr neutron at 30cm, which is above the normal readings of 2 mR/hr. Surveys of the bottom portion of the TC indicated a neutron dose rate of 10 mR/hr at 30cm. Actions per 5.1 RAD were subsequently performed. An emergency declaration was not required, because no confinement boundary was adversely affected and neutron levels did not meet a factor of 1,000 over normal levels. Since dose rates were no greater than noted above, and because neutron dose was being directed upward due to the shielding loss being in the upper portion of transfer cask, the Technical Support Center (TSC), which is located in the Administration Building, was determined to support habitability. Furthermore the TSC is provided with additional shielding for personnel protection during an event. "This is being reported as a 24 hour report under 10 CFR 72.75(d) for an important to safety fuel storage equipment that failed to function as designed when required to prevent releases, prevent exposures in excess of regulatory limits, or mitigate the consequences of an accident and no redundant equipment was available or operable to perform the required safety function. The cause of the drain down is under investigation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 72.75(d)(1) |  |  |  | 0 | 2010-11-03
46390 | 0 | WATERFORD | 3 |  |  | [3] CE | 2010-11-03 12:00 | 2010-11-03 13:58 | 2010-11-03 | NON-LICENSED CONTRACTOR POTENTIALLY SUBVERTED A DRUG SCREENING TEST A non-licensed contract employee admitted to the sample collector using unspecified drugs prior to undergoing a "for cause" drug screening. The employee's unescorted access to the plant has been terminated. There are no systems affected; nor was there an effect on plant operation. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | SAFEGUARDS REPORTS |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 | 73.71(b)(1) |  |  | 1 | 2010-11-03
46389 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2010-10-22 14:45 | 2010-11-03 13:43 | 2010-11-03 | AGREEMENT STATE REPORT - MEDICAL EVENT - DOSE ADMINISTERED IN WRONG LOCATION The following report was received from the State of North Carolina via email: "The patient has persistent small cell lung cancer after chemotherapy, in an area that has received prior external beam radiation therapy, and was symptomatic. Therefore, a course of endobronchial brachytherapy with a high-dose rate unit (HDR) was recommended to the left upper and left lower lobe bronchus where the tumor was present. The treatment prescription was 10 Gy x 2 fractions to the target volume as defined in the planning CT. The first treatment was delivered between 2 to 3 pm, on Oct 22, 2010. Unfortunately, due to errors in defining the starting dwelling positions of the source during the treatment planning, the actual dose was delivered to the wrong location along the catheters. Details of the process are described below. "After two endobronchial catheters were placed under bronchoscopy in the OR [operating room], the patient was transferred to Radiation Oncology Department where a CT was obtained for treatment planning purposes. The two catheters were positioned correctly based on CT. "In the first step of the treatment planning, the locations of the two endobronchial catheters were correctly identified in the CT images. The direction of the catheters was mistakenly reversed afterwards during the treatment planning, thereby changing the starting position of the HDR source. Therefore, instead of the patient being treated correctly to the identified tumor region in the left-sided airways, she was treated to a position more proximally along the path of the catheters (the larynx area). Although the plan was checked by a number of qualified physicists per operational protocol, the subtle orientation error was missed, both in the plan check and in the delivery check. The wrong treatment was delivered around 2:45 pm. "The error was identified by the planning physicists when they were working on another patient case, about one hour after the patient's treatment. A computerized 3-D plan was generated to calculate the actual location and dose delivered due to this error. The estimated dose to the neck region was about 15-20 Gy. The plan delivered to the patient was also delivered on radiochromic film to confirm the location of the delivered dose. "The attending physician, clinical director, and the director of physics were all notified immediately after the error was identified and confirmed. The Radiation Oncology Department chair was notified by the clinical director. The Radiation Safety Officer was notified also by the chief physicist. "The attending physician reviewed the case and the dosimetry, and immediately tried to contact the patient. After several attempts the patient was reached around 6:00 PM and asked to come back to the hospital immediately for observation and prophylactic treatments. The patient was admitted to hospital around 9:00 PM on the same day (the time required for her to travel back to Duke from her home). "Licensee's evaluation of why the event occurred: a. Staff physicists were more focused on dose optimization and missed the catheter's orientation. B The wrong orientation was again missed during the plan and delivery checks. C. In addition to calculation checks, there was no experimental check, i.e. delivering dose to the film to verify the distance. "The effect, if any, on the individual(s) who received the administration: The patient was admitted to Duke Hospital immediately after the error was discovered. She remained hospitalized for 4 days during which time she remained relatively asymptomatic. She did not develop increasing hoarseness, shortness of breath, or odynophagia. She underwent fiber optic laryngoscopy 36 hours after her treatment which showed minor edema of the supraglottic larynx but no airway compromise. She received the correct treatment while an inpatient, and after one additional day of observation was discharged home. "What actions, if any, have been taken or are planned to prevent recurrence: a. Conducted a root-cause analysis of the event among the physicists. B. A new and more detailed standard operational procedure (SOP) for this type of treatment was generated by the members of the Brachytherapy team. C. The existent HDR Patient QA form was edited to add extra check levels that will prevent this error from happening again. D. A new verification procedure was added to the existent set of verification procedures. It involves the delivery of the treatment on Gafchromic film or alternative imaging device to verify the exact starting point of the treatment. This film will be compared with the plan and will have to be approved by two physicists and the attending for each case. "Certification that the licensee notified the individual (or the individual's responsible relative or guardian) and if not, why not: The patient was contacted, was returned to Duke and was admitted for evaluation and management." Log # NC 10-47 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2010-11-09
46388 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-11-03 12:35 | 2010-11-03 13:15 | 2010-11-06 | SPDS AND ERDS REMOVED FROM SERVICE FOR MAINTENANCE "On 11/3/10 at 1235 EDT Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 48 hours. During this time, the majority of the Control Room indications remain available to the plant staff, and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems, if needed. The plant is currently in Mode 5, and will remain in Mode 5, for the duration of the SPDS and ERDS unavailability. Since the unavailability will last greater than 8 hours, this is considered a Loss of Emergency Assessment Capability, and reportable under 10CFR50.72(b)(3)(xiii). "Follow-up notification will be made when SPDS and ERDS have been restored." * * * UPDATE TO PETE SNYDER FROM MARK EGHIGIAN AT 1414 EDT ON 11/6/2010 * * * "Update to event # 46388: on 11/6/2010 at 1000 EDT, regarding SPDS and ERDS system removed from service to support planned outage on the UPS vital power supply. "Planned work which resulted in the removal from service of the SPDS and ERDS has been completed. All emergency assessment capabilities have been restored." The licensee notified the NRC Resident Inspector. Notified R3DO (Giessner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-11-03
46387 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2010-11-03 10:21 | 2010-11-03 12:09 | 2010-11-04 | UNUSUAL EVENT DECLARED DUE TO AN EXPLOSION IN THE PROTECTED AREA WHICH AFFECTS NORMAL OPERATIONS On November 3, 2010 at 1021 CDT, operators attempted to start the Unit 2 startup feedpump to support a two hour maintenance run. The feeder breaker for the startup feedpump exploded causing an undervoltage condition on Auxiliary Bus 1H and Standby Bus 1H which resulted in an automatic reactor trip due to reactor coolant pump undervoltage. All control rods inserted into the core. At 1038 CDT, the site declared an UNUSUAL EVENT (HU-2) due to an explosion in the protected area which affects normal plant operations. The standby diesel generator (EDG-23) started and loaded to the 'C' train loads which sequenced properly. The auxiliary feedwater system automatically started as expected providing feedwater to the steam generators. The normal feedwater pumps were secured. Decay heat is being removed from Unit 2 using the normal steam dump valves to the main condenser. There is no primary to secondary leakage. The plant is stable and in MODE 3 with no challenges to reactor safety. There was no impact on Unit 1. At 1240 CDT the licensee terminated the UNUSUAL EVENT. The licensee is investigating the cause of the breaker explosion and if the other standby diesel generator (EDG-21) should have started due to the undervoltage condition. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TAPLETT TO KLCO ON 11/3/10 AT 1530 EDT * * * "A News Release is being planned so this condition is also being reported pursuant to 10 CFR 50.72(b)(2)(xi). "During the electrical fault condition, some Train A components stopped running although no Train A low voltage ESF actuation occurred, The reason for this occurrence is not fully understood, "The breaker malfunction did not result in a fire." The licensee will notify the NRC Resident Inspector. Notified: R4DO (Spitzberg); NRR (Thorp); R4RA (Collins); NRR (Boger); IRD (Gott) DHS (Hill); FEMA (Hollis) * * * UPDATE FROM HARRISON TO SNYDER ON 11/4/10 AT 1920 EDT * * * The licensee called to correct an editorial error in the original report above. The second sentence of the original report above should refer to Auxiliary Bus 2H and Standby Bus 2H since this is a Unit 2 issue. Notified: R4DO (Spitzberg). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2010-11-03
46386 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-11-02 | 2010-11-03 09:43 | 2010-12-28 | AGREEMENT STATE REPORT INVOLVING A MEDICAL EVENT DUE TO A DOSAGE DIFFERING FROM THE PRESCRIBED DOSE The following information was received via fax from the Commonwealth of Pennsylvania: "Notifications: On November 2, 2010 PaDEP [Pennsylvania Department of Environmental Protection] Central Office was notified by the licensee of a medical event involving a dosage that differs from the prescribed dose by 20% as required under 10 CFR 35.3045. This event also meets the criteria for Abnormal Occurrence reporting. "Event Description: On November 2, 2010 a patient was undergoing brachytherapy treatment for prostate cancer. A partial seed implant of 85 Gy was prescribed, however, the full treatment of 144 Gy was implanted. This event was discovered upon completion of the procedure. "Cause of the Event: Human Error "Actions: The Department is awaiting more event details at this time and plans to send regional staff to conduct a follow-up inspection. Final event details will be communicated in an NMED and Abnormal Occurrence report." PA Report ID No.: PA100025 * * * UPDATE FROM DAVID ALLARD TO JOE O'HARA VIA FAX AT 1741 ON 12/28/10 * * * "NOTIFICATIONS: The licensee called the PaDEP Bureau of Radiation Protection on the afternoon of November 2, 2010 to provide a 24-hour verbal notice of a Medical Event. The event involved a patient dosage that differed from the intended [written directive] dose by greater than 20%, consequently requiring a 24-hour report per 10 CFR 35.3045(a)(1)(i). Subsequently, the licensee provided a written report to PaDEP on November 5th. "EVENT DESCRIPTION: On November 2, 2010 a patient was undergoing brachytherapy Cesium-131 seed implant treatment for prostate cancer. A partial seed implant of 85 gray (Gy) was directed, with a 45 Gy follow-up external [IMRT] beam therapy. However, the full seed treatment of 114 Gy was implanted. The event was discovered upon completion of the implants. "CAUSE OF THE EVENT: Human error was the cause of the event. Specifically, the incorrect prescribed prostate dose was entered into the licensee's VariSeed planning system (i.e.114 Gy vs. 85 Gy), and an incorrect seed order was placed with the vendor. The error persisted because the licensee's staff did not directly compare the written directive to the printed treatment plan. Such a comparison would have alerted the staff to the error. "ACTIONS: The PaDEP performed a reactive inspection at the hospital on 11/4/2010. Warren General also initiated the following changes: Their current Operating Room (OR) "time-out" procedure will be altered to include the expected prescription dose. A copy of the original written directive will be utilized in the OR for reference before and during the implant. Forms will be amended to have the physician's written directive and the planned dose on the same form for easy review and comparison. Lastly, the weekly physics chart review that involves a check of the written directive has been altered such that a summary sheet that is normally used for external beam patients will now also be used for seed implant patients. This event will be also communicated to NRC via NMED. However, there was an initial miscommunication between the licensee and PaDEP. The full treatment of 114 Gy was used, not 144 Gy. Thus, there will not be an Abnormal Occurrence report from PaDEP to NRC." Notified R1DO(Hansell) and FSME EO(Watson) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2010-11-09
46385 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2010-11-01 20:04 | 2010-11-01 23:30 | 2010-11-01 | OFFSITE NOTIFICATION DUE TO OIL SPILL "During the performance of rounds an operator found a leak on the traveling water screens. The traveling water screens are part of the Service Water System. The travelling screen drive chain oil reservoir was found empty. It is estimated that approximately 5 gallons of oil entered the Service Water System forebay. The oil residue has been cleaned up. The environmental impact will be assessed following further investigation. "Notifications have been made to NYSDEC [New York State Department of Environmental Conservation] and National Response Center." NYS (New York State) spill #: 1008090 National Response Center spill #: 958672. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-11-01
46384 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2010-11-01 10:00 | 2010-11-01 20:18 | 2010-11-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received via e-mail: "At approximately 1000 [PDT] today an iron piling fell on top of a portable gauge and left significant damage. The incident happened in a sparsely populated area of Overton, Nevada. The RSO was on his way to the location with a survey meter. The gauge has been moved and a 100 foot perimeter around it has been established. "The gauge was damaged such that the source tube can be pulled from the shielding. The RSO has secured the source tube in the shielded position and determined that the source is intact. He will be transporting the gauge directly to Instrotek for repairs and will be submitting a written report shortly." The damaged portable gauge is a Troxler model number 3430; serial number 17916. The gauge sources include Cs-137 (.011Ci); model number A-102112; Serial Number 50-7401 and a sealed source that includes Am-Be (.044 Ci); model number A-102451; Serial number 47-13357. Nevada Item Number: NV100021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2010-11-04
46383 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2010-11-01 10:15 | 2010-11-01 19:10 | 2010-11-01 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received by e-mail: "On November 1, 2010, at [1015 PDT] the authorized user from Soil Surveys, Inc., License Number 3428-27, called RHB [Radiologic Health Branch] Richmond, [CA] to notify that a moisture/density gauge was missing from his residence located at Salinas, CA. On October 29, 2010, authorized user checked out the nuclear gauge, Troxler, Model TEL, 3440, S/N 18026 from the permanent storage location to be used on October 30, 2010. The gauge was stored inside the company's transportation truck and parked at the residence indicated above, until November 1, 2010. As the authorized user approached the company's truck the early morning of November 1, 2010, he found out that the two locks that were used to fasten the nuclear gauge case to the bed of the truck were cut with a bolt cutter, and the nuclear gauge was removed with its transportation case from the company's transportation vehicle." The licensee notified the Salinas Police Department of the incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2010-11-04
46382 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-11-01 10:00 | 2010-11-01 17:49 | 2010-11-01 | AGREEMENT STATE REPORT - SHUTTER INDICATOR SHOWED INCORRECT POSITION The following information was received via email: "[The licensee Radiation Safety Officer (RSO)], for Ames Municipal, Iowa License 0147-1-85-FG reported [to the state] via phone a 'sticky' shutter for their Texas Nuclear fixed gauge device, model number 5197, Cs-137, 100 mCi (September 1980), serial number B843. The RSO said that during a shutter check this morning at approximately 10:00 a.m. the shutter was in the closed position, however the indicator showed that it was not completely closed. This fixed gauge is usually in the open position as it is a level detection device for the coal hopper. They only close it when doing scheduled work on the machine/hopper that requires the shutter to be closed. He reports that a leak test on October 15th was good and that a radiation worker adjusted a detector on October 28th and was able to close the shutter on that day. "[The RSO] reports that no employees were exposed to radiation as a result of this event and that they are going to attempt to mitigate the issue on the morning of November 2nd. He will report to the Iowa Department of Public Health for updates." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-11-04
46381 | -1 | COMMUNITY HEALTHCARE SYSTEM |  |  |  |  | 2008-05-28 | 2010-11-01 16:25 | 2011-01-25 | TWO MEDICAL EVENTS INVOLVING RECEIVED DOSE LESS THAN PRESCRIBED DOSE During an on-site NRC Inspection two (2) medical events were identified both involving a delivered dose less than the prescribed dose following implant of Palladium-103 seed for prostate therapy. Specific details as follows: First Medical Event Preplanning date: 5/18/08 Post planning date: 5/18/08 Dose received by prostate volume: 44% Underdose: 56% Prescribed: Palladium-103, 140.42U consisting of 59 seeds, 2.38U/seed Second Medical Event Preplanning date: 7/8/08 Post planning date: 7/8/08 Dose received by prostate volume: 44% Underdose: 56% Prescribed: Palladium-103, 196.80U consisting of 82 seeds, 2.38U/seed Both underdoses are attributed to prostate swelling. The physician reviewing the results concluded that there was no adverse impact on either patient. The licensee will continue reviewing medical records to identify any additional occurrences of this nature. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM MIREL PALAMARU TO VINCE KLCO ON 1/25/11 AT 1829 EST * * * Based on a post evaluation by the licensee's Radiation Safety Officer and physicians, all delivered dose came within 20% of overall prescribed dose. Thus, this is not considered a medical event. Notified the R3DO (Stone), and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-11-01
46380 | -1 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-10-30 07:00 | 2010-11-01 13:17 | 2012-02-01 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY CAMERA INVOLVED IN A TRANSPORTATION ACCIDENT A previously terminated Quality Inspection and Testing employee gained unauthorized access to keys of a company vehicle loaded with a radiography camera. The individual appeared intent to drive the vehicle to the Rock Springs Airport located in Wyoming when the truck experienced an accident on Highway 191 about 4 miles south of Dutch John, Utah. When the Utah highway patrol drove up to the accident scene, the patrol found the radiography camera outside of the truck. The SPEC Model 150 radiography camera S/N 1195 containing 40 Curies of Ir-192 was undamaged and placed into the custody of a representative of Quality Inspection and Testing Inc. The individual driving the truck was transported to a medical facility. A survey of the site indicated no spread of contamination or radiation levels above background. A survey of the radiography camera revealed no leakage. The radiography company was a Louisiana licensee with reciprocity in the State of Utah. Utah Incident Number: 100006 * * * UPDATE FROM GWYN GALLOWAY TO JOE O'HARA AT 1940 EST ON 1/26/12 * * * "During the investigation, DRC [Division of Radiation Control] personnel obtained conflicting statements from QIT [Quality Inspection and Testing Inc] management personnel regarding the employee's termination prior to the incident. Additionally, the driver worked two shifts after QIT management stated he had been terminated. The driver claimed he was not terminated until a number of days after his release from the hospital. Other QIT personnel were not aware the driver had been 'terminated' prior to the incident; therefore, the driver was allowed unescorted access to vehicles and devices containing sources from the day QIT management indicated the driver was terminated until the day the accident occurred (approximately 2 to 3 days). Although initially reported as 'stolen' to DRC personnel, to date, the driver has not been charged with the theft of the vehicle or the source and the DRC does not believe that the employee had been terminated." The state believes that this event does not meet the abnormal occurrence criteria as determined by the Utah Division of Radiation Control. Utah Incident Number: 100006 Notified R4DO(Drake), NMSS(McCartin), FSME EO(Hsueh), and ILTAB(Hahn) * * RETRACTION FROM GWYN GALLOWAY TO JOHN KNOKE AT 1741 EST ON 02/01/12 * * This information was provided by the State of Utah via email. "During the investigation of this event, it was determined that the device was not actually stolen. Additionally, according to NRC Region IV and the U.S. DOT, the event did not meet the criteria for a reportable transportation event. Therefore, we are requesting the Event No. 46380 be retracted and will contact NMED personnel to retract NMED event 100544." Notified the R4DO (Clark), FSME EO (Suber), NMSS EO (Pstrak), ILTAB (Matt Hahn) THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-11-04
46379 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2010-10-29 16:21 | 2010-10-29 20:59 | 2010-10-29 | DEGRADED CONDITION - 71% THROUGH WALL INDICATION ON REACTOR RECIRC NOZZLE "Information from a Phased Array UT [Ultrasonic Testing] examination of RRA-F002A indicates that a linear indication 6.5" long and a maximum depth of 71 % through wall extent (ID [Inner Diameter] connected) exists. The Phased Array UT examination of RRA-F002A was performed as part of scheduled outage activities. "TRM [Technical Requirements Manual] LCO [Limiting Condition for Operation] 3.7.3 for Structural Integrity, Condition B has been entered for the Recirc nozzle/piping. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A) based on the fact that the indications result in a material defect in the primary coolant system which cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws' or ASME Section XI, Table IWB-3410-1, 'Acceptance Standards.' "The licensee informed the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-10-29
46378 | 0 | GE HEALTH CARE |  |  |  |  | 2010-10-26 13:00 | 2010-10-29 15:34 | 2010-10-29 | PACKAGE SURFACE CONTAMINATION IN EXCESS OF REPORTING LIMITS The licensee reported receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than the reporting limits of 220 dpm per cm squared. The package contained returned material, Tc-99m (Technetium), that was being shipped back to the company from a nearby customer in Rodchester Hills, MI. A wipe test performed on the external surface of the package indicated a removable contamination level of 583 dpm per cm squared. A survey inspection of the receiving area did not find any contamination and other survey results were inconclusive. The surface contamination appears to be Tc-99m. No personnel contamination resulted from the incident and the package is being stored in a secured area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2010-10-29
46377 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2010-10-29 14:00 | 2010-10-29 14:11 | 2010-10-29 | OFFSITE NOTIFICATION DUE TO INCREASE IN TRITIUM LEVELS IN A GROUND WATER SAMPLE "This report is being made pursuant to 10 CFR 50.72(b)(2)(xi) for notification to other government agencies. "Dominion North Anna Power Station intends to voluntarily notify state and local agencies regarding an increase in tritium levels in one (1) onsite ground water monitoring sample point. This increase in tritium levels has not exceeded any NRC regulatory dose limits nor has it exceeded the voluntary reporting limits (i.e., 20,000 picoCuries per liter) specified in NEI 07-07 Industry Ground Water Protection - Final Guidance Document. Two (2) adjacent onsite ground water monitoring sample points have not shown a similar increase. None of the eight (8) ground water monitoring sample points surrounding the station have shown any detectable levels of tritium. All indications show that the tritium in the one (1) onsite ground water monitoring sample point has not migrated to the lake or any drinking water sources. "The station continues to monitor, sample and investigate the source of the tritium anomaly. This condition does not present a health hazard to station employees or the general public." Normal tritium levels at the particular sample point are 3-4000 picoCuries per liter. One sample read 16,500 picoCuries per liter. Samples afterwards have return to normal readings. The NRC Resident Inspector has been notified. | 7 | 100 | 0 | 7 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-10-29
46376 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2010-10-29 | 2010-10-29 10:14 | 2010-10-29 | AGREEMENT STATE - DOSE DELIVERED TO WRONG ORGAN The following was received from the state of Ohio via email: "Approximately three (3) weeks prior to therapy, the patient was scanned for extra hepatic shunting through injection of Tc-99m MAA into the hepatic artery per protocol. No shunting to the duodenum was identified. "On Tuesday, October 26, 2010, at approximately 1455 hours, the patient was treated with 3.959 GBq Y-90 TheraSphere microspheres per protocol. A Interventional Radiologist properly placed catheter, and confirmed by second Interventionist Radiologist. "On Tuesday, October 26, 2010, at approximately 1930 hours, a post-procedure scan identified significant activity in the duodenum. Initial estimate indicates dose to duodenum approximately 90 Gy (90 Sv). "Patient has been hospitalized at Cleveland Clinic for observation and possible intervention as a result of dose to the duodenum. "[The] patient has been notified. [The] referring physician has been notified. [A] literature search indicates patient may have developed vascularization post-scan, pre-treatment." Ohio Report #: OH 2010-060 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2010-11-03
46375 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-10-28 12:40 | 2010-10-29 09:39 | 2010-10-29 | DEFECT DISCOVERED IN TUBE STEEL THAT COULD BE USED IN VARIOUS SAFETY RELATED STRUCTUAL APPLICATIONS "On October 28, 2010, Duke Energy completed a reportability determination which concluded that a defect associated with four inch by four inch tube steel with one-half inch wall thickness is reportable under Part 21. The tube steel was procured safety-related from Mackson, Inc. on May 26, 2010. Receipt of the material occurred on June 14, 2010. During construction of the Protected Service Water (PSW) ductbank elevated cable raceway, Craft reported a longitudinal crack in the tube steel, approximately four feet in length, adjacent to a raceway fabrication weld. The crack was located in the manufacturer's longitudinal seam weld in the tube steel. Follow-up investigation and laboratory evaluation revealed that the structural steel tubing in question contains surface breaking flaws located along the centerline of the seam weld which are attributable to lack of fusion that occurred during tubing manufacture. Additional testing of samples from the same heat of material indicated that the seam weld flaw depth varied with some localized areas reaching depths of at least 40 percent through the wall thickness prior to raceway fabrication welding. According to documents received from the supplier, during dedication, the supplier performed chemical, physical and 100 percent visual exam in accordance with their accepted dedication procedures for ASTM A500 for Grade B material. However, the supplied product did not conform to the requirements of ASTM A500 in that the longitudinal butt joint was not welded across its thickness (Reference ASTM A500, Section 6.2). Duke Energy will provide follow-up written notification within 30 days pursuant to Part 21.21(d)(3)(ii). "Initial Safety Significance: None. The defective tube steel utilized in the PSW structure was not placed into service. Tube steel sections of the same heat of material not used in pre-fabrication efforts were scrapped. Those installed were cut out or evaluated for acceptability by Engineering. The failure of this weld significantly impairs the structural properties of the hollow structural section. The generic implications associated with the potential to use these structural members in various nuclear safety-related applications at this site and at other stations results in a substantial safety hazard were it to remain uncorrected. "Corrective Action(s): 1. Notified supplier, Mackson, Inc. 2. Re-worked all uses of the defective structural tube steel. 3. Developed additional, required testing for safety -related tube steel." The supplier (Mackson, Inc) indicated to Oconee that no other nuclear power plants have received this type of tube steel from Mackson. Oconee also has concluded that the condition is confined to only one heat of the tubing used onsite. All the tube steel of this heat has been either disposed of, removed, or verified acceptable. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2010-10-29
46374 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-10-28 17:51 | 2010-10-28 20:25 | 2010-10-28 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE LEAK FROM UNDERGROUND PIPING "On October 28, 2010, at 1740 hours, the plant entered the Off-Normal Instruction for spills and unauthorized discharges. At 1751 hours, notification of a sodium hypochlorite spill was made to the U.S. Environmental Protection Agency (EPA), National Response Center. At the time of the event, the plant was in Mode 1 at 100% power. The sodium hypochlorite spill is believed to be the result of a leak in an underground piping supply line to the Emergency Service Water pump house. The leak is estimated to be approximately 130 gallons of a 12.5% Sodium Hypochlorite (Bleach) solution (80 gallons in a 24 hour period is the reportable quantity). The associated chlorination systems have been isolated, and current storage tank level is stable, indicating no more leakage in progress. "Additionally, the Ohio EPA: State Emergency Response Commission, Perry Township Fire Department, Lake County Emergency Planning Committee, and the U.S. Coast Guard were notified in accordance with plant procedures. This event is also being reported in accordance with the Operating License, Appendix B, Environment Protection Plan, which states in part, 'Any occurrence of an unusual or important event that indicates or could result in significant environmental impact causally related to plant operation shall be recorded and reported to the NRC within 24 hours followed by a written report ..' Specifically, ' ..unanticipated or emergency discharge of waste water or chemical substances.' The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2010-10-28
46373 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-10-27 11:07 | 2010-10-27 16:25 | 2010-10-28 | SPENT FUEL STORAGE RELATED DEFECT - CASK LEAKAGE RATE GREATER THAN TECHNICAL SPECIFICATION "On 10/27/10, at 1107 [EDT], troubleshooting of Independent Spent Fuel Storage Installation (ISFSI) Cask TN-68-01 identified that a helium leak exists in the cask lid sealing area at a leak rate greater than allowed by ISFSI Cask Technical Specification Section 3.1.3, Cask Helium Leak Rate. TS 3.1.3 limits the Cask Helium Leak Rate to 1.0 E-O5 ref-cc/sec. The cask was in LOADING OPERATIONS and is currently located within the [Peach Bottom Atomic Power Station] PBAPS Unit 2 containment building. Preliminary review indicates that a leak exists in the Cask Main Lid Outer Closure Seal. The cask will be repaired and tested prior to returning the cask to the Independent Spent Fuel Storage Installation (ISFSI). No release of radiation occurred as a result of this issue. "This report is being submitted pursuant to 10CFR 72.75(c)(2) as a result of a reduction in the effectiveness of the cask confinement system. "The Certificate of Compliance for this cask is 1027 (Amendment 0)." The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SPENT FUEL, HLW OR RX-REL GTCC RED. EFECT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 72.75(c )(2) |  |  |  | 0 | 2010-10-28
46372 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2010-10-28 10:45 | 2010-10-28 15:21 | 2010-10-28 | STANDBY LIQUID CONTROL SYSTEM TEST TANK SEISMIC ANALYSIS FAULTY "This report is being made pursuant to 10CFR50.72(b)(3)(v), Event or Condition that could have prevented fulfillment of a Safety Function. As part of a recent NRC Component Design Basis Inspection (CDBI), the seismic analysis of the Unit One and Unit Two Standby Liquid Control (SBLC) system test tanks was questioned. During the formal operability determination process initiated on 10/27/10, Engineering was verifying design data and calculations. During this review, on 10/28/10, Engineering determined that the historical calculation used the wrong formula in determining the test tank's natural frequency. The consequence is that if the test tank is filled with water, the possibility exists that the test tank could fall over or collapse during a seismic event and adversely affect adjacent safety-related items (i.e. SBLC). Calculations confirm that empty test tanks are seismically qualified. "The SBLC test tanks on both units had been drained of water on 10/27/10 and thus both Unit One and Unit Two SBLC systems are fully operable at this time." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT UNCNTRL RAD REL |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2010-10-28
46371 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2010-10-28 | 2010-10-28 12:06 | 2010-10-28 | AGREEMENT STATE REPORT - IOWA LICENSEE LOST A STATIC ELIMINATOR The Iowa Department of Public Health provided the following report via e-mail: "The Iowa Department of Public Health was informed on 10/28/10 that Registrant number 3272-1-0403, Plasti-Paint, lost a Static Eliminator (SN: A2GV069)." The radionuclide is a 0.01 Ci sealed source of Po-210. The Static Eliminator was manufactured by NRD, Inc, Model number: P-2021-8201. The cause of this loss was human error. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2010-11-02
46370 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2010-10-28 07:59 | 2010-10-28 07:59 | 2010-10-28 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) OOS "Beginning at approximately 0800 hours EDT on October 28, 2010, Perry Plant personnel will be taking the plant Integrated Computer System (ICS) out of service for planned maintenance. During the time ICS is out of service, the Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS), and the automatic mode calculation of the Computer Aided Dose Assessment Program (CADAP) will be unavailable. The computer outage is scheduled for six hours. "In the event of an emergency, plant parameter data will be orally transmitted to the facilities through the Status Board Ring Down circuit with back-up [using] the Private Branch Exchange, Off-Premise Exchange, and various redundant intra-facility circuits throughout the emergency facilities. The dose assessment function will be maintained during the out of service time period by manual input of data into CADAP and, if required, by manual calculation. The ability to open and maintain an 'open line' using the Emergency Notification System will not be affected and will be the primary means of transferring plant data to the NRC as a contingency until the ERDS can be returned to service during the period of unavailability. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(xiii), as a condition that results in a major loss of offsite communications capability. A follow-up notification will be made when the maintenance activities are completed and the equipment is restored. The NRC Resident Inspector has been notified." * * * UPDATE AT 1301 EDT ON 10/28/10 FROM GLENDON BURNHAM TO DONG PARK * * * At 1100 EDT, the plant ICS has been returned to service and functioning normally. The NRC Resident Inspector has been informed. Notified R3DO (Skokowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-28
46369 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2010-10-27 | 2010-10-27 18:34 | 2010-10-27 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISOR A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2010-10-27
46368 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2010-10-27 12:22 | 2010-10-27 17:05 | 2010-12-17 | UNIT COMMENCED SHUTDOWN AFTER DECLARING CONTAINMENT SPRAY INOPERABLE "During pressure drop testing of the backup nitrogen supply for HCV-345 (Containment Spray Header isolation valve) the accumulator failed its test. This renders HCV-345 inoperable. HCV-344 the opposite header isolation valve also has an air leak that appears to be of similar magnitude to the leak on HCV-345. Fort Calhoun Station is conservatively considering both valves inoperable and has entered technical specification 2.0.1 which requires shutting the plant down to hot standby within 6 hours. The plant shutdown began at 1513 CDT. Repair efforts are underway on HCV-345 and HCV-344." The leakage on both valves was identified by systems engineering during testing. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1756 EDT ON 10/27/10 FROM AARON CHLADIL TO S. SANDIN * * * At 1647 CDT, the licensee exited technical specification 2.0.1 after declaring HCV-344 operable. The Unit is currently at 74% power. The licensee will stabilize power at 70% and then commence power escalation. The licensee informed the NRC Resident Inspector. Notified R4DO (Proulx). * * * RETRACTION FROM ERICK MATZKE TO HOWIE CROUCH AT 1155 EST ON 12/17/10 * * * "Following the original notification, the Fort Calhoun Station reviewed and reanalyzed the acceptance criteria for the subject valve air accumulators. The analysis determined that the valves had been and were operable during the event. Therefore, the report under 10CFR50.72(b)(3)(v)(D) is being retracted." The licensee has notified the NRC Resident Inspector. Notified R4D0 (Howell). | 81 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2010-10-27
46367 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2010-08-31 17:37 | 2010-10-27 16:39 | 2010-10-27 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO A VOLTAGE TRANSIENT "This telephone report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition caused by an invalid signal that resulted in an automatic Group 6 isolation. On August 31, 2010 at 1737 CDT, Group 6 of Primary Containment Isolation System (PCIS) actuated. This resulted in completion of Secondary Containment isolation, initiation of the Standby Gas Treatment System and Control Room Emergency Filtration System. An invalid signal occurred apparently as a result of a voltage transient on the Nebraska City 345kV line. This was from a 3-phase fault to ground due to a structural failure during a severe thunder storm with high winds. "The equipment associated with the Group 6 isolation functioned successfully and the isolation was complete. The Group 6 PCIS was reset. Cooper Nuclear Station operators reviewed the parameters that would cause a Group 6 trip signal (i.e. reactor water level, drywell pressure, reactor building radiation) and determined there were no valid conditions that would have caused the isolation. "This event was most likely due an act of nature, thus no corrective actions were required." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2010-10-27
46366 | -1 | COMMUNITY HOSPITAL |  |  |  |  | 2010-10-26 | 2010-10-27 15:45 | 2011-01-25 | TWO MEDICAL EVENTS INVOLVING RECEIVED DOSE LESS THAN PRESCRIBED DOSE During an on-site NRC Inspection on 10/26/10, two (2) medical events were identified both involving a delivered dose less than the prescribed dose following implant of Palladium-103 seed for prostate therapy. Specific details as follows: First Medical Event Preplanning date: 08/26/09 Post planning date: 09/03/09 D-90 (dose received by 90% of the prostate volume): 72% Underdose: 28% Prescribed: Palladium-103, 156U consisting of 65 seeds, 2.4U/seed Second Medical Event Preplanning date: 12/08/09 Post planning date: 12/29/09 D-90 (dose received by 90% of the prostate volume): 64% Underdose: 36% Prescribed: Palladium-103, 173U consisting of 74 seeds, 2.4U/seed Both underdoses are attributed to prostate swelling. The physician reviewing the results concluded that there was no adverse impact on either patient. The licensee will continue reviewing medical records to identify any additional occurrences of this nature. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM MIREL PALAMARU TO VINCE KLCO ON 1/25/11 AT 1829 EST * * * Based on a post evaluation by the licensee's Radiation Safety Officer and physicians, all delivered dose came within 20% of overall prescribed dose. Thus, this is not considered a medical event. Notified the R3DO (Stone), and FSME (McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2010-11-02
46365 | 0 | CONSTRUCTION TESTING AND ENGINEERIN |  |  |  |  | 2010-10-26 16:15 | 2010-10-26 16:30 | 2010-10-26 | TROXLER MOISTURE DENSITY GAUGE STOLEN At approximately 1615 EDT on 10/26/10, a vehicle containing a Troxler Moisture Density Gauge, Model #3440, S/N 34482, with 8 mCi Cs-137 and 40 mCi Am-241/Be was stolen at 1800 Alabama Ave, SE, DC. The RSO reported the theft to the DC Police who are on-scene. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-10-26
46364 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2010-10-26 14:40 | 2010-10-26 15:25 | 2010-10-26 | SECURITY REPORT DUE TO ADVERSE WEATHER Safeguards system degradation related to the monitoring and detection of PA boundary. Compensatory actions taken. Call the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-10-26
46363 | 0 | EVONIK DEGGUSSA CORP |  |  |  |  | 2010-10-06 10:00 | 2010-10-26 11:50 | 2010-10-26 | IMPROPERLY DISPOSED OF TRITIUM SIGNS Notified by the licensee that two tritium exit signs were improperly disposed of as trash. The signs were manufactured on April/1999 and the tritium gas was in sealed tubes. The sign manufacturer was NRD-LLC\Penteco and the original source strength was 25 Ci for each sign. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2010-10-26
46362 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2010-10-25 22:00 | 2010-10-25 22:30 | 2010-10-25 | CONTAINMENT LINER CORROSION DEGRADATION "This report is made in accordance with 10 CFR 50.72(b)(3)(ii) as a condition resulting in a serious degradation of the Containment liner. During a visual inspection on 10/22/10, corrosion was found in the containment sump liner on Unit 3, A more detailed inspection was performed on 10/24/10 after the corroded area was cleaned. Evaluation of the inspection results has determined that the corrosion is greater than allowed by the ASME Code, including through wall areas, and requires repair. At this time, it is not known whether any leakage caused by the through-wall condition would have resulted in exceeding the containment allowed leakage limit. Unit 3 is currently in Mode 5 preparing to return to service following refueling. The corroded areas will be repaired prior to entering Mode 4." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2010-10-25
46361 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-10-24 | 2010-10-25 13:30 | 2010-10-25 | SHUTTER FOUND PARTIALLY STUCK OPEN ON A FIXED NUCLEAR GAUGE The following information was received from the State of Texas via email: "On October 25, 2010, the licensee reported that while making preparations to perform plant maintenance, the shutter on a Ohmart Corporation model SH-F2-45 nuclear gauge containing 60 milliCuries (original activity) of Cesium (Cs)-137 was found to be stuck in a partially opened position. The licensee stated that they are going to shield the source to reduce the dose rate to below 2 millirem/hour, remove it form the vessel, and lock it in their Radioactive Material storage building. No significant exposure has occurred due to this event. The licensee has contacted the manufacture for repairs or replacement of the gauge. The cause for the event is under investigation. Additional information will be provided as it is received IAW SA 300." Texas Incident #: I-8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-10-28
46360 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-10-25 07:00 | 2010-10-25 12:04 | 2010-10-25 | CONTRACT NON-LICENSED SUPERVISOR TESTED POSITIVE FOR A CONTROLLED SUBSTANCE A non-licensed contract employee supervisor had a confirmed positive for a controlled substance during a random fitness for duty test. The employee's unescorted access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2010-10-25
46359 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2010-10-24 16:41 | 2010-10-24 18:09 | 2010-10-24 | AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP RESULTING FROM A LOW CONDENSER VACUUM "At 1641 EDT 10/24/10, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip, caused by a loss of [condenser] vacuum. The scram was uncomplicated, Control Rod 10-35 did not fully insert on scram and was manually inserted from position 38. The lowest reactor vessel water level reached was 137 inches, and as expected, HPCI, RCIC. & SRVs did not actuate. Reactor water level is being controlled in the normal band using the CRD [Control Rod Drive] and reactor feedwater systems. All isolations and actuations for reactor water level 3 occurred as expected. "The loss of condenser vacuum is under investigation. "All Emergency Core Cooling Systems and EDG's [Emergency Diesel Generators] were operable, and no safety related equipment was out of service. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), as an event that results in actuation of the reactor protection system (RPS) when the reactor is critical. "Decay heat is being removed through the main turbine bypass valves to the main condenser." Electrical offsite power lineups are normal. Reactor pressure is 882 psig and reactor temperature is 515 degrees F (NOP and NOT). The reactor is stable in mode 3. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-10-24
46358 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2010-10-24 12:34 | 2010-10-24 17:19 | 2010-12-17 | 'A' TRAIN RHR INOPERABLE DUE TO TEMPERATURE SWITCH FAILURE ON 'A' CONTROL ROOM CHILLER "On 10/24/2010, while in Mode 5 in natural circulation cooling and no fuel movement in progress, the 'A' Control Room Chiller (AK400) tripped apparently due to an equipment failure of a temperature switch. This system was providing cooling for the Safety Auxiliaries Cooling System (SACS) room coolers. This caused the 'A' train of SACS and 'A' Train of Residual Heat Removal (RHR) to be administratively declared inoperable with the remaining train out of service for maintenance. As a result of the inoperable systems, the ability to remove residual heat could have been prevented. The 'A' RHR train, the alternate 'C' RHR train and the 'A' SACS Loop remained continuously available. No personnel were injured." The licensee is in Technical Specification 3.9.11.1 Shutdown Cooling and 3.8.1.2 for SACS inoperable. The Emergency Diesel Generators (EDG) are available but inoperable as a result of SACS being inoperable. Offsite power is not affected and plant risk remains 'Green'. There were no significant events on-going at the time of the event. The licensee is bench testing a replacement switch at this time, and the chiller has been returned to service. The licensee is maintaining natural circulation and ensuring the availability of redundant RHR once a shift. The NRC Resident Inspector and Lower Alloyways Township have been notified. * * * RETRACTION FROM J.R. TRAUTVETTER TO J. KNOKE AT 1015 EST ON 12/17/10 * * * Licensee is retracting this event based on the following: "Hope Creek Technical Specification 3.9.11 action statement (a) for no OPERABLE RHR loops is to demonstrate the operability of at least one alternate method of decay heat removal within one hour and once per 24 hours thereafter. Prior to and throughout the event, decay heat, removal was maintained via the Fuel Pooling Cooling system through the available heat exchangers with core circulation maintained by natural circulation. Use of the Fuel Pool Cooling for decay heat removal is recognized in station procedures as an alternate method of decay heat removal in technical specification action statement (TSAS) 3.9.11. This retraction is to clarify that the inoperable systems did not prevent the ability to remove residual heat. The outage risk assessment remained Green throughout the period that both RHR loops were inoperable. "There was no loss of safety function, and therefore, the event is not reportable as an event that prevents the fulfillment of a safety function in accordance with 50.72 (b)(3)(v)(B)." Notified the R1DO (Daniel Holody) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2010-10-24
46357 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2010-10-24 06:00 | 2010-10-24 11:34 | 2010-10-24 | AGREEMENT STATE REPORT - RADIOGRAPHER TRUCK IN ROLLOVER ACCIDENT A radiographer from Quality Inspection and Testing, Inc was involved in a single vehicle accident 18 miles west of Vernal, Utah on highway 40. According to witnesses, the truck rolled numerous times. The state police arrived, secured the highway, contacted state radiation control, and surveyed the area. The results of the survey indicated no spread of contamination or radiation levels above background. The SPEC Model 150 radiography camera S/N 1195 containing 40 Curies of Ir-192 was undamaged and placed into the custody of another representative of Quality Inspection and Testing Inc., who arrived on the scene at the request of the state. The driver survived the accident. The radiography company is a Louisiana licensee with reciprocity in the State of Utah. Utah Incident Number: 100005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2010-10-27
46356 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2010-10-21 09:12 | 2010-10-23 14:07 | 2010-10-23 | AGREEMENT STATE REPORT - DAMAGE TO TROXLER PORTABLE DENSITY GAUGE A Troxler portable density gauge was run over by a forklift at a construction site. The source rod was retrieved into the gauge by the RSO. The damaged gauge was surveyed and then the gauge was removed for transport to the company office. The construction site was surveyed to ensure both sources were in the gauge. The licensee is reviewing their procedures to determine what can be done to reduce the risk of this type of incident happening again. The density gauge is a Model 3430 Troxler with a nominal 8 mCi Cs-137 gamma source and a 40 mCi Am-241:Be neutron source. North Dakota Incident #: ND10005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2010-10-27
46355 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2010-10-23 00:45 | 2010-10-23 02:54 | 2010-10-23 | HPCI DECLARED INOPERABLE DUE TO POWER SUPPLY FAILURE "The High Pressure Coolant Injection (HPCI) system was declared inoperable due to an instrument power supply failure. The cause of the failure is under investigation. "All other ECCS, Emergency Diesels, and Reactor Core Isolation Cooling (RCIC) are operable." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2010-10-23
46354 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2010-10-22 17:51 | 2010-10-22 23:05 | 2010-12-03 | POTENTIAL INOPERABILITY OF OSCILLATION POWER RANGE MONITORS "At 1751 [CDT] on Oct 22, 2010, Dresden Nuclear Power Station (DNPS) determined that current Oscillation Power Range Monitors (OPRM's) setpoints, as outlined in the Core Operating Limits Report (COLR), for Dresden U2 are non-conservative. This renders the Technical Specification (TS) function of the OPRM's in the Reactor Protection System (RPS) inoperable. "This event was initiated as a result of notification by Westinghouse Nuclear Fuels (NF-BEX-10-157) that an error exists in the McSLAP computer code which affects the Safely Limit Minimum Critical Power Ratios (SLMCPR) for Dresden. Currently the COLR and installed, amplitude setpoint (Sp) is 1.13 and the confirmation count setpoint (Np) is 15. This is required to be adjusted to 1.12 (Sp) and 14 (Np). "Alternative methods to detect and suppress thermal hydraulic instabilities were initiated as required by Technical Specifications. "This non-conservative computer code error could potentially have prevented fulfillment of the OPRM system's safety function and is therefore reportable per 10 CFR 50.72(b)(3)(v)(A), 'An event or condition that could have prevented the fulfillment of a safety function - shutdown the reactor and maintain it in a safe shutdown condition.'" Corrective actions include the following: "1. Revise U2 Core Operating Limit Report (COLR) to reflect correct values as determined by Westinghouse Nuclear Fuels Letter (NF-BEXÀl0-157). "2. Adjust OPRM setpoints to comply with COLR values." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM RILEY RUFFIN TO ERIC SIMPSON AT 1207 EST ON 12/3/10 * * * "On October 22, 2010, Dresden Nuclear Power Station was notified by Westinghouse that an error in McSlap computer code resulted in a non-conservative MCPR safety limit. The preliminary results of the Westinghouse evaluation concluded that the setpoints for the Oscillation Power Range Monitors were also non-conservative. As a result of the notification, Dresden declared all channels of OPRM inoperable and took the required action of the plant's technical specifications. This was considered a loss of function. "This condition was reported as a condition that could have potentially prevented the fulfillment of the OPRM system's safety function in accordance with 10 CFR 50.72(b)(3)(v)(A), an event or condition that could have prevented the fulfillment of a safety function - shutdown the reactor and maintain it in a safe shutdown condition. "However, subsequent evaluation of the preliminary result determined that the original conclusions were overly conservative and the OPRM setpoints did not require revision. Based on the later evaluation, the function of the OPRMs was not adversely impacted by the installed setpoints. Thus, the system was always capable of performing its intended safety function. "Therefore the notification associated with Event Number 46354 is being retracted." The licensee notified the NRC Resident Inspector. The R3DO (Ring) was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2010-10-22
46353 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2010-10-22 10:58 | 2010-10-22 16:52 | 2010-10-27 | SPENT FUEL STORAGE RELATED DEFECT - CASK LEAKAGE RATE GREATER THAN TECHNICAL SPECIFICATION "On 10/22/10, at 1058 EDT, a troubleshooting of Independent Spent Fuel Storage Installation (ISFSI) Cask TN-50-A indicated that a leak existed in the cask lid sealing area at a rate greater than allowed by ISFSI Cask Technical Specification (TS) Section 3.1.3, Cask Helium Leak Rate. TS 3.1.3 limits the Cask Helium Leak Rate to 1.0 E-05 ref-cc/sec. The cask is currently in unloading operations and is located within the Peach Bottom Atomic Power Station Unit 3 containment building. Preliminary review indicates that a leak exists at the weld plug that provides sealing of the drilled interseal passageway associated with the drain port penetration of the cask lid. This leak effectively provides a bypass of the main lid outer confinement seal. "This report if being submitted pursuant to 10CFR72.75(c)(1) as a result of a material defect in a weld in the cask main lid. This report is also being submitted pursuant to 10CFR72.75 (c) (2) as a result of a resolution in the effectiveness of the cask confinement system. "The Certificate of Compliance for this cask is 1027 (Amendment 1). "The NRC Resident Inspector has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SPENT FUEL, HLW, RX GTCC DEFECT | SPENT FUEL, HLW OR RX-REL GTCC RED. EFECT |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 72.75(c )(1) | 72.75(c )(2) |  |  | 0 | 2010-10-22
46352 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2010-10-22 06:36 | 2010-10-22 09:46 | 2010-10-22 | MANUAL REACTOR TRIP DURING PHYSICS TESTING DUE TO PROBLEMS WITH THE ROD CONTROL IN HOLD OUT SWITCH "On 10/22/2010 at 0636 hours, North Anna Unit-1 reactor was manually tripped during physics testing and 1-E-0 was entered due to problems with the Rod Control In Hold Out Switch. The out direction of the switch was not functioning properly and the reactor was tripped to put the plant in a condition to perform maintenance. All control rods fully inserted into the reactor core. This was an uncomplicated reactor trip with no automatic ESF actuation required. "Unit 1 is currently stable at normal operating temperature and pressure in MODE 3 (Hot Standby)." The plant electrical line-up is normal. Decay heat removal is via the steam dumps. Notification will be made to the local county administrator's office. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2010-10-22
46351 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2010-10-21 | 2010-10-21 17:58 | 2010-10-21 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER INOPERABLE The following was received from the State of Texas via e-mail: "On October 21, 2010, the Agency [State of Texas] received a 'Notice of reciprocity' from Berthold Technologies. The notice stated that a Berthold Technologies service representative would be replacing the shutters on two gauges at the licensee's (International Paper Company) facility on October 22, 2010. The Agency contacted the licensee and asked to speak with the Radiation Safety Officer (RSO). The Agency was forwarded to the RSO's voicemail box and left a message. The Agency then contacted one of the licensee's employees whose information was obtained from the 'Notice of Reciprocity.' The employee then reported that the licensee had experienced a shutter failure. "The licensee stated that on Monday, October 18, 2010, another licensee properly authorized by the Agency [State of Texas] to remove the gauges came to the licensee's facility to remove the gauge from the pipe it was fixed to. The gauge was manufactured by Berthold Technologies (Model: LB7440; Serial Number: 1335) and it houses a 30 milliCurie Cesium (Cs) 137 source (Serial Number: 1335- 5-89). The gauge was removed so that the licensee could perform maintenance on the pipe. The licensee stated that the shutter was hard to turn at that time, but the shutter properly closed prior to the authorized person removing the gauge. On Wednesday, October 20, 2010, the authorized person returned to reattach the gauge and attempted to open the shutter, and the shutter would not open. The licensee then stated that they contacted Berthold Technologies to repair the shutter that failed, as well as another shutter on different gauge that was difficult to operate. The shutters are scheduled to be repaired on Friday, October 22, 2010. The RSO was later contacted and he agreed to submit a written report to the Agency within thirty days." TX Incident No. I-8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2010-10-26
46350 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2010-10-21 11:01 | 2010-10-21 11:21 | 2010-10-21 | SAFEGUARDS REPORT - DOCUMENT CONTROL VULNERABILITY DETECTED Document control related safeguards vulnerability detected. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-10-21
46349 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2010-10-20 10:30 | 2010-10-20 14:08 | 2010-10-20 | LOOSE SURFACE CONTAMINATION FOUND ON OUTSIDE OF RADIOPHARMACEUTICAL PACKAGING "The package was received today (October 20, 2010) at about 10:00 AM EDT by the VA Maryland Healthcare System, Baltimore, Maryland. "A wipe test performed on the external surface of the package indicated a removable contamination level of about 1800 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. "The package contained a unit dosage of around 12 milliCuries of Fluorine-18 labeled radiopharmaceuticals and was shipped from Cardinal Health, Baltimore, Maryland. The vendor/shipper also serves as the delivery carrier. The VA nuclear medicine staff immediately notified staff at Cardinal Health about the contaminated package around 10:30 AM EDT. "As corrective actions, additional wipe samples were taken in the VA nuclear medicine department, and the indication was that the package was most likely inadvertently cross-contaminated by a technologist who had handled similar materials just before checking in the package. Specifically, a contaminated absorbant pad was identified near the check-in area. The healthcare system Radiation Safety Officer (RSO) indicated that additional area and personnel surveys were performed to ensure that residual contamination in the area was identified and addressed appropriately. Also, the RSO reinstructed the technologists involved in the incident on proper material handling techniques to avoid future cross-contamination of items and packages. Additional reinstruction of technologists is planned. "As additional follow-up information, the RSO spoke to the pharmacy supervisor at Cardinal Health around 12:00 PM EDT and again at 1:30 PM EDT and learned that the driver and the vehicle were surveyed by the vendor and found to be free of contamination. Also, the vendor received no other reports of contaminated packages from other customers. This information supports a conclusion that the contamination was most likely from cross-contamination after package receipt. "We will notify our NRC Project Manager at NRC Region III of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | MD | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2010-10-20
46348 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2010-10-20 | 2010-10-20 12:54 | 2011-02-15 | PART 21 - CRACK INDICATIONS IN MARATHON CONTROL ROD BLADES The following was received via facsimile: "A recent inspection of near 'End-of-Life' Marathon Control Rod Blades (CRB) at an international BWR/6 has revealed crack indications. The CRB assemblies in question were manufactured in 1997. GE Hitachi Nuclear Energy (GEH) continues to investigate the cause(s) of the crack indications. Once the cause of the crack indications is determined, GEH will evaluate the nuclear and mechanical lifetime limits of the Marathon Control Rod Blade design in light of the new inspection data, and make revised lifetime recommendations, if necessary. "This 60-day interim notification, in accordance with 10CFR Part 21.21(a)(2), is sent for all plants that are D lattice, BWR/2-4 or S lattice, BWR/6 plants. Since there have been no reported cracking occurrences in C lattice assemblies to date, these CRBs are tentatively eliminated from the investigation. C lattice, BWR/4-5 plants have been included on Attachment 2 for identification. Should the results of the investigation implicate the C lattice plants, the final resolution to this 10CFR Part 21 evaluation will include the C lattice plants." The D lattice and S lattice plants in the US that are affected by this notification include Nine Mile Point, Unit 1; Millstone, Unit 1; Fitzpatrick; Pilgrim; Vermont Yankee; Grand Gulf; River Bend; Clinton; Oyster Creek; Dresden, Unit 2; Dresden, Unit 3; Peach Bottom, Unit 2; Peach Bottom, Unit 3; Quad Cities, Unit 1; Quad Cities, Unit 2; Perry, Unit 1; Duane Arnold; Cooper; Monticello; Brunswick, Unit 1; Brunswick, Unit 2; Hatch, Unit 1; Hatch, Unit 2; Browns Ferry, Unit 1; Browns Ferry, Unit 2; and Browns Ferry, Unit 3. * * * UPDATE FROM DALE PORTER TO ERIC SIMPSON VIA FAX AT 1556 ON 12/1/2010 * * * "In August 2010, GE Hitachi (GEH) performed the planned inspection of four near 'End-of-Life' CRBs at 'Plant O.' The inspection revealed crack indications on all four Control Rod Blades (CRBs). The observed cracks are much more numerous, and have more material distortion than previously observed. Further, the cracks occur at a much lower reported local B-10 depletion than previously observed, with cracking predominantly starting at approximately 40% local depletion, whereas previous inspections observed cracking only above 60% local depletion. "The cracks at 'Plant O' are also more severe, in that they resulted in missing capsule tube fragments from two of the inspected CRBs. A lost parts analysis performed for 'Plant O' determined that there is no negative affect on plant performance due to the missing tube fragments. "At this point in the investigation, no causal or contributing factors unique to the 'Plant O' CRBs, nor their operation, has been identified. "Including the inspections at 'Plant O,' GEH has now completed the visual inspection of 97 irradiated Marathon CRBs, with 10 showing crack indications. As 'Plant O' is an S lattice design, all crack indications are still confined to D and S lattice applications, with no crack indications on C lattice designs. When considering only D and S lattice applications that are near 'End-of-Life' depletion limits, 10 of 23 control rod inspections have revealed crack indications." Notified R1DO (Schmidt), R2DO (Shaeffer), R3DO (Ring), R4DO (Powers) and Part 21 Group. * * * UPDATE FROM DALE PORTER TO JOHN SHOEMAKER VIA FACSIMILE AT 0934 EST ON 02/15/2001 * * * "Subject: Part 21 Reportable Condition Notification: Design Life of D and S Lattice Marathon Control Blades "GE Hitachi Nuclear Energy (GEH) has completed its evaluation of the cracking of Marathon Control Rod Blades (CRB) at an international BWR/6. This issue was initially reported on October 20, 2010 as GEH letter MFN 10-327 (Reference 1). Additional information was provided on December 1, 2010 as GEH letter MFN 10-351 (Reference 2). "GEH has determined that the design life, of D and S lattice Marathon Control Blades may be less than previously stated. The design life if not revised, could result in significant control blade cracking and could, if not corrected, create a substantial safety hazard and is considered a reportable condition under 10 CFR Part 21.21 (d). Marathon C lattice Control Blades are not affected by this condition. The information contained in this document informs the NRC of the conclusions and recommendations derived from GEH's investigation of this issue." Notified R1DO (Ferdas), R2DO (McCoy), R3DO (Kozak), R4DO (Gaddy) and Part 21 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2010-10-20
46347 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2010-10-19 21:08 | 2010-10-19 21:14 | 2010-10-20 | FAILURE OF PLANT PROCESS COMPUTER DISPLAYS AND SPDS TO UPDATE "This 8-hour non-emergency report is being made based upon requirements of 10 CFR 50.72(b)(3)(xiii) which states that the licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of: 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).' "At 1308 EDT on Tuesday, October 19, 2010, the Nine Mile Point Unit 1 Control Room received the annunciator for Process Computer Trouble. At the same time, all Process Computer displays stopped updating, including the Safety Parameter Display System (SPDS). "All Control Room panel indicators and annunciators continue to respond properly providing operators with non-computer based emergency assessment capability. An additional Plant Operator has reported to shift in accordance with Technical Specification 6.2.2.a for minimum shift complement with the process computer out of service. "An update to this notification will be made after repairs are completed and the SPDS is returned to service." The licensee informed the NRC Resident Inspector. * * * UPDATE AT 0802 EDT ON 10/20/10 FROM JOHN DRISCOLL TO DONG PARK * * * "On Wednesday, October 20, 2010, repairs were completed and at 0439 EDT, the Plant Process Computer (PPC) was successfully restarted. Upon restart, SPDS was verified operable." The licensee informed the NRC Resident Inspector. Notified R1DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2010-10-19
46346 | -1 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2010-10-19 15:15 | 2010-10-19 20:09 | 2010-10-21 | VALID SPECIFIED SYSTEM ACTUATION "On October 19, 2010, at about 1515 PDT, SONGS Unit 3 RPS channels 'B' and 'D' were tested for maintenance. During this testing, both channels were powered off, which brought in LPD/DNBR [local power density/departure from nucleate boiling] trips on both channels. There are no applicable Technical Specifications required for these RPS channels in Mode 5. "Southern California Edison(SCE) is reporting this occurrence as a valid actuation of RPS in accordance with 10 CFR 50.72(b)(3)(iv)(a). "SCE has taken actions to restore both channels 'B' and 'D' of RPS and cleared the RPS trip signal. At the time of this occurrence, Unit 2 was at approximately 100% power and Unit 3 was in a Steam Generator Replacement Outage, Mode 5, shutdown and cooldown with the RCS open, proceeding to Mode 6." The NRC Resident Inspector has been notified. * * * RETRACTION FROM DENNIS MORRIS TO PETE SNYDER AT 0045 EDT ON 10/21/10 * * * "On October 19, 2010, SCE reported (Event No. 46346) a valid actuation of the Reactor Protection System (RPS) in accordance with 10 CFR 50.72(b)(3)(iv)(A). Upon further review, SCE determined the actuation was invalid and is retracting the notification. "Maintenance and surveillance testing was being conducted by Computer Technicians on the Core Protection Calculator [CPC] Channels 'A' and 'D', respectively, following station procedures. De-energizing the CPC channels was expected to bring in an RPS trip signal. The process to disable the control room RPS alarms had not as yet, been completed by the Instrument and Controls group when the CPCs were de-energized by procedure, actuating the RPS logic and causing the control room alarms. "The actuation is considered invalid, as the equipment that would have been actuated by the trip safety function was previously de-energized and removed from service for the refueling outage. The Unit 3 reactor was in Mode 5, with the reactor trip breakers open, and control rods inserted. Unit 2 reactor remains at 100% power." The licensee notified the NRC Resident Inspector. Notified R4DO (V.Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2010-10-19
46345 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2010-10-19 08:42 | 2010-10-19 17:45 | 2010-10-19 | FITNESS FOR DUTY - POSITIVE TEST FOR ALCOHOL OF CONTRACT SUPERVISOR. "A non-licensed contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2010-10-19
46344 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2010-10-15 08:00 | 2010-10-19 16:00 | 2010-10-19 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was received from the Arizona Radiation Regulatory Agency via email: "Date and Time Agency Notified: 8:00 AM, 10/15/2010. "Type of Incident: Missing Radioactive Material. "Device Manufacturer, Model No. and Serial No.: Humbolt 5001C, SN 1143. "Sources and Activity: Cs-137, 10mCi; Am-241:Be, 40mCi. "Date last seen or used: 12/03/2007. "Circumstances: The missing gauge was in need of servicing or replacement therefore it was removed from service. The program that generated the inventory list for all equipment, omits the equipment removed from service. The licensee discovered this part of the program on 10/14/2010. "Conclusion: The gauge could have been removed from licensee control any time after 12/03/2007. "The Agency continues to investigate the actions of the licensee and timeliness of reporting the missing device. "The U.S. NRC and the Arizona Governor's office have been notified of this event. "Press coverage is anticipated." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2010-10-22
46343 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2010-10-18 | 2010-10-19 13:07 | 2010-10-19 | AGREEMENT STATE REPORT - STUCK SOURCE The following report was received via fax: "This memo is to serve as a preliminary report for an incident with a Colorado radiography licensee. Utah Inspection, LLC (Colorado license 1043-01) reported to the [Colorado Department of Health (CDH)] on October 18, 2010 a stuck source/source disconnect for a radiography source. The job site was at a gas compressor station in De Beque, Colorado. Initial reports indicate the source was approximately 60 Ci of Ir-I92. "Utah Inspection contacted the CDH at approximately 2:30 pm on October 18,2010 to report the incident. The licensee reported that while performing a radiography shot, the camera slipped off a wet pipe and landed on the guide tube causing a crimp in the tube which prevented the source from being retracted. The licensee extended the boundaries around the source and maintained surveillance of the source. The licensee contracted with a local Radiation Safety Officer trained in source retrieval activities and was able to retract the source to the shielded position at approximately 7:15 pm on October 18, 2010. "A member of the CDH responded to the incident scene as the retraction efforts were being completed. The RSO contracted for the source retrieval reported an estimated 138 mrem whole body, and the radiographer estimated doses at 50 mrem whole body for himself and 25 mrem whole body for his assistant. Individual overexposure does not appear to be an issue at this point for this incident. The individual from the CDH confirmed that the area was very isolated and the radiographer and assistant were able to maintain their distance from the source." Colorado Incident I10-13. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2010-10-22
46342 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2010-10-18 15:27 | 2010-10-18 17:00 | 2010-10-21 | SAFEGUARDS REPORT - DOCUMENT CONTROL VULNERABILITY DETECTED Document control related safeguards vulnerability detected. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM JOHN KEMPKES TO JOE O'HARA ON 10/21/10 AT 1830 EDT * * * The licensee has determined that no safeguards vulnerability existed and has retracted the event. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R3DO(Orth). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2010-10-18
46341 | 0 | ARCELORMITTAL BURNS HARBOR |  |  |  |  | 2010-10-18 07:00 | 2010-10-18 13:38 | 2010-10-18 | STUCK GAUGE SHUTTER On 10/18/10 at approximately 8:32 am, the site Radiation Safety Officer (RSO) was contacted by a radiation worker at the 80" Hot Strip Mill location, indicating that the shutter on one of the slab detection radiation gauges would not close. The worker was in the process of performing a semi-annual wipe test when the situation was noticed. The RSO directed site workers to barricade the area until he arrived. Upon arrival, the RSO conducted a survey of the area, compared the levels to a prior survey and found no significant difference in radiation levels. The RSO also performed a wipe test on the gauge and checked it with a survey meter and pancake probe, finding no detectable contamination. The radiation worker was directed to check the device counts using a survey meter and to compare them to counts on an adjacent gauge. The counts were similar, indicating proper function. A melted metallic material was noted adjacent to the gauge whose shutter would not close. The material was analyzed and it showed to be 90-95% lead. As a result, it is believed some shielding may have overheated and blocked the shutter open or debris entered the shutter arm blocking it from closing. Although radiation levels in the area are normal, the RSO will attempt to safely remove the gauge to a secure location until the device can be serviced by the manufacturer. The Cs-137 source is S/N 6326CM of a slab detection device manufactured by Ronan Engineering. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2010-10-18